## Help
Objective | This tool helps to convert measured influent data into Sumo1 model input fractions
Tabs | Use
Help | This sheet
Data | Enter measured data - estimate missing data. The tool will help to refine your estimates.
Check fractions | Estimate key organic fractions and check if your estimated BOD and COD matches the measured data
Sumo forms | Copy results to Sumo (Sumo1 Concentration based influent, Input Setup tab)
Balances | Check that COD, N, P components add up to totals
Diurnal flow | Create diurnal influent
Calculations | BOD calculations and error tolerances
Color code | Meaning
Blue | Input data
Green | Calculation result, cannot be edited
Black | Intermediate result, cannot be edited
Grey | Parameter under development, not used
Version | Sumo22
www.dynamita.com

## Data
Key measurements | Value | Unit | Key indicators for sanity check | Value | Unit | Usual value in US
Flow | 24000 | MGD or m3/d
TSS | 185 | mg/L | VSS/TSS fraction | 84.8649 | % | 85
VSS | 157 | mg/L | Particulate COD/VSS | 1.5924 | mg COD/mg VSS | 1.6
TDM | 800 | mg/L | Dissolved material | 615 | mg/L
TKN | 34.4 | mg N/L
TP | 4.3 | mgP/L
Total Sulfur | 20 | mgS/L
Alkalinity | 330 | mg CaCO3/L | Alkalinity in molar units | 6.6 | meq/L | 3 - 8
pH | 7.2 | -
COD - BOD | Value | Unit | COD - BOD indicators for sanity check | Value | Unit | Usual value in US
Influent COD | 420 | mg COD/L | Particulate COD | 250 | mg COD/L
Influent filtered COD | 170 | mg COD/L | Filtered COD fraction | 40.4762 | % | 40
Influent filtered flocculated COD | 85 | mg COD/L | Filtered flocculated COD fraction | 20.2381 | % | 20
Effluent filtered COD (inert) | 20 | mg COD/L | Unbiodegradable fraction of filtered COD | 11.7647 | % | 12 - 15
Influent cBOD5 | 200 | mg BOD/L | COD/BOD ratio | 2.1 | - | 2.2
|  |  | BOD/TSS ratio | 1.0811 | - | 1.1
Other influent measurements | Value | Unit | Other measurements indicators for sanity check | Value | Unit | Usual value in US
VFA | 20 | mg COD/L | VFA fraction of filtered COD | 11.7647 | % | 10 -20
Ammonia | 24 | mg N/L | NH4 fraction of TKN | 69.7674 | % | 65 - 75
Phosphate | 2.5 | mg P/L | PO4 fraction of TP | 58.1395 | % | 50- 60
Nitrite+nitrate | 0 | mg N/L
Calcium | 150 | mg/L
Magnesium | 15 | mg/L | Other salts expressed as H2CO3 and NaCl | 431.5 | mg/L | 100-300
Potassium | 16 | mg/L
Anions (expressed as chloride) | 300 | mg/L
Cations (expressed as Sodium) | 110 | mg/L
Note on B2: Dynamita: Enter measured data or estimate missing data
Note on B5: Dynamita: 85 - 90% of TSS
Note on B14: Dynamita: If COD is not available, use 2.2*cBOD5 in US 2.5*cBOD5 in Europe
Note on B15: Dynamita: Usually 40% of COD
Note on B16: Dynamita: Usually 60% of filtered COD
Note on B17: Dynamita: From processes where SRT>3days
Note on B18: Dynamita: If ATU or TCMP was used to inhibit nitrification, the actual cBOD may be 15-20% higher than measured.
Note on B22: Imre Takacs: Important for bio-P plants
Note on B25: Dynamita: Usually negligible
Note on B26: Dynamita: required for biomass growth
Note on B27: Dynamita: required for biomass growth

## Check fractions
Influent fractions from data | Default % | Calculated from data % | COD/BOD/TSS/VSS match | Measured data | Calculated from estimated fractions | Verdict
Fraction of filtered COD (SCCOD, 1.5 µm, incl. colloids) in total COD (TCOD) | 40.5 | 40.4762 | Influent COD | 420 | 420 | good match
Fraction of flocculated filtered (SCOD, wo colloids) COD in total COD (TCOD) | 20.2 | 20.2381 | Calculated influent filtered COD | 170 | 170 | good match
Fraction of VFA in filtered COD (SCCOD, 1.5 µm, incl. colloids) | 11.8 | 11.7647 | Calculated Influent filtered flocculated COD | 85 | 85 | good match
Fraction of soluble unbiodegradable organics (SU) in filtered COD (SCCOD, 1.5 µm, incl. colloids) | 11.8 | 11.7647 | Calculated influent BOD5 | 200 | 183.16 | good match
|  |  | TSS | 185 | 182.9056 | good match
|  |  | VSS | 157 | 155.2226 | good match
Influent fractions to estimate | Default % | To be estimated %
Fraction of particulate unbiodegradable organics (XU) in total COD (TCOD) | 14 | 14 | Balances | Balance passed
Fraction of heterotrophs (OHO) in total COD (TCOD) | 5 | 5 | COD | OK
Fraction of endogenous products (XE) of OHOs | 20 | 20 | TKN | OK
Fraction of colloidal unbiodegradable organics (CU) in colloidal COD (SCCOD-SCOD) | 20 | 20 | TP | OK
Fraction of N in readily biodegradable substrate (SB) | 4 | 4 | TSS | OK
Fraction of N in particulate unbiodegradable substrate (XU) | 1 | 1
Fraction of P in readily biodegradable substrate (SB) | 1 | 1
Fraction of P in particulate unbiodegradable substrate (XU) | 0.1 | 0.1
Particulate COD/VSS ratios by component | Default | To be estimated g COD/g VSS | Overall COD/VSS ratio | Measured | Calculated from weighted average | Verdict
COD of biomass in volatile solids | 1.42 | 1.42 | Weighted average COD/VSS | 1.5924 | 1.6432 | good match
COD of biodegradable substrate in volatile solids | 1.8 | 1.8
COD of particulate unbiodegradable organics in volatile solids | 1.3 | 1.3
COD of endogenous products in volatile solids | 1.42 | 1.42
BOD calculation | Default | To be estimated
Yield on ultimate BOD (g O2.g COD-1) | 0.95 | 0.95
Fraction of BOD5 to ultimate BOD in soluble biodegradable substrates (-) | 0.9 | 0.9
Fraction of BOD5 to ultimate BOD in colloidal biodegradable substrates (-) | 0.6 | 0.6
Fraction of BOD5 to ultimate BOD in particulate biodegradable substrates (-) | 0.5 | 0.5

## Sumo forms
Influent input setup | [5 empty] | Model setup
|  | Influent components | [5 empty] | Key parameters
| Symbol | Name | Value | SI unit | US Unit |  | Symbol | Name | Value | SI unit | US Unit
| Q | Flow rate | 24000 | m3/d | MGD |  | iCV,XB | COD of biodegradable substrate in volatile solids | 1.8 | g COD/g VSS | g COD/g VSS
| TCOD | Total COD | 420 | g COD/m3 | mg COD/L |  | iCV,XU | COD of particulate unbiodegradable organics in volatile solids | 1.3 | g COD/g VSS | g COD/g VSS
| TKN | TKN | 34.4 | g N/m3 | mg N/L |  | iCV,BIO | COD of biomass in volatile solids | 1.42 | g COD/g VSS | g COD/g VSS
| TP | Total phosphorus | 4.3 | g P/m3 | mg P/L |  | iCV,XE | COD of endogenous products in volatile solids | 1.42 | g COD/g VSS | g COD/g VSS
|  | pH and alkalinity | only if "Calculated pH" option is on |  |  |  |  | BOD stoichiometry
| Symbol | Name | Value | SI unit | US Unit |  | Symbol | Name | Value | SI unit | US Unit
| SALK,input | Alkalinity | 330 | g CaCO3/m3 | mg CaCO3/L |  | YBOD,ult | Yield on ultimate BOD | 0.95 | g O2/g DCO | g O2/g DCO
| pH | pH | 7.2 | - | - |  | fS,BOD5,BODult | Fraction of BOD5 to ultimate BOD in soluble biodegradable substrates (-) | 0.9 | - | -
[7 empty] | fC,BOD5,BODult | Fraction of BOD5 to ultimate BOD in colloidal biodegradable substrates (-) | 0.6 | - | -
|  | Influent fractions |  |  |  |  | fX,BOD5,BODult | Fraction of BOD5 to ultimate BOD in particulate biodegradable substrates (-) | 0.5 | - | -
| Symbol | Name | Value | SI unit | US Unit
| frVSS,TSS | Fraction of VSS/TSS | 84.8649 | % | %
| frSCCOD,TCOD | Fraction of filtered COD (SCCOD, 1.5 µm, incl. colloids) in total COD (TCOD) | 40.4762 | % | %
| frSCOD,TCOD | Fraction of flocculated filtered (SCOD, wo colloids) COD in total COD (TCOD) | 20.2381 | % | %
| frVFA,SCCOD | Fraction of VFA in filtered COD (SCCOD, 1.5 µm, incl. colloids) | 11.7647 | % | %
| frSU,SCCOD | Fraction of soluble unbiodegradable organics (SU) in filtered COD (SCCOD, 1.5 µm, incl. colloids) | 11.7647 | % | %
| frXU,TCOD | Fraction of particulate unbiodegradable organics (XU) in total COD (TCOD) | 14 | % | %
| frXOHO,TCOD | Fraction of heterotrophs (OHO) in total COD | 5 | % | %
| frXE,XOHO | Fraction of endogenous products (XE) of OHOs | 20 | % | %
| frCU,CCOD | Fraction of colloidal unbiodegradable organics (CU) in colloidal COD (SCCOD-SCOD) | 20 | % | %
| frSNHx,TKN | Fraction of NHx in total Kjeldahl nitrogen (TKN) | 69.7674 | % | %
| frSPO4,TP | Fraction of PO4 in total phosphorus (TP) | 58.1395 | % | %
| frN,SB | Fraction of N in readily biodegradable substrate (SB) | 4 | % | %
| frN,XU | Fraction of N in particulate unbiodegradable substrate (XU) | 1 | % | %
| frP,SB | Fraction of P in readily biodegradable substrate (SB) | 1 | % | %
| frP,XU | Fraction of P in particulate unbiodegradable substrate (XU) | 0.1 | % | %
Ionic components
| Symbol | Name | Value | SI unit | US Unit
| SCa | Calcium | 150 | g Ca.m-3 | mg Ca/L
| SMg | Magnesium | 15 | g Mg.m-3 | mg Mg/L
| SK | Potassium | 16 | g K.m-3 | mg Mg/L
| SAN | Other strong anions (as chloride) | 300 | g Cl.m-3 | mg Cl/L
| SCAT | Other strong cations (as sodium) | 110 | g Na.m-3 | mg Na/L
Influent constituents (usually zero or otherwise calculated)
| Symbol | Name | Value | SI unit | US Unit
| SO2 | Dissolved oxygen (O2) | 0 | g O2/m3 | mg O2/L
| SMEOL | Methanol (MEOL) | 0 | g COD/m3 | mg COD/L
| XPHA | Stored polyhydroxyalkanoates (PHA) | 0.1 | g COD/m3 | mg COD/L
| XGLY | Stored glycogen (GLY) | 0.1 | g COD/m3 | mg COD/L
| XE,ana | Anaerobic endogenous decay products | 0 | g COD/m3 | mg COD/L
| XCASTO | Carbon storing organisms (CASTO) | 0.1 | g COD/m3 | mg COD/L
| XMEOLO | Anoxic methanol utilizers (MEOLO) | 0.1 | g COD/m3 | mg COD/L
| XNITO | Aerobic nitrifying organisms (NITO) | 0.1 | g COD/m3 | mg COD/L
| XAMETO | Acidoclastic methanogens (AMETO) | 0.1 | g COD/m3 | mg COD/L
| XHMETO | Hydrogenotrophic methanogens (HMETO) | 0.1 | g COD/m3 | mg COD/L
| SNOx | Nitrite and nitrate (NOx) | 0 | g N/m3 | mg N/L
| SN2 | Dissolved nitrogen (N2) | 16 | g N/m3 | mg N/L
| XPP | Stored polyphosphate (PP) | 0.1 | g P/m3 | mg P/L
| SCH4 | Dissolved methane (CH4) | 0 | g COD/m3 | mg COD/L
| SH2 | Dissolved hydrogen (H2) | 0 | g COD/m3 | mg COD/L
| SFe3 | Ferric ion (Fe3) | 0 | g Fe/m3 | mg Fe/L
| SFe2 | Ferrous ion (Fe2) | 0 | g Fe/m3 | mg Fe/L
| SAl | Aluminium (Al) | 0 | g Al/m3 | mg Al/L
| XHFO,old | Aged unused hydrous ferric oxide (HFO,old) | 0.01 | g Fe/m3 | mg Fe/L
| XHFO,H,P | P-bound hydrous ferric oxide, high surface (HFO,H,P) | 0 | g Fe/m3 | mg Fe/L
| XHFO,L,P | P-bound hydrous ferric oxide, low surface (HFO,L,P) | 0 | g Fe/m3 | mg Fe/L
| XHFO,H,P,old | Aged P-bound hydrous ferric oxide, high surface (HFO,H,P,old) | 0 | g Fe/m3 | mg Fe/L
| XHFO,L,P,old | Aged P-bound hydrous ferric oxide, low surface (HFO,L,P,old) | 0 | g Fe/m3 | mg Fe/L
| XHAO,old | Aged unused hydrous aluminium oxide (HAO,old) | 0.01 | g Al/m3 | mg Al/L
| XHAO,H,P | P-bound hydrous aluminium oxide, high surface (HAO,H,P) | 0 | g Al/m3 | mg Al/L
| XHAO,L,P | P-bound hydrous aluminium oxide, low surface (HAO,L,P) | 0 | g Al/m3 | mg Al/L
| XHAO,H,P,old | Aged P-bound hydrous aluminium oxide, high surface (HAO,H,P,old) | 0 | g Al/m3 | mg Al/L
| XHAO,L,P,old | Aged P-bound hydrous aluminium oxide, low surface (HAO,L,P,old) | 0 | g Al/m3 | mg Al/L
| XCaCO3 | Calcium carbonate (CaCO3) | 0 | g TSS/m3 | mg TSS/L
| XACP | Amorphous calcium phosphate (ACP) | 0 | g TSS/m3 | mg TSS/L
| XBSH | Brushite (BSH) | 0 | g TSS/m3 | mg TSS/L
| XSTR | Struvite (STR) | 0 | g TSS/m3 | mg TSS/L
| XVivi | Vivianite (Vivi) | 0 | g TSS/m3 | mg TSS/L

## Fractionation tree
| % | Percentage distribution based on subgroups
| % | Percentage based on total
[6 empty] | Total chemical oxidation demand | [12 empty] | Total suspended solids
[6 empty] | 420 |  | mg COD/L | [10 empty] | 182.9056 |  | mg SS/L
[6 empty] | 100 |  | % | [10 empty] | 100 |  | %
[6 empty] | 100 |  | % | [10 empty] | 100 |  | %
| Particulate chemical oxidation demand | [7 empty] | Filtered chemical oxidation demand
| 250 |  |  | mg COD/L |  |  |  |  | 170 |  | mg COD/L | [5 empty] | Inorganic suspended solids |  |  |  |  | Volatile suspended solids
| 59.5238 |  |  | % |  |  |  |  | 40.4762 |  | % | [5 empty] | 27.683 |  |  | mg SS/L |  | 155.2226 |  |  | mg SS/L
| 59.5238 |  |  | % |  |  |  |  | 40.4762 |  | % | [5 empty] | 15.1351 |  |  | % |  | 84.8649 |  |  | %
[17 empty] | 8.2748 |  |  | % |  | 46.3982 |  |  | %
[8 empty] | cCOD |  |  |  | ffCOD
[8 empty] | 85 | mg COD/L |  |  | 85 | mg COD/L
[8 empty] | 50 | % |  |  | 50 | %
[8 empty] | 20.2381 | % |  |  | 20.2381 | % | [7 empty] | XB | XU | XOHO | XE | Others
[21 empty] | 91.8333 | 45.2308 | 14.7887 | 2.9577 | 0.49296 | mg SS/L
[21 empty] | 59.1624 | 29.1393 | 9.5274 | 1.9055 | 0.31758 | %
XB | XU | XOHO | XE | Others |  |  | CB | CU |  |  | SVFA | SB | SU | [7 empty] | 50.2081 | 24.729 | 8.0854 | 1.6171 | 0.26951 | %
165.3 | 58.8 | 21 | 4.2 | 0.7 | mg COD/L |  | 68 | 17 | mg COD/L |  | 20 | 45 | 20 | mg COD/L
66.12 | 23.52 | 8.4 | 1.68 | 0.28 | % |  | 80 | 20 | % |  | 23.5294 | 52.9412 | 23.5294 | %
39.3571 | 14 | 5 | 1 | 0.16667 | % |  | 16.1905 | 4.0476 | % |  | 4.7619 | 10.7143 | 4.7619 | %
[6 empty] | Total Nitrogen | [10 empty] | Total Phosphorus
[6 empty] | 34.4 |  | mgN/L | [8 empty] | 4.3 |  | mgP/L
[6 empty] | 100 |  | % | [8 empty] | 100 |  | %
[6 empty] | 100 |  | % | [8 empty] | 100 |  | %
|  |  | Total Kjeldahl Nitrogen | [5 empty] | Nitrate plus nitrite | [5 empty] | Ortho phosphate |  |  |  |  | Total organic P
|  |  | 34.4 | mgN/L |  |  |  |  | 0 | mgN/L |  |  |  |  | 2.5 | mgP/L |  |  |  | 1.8 | mgP/L
|  |  | 100 | % |  |  |  |  | 0 | % |  |  |  |  | 58.1395 | % |  |  |  | 41.8605 | %
|  |  | 100 | % |  |  |  |  | 0 | % |  |  |  |  | 58.1395 | % |  |  |  | 41.8605 | %
Total ammonia | [5 empty] | Total Organic Nitrogen | [12 empty] | Particulate organic P |  |  |  | Colloidal organic P |  |  | Soluble organic P
24 | mgN/L |  |  |  |  | 10.4 | mgN/L | [11 empty] | 1.14 | mgP/L |  |  | 0.17 | mgP/L |  | 0.49 | mgP/L
69.7674 | % |  |  |  |  | 30.2326 | % | [11 empty] | 63.3333 | % |  |  | 9.4444 | % |  | 27.2222 | %
69.7674 | % |  |  |  |  | 30.2326 | % | [11 empty] | 26.5116 | % |  |  | 3.9535 | % |  | 11.3953 | %
|  |  |  | Particulate organic N |  |  |  | Colloidal organic N |  |  | Soluble organic N
|  |  |  | 7.55 | mgN/L |  |  | 0.85 | mgN/L |  | 2 | mgN/L
|  |  |  | 72.5962 | % |  |  | 8.1731 | % |  | 19.2308 | % |  |  | P of biomass | Stored P | XP,B | XP,U |  |  | P content of CB | P content of CU |  |  | SP,B | P content of SU
|  |  |  | 21.9477 | % |  |  | 2.4709 | % |  | 5.814 | % |  |  | 0.514 | 0.1 | 0.4672 | 0.0588 | mgP/L |  | 0.136 | 0.034 | mgP/L |  | 0.45 | 0.04 | mgP/L
[15 empty] | 45.0877 | 8.7719 | 40.9825 | 5.1579 | % |  | 80 | 20 | % |  | 91.8367 | 8.1633 | %
[15 empty] | 11.9535 | 2.3256 | 10.8651 | 1.3674 | % |  | 3.1628 | 0.7907 | % |  | 10.4651 | 0.93023 | %
N of biomass | N of XE | XN,B | XN,U |  |  | N content of CB | N content of CU |  |  | SN,B | N content of SU
1.505 | 0.252 | 5.205 | 0.588 | mgN/L |  | 0.68 | 0.17 | mgN/L |  | 1.8 | 0.2 | mgN/L
14.4712 | 2.4231 | 50.0481 | 5.6538 | % |  | 6.5385 | 1.6346 | % |  | 17.3077 | 1.9231 | %
4.375 | 0.73256 | 15.1308 | 1.7093 | % |  | 1.9767 | 0.49419 | % |  | 5.2326 | 0.5814 | %

## Balances
Key components | mg COD/L | % of total | Key components N | mg N/L | % of total | Model parameters | Default | Unit
VFAs | 20 | 4.762% | Ammonia | 24 | 69.77% | N content of biomasses | 0.07 | g N.g COD-1
Readily biodegradable substrate (non-VFA) | 45 | 10.71% | N in biomass | 1.505 | 4.375% | N content of endogenous products | 0.06 | g N.g COD-1
Colloidal slowly biodegradable substrate | 68 | 16.19% | N in endogenous decay product | 0.252 | 0.7326% | N content of colloidal substrate | 0.01 | g N.g COD-1
Particulate slowly biodegradable substrate | 165.3 | 39.36% | Soluble biodegradable organic N | 1.8 | 5.233% | N content of soluble inerts | 0.01 | g N.g COD-1
Soluble unbiodegradable organics | 20 | 4.762% | Colloidal biodegradable organic N | 0.68 | 1.977% | N content of colloidal inert organics | 0.01 | g N.g COD-1
Colloidal unbiodegradable organics | 17 | 4.048% | Soluble unbiodegradable organic N | 0.2 | 0.5814% | P content of biomasses | 0.02 | g P.g COD-1
Particulate unbiodegradable organics | 58.8 | 14% | Colloidal unbiodegradable organic N | 0.17 | 0.4942% | P content of colloidal substrate | 0.002 | g P.g COD-1
Ordinary heterotrophs (OHO) | 21 | 5% | Particulate unbiodegradable organic N | 0.588 | 1.709% | P content of soluble inerts | 0.002 | g P.g COD-1
Endogenous decay products | 4.2 | 1% | Particulate biodegradable organic N | 5.205 | 15.13% | P content of colloidal inert organics | 0.002 | g P.g COD-1
|  |  | Total TKN | 34.4 | 100% | Active site factor for HFOH | 1.2 | mol P.mol Fe-1
Other components | mg COD/L | % of total |  |  |  | Active site factor for HFOL | 0.2 | mol P.mol Fe-1
Methanol | 0 | 0% |  |  |  | Fraction of H2O loss in TSS test for HFO | 0.0829 | g H2O.g Fe(OH)3-1
Carbon storing organisms (CASTO) | 0.1 | 0.02381% | Key components P | mg P/L | % of total | Active site factor for HAO,H | 1 | mol P.mol Al-1
Anoxic methanol utilizers (MEOLO) | 0.1 | 0.02381% | Phosphate | 2.5 | 58.14% | Active site factor for HAO,L | 0.1 | mol P.mol Al-1
Aerobic nitrifying organisms (NITO) | 0.1 | 0.02381% | P in biomass | 0.514 | 11.95% | Fraction of H2O loss in TSS test for HAO | 0.1135 | g H2O.g Al(OH)3-1
Acidoclastic methanogens (AMETO) | 0.1 | 0.02381% | Stored polyphosphates | 0.1 | 2.326% | TSS content of PP | 3.5161 | g XTSS.g XPP-1
Hydrogenotrophic methanogens (HMETO) | 0.1 | 0.02381% | Total phosphorus in HFOs | 0 | 0% | COD of PHA in volatile solids | 1.67 | g COD.g VS-1
Stored polyhydroxyalkanoates (PHA) | 0.1 | 0.02381% | Total phosphorus in HAOs | 0 | 0% | Atomic mass of iron | 55.845 | g.mol-1
Stored glycogen (GLY) | 0.1 | 0.02381% | Soluble biodegradable organic P | 0.45 | 10.47% | Atomic mass of aluminium | 26.9815 | g.mol-1
Anaerobic endogenous decay product | 0 | 0% | Colloidal biodegradable organic P | 0.136 | 3.163% | Atomic mass of phosphorus | 30.9738 | g.mol-1
|  |  | Soluble unbiodegradable organic P | 0.04 | 0.9302% | Molecular mass of Fe(OH)3 | 106.867 | g.mol-1
Total COD | 420 | 100% | Colloidal unbiodegradable organic P | 0.034 | 0.7907% | Molecular mass of Al(OH)3 | 78.0035 | g.mol-1
|  |  | Particulate unbiodegradable organic P | 0.0588 | 1.367% | Molecular mass of phosphate | 94.9714 | g.mol-1
Total suspended solids | mg TSS/L | % of total | Particulate biodegradable organic P | 0.4672 | 10.87%
Inorganic (fixed) suspended solids | 27.2882 | 14.92% | Total P | 4.3 | 100%
Total HFOs in TSS unit | 0.01755 | 0.009595%
Total HAOs in TSS unit | 0.025629 | 0.01401%
Total precipitates | 0 | 0%
Stored polyphosphates in TSS unit | 0.35161 | 0.1922%
Total volatile solid | 155.2226 | 84.86%
Total TSS | 182.9056 | 100%

## Diurnal flow
Hourly diurnal flow data generator
HELP
Average Q m3/d | 2400 | 24000 | 240000 | Influent flow for: | [5 empty] | Modify damping factor if needed (higher damping = bigger plant, less variation)
Size factor | 0.1 |  | 10 | [6 empty] | For one day simulation, copy-paste ONE of the blue highlighted areas to Sumo influent dynamics
Damping factor | 1 | 2 | 4 | small plant |  | medium plant |  | large plant |  | For longer diurnal simulation, use 24 hour cycletime in Sumo Input Setup/Dynamics
Average check | 1 | 1 | 1 |  | 2400 |  | 24000 |  | 240000
time | small | medium | large | time | Q | time | Q | time | Q
d | - | - | - | h | m3/d | h | m3/d | h | m3/d
0 | 0.92371 | 0.96185 | 0.98093 | 0 | 2216.9004 | 0 | 23084.5018 | 0 | 235422.5088
0.041667 | 0.79843 | 0.89921 | 0.94961 | 1 | 1916.2258 | 1 | 21581.129 | 1 | 227905.6451
0.083333 | 0.67607 | 0.83803 | 0.91902 | 2 | 1622.5639 | 2 | 20112.8194 | 2 | 220564.0968
0.125 | 0.58387 | 0.79193 | 0.89597 | 3 | 1401.2826 | 3 | 19006.413 | 3 | 215032.0652
0.16667 | 0.54484 | 0.77242 | 0.88621 | 4 | 1307.6193 | 4 | 18538.0965 | 4 | 212690.4823
0.20833 | 0.57173 | 0.78587 | 0.89293 | 5 | 1372.156 | 5 | 18860.7801 | 5 | 214303.9003
0.25 | 0.66344 | 0.83172 | 0.91586 | 6 | 1592.2514 | 6 | 19961.257 | 6 | 219806.285
0.29167 | 0.8049 | 0.90245 | 0.95122 | 7 | 1931.7499 | 7 | 21658.7497 | 7 | 228293.7486
0.33333 | 0.97046 | 0.98523 | 0.99262 | 8 | 2329.1147 | 8 | 23645.5737 | 8 | 238227.8686
0.375 | 1.13 | 1.065 | 1.0325 | 9 | 2711.9106 | 9 | 25559.5529 | 9 | 247797.7646
0.41667 | 1.2558 | 1.1279 | 1.0639 | 10 | 3013.8932 | 10 | 27069.4661 | 10 | 255347.3305
0.45833 | 1.3293 | 1.1646 | 1.0823 | 11 | 3190.284 | 11 | 27951.4198 | 11 | 259757.0988
0.5 | 1.3447 | 1.1724 | 1.0862 | 12 | 3227.3053 | 12 | 28136.5267 | 12 | 260682.6335
0.54167 | 1.3098 | 1.1549 | 1.0775 | 13 | 3143.5908 | 13 | 27717.9541 | 13 | 258589.7703
0.58333 | 1.243 | 1.1215 | 1.0608 | 14 | 2983.246 | 14 | 26916.2301 | 14 | 254581.1503
0.625 | 1.1677 | 1.0839 | 1.0419 | 15 | 2802.5536 | 15 | 26012.7682 | 15 | 250063.8408
0.66667 | 1.1058 | 1.0529 | 1.0265 | 16 | 2653.9849 | 16 | 25269.9245 | 16 | 246349.6225
0.70833 | 1.0716 | 1.0358 | 1.0179 | 17 | 2571.8636 | 17 | 24859.3181 | 17 | 244296.5903
0.75 | 1.0681 | 1.0341 | 1.017 | 18 | 2563.5429 | 18 | 24817.7145 | 18 | 244088.5726
0.79167 | 1.0868 | 1.0434 | 1.0217 | 19 | 2608.4334 | 19 | 25042.1672 | 19 | 245210.836
0.83333 | 1.1104 | 1.0552 | 1.0276 | 20 | 2665.0754 | 20 | 25325.3768 | 20 | 246626.8842
0.875 | 1.1184 | 1.0592 | 1.0296 | 21 | 2684.2532 | 21 | 25421.2659 | 21 | 247106.3294
0.91667 | 1.0935 | 1.0468 | 1.0234 | 22 | 2624.5026 | 22 | 25122.5129 | 22 | 245612.5647
0.95833 | 1.0274 | 1.0137 | 1.0068 | 23 | 2465.6964 | 23 | 24328.4821 | 23 | 241642.4105
Note on A6: Dynamita: must be 1.0000

## Birthday Cake
Crushed (16d) Birthday Cake |  | Qavg, dry | TCOD | TKN | TP | Red is input
|  | 24000 | 420 | 34.4 | 4.3 | [6 empty] | Scaling table
| time | Q | TCOD | TKN | TP |  | fQ | fConc |  |  |  |  | hr | fQ | fConc
day | h | m3/d | mg COD/L | mg N/L | mg P/L | [5 empty] | 0 | dry | 0 | 1 | 1
0 | 0 | 23084.5018 | 420 | 34.4 | 4.3 |  | 1 | 1 |  | Dry | 1 | dry | 24
0.041667 | 1 | 21581.129 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 2 | dry | 48
0.083333 | 2 | 20112.8194 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 3 | max month | 72 | 2 | 0.8
0.125 | 3 | 19006.413 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 4 | max month | 96
0.16667 | 4 | 18538.0965 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 5 | max month | 120
0.20833 | 5 | 18860.7801 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 6 | max month | 144
0.25 | 6 | 19961.257 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 7 | max month | 168
0.29167 | 7 | 21658.7497 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 8 | max day | 192 | 4 | 0.5
0.33333 | 8 | 23645.5737 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 9 | max month | 216 | 2 | 0.8
0.375 | 9 | 25559.5529 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 10 | max month | 240
0.41667 | 10 | 27069.4661 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 11 | max month | 264
0.45833 | 11 | 27951.4198 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 12 | max month | 288
0.5 | 12 | 28136.5267 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 13 | max month | 312
0.54167 | 13 | 27717.9541 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 14 | dry | 336 | 1 | 1
0.58333 | 14 | 26916.2301 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 15 | dry | 360
0.625 | 15 | 26012.7682 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 16 | dry | 384
0.66667 | 16 | 25269.9245 | 420 | 34.4 | 4.3 |  | 1 | 1 |  |  | 17 | end | 408
0.70833 | 17 | 24859.3181 | 420 | 34.4 | 4.3 |  | 1 | 1
0.75 | 18 | 24817.7145 | 420 | 34.4 | 4.3 |  | 1 | 1
0.79167 | 19 | 25042.1672 | 420 | 34.4 | 4.3 |  | 1 | 1
0.83333 | 20 | 25325.3768 | 420 | 34.4 | 4.3 |  | 1 | 1
0.875 | 21 | 25421.2659 | 420 | 34.4 | 4.3 |  | 1 | 1
0.91667 | 22 | 25122.5129 | 420 | 34.4 | 4.3 |  | 1 | 1
0.95833 | 23 | 24328.4821 | 420 | 34.4 | 4.3 |  | 1 | 1
1 | 24 | 23084.5018 | 420 | 34.4 | 4.3 |  | 1 | 1
1.0417 | 25 | 21581.129 | 420 | 34.4 | 4.3 |  | 1 | 1
1.0833 | 26 | 20112.8194 | 420 | 34.4 | 4.3 |  | 1 | 1
1.125 | 27 | 19006.413 | 420 | 34.4 | 4.3 |  | 1 | 1
1.1667 | 28 | 18538.0965 | 420 | 34.4 | 4.3 |  | 1 | 1
1.2083 | 29 | 18860.7801 | 420 | 34.4 | 4.3 |  | 1 | 1
1.25 | 30 | 19961.257 | 420 | 34.4 | 4.3 |  | 1 | 1
1.2917 | 31 | 21658.7497 | 420 | 34.4 | 4.3 |  | 1 | 1
1.3333 | 32 | 23645.5737 | 420 | 34.4 | 4.3 |  | 1 | 1
1.375 | 33 | 25559.5529 | 420 | 34.4 | 4.3 |  | 1 | 1
1.4167 | 34 | 27069.4661 | 420 | 34.4 | 4.3 |  | 1 | 1
1.4583 | 35 | 27951.4198 | 420 | 34.4 | 4.3 |  | 1 | 1
1.5 | 36 | 28136.5267 | 420 | 34.4 | 4.3 |  | 1 | 1
1.5417 | 37 | 27717.9541 | 420 | 34.4 | 4.3 |  | 1 | 1
1.5833 | 38 | 26916.2301 | 420 | 34.4 | 4.3 |  | 1 | 1
1.625 | 39 | 26012.7682 | 420 | 34.4 | 4.3 |  | 1 | 1
1.6667 | 40 | 25269.9245 | 420 | 34.4 | 4.3 |  | 1 | 1
1.7083 | 41 | 24859.3181 | 420 | 34.4 | 4.3 |  | 1 | 1
1.75 | 42 | 24817.7145 | 420 | 34.4 | 4.3 |  | 1 | 1
1.7917 | 43 | 25042.1672 | 420 | 34.4 | 4.3 |  | 1 | 1
1.8333 | 44 | 25325.3768 | 420 | 34.4 | 4.3 |  | 1 | 1
1.875 | 45 | 25421.2659 | 420 | 34.4 | 4.3 |  | 1 | 1
1.9167 | 46 | 25122.5129 | 420 | 34.4 | 4.3 |  | 1 | 1
1.9583 | 47 | 24328.4821 | 420 | 34.4 | 4.3 |  | 1 | 1
2 | 48 | 23084.5018 | 420 | 34.4 | 4.3 |  | 1 | 1
2.0417 | 49 | 21581.129 | 420 | 34.4 | 4.3 |  | 1 | 1
2.0833 | 50 | 20112.8194 | 420 | 34.4 | 4.3 |  | 1 | 1
2.125 | 51 | 19006.413 | 420 | 34.4 | 4.3 |  | 1 | 1
2.1667 | 52 | 18538.0965 | 420 | 34.4 | 4.3 |  | 1 | 1
2.2083 | 53 | 18860.7801 | 420 | 34.4 | 4.3 |  | 1 | 1
2.25 | 54 | 19961.257 | 420 | 34.4 | 4.3 |  | 1 | 1
2.2917 | 55 | 21658.7497 | 420 | 34.4 | 4.3 |  | 1 | 1
2.3333 | 56 | 23645.5737 | 420 | 34.4 | 4.3 |  | 1 | 1
2.375 | 57 | 25559.5529 | 420 | 34.4 | 4.3 |  | 1 | 1
2.4167 | 58 | 27069.4661 | 420 | 34.4 | 4.3 |  | 1 | 1
2.4583 | 59 | 27951.4198 | 420 | 34.4 | 4.3 |  | 1 | 1
2.5 | 60 | 28136.5267 | 420 | 34.4 | 4.3 |  | 1 | 1
2.5417 | 61 | 27717.9541 | 420 | 34.4 | 4.3 |  | 1 | 1
2.5833 | 62 | 26916.2301 | 420 | 34.4 | 4.3 |  | 1 | 1
2.625 | 63 | 26012.7682 | 420 | 34.4 | 4.3 |  | 1 | 1
2.6667 | 64 | 25269.9245 | 420 | 34.4 | 4.3 |  | 1 | 1
2.7083 | 65 | 24859.3181 | 420 | 34.4 | 4.3 |  | 1 | 1
2.75 | 66 | 24817.7145 | 420 | 34.4 | 4.3 |  | 1 | 1
2.7917 | 67 | 25042.1672 | 420 | 34.4 | 4.3 |  | 1 | 1
2.8333 | 68 | 25325.3768 | 420 | 34.4 | 4.3 |  | 1 | 1
2.875 | 69 | 25421.2659 | 420 | 34.4 | 4.3 |  | 1 | 1
2.9167 | 70 | 25122.5129 | 420 | 34.4 | 4.3 |  | 1 | 1
2.9583 | 71 | 24328.4821 | 420 | 34.4 | 4.3 |  | 1 | 1
3 | 72 | 46169.0035 | 336 | 27.52 | 3.44 |  | 2 | 0.8 |  | max month
3.0417 | 73 | 43162.258 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.0833 | 74 | 40225.6387 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.125 | 75 | 38012.8261 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.1667 | 76 | 37076.1929 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.2083 | 77 | 37721.5601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.25 | 78 | 39922.514 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.2917 | 79 | 43317.4994 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.3333 | 80 | 47291.1475 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.375 | 81 | 51119.1058 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.4167 | 82 | 54138.9322 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.4583 | 83 | 55902.8395 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.5 | 84 | 56273.0534 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.5417 | 85 | 55435.9081 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.5833 | 86 | 53832.4601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.625 | 87 | 52025.5363 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.6667 | 88 | 50539.849 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.7083 | 89 | 49718.6361 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.75 | 90 | 49635.4291 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.7917 | 91 | 50084.3344 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.8333 | 92 | 50650.7537 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.875 | 93 | 50842.5318 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.9167 | 94 | 50245.0259 | 336 | 27.52 | 3.44 |  | 2 | 0.8
3.9583 | 95 | 48656.9642 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4 | 96 | 46169.0035 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.0417 | 97 | 43162.258 | 336 | 27.52 | 3.44 |  | 2 | 0.8 | 0.8
4.0833 | 98 | 40225.6387 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.125 | 99 | 38012.8261 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.1667 | 100 | 37076.1929 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.2083 | 101 | 37721.5601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.25 | 102 | 39922.514 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.2917 | 103 | 43317.4994 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.3333 | 104 | 47291.1475 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.375 | 105 | 51119.1058 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.4167 | 106 | 54138.9322 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.4583 | 107 | 55902.8395 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.5 | 108 | 56273.0534 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.5417 | 109 | 55435.9081 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.5833 | 110 | 53832.4601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.625 | 111 | 52025.5363 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.6667 | 112 | 50539.849 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.7083 | 113 | 49718.6361 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.75 | 114 | 49635.4291 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.7917 | 115 | 50084.3344 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.8333 | 116 | 50650.7537 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.875 | 117 | 50842.5318 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.9167 | 118 | 50245.0259 | 336 | 27.52 | 3.44 |  | 2 | 0.8
4.9583 | 119 | 48656.9642 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5 | 120 | 46169.0035 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.0417 | 121 | 43162.258 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.0833 | 122 | 40225.6387 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.125 | 123 | 38012.8261 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.1667 | 124 | 37076.1929 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.2083 | 125 | 37721.5601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.25 | 126 | 39922.514 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.2917 | 127 | 43317.4994 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.3333 | 128 | 47291.1475 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.375 | 129 | 51119.1058 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.4167 | 130 | 54138.9322 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.4583 | 131 | 55902.8395 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.5 | 132 | 56273.0534 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.5417 | 133 | 55435.9081 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.5833 | 134 | 53832.4601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.625 | 135 | 52025.5363 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.6667 | 136 | 50539.849 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.7083 | 137 | 49718.6361 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.75 | 138 | 49635.4291 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.7917 | 139 | 50084.3344 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.8333 | 140 | 50650.7537 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.875 | 141 | 50842.5318 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.9167 | 142 | 50245.0259 | 336 | 27.52 | 3.44 |  | 2 | 0.8
5.9583 | 143 | 48656.9642 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6 | 144 | 46169.0035 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.0417 | 145 | 43162.258 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.0833 | 146 | 40225.6387 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.125 | 147 | 38012.8261 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.1667 | 148 | 37076.1929 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.2083 | 149 | 37721.5601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.25 | 150 | 39922.514 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.2917 | 151 | 43317.4994 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.3333 | 152 | 47291.1475 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.375 | 153 | 51119.1058 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.4167 | 154 | 54138.9322 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.4583 | 155 | 55902.8395 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.5 | 156 | 56273.0534 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.5417 | 157 | 55435.9081 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.5833 | 158 | 53832.4601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.625 | 159 | 52025.5363 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.6667 | 160 | 50539.849 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.7083 | 161 | 49718.6361 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.75 | 162 | 49635.4291 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.7917 | 163 | 50084.3344 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.8333 | 164 | 50650.7537 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.875 | 165 | 50842.5318 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.9167 | 166 | 50245.0259 | 336 | 27.52 | 3.44 |  | 2 | 0.8
6.9583 | 167 | 48656.9642 | 336 | 27.52 | 3.44 |  | 2 | 0.8
7 | 168 | 92338.0071 | 210 | 17.2 | 2.15 |  | 4 | 0.5 |  | max day
7.0417 | 169 | 86324.516 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.0833 | 170 | 80451.2775 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.125 | 171 | 76025.6521 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.1667 | 172 | 74152.3858 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.2083 | 173 | 75443.1202 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.25 | 174 | 79845.028 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.2917 | 175 | 86634.9989 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.3333 | 176 | 94582.2949 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.375 | 177 | 102238.2117 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.4167 | 178 | 108277.8644 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.4583 | 179 | 111805.6791 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.5 | 180 | 112546.1068 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.5417 | 181 | 110871.8163 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.5833 | 182 | 107664.9202 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.625 | 183 | 104051.0727 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.6667 | 184 | 101079.698 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.7083 | 185 | 99437.2723 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.75 | 186 | 99270.8581 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.7917 | 187 | 100168.6688 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.8333 | 188 | 101301.5074 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.875 | 189 | 101685.0635 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.9167 | 190 | 100490.0517 | 210 | 17.2 | 2.15 |  | 4 | 0.5
7.9583 | 191 | 97313.9284 | 210 | 17.2 | 2.15 |  | 4 | 0.5
8 | 192 | 46169.0035 | 336 | 27.52 | 3.44 |  | 2 | 0.8 |  | max month
8.0417 | 193 | 43162.258 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.0833 | 194 | 40225.6387 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.125 | 195 | 38012.8261 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.1667 | 196 | 37076.1929 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.2083 | 197 | 37721.5601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.25 | 198 | 39922.514 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.2917 | 199 | 43317.4994 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.3333 | 200 | 47291.1475 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.375 | 201 | 51119.1058 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.4167 | 202 | 54138.9322 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.4583 | 203 | 55902.8395 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.5 | 204 | 56273.0534 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.5417 | 205 | 55435.9081 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.5833 | 206 | 53832.4601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.625 | 207 | 52025.5363 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.6667 | 208 | 50539.849 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.7083 | 209 | 49718.6361 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.75 | 210 | 49635.4291 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.7917 | 211 | 50084.3344 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.8333 | 212 | 50650.7537 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.875 | 213 | 50842.5318 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.9167 | 214 | 50245.0259 | 336 | 27.52 | 3.44 |  | 2 | 0.8
8.9583 | 215 | 48656.9642 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9 | 216 | 46169.0035 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.0417 | 217 | 43162.258 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.0833 | 218 | 40225.6387 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.125 | 219 | 38012.8261 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.1667 | 220 | 37076.1929 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.2083 | 221 | 37721.5601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.25 | 222 | 39922.514 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.2917 | 223 | 43317.4994 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.3333 | 224 | 47291.1475 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.375 | 225 | 51119.1058 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.4167 | 226 | 54138.9322 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.4583 | 227 | 55902.8395 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.5 | 228 | 56273.0534 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.5417 | 229 | 55435.9081 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.5833 | 230 | 53832.4601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.625 | 231 | 52025.5363 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.6667 | 232 | 50539.849 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.7083 | 233 | 49718.6361 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.75 | 234 | 49635.4291 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.7917 | 235 | 50084.3344 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.8333 | 236 | 50650.7537 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.875 | 237 | 50842.5318 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.9167 | 238 | 50245.0259 | 336 | 27.52 | 3.44 |  | 2 | 0.8
9.9583 | 239 | 48656.9642 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10 | 240 | 46169.0035 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.0417 | 241 | 43162.258 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.0833 | 242 | 40225.6387 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.125 | 243 | 38012.8261 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.1667 | 244 | 37076.1929 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.2083 | 245 | 37721.5601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.25 | 246 | 39922.514 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.2917 | 247 | 43317.4994 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.3333 | 248 | 47291.1475 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.375 | 249 | 51119.1058 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.4167 | 250 | 54138.9322 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.4583 | 251 | 55902.8395 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.5 | 252 | 56273.0534 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.5417 | 253 | 55435.9081 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.5833 | 254 | 53832.4601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.625 | 255 | 52025.5363 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.6667 | 256 | 50539.849 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.7083 | 257 | 49718.6361 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.75 | 258 | 49635.4291 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.7917 | 259 | 50084.3344 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.8333 | 260 | 50650.7537 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.875 | 261 | 50842.5318 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.9167 | 262 | 50245.0259 | 336 | 27.52 | 3.44 |  | 2 | 0.8
10.9583 | 263 | 48656.9642 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11 | 264 | 46169.0035 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.0417 | 265 | 43162.258 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.0833 | 266 | 40225.6387 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.125 | 267 | 38012.8261 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.1667 | 268 | 37076.1929 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.2083 | 269 | 37721.5601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.25 | 270 | 39922.514 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.2917 | 271 | 43317.4994 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.3333 | 272 | 47291.1475 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.375 | 273 | 51119.1058 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.4167 | 274 | 54138.9322 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.4583 | 275 | 55902.8395 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.5 | 276 | 56273.0534 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.5417 | 277 | 55435.9081 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.5833 | 278 | 53832.4601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.625 | 279 | 52025.5363 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.6667 | 280 | 50539.849 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.7083 | 281 | 49718.6361 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.75 | 282 | 49635.4291 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.7917 | 283 | 50084.3344 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.8333 | 284 | 50650.7537 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.875 | 285 | 50842.5318 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.9167 | 286 | 50245.0259 | 336 | 27.52 | 3.44 |  | 2 | 0.8
11.9583 | 287 | 48656.9642 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12 | 288 | 46169.0035 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.0417 | 289 | 43162.258 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.0833 | 290 | 40225.6387 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.125 | 291 | 38012.8261 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.1667 | 292 | 37076.1929 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.2083 | 293 | 37721.5601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.25 | 294 | 39922.514 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.2917 | 295 | 43317.4994 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.3333 | 296 | 47291.1475 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.375 | 297 | 51119.1058 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.4167 | 298 | 54138.9322 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.4583 | 299 | 55902.8395 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.5 | 300 | 56273.0534 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.5417 | 301 | 55435.9081 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.5833 | 302 | 53832.4601 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.625 | 303 | 52025.5363 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.6667 | 304 | 50539.849 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.7083 | 305 | 49718.6361 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.75 | 306 | 49635.4291 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.7917 | 307 | 50084.3344 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.8333 | 308 | 50650.7537 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.875 | 309 | 50842.5318 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.9167 | 310 | 50245.0259 | 336 | 27.52 | 3.44 |  | 2 | 0.8
12.9583 | 311 | 48656.9642 | 336 | 27.52 | 3.44 |  | 2 | 0.8
13 | 312 | 23084.5018 | 420 | 34.4 | 4.3 |  | 1 | 1 |  | dry
13.0417 | 313 | 21581.129 | 420 | 34.4 | 4.3 |  | 1 | 1
13.0833 | 314 | 20112.8194 | 420 | 34.4 | 4.3 |  | 1 | 1
13.125 | 315 | 19006.413 | 420 | 34.4 | 4.3 |  | 1 | 1
13.1667 | 316 | 18538.0965 | 420 | 34.4 | 4.3 |  | 1 | 1
13.2083 | 317 | 18860.7801 | 420 | 34.4 | 4.3 |  | 1 | 1
13.25 | 318 | 19961.257 | 420 | 34.4 | 4.3 |  | 1 | 1
13.2917 | 319 | 21658.7497 | 420 | 34.4 | 4.3 |  | 1 | 1
13.3333 | 320 | 23645.5737 | 420 | 34.4 | 4.3 |  | 1 | 1
13.375 | 321 | 25559.5529 | 420 | 34.4 | 4.3 |  | 1 | 1
13.4167 | 322 | 27069.4661 | 420 | 34.4 | 4.3 |  | 1 | 1
13.4583 | 323 | 27951.4198 | 420 | 34.4 | 4.3 |  | 1 | 1
13.5 | 324 | 28136.5267 | 420 | 34.4 | 4.3 |  | 1 | 1
13.5417 | 325 | 27717.9541 | 420 | 34.4 | 4.3 |  | 1 | 1
13.5833 | 326 | 26916.2301 | 420 | 34.4 | 4.3 |  | 1 | 1
13.625 | 327 | 26012.7682 | 420 | 34.4 | 4.3 |  | 1 | 1
13.6667 | 328 | 25269.9245 | 420 | 34.4 | 4.3 |  | 1 | 1
13.7083 | 329 | 24859.3181 | 420 | 34.4 | 4.3 |  | 1 | 1
13.75 | 330 | 24817.7145 | 420 | 34.4 | 4.3 |  | 1 | 1
13.7917 | 331 | 25042.1672 | 420 | 34.4 | 4.3 |  | 1 | 1
13.8333 | 332 | 25325.3768 | 420 | 34.4 | 4.3 |  | 1 | 1
13.875 | 333 | 25421.2659 | 420 | 34.4 | 4.3 |  | 1 | 1
13.9167 | 334 | 25122.5129 | 420 | 34.4 | 4.3 |  | 1 | 1
13.9583 | 335 | 24328.4821 | 420 | 34.4 | 4.3 |  | 1 | 1
14 | 336 | 23084.5018 | 420 | 34.4 | 4.3 |  | 1 | 1
14.0417 | 337 | 21581.129 | 420 | 34.4 | 4.3 |  | 1 | 1
14.0833 | 338 | 20112.8194 | 420 | 34.4 | 4.3 |  | 1 | 1
14.125 | 339 | 19006.413 | 420 | 34.4 | 4.3 |  | 1 | 1
14.1667 | 340 | 18538.0965 | 420 | 34.4 | 4.3 |  | 1 | 1
14.2083 | 341 | 18860.7801 | 420 | 34.4 | 4.3 |  | 1 | 1
14.25 | 342 | 19961.257 | 420 | 34.4 | 4.3 |  | 1 | 1
14.2917 | 343 | 21658.7497 | 420 | 34.4 | 4.3 |  | 1 | 1
14.3333 | 344 | 23645.5737 | 420 | 34.4 | 4.3 |  | 1 | 1
14.375 | 345 | 25559.5529 | 420 | 34.4 | 4.3 |  | 1 | 1
14.4167 | 346 | 27069.4661 | 420 | 34.4 | 4.3 |  | 1 | 1
14.4583 | 347 | 27951.4198 | 420 | 34.4 | 4.3 |  | 1 | 1
14.5 | 348 | 28136.5267 | 420 | 34.4 | 4.3 |  | 1 | 1
14.5417 | 349 | 27717.9541 | 420 | 34.4 | 4.3 |  | 1 | 1
14.5833 | 350 | 26916.2301 | 420 | 34.4 | 4.3 |  | 1 | 1
14.625 | 351 | 26012.7682 | 420 | 34.4 | 4.3 |  | 1 | 1
14.6667 | 352 | 25269.9245 | 420 | 34.4 | 4.3 |  | 1 | 1
14.7083 | 353 | 24859.3181 | 420 | 34.4 | 4.3 |  | 1 | 1
14.75 | 354 | 24817.7145 | 420 | 34.4 | 4.3 |  | 1 | 1
14.7917 | 355 | 25042.1672 | 420 | 34.4 | 4.3 |  | 1 | 1
14.8333 | 356 | 25325.3768 | 420 | 34.4 | 4.3 |  | 1 | 1
14.875 | 357 | 25421.2659 | 420 | 34.4 | 4.3 |  | 1 | 1
14.9167 | 358 | 25122.5129 | 420 | 34.4 | 4.3 |  | 1 | 1
14.9583 | 359 | 24328.4821 | 420 | 34.4 | 4.3 |  | 1 | 1
15 | 360 | 23084.5018 | 420 | 34.4 | 4.3 |  | 1 | 1
15.0417 | 361 | 21581.129 | 420 | 34.4 | 4.3 |  | 1 | 1
15.0833 | 362 | 20112.8194 | 420 | 34.4 | 4.3 |  | 1 | 1
15.125 | 363 | 19006.413 | 420 | 34.4 | 4.3 |  | 1 | 1
15.1667 | 364 | 18538.0965 | 420 | 34.4 | 4.3 |  | 1 | 1
15.2083 | 365 | 18860.7801 | 420 | 34.4 | 4.3 |  | 1 | 1
15.25 | 366 | 19961.257 | 420 | 34.4 | 4.3 |  | 1 | 1
15.2917 | 367 | 21658.7497 | 420 | 34.4 | 4.3 |  | 1 | 1
15.3333 | 368 | 23645.5737 | 420 | 34.4 | 4.3 |  | 1 | 1
15.375 | 369 | 25559.5529 | 420 | 34.4 | 4.3 |  | 1 | 1
15.4167 | 370 | 27069.4661 | 420 | 34.4 | 4.3 |  | 1 | 1
15.4583 | 371 | 27951.4198 | 420 | 34.4 | 4.3 |  | 1 | 1
15.5 | 372 | 28136.5267 | 420 | 34.4 | 4.3 |  | 1 | 1
15.5417 | 373 | 27717.9541 | 420 | 34.4 | 4.3 |  | 1 | 1
15.5833 | 374 | 26916.2301 | 420 | 34.4 | 4.3 |  | 1 | 1
15.625 | 375 | 26012.7682 | 420 | 34.4 | 4.3 |  | 1 | 1
15.6667 | 376 | 25269.9245 | 420 | 34.4 | 4.3 |  | 1 | 1
15.7083 | 377 | 24859.3181 | 420 | 34.4 | 4.3 |  | 1 | 1
15.75 | 378 | 24817.7145 | 420 | 34.4 | 4.3 |  | 1 | 1
15.7917 | 379 | 25042.1672 | 420 | 34.4 | 4.3 |  | 1 | 1
15.8333 | 380 | 25325.3768 | 420 | 34.4 | 4.3 |  | 1 | 1
15.875 | 381 | 25421.2659 | 420 | 34.4 | 4.3 |  | 1 | 1
15.9167 | 382 | 25122.5129 | 420 | 34.4 | 4.3 |  | 1 | 1
15.9583 | 383 | 24328.4821 | 420 | 34.4 | 4.3 |  | 1 | 1

## Calculations
cBOD estimation | Unit | Total | Filtered | Filtered flocculated | Sumo1 components considered for COD and BOD calculations
Biodegradable COD | mg COD/L | 320 | 133 | 65 | Name | Total | Filtered | Filtered flocculated
BOD20 (Ultimate BOD) | mg O2/L | 304 | 126.35 | 61.75 | VFAs | SVFA | SVFA | SVFA
cBOD5 | mg O2/L | 183.16 | 94.335 | 55.575 | Readily biodegradable substrate (non-VFA) | SB | SB | SB
[5 empty] | Methanol | SMEOL | SMEOL | SMEOL
[5 empty] | Colloidal biodegradable substrate | CB | CB
Error tolerances | good match | so-so… | no match |  | Slowly biodegradable substrate | XB
COD | 5% |  | 15% |  | Soluble unbiodegradable organics | SU | SU | SU
BOD | 10% |  | 25% |  | Colloidal unbiodegradable organics | CU | CU
TSS&VSS | 5% |  | 15% |  | Particulate unbiodegradable organics | XU
[5 empty] | Stored PHA | XPHA
[5 empty] | Stored Glycogen | XGLY
[5 empty] | Endogenous decay products | XE
[5 empty] | Anaerobic endogenous decay products | XE,ana
[5 empty] | Ordinary heterotrophs (OHO) | XOHO
[5 empty] | Carbon storing organisms (CASTO) | XCASTO
[5 empty] | Anoxic methanol utilizers (MEOLO) | XMEOLO
[5 empty] | Aerobic nitrifying organisms (NITO) | XNITO
[5 empty] | Acidoclastic methanogens (AMETO) | XAMETO
[5 empty] | Hydrogenotrophic methanogens (HMETO) | XHMETO