## LowH2O Convectors
[5 empty] | Entering T | ºC |  |  | 75 | EWT ºF | Minimum flow rate of 0.15GPM to maintain turbulent flow.
[5 empty] | Return T | ºC |  |  | 65 | LWT ºF | Return water temperature increases in certain cases.
[5 empty] | Air T | ºC |  |  | 20 | AT ºF
[5 empty] | Mean T | ºC |  |  | 70
HEATING (if with DBE-option: fans in comfort speed)
LA/220615 | [8 empty] | 75/65/20º |  | 50/40/20º |  | 80/70/20º
Group | Model | Productcode | H in cm | L in cm | Type | D in cm | 75/65/20ºC | 167/149/68ºF | Watt | Flow in l/s | Watt | Flow in l/s | Watt | Flow in l/s | N-Waarde (EN442) | SalesGroup | JagaSourceCode Stnd
Horizontal Wall | Basic | BASW.02205010/05 | 22 | 50 | 10 | 12 | 360 | 360 | 360 | 0.0085714 | 135 | 0.0032143 | 412 | 0.0098095 | 1.418 | A17 | BASW0.02205010/05
Horizontal Wall | Basic | BASW.02205015/05 | 22 | 50 | 15 | 17 | 571 | 571 | 571 | 0.013595 | 219 | 0.0052143 | 652 | 0.015524 | 1.38 | A17 | BASW0.02205015/05
Horizontal Wall | Basic | BASW.02205020/05 | 22 | 50 | 20 | 22 | 800 | 800 | 800 | 0.019048 | 314 | 0.0074762 | 910 | 0.021667 | 1.351 | A17 | BASW0.02205020/05
Horizontal Wall | Basic | BASW.02206010/05 | 22 | 60 | 10 | 12 | 432 | 432 | 432 | 0.010286 | 162 | 0.0038571 | 495 | 0.011786 | 1.418 | A17 | BASW0.02206010/05
Horizontal Wall | Basic | BASW.02206015/05 | 22 | 60 | 15 | 17 | 685 | 685 | 685 | 0.01631 | 263 | 0.0062619 | 782 | 0.018619 | 1.38 | A17 | BASW0.02206015/05
Horizontal Wall | Basic | BASW.02206020/05 | 22 | 60 | 20 | 22 | 960 | 960 | 960 | 0.022857 | 376 | 0.0089524 | 1092 | 0.026 | 1.351 | A17 | BASW0.02206020/05
Horizontal Wall | Basic | BASW.02207010/05 | 22 | 70 | 10 | 12 | 504 | 504 | 504 | 0.012 | 188 | 0.0044762 | 577 | 0.013738 | 1.418 | A17 | BASW0.02207010/05
Horizontal Wall | Basic | BASW.02207015/05 | 22 | 70 | 15 | 17 | 799 | 799 | 799 | 0.019024 | 307 | 0.0073095 | 912 | 0.021714 | 1.38 | A17 | BASW0.02207015/05
Horizontal Wall | Basic | BASW.02207020/05 | 22 | 70 | 20 | 22 | 1120 | 1120 | 1120 | 0.026667 | 439 | 0.010452 | 1273 | 0.03031 | 1.351 | A17 | BASW0.02207020/05
Horizontal Wall | Basic | BASW.02208010/05 | 22 | 80 | 10 | 12 | 576 | 576 | 576 | 0.013714 | 215 | 0.005119 | 660 | 0.015714 | 1.418 | A17 | BASW0.02208010/05
Horizontal Wall | Basic | BASW.02208015/05 | 22 | 80 | 15 | 17 | 913 | 913 | 913 | 0.021738 | 351 | 0.0083571 | 1042 | 0.02481 | 1.38 | A17 | BASW0.02208015/05
Horizontal Wall | Basic | BASW.02208020/05 | 22 | 80 | 20 | 22 | 1280 | 1280 | 1280 | 0.030476 | 502 | 0.011952 | 1455 | 0.034643 | 1.351 | A17 | BASW0.02208020/05
Horizontal Wall | Basic | BASW.02209010/05 | 22 | 90 | 10 | 12 | 648 | 648 | 648 | 0.015429 | 242 | 0.0057619 | 742 | 0.017667 | 1.418 | A17 | BASW0.02209010/05
Horizontal Wall | Basic | BASW.02209015/05 | 22 | 90 | 15 | 17 | 1027 | 1027 | 1027 | 0.024452 | 394 | 0.009381 | 1172 | 0.027905 | 1.38 | A17 | BASW0.02209015/05
Horizontal Wall | Basic | BASW.02209020/05 | 22 | 90 | 20 | 22 | 1440 | 1440 | 1440 | 0.034286 | 564 | 0.013429 | 1637 | 0.038976 | 1.351 | A17 | BASW0.02209020/05
Horizontal Wall | Basic | BASW.02210010/05 | 22 | 100 | 10 | 12 | 720 | 720 | 720 | 0.017143 | 269 | 0.0064048 | 824 | 0.019619 | 1.418 | A17 | BASW0.02210010/05
Horizontal Wall | Basic | BASW.02210015/05 | 22 | 100 | 15 | 17 | 1141 | 1141 | 1141 | 0.027167 | 438 | 0.010429 | 1302 | 0.031 | 1.38 | A17 | BASW0.02210015/05
Horizontal Wall | Basic | BASW.02210020/05 | 22 | 100 | 20 | 22 | 1600 | 1600 | 1600 | 0.038095 | 627 | 0.014929 | 1819 | 0.04331 | 1.351 | A17 | BASW0.02210020/05
Horizontal Wall | Basic | BASW.02211010/05 | 22 | 110 | 10 | 12 | 792 | 792 | 792 | 0.018857 | 296 | 0.0070476 | 907 | 0.021595 | 1.418 | A17 | BASW0.02211010/05
Horizontal Wall | Basic | BASW.02211015/05 | 22 | 110 | 15 | 17 | 1255 | 1255 | 1255 | 0.029881 | 482 | 0.011476 | 1432 | 0.034095 | 1.38 | A17 | BASW0.02211015/05
Horizontal Wall | Basic | BASW.02211020/05 | 22 | 110 | 20 | 22 | 1760 | 1760 | 1760 | 0.041905 | 690 | 0.016429 | 2001 | 0.047643 | 1.351 | A17 | BASW0.02211020/05
Horizontal Wall | Basic | BASW.02212010/05 | 22 | 120 | 10 | 12 | 864 | 864 | 864 | 0.020571 | 323 | 0.0076905 | 989 | 0.023548 | 1.418 | A17 | BASW0.02212010/05
Horizontal Wall | Basic | BASW.02212015/05 | 22 | 120 | 15 | 17 | 1369 | 1369 | 1369 | 0.032595 | 526 | 0.012524 | 1562 | 0.03719 | 1.38 | A17 | BASW0.02212015/05
Horizontal Wall | Basic | BASW.02212020/05 | 22 | 120 | 20 | 22 | 1920 | 1920 | 1920 | 0.045714 | 753 | 0.017929 | 2183 | 0.051976 | 1.351 | A17 | BASW0.02212020/05
Horizontal Wall | Basic | BASW.02214010/05 | 22 | 140 | 10 | 12 | 1008 | 1008 | 1008 | 0.024 | 377 | 0.0089762 | 1154 | 0.027476 | 1.418 | A17 | BASW0.02214010/05
Horizontal Wall | Basic | BASW.02214015/05 | 22 | 140 | 15 | 17 | 1597 | 1597 | 1597 | 0.038024 | 613 | 0.014595 | 1822 | 0.043381 | 1.38 | A17 | BASW0.02214015/05
Horizontal Wall | Basic | BASW.02214020/05 | 22 | 140 | 20 | 22 | 2240 | 2240 | 2240 | 0.053333 | 878 | 0.020905 | 2547 | 0.060643 | 1.351 | A17 | BASW0.02214020/05
Horizontal Wall | Basic | BASW.02216010/05 | 22 | 160 | 10 | 12 | 1152 | 1152 | 1152 | 0.027429 | 431 | 0.010262 | 1319 | 0.031405 | 1.418 | A17 | BASW0.02216010/05
Horizontal Wall | Basic | BASW.02216015/05 | 22 | 160 | 15 | 17 | 1826 | 1826 | 1826 | 0.043476 | 701 | 0.01669 | 2083 | 0.049595 | 1.38 | A17 | BASW0.02216015/05
Horizontal Wall | Basic | BASW.02216020/05 | 22 | 160 | 20 | 22 | 2560 | 2560 | 2560 | 0.060952 | 1004 | 0.023905 | 2911 | 0.06931 | 1.351 | A17 | BASW0.02216020/05
Horizontal Wall | Basic | BASW.02218010/05 | 22 | 180 | 10 | 12 | 1296 | 1296 | 1296 | 0.030857 | 485 | 0.011548 | 1484 | 0.035333 | 1.418 | A17 | BASW0.02218010/05
Horizontal Wall | Basic | BASW.02218015/05 | 22 | 180 | 15 | 17 | 2054 | 2054 | 2054 | 0.048905 | 789 | 0.018786 | 2344 | 0.05581 | 1.38 | A17 | BASW0.02218015/05
Horizontal Wall | Basic | BASW.02218020/05 | 22 | 180 | 20 | 22 | 2880 | 2880 | 2880 | 0.068571 | 1129 | 0.026881 | 3275 | 0.077976 | 1.351 | A17 | BASW0.02218020/05
Horizontal Wall | Basic | BASW.02220010/05 | 22 | 200 | 10 | 12 | 1440 | 1440 | 1440 | 0.034286 | 539 | 0.012833 | 1649 | 0.039262 | 1.418 | A17 | BASW0.02220010/05
Horizontal Wall | Basic | BASW.02220015/05 | 22 | 200 | 15 | 17 | 2282 | 2282 | 2282 | 0.054333 | 876 | 0.020857 | 2604 | 0.062 | 1.38 | A17 | BASW0.02220015/05
Horizontal Wall | Basic | BASW.02220020/05 | 22 | 200 | 20 | 22 | 3200 | 3200 | 3200 | 0.07619 | 1254 | 0.029857 | 3638 | 0.086619 | 1.351 | A17 | BASW0.02220020/05
Horizontal Wall | Basic | BASW.02224010/05 | 22 | 240 | 10 | 12 | 1728 | 1728 | 1728 | 0.041143 | 646 | 0.015381 | 1979 | 0.047119 | 1.418 | A17 | BASW0.02224010/05
Horizontal Wall | Basic | BASW.02224015/05 | 22 | 240 | 15 | 17 | 2738 | 2738 | 2738 | 0.06519 | 1051 | 0.025024 | 3124 | 0.074381 | 1.38 | A17 | BASW0.02224015/05
Horizontal Wall | Basic | BASW.02224020/05 | 22 | 240 | 20 | 22 | 3840 | 3840 | 3840 | 0.091429 | 1505 | 0.035833 | 4366 | 0.10395 | 1.351 | A17 | BASW0.02224020/05
Horizontal Wall | Basic | BASW.02228010/05 | 22 | 280 | 10 | 12 | 2016 | 2016 | 2016 | 0.048 | 754 | 0.017952 | 2308 | 0.054952 | 1.418 | A17 | BASW0.02228010/05
Horizontal Wall | Basic | BASW.02228015/05 | 22 | 280 | 15 | 17 | 3195 | 3195 | 3195 | 0.076071 | 1227 | 0.029214 | 3645 | 0.086786 | 1.38 | A17 | BASW0.02228015/05
Horizontal Wall | Basic | BASW.02228020/05 | 22 | 280 | 20 | 22 | 4480 | 4480 | 4480 | 0.10667 | 1756 | 0.04181 | 5094 | 0.12129 | 1.351 | A17 | BASW0.02228020/05
Horizontal Wall | Basic | BASW.03205010/05 | 32 | 50 | 10 | 12 | 420 | 420 | 420 | 0.01 | 158 | 0.0037619 | 480 | 0.011429 | 1.407 | A17 | BASW0.03205010/05
Horizontal Wall | Basic | BASW.03205011/05 | 32 | 50 | 11 | 12 | 489 | 489 | 489 | 0.011643 | 178 | 0.0042381 | 562 | 0.013381 | 1.454 | A17 | BASW0.03205011/05
Horizontal Wall | Basic | BASW.03205015/05 | 32 | 50 | 15 | 17 | 669 | 669 | 669 | 0.015929 | 259 | 0.0061667 | 763 | 0.018167 | 1.371 | A17 | BASW0.03205015/05
Horizontal Wall | Basic | BASW.03205016/05 | 32 | 50 | 16 | 17 | 745 | 745 | 745 | 0.017738 | 270 | 0.0064286 | 857 | 0.020405 | 1.464 | A17 | BASW0.03205016/05
Horizontal Wall | Basic | BASW.03205020/05 | 32 | 50 | 20 | 22 | 933 | 933 | 933 | 0.022214 | 369 | 0.0087857 | 1060 | 0.025238 | 1.341 | A17 | BASW0.03205020/05
Horizontal Wall | Basic | BASW.03205021/05 | 32 | 50 | 21 | 22 | 1013 | 1013 | 1013 | 0.024119 | 363 | 0.0086429 | 1167 | 0.027786 | 1.482 | A17 | BASW0.03205021/05
Horizontal Wall | Basic | BASW.03206010/05 | 32 | 60 | 10 | 12 | 503 | 503 | 503 | 0.011976 | 190 | 0.0045238 | 575 | 0.01369 | 1.407 | A17 | BASW0.03206010/05
Horizontal Wall | Basic | BASW.03206011/05 | 32 | 60 | 11 | 12 | 587 | 587 | 587 | 0.013976 | 214 | 0.0050952 | 674 | 0.016048 | 1.454 | A17 | BASW0.03206011/05
Horizontal Wall | Basic | BASW.03206011/05/DBE | 32 | 60 | 11 | 12 | 887 | 887 | 887 | 0.021119 | 444 | 0.010571 | 976 | 0.023238 | 1 | A17 | BASW0.03206011/05/DBE
Horizontal Wall | Basic | BASW.03206015/05 | 32 | 60 | 15 | 17 | 803 | 803 | 803 | 0.019119 | 311 | 0.0074048 | 915 | 0.021786 | 1.371 | A17 | BASW0.03206015/05
Horizontal Wall | Basic | BASW.03206016/05 | 32 | 60 | 16 | 17 | 894 | 894 | 894 | 0.021286 | 324 | 0.0077143 | 1028 | 0.024476 | 1.464 | A17 | BASW0.03206016/05
Horizontal Wall | Basic | BASW.03206016/05/DBE | 32 | 60 | 16 | 17 | 1374 | 1374 | 1374 | 0.032714 | 687 | 0.016357 | 1511 | 0.035976 | 1 | A17 | BASW0.03206016/05/DBE
Horizontal Wall | Basic | BASW.03206020/05 | 32 | 60 | 20 | 22 | 1119 | 1119 | 1119 | 0.026643 | 442 | 0.010524 | 1271 | 0.030262 | 1.341 | A17 | BASW0.03206020/05
Horizontal Wall | Basic | BASW.03206021/05 | 32 | 60 | 21 | 22 | 1216 | 1216 | 1216 | 0.028952 | 435 | 0.010357 | 1401 | 0.033357 | 1.482 | A17 | BASW0.03206021/05
Horizontal Wall | Basic | BASW.03206021/05/DBE | 32 | 60 | 21 | 22 | 1696 | 1696 | 1696 | 0.040381 | 848 | 0.02019 | 1866 | 0.044429 | 1 | A17 | BASW0.03206021/05/DBE
Horizontal Wall | Basic | BASW.03207010/05 | 32 | 70 | 10 | 12 | 587 | 587 | 587 | 0.013976 | 221 | 0.0052619 | 672 | 0.016 | 1.407 | A17 | BASW0.03207010/05
Horizontal Wall | Basic | BASW.03207011/05 | 32 | 70 | 11 | 12 | 685 | 685 | 685 | 0.01631 | 250 | 0.0059524 | 787 | 0.018738 | 1.454 | A17 | BASW0.03207011/05
Horizontal Wall | Basic | BASW.03207011/05/DBE | 32 | 70 | 11 | 12 | 985 | 985 | 985 | 0.023452 | 493 | 0.011738 | 1084 | 0.02581 | 1 | A17 | BASW0.03207011/05/DBE
Horizontal Wall | Basic | BASW.03207015/05 | 32 | 70 | 15 | 17 | 937 | 937 | 937 | 0.02231 | 363 | 0.0086429 | 1068 | 0.025429 | 1.371 | A17 | BASW0.03207015/05
Horizontal Wall | Basic | BASW.03207016/05 | 32 | 70 | 16 | 17 | 1043 | 1043 | 1043 | 0.024833 | 378 | 0.009 | 1199 | 0.028548 | 1.464 | A17 | BASW0.03207016/05
Horizontal Wall | Basic | BASW.03207016/05/DBE | 32 | 70 | 16 | 17 | 1523 | 1523 | 1523 | 0.036262 | 762 | 0.018143 | 1675 | 0.039881 | 1 | A17 | BASW0.03207016/05/DBE
Horizontal Wall | Basic | BASW.03207020/05 | 32 | 70 | 20 | 22 | 1306 | 1306 | 1306 | 0.031095 | 516 | 0.012286 | 1484 | 0.035333 | 1.341 | A17 | BASW0.03207020/05
Horizontal Wall | Basic | BASW.03207021/05 | 32 | 70 | 21 | 22 | 1418 | 1418 | 1418 | 0.033762 | 508 | 0.012095 | 1634 | 0.038905 | 1.482 | A17 | BASW0.03207021/05
Horizontal Wall | Basic | BASW.03207021/05/DBE | 32 | 70 | 21 | 22 | 1898 | 1898 | 1898 | 0.04519 | 949 | 0.022595 | 2088 | 0.049714 | 1 | A17 | BASW0.03207021/05/DBE
Horizontal Wall | Basic | BASW.03208010/05 | 32 | 80 | 10 | 12 | 671 | 671 | 671 | 0.015976 | 253 | 0.0060238 | 768 | 0.018286 | 1.407 | A17 | BASW0.03208010/05
Horizontal Wall | Basic | BASW.03208011/05 | 32 | 80 | 11 | 12 | 782 | 782 | 782 | 0.018619 | 285 | 0.0067857 | 899 | 0.021405 | 1.454 | A17 | BASW0.03208011/05
Horizontal Wall | Basic | BASW.03208011/05/DBE | 32 | 80 | 11 | 12 | 1082 | 1082 | 1082 | 0.025762 | 541 | 0.012881 | 1190 | 0.028333 | 1 | A17 | BASW0.03208011/05/DBE
Horizontal Wall | Basic | BASW.03208015/05 | 32 | 80 | 15 | 17 | 1070 | 1070 | 1070 | 0.025476 | 414 | 0.0098571 | 1220 | 0.029048 | 1.371 | A17 | BASW0.03208015/05
Horizontal Wall | Basic | BASW.03208016/05 | 32 | 80 | 16 | 17 | 1192 | 1192 | 1192 | 0.028381 | 432 | 0.010286 | 1371 | 0.032643 | 1.464 | A17 | BASW0.03208016/05
Horizontal Wall | Basic | BASW.03208016/05/DBE | 32 | 80 | 16 | 17 | 1672 | 1672 | 1672 | 0.03981 | 836 | 0.019905 | 1839 | 0.043786 | 1 | A17 | BASW0.03208016/05/DBE
Horizontal Wall | Basic | BASW.03208020/05 | 32 | 80 | 20 | 22 | 1492 | 1492 | 1492 | 0.035524 | 589 | 0.014024 | 1695 | 0.040357 | 1.341 | A17 | BASW0.03208020/05
Horizontal Wall | Basic | BASW.03208021/05 | 32 | 80 | 21 | 22 | 1621 | 1621 | 1621 | 0.038595 | 580 | 0.01381 | 1867 | 0.044452 | 1.482 | A17 | BASW0.03208021/05
Horizontal Wall | Basic | BASW.03208021/05/DBE | 32 | 80 | 21 | 22 | 2101 | 2101 | 2101 | 0.050024 | 1051 | 0.025024 | 2311 | 0.055024 | 1 | A17 | BASW0.03208021/05/DBE
Horizontal Wall | Basic | BASW.03209010/05 | 32 | 90 | 10 | 12 | 755 | 755 | 755 | 0.017976 | 285 | 0.0067857 | 864 | 0.020571 | 1.407 | A17 | BASW0.03209010/05
Horizontal Wall | Basic | BASW.03209011/05 | 32 | 90 | 11 | 12 | 880 | 880 | 880 | 0.020952 | 321 | 0.0076429 | 1011 | 0.024071 | 1.454 | A17 | BASW0.03209011/05
Horizontal Wall | Basic | BASW.03209011/05/DBE | 32 | 90 | 11 | 12 | 1480 | 1480 | 1480 | 0.035238 | 740 | 0.017619 | 1628 | 0.038762 | 1 | A17 | BASW0.03209011/05/DBE
Horizontal Wall | Basic | BASW.03209015/05 | 32 | 90 | 15 | 17 | 1204 | 1204 | 1204 | 0.028667 | 466 | 0.011095 | 1373 | 0.03269 | 1.371 | A17 | BASW0.03209015/05
Horizontal Wall | Basic | BASW.03209016/05 | 32 | 90 | 16 | 17 | 1341 | 1341 | 1341 | 0.031929 | 485 | 0.011548 | 1542 | 0.036714 | 1.464 | A17 | BASW0.03209016/05
Horizontal Wall | Basic | BASW.03209016/05/DBE | 32 | 90 | 16 | 17 | 2301 | 2301 | 2301 | 0.054786 | 1151 | 0.027405 | 2531 | 0.060262 | 1 | A17 | BASW0.03209016/05/DBE
Horizontal Wall | Basic | BASW.03209020/05 | 32 | 90 | 20 | 22 | 1679 | 1679 | 1679 | 0.039976 | 663 | 0.015786 | 1907 | 0.045405 | 1.341 | A17 | BASW0.03209020/05
Horizontal Wall | Basic | BASW.03209021/05 | 32 | 90 | 21 | 22 | 1823 | 1823 | 1823 | 0.043405 | 653 | 0.015548 | 2100 | 0.05 | 1.482 | A17 | BASW0.03209021/05
Horizontal Wall | Basic | BASW.03209021/05/DBE | 32 | 90 | 21 | 22 | 2783 | 2783 | 2783 | 0.066262 | 1392 | 0.033143 | 3061 | 0.072881 | 1 | A17 | BASW0.03209021/05/DBE
Horizontal Wall | Basic | BASW.03210010/05 | 32 | 100 | 10 | 12 | 839 | 839 | 839 | 0.019976 | 316 | 0.0075238 | 960 | 0.022857 | 1.407 | A17 | BASW0.03210010/05
Horizontal Wall | Basic | BASW.03210011/05 | 32 | 100 | 11 | 12 | 978 | 978 | 978 | 0.023286 | 357 | 0.0085 | 1124 | 0.026762 | 1.454 | A17 | BASW0.03210011/05
Horizontal Wall | Basic | BASW.03210011/05/DBE | 32 | 100 | 11 | 12 | 1578 | 1578 | 1578 | 0.037571 | 789 | 0.018786 | 1736 | 0.041333 | 1 | A17 | BASW0.03210011/05/DBE
Horizontal Wall | Basic | BASW.03210015/05 | 32 | 100 | 15 | 17 | 1338 | 1338 | 1338 | 0.031857 | 518 | 0.012333 | 1525 | 0.03631 | 1.371 | A17 | BASW0.03210015/05
Horizontal Wall | Basic | BASW.03210016/05 | 32 | 100 | 16 | 17 | 1490 | 1490 | 1490 | 0.035476 | 539 | 0.012833 | 1714 | 0.04081 | 1.464 | A17 | BASW0.03210016/05
Horizontal Wall | Basic | BASW.03210016/05/DBE | 32 | 100 | 16 | 17 | 2450 | 2450 | 2450 | 0.058333 | 1225 | 0.029167 | 2695 | 0.064167 | 1 | A17 | BASW0.03210016/05/DBE
Horizontal Wall | Basic | BASW.03210020/05 | 32 | 100 | 20 | 22 | 1865 | 1865 | 1865 | 0.044405 | 737 | 0.017548 | 2119 | 0.050452 | 1.341 | A17 | BASW0.03210020/05
Horizontal Wall | Basic | BASW.03210021/05 | 32 | 100 | 21 | 22 | 2026 | 2026 | 2026 | 0.048238 | 725 | 0.017262 | 2334 | 0.055571 | 1.482 | A17 | BASW0.03210021/05
Horizontal Wall | Basic | BASW.03210021/05/DBE | 32 | 100 | 21 | 22 | 2986 | 2986 | 2986 | 0.071095 | 1493 | 0.035548 | 3285 | 0.078214 | 1 | A17 | BASW0.03210021/05/DBE
Horizontal Wall | Basic | BASW.03211010/05 | 32 | 110 | 10 | 12 | 923 | 923 | 923 | 0.021976 | 348 | 0.0082857 | 1056 | 0.025143 | 1.407 | A17 | BASW0.03211010/05
Horizontal Wall | Basic | BASW.03211011/05 | 32 | 110 | 11 | 12 | 1076 | 1076 | 1076 | 0.025619 | 393 | 0.0093571 | 1236 | 0.029429 | 1.454 | A17 | BASW0.03211011/05
Horizontal Wall | Basic | BASW.03211011/05/DBE | 32 | 110 | 11 | 12 | 1676 | 1676 | 1676 | 0.039905 | 838 | 0.019952 | 1844 | 0.043905 | 1 | A17 | BASW0.03211011/05/DBE
Horizontal Wall | Basic | BASW.03211015/05 | 32 | 110 | 15 | 17 | 1472 | 1472 | 1472 | 0.035048 | 570 | 0.013571 | 1678 | 0.039952 | 1.371 | A17 | BASW0.03211015/05
Horizontal Wall | Basic | BASW.03211016/05 | 32 | 110 | 16 | 17 | 1639 | 1639 | 1639 | 0.039024 | 593 | 0.014119 | 1885 | 0.044881 | 1.464 | A17 | BASW0.03211016/05
Horizontal Wall | Basic | BASW.03211016/05/DBE | 32 | 110 | 16 | 17 | 2599 | 2599 | 2599 | 0.061881 | 1300 | 0.030952 | 2859 | 0.068071 | 1 | A17 | BASW0.03211016/05/DBE
Horizontal Wall | Basic | BASW.03211020/05 | 32 | 110 | 20 | 22 | 2052 | 2052 | 2052 | 0.048857 | 811 | 0.01931 | 2331 | 0.0555 | 1.341 | A17 | BASW0.03211020/05
Horizontal Wall | Basic | BASW.03211021/05 | 32 | 110 | 21 | 22 | 2229 | 2229 | 2229 | 0.053071 | 798 | 0.019 | 2568 | 0.061143 | 1.482 | A17 | BASW0.03211021/05
Horizontal Wall | Basic | BASW.03211021/05/DBE | 32 | 110 | 21 | 22 | 3189 | 3189 | 3189 | 0.075929 | 1595 | 0.037976 | 3508 | 0.083524 | 1 | A17 | BASW0.03211021/05/DBE
Horizontal Wall | Basic | BASW.03212010/05 | 32 | 120 | 10 | 12 | 1007 | 1007 | 1007 | 0.023976 | 380 | 0.0090476 | 1152 | 0.027429 | 1.407 | A17 | BASW0.03212010/05
Horizontal Wall | Basic | BASW.03212011/05 | 32 | 120 | 11 | 12 | 1174 | 1174 | 1174 | 0.027952 | 429 | 0.010214 | 1349 | 0.032119 | 1.454 | A17 | BASW0.03212011/05
Horizontal Wall | Basic | BASW.03212011/05/DBE | 32 | 120 | 11 | 12 | 1774 | 1774 | 1774 | 0.042238 | 887 | 0.021119 | 1951 | 0.046452 | 1 | A17 | BASW0.03212011/05/DBE
Horizontal Wall | Basic | BASW.03212015/05 | 32 | 120 | 15 | 17 | 1606 | 1606 | 1606 | 0.038238 | 622 | 0.01481 | 1831 | 0.043595 | 1.371 | A17 | BASW0.03212015/05
Horizontal Wall | Basic | BASW.03212016/05 | 32 | 120 | 16 | 17 | 1788 | 1788 | 1788 | 0.042571 | 647 | 0.015405 | 2056 | 0.048952 | 1.464 | A17 | BASW0.03212016/05
Horizontal Wall | Basic | BASW.03212016/05/DBE | 32 | 120 | 16 | 17 | 2748 | 2748 | 2748 | 0.065429 | 1374 | 0.032714 | 3023 | 0.071976 | 1 | A17 | BASW0.03212016/05/DBE
Horizontal Wall | Basic | BASW.03212020/05 | 32 | 120 | 20 | 22 | 2238 | 2238 | 2238 | 0.053286 | 884 | 0.021048 | 2542 | 0.060524 | 1.341 | A17 | BASW0.03212020/05
Horizontal Wall | Basic | BASW.03212021/05 | 32 | 120 | 21 | 22 | 2431 | 2431 | 2431 | 0.057881 | 870 | 0.020714 | 2801 | 0.06669 | 1.482 | A17 | BASW0.03212021/05
Horizontal Wall | Basic | BASW.03212021/05/DBE | 32 | 120 | 21 | 22 | 3391 | 3391 | 3391 | 0.080738 | 1696 | 0.040381 | 3730 | 0.08881 | 1 | A17 | BASW0.03212021/05/DBE
Horizontal Wall | Basic | BASW.03214010/05 | 32 | 140 | 10 | 12 | 1175 | 1175 | 1175 | 0.027976 | 443 | 0.010548 | 1344 | 0.032 | 1.407 | A17 | BASW0.03214010/05
Horizontal Wall | Basic | BASW.03214011/05 | 32 | 140 | 11 | 12 | 1369 | 1369 | 1369 | 0.032595 | 500 | 0.011905 | 1573 | 0.037452 | 1.454 | A17 | BASW0.03214011/05
Horizontal Wall | Basic | BASW.03214011/05/DBE | 32 | 140 | 11 | 12 | 1969 | 1969 | 1969 | 0.046881 | 985 | 0.023452 | 2166 | 0.051571 | 1 | A17 | BASW0.03214011/05/DBE
Horizontal Wall | Basic | BASW.03214015/05 | 32 | 140 | 15 | 17 | 1873 | 1873 | 1873 | 0.044595 | 725 | 0.017262 | 2135 | 0.050833 | 1.371 | A17 | BASW0.03214015/05
Horizontal Wall | Basic | BASW.03214016/05 | 32 | 140 | 16 | 17 | 2086 | 2086 | 2086 | 0.049667 | 755 | 0.017976 | 2399 | 0.057119 | 1.464 | A17 | BASW0.03214016/05
Horizontal Wall | Basic | BASW.03214016/05/DBE | 32 | 140 | 16 | 17 | 3046 | 3046 | 3046 | 0.072524 | 1523 | 0.036262 | 3351 | 0.079786 | 1 | A17 | BASW0.03214016/05/DBE
Horizontal Wall | Basic | BASW.03214020/05 | 32 | 140 | 20 | 22 | 2611 | 2611 | 2611 | 0.062167 | 1031 | 0.024548 | 2966 | 0.070619 | 1.341 | A17 | BASW0.03214020/05
Horizontal Wall | Basic | BASW.03214021/05 | 32 | 140 | 21 | 22 | 2836 | 2836 | 2836 | 0.067524 | 1015 | 0.024167 | 3267 | 0.077786 | 1.482 | A17 | BASW0.03214021/05
Horizontal Wall | Basic | BASW.03214021/05/DBE | 32 | 140 | 21 | 22 | 3796 | 3796 | 3796 | 0.090381 | 1898 | 0.04519 | 4176 | 0.099429 | 1 | A17 | BASW0.03214021/05/DBE
Horizontal Wall | Basic | BASW.03216010/05 | 32 | 160 | 10 | 12 | 1342 | 1342 | 1342 | 0.031952 | 506 | 0.012048 | 1535 | 0.036548 | 1.407 | A17 | BASW0.03216010/05
Horizontal Wall | Basic | BASW.03216011/05 | 32 | 160 | 11 | 12 | 1565 | 1565 | 1565 | 0.037262 | 571 | 0.013595 | 1798 | 0.04281 | 1.454 | A17 | BASW0.03216011/05
Horizontal Wall | Basic | BASW.03216011/05/DBE | 32 | 160 | 11 | 12 | 2765 | 2765 | 2765 | 0.065833 | 1383 | 0.032929 | 3042 | 0.072429 | 1 | A17 | BASW0.03216011/05/DBE
Horizontal Wall | Basic | BASW.03216015/05 | 32 | 160 | 15 | 17 | 2141 | 2141 | 2141 | 0.050976 | 829 | 0.019738 | 2441 | 0.058119 | 1.371 | A17 | BASW0.03216015/05
Horizontal Wall | Basic | BASW.03216016/05 | 32 | 160 | 16 | 17 | 2384 | 2384 | 2384 | 0.056762 | 863 | 0.020548 | 2742 | 0.065286 | 1.464 | A17 | BASW0.03216016/05
Horizontal Wall | Basic | BASW.03216016/05/DBE | 32 | 160 | 16 | 17 | 4304 | 4304 | 4304 | 0.10248 | 2152 | 0.051238 | 4734 | 0.11271 | 1 | A17 | BASW0.03216016/05/DBE
Horizontal Wall | Basic | BASW.03216020/05 | 32 | 160 | 20 | 22 | 2984 | 2984 | 2984 | 0.071048 | 1179 | 0.028071 | 3390 | 0.080714 | 1.341 | A17 | BASW0.03216020/05
Horizontal Wall | Basic | BASW.03216021/05 | 32 | 160 | 21 | 22 | 3242 | 3242 | 3242 | 0.07719 | 1161 | 0.027643 | 3735 | 0.088929 | 1.482 | A17 | BASW0.03216021/05
Horizontal Wall | Basic | BASW.03216021/05/DBE | 32 | 160 | 21 | 22 | 5162 | 5162 | 5162 | 0.1229 | 2581 | 0.061452 | 5678 | 0.13519 | 1 | A17 | BASW0.03216021/05/DBE
Horizontal Wall | Basic | BASW.03218010/05 | 32 | 180 | 10 | 12 | 1510 | 1510 | 1510 | 0.035952 | 569 | 0.013548 | 1727 | 0.041119 | 1.407 | A17 | BASW0.03218010/05
Horizontal Wall | Basic | BASW.03218011/05 | 32 | 180 | 11 | 12 | 1760 | 1760 | 1760 | 0.041905 | 642 | 0.015286 | 2022 | 0.048143 | 1.454 | A17 | BASW0.03218011/05
Horizontal Wall | Basic | BASW.03218011/05/DBE | 32 | 180 | 11 | 12 | 2960 | 2960 | 2960 | 0.070476 | 1480 | 0.035238 | 3256 | 0.077524 | 1 | A17 | BASW0.03218011/05/DBE
Horizontal Wall | Basic | BASW.03218015/05 | 32 | 180 | 15 | 17 | 2408 | 2408 | 2408 | 0.057333 | 932 | 0.02219 | 2745 | 0.065357 | 1.371 | A17 | BASW0.03218015/05
Horizontal Wall | Basic | BASW.03218016/05 | 32 | 180 | 16 | 17 | 2682 | 2682 | 2682 | 0.063857 | 971 | 0.023119 | 3084 | 0.073429 | 1.464 | A17 | BASW0.03218016/05
Horizontal Wall | Basic | BASW.03218016/05/DBE | 32 | 180 | 16 | 17 | 4602 | 4602 | 4602 | 0.10957 | 2301 | 0.054786 | 5062 | 0.12052 | 1 | A17 | BASW0.03218016/05/DBE
Horizontal Wall | Basic | BASW.03218020/05 | 32 | 180 | 20 | 22 | 3357 | 3357 | 3357 | 0.079929 | 1326 | 0.031571 | 3814 | 0.09081 | 1.341 | A17 | BASW0.03218020/05
Horizontal Wall | Basic | BASW.03218021/05 | 32 | 180 | 21 | 22 | 3647 | 3647 | 3647 | 0.086833 | 1306 | 0.031095 | 4201 | 0.10002 | 1.482 | A17 | BASW0.03218021/05
Horizontal Wall | Basic | BASW.03218021/05/DBE | 32 | 180 | 21 | 22 | 5567 | 5567 | 5567 | 0.13255 | 2784 | 0.066286 | 6124 | 0.14581 | 1 | A17 | BASW0.03218021/05/DBE
Horizontal Wall | Basic | BASW.03220010/05 | 32 | 200 | 10 | 12 | 1678 | 1678 | 1678 | 0.039952 | 633 | 0.015071 | 1920 | 0.045714 | 1.407 | A17 | BASW0.03220010/05
Horizontal Wall | Basic | BASW.03220011/05 | 32 | 200 | 11 | 12 | 1956 | 1956 | 1956 | 0.046571 | 714 | 0.017 | 2247 | 0.0535 | 1.454 | A17 | BASW0.03220011/05
Horizontal Wall | Basic | BASW.03220011/05/DBE | 32 | 200 | 11 | 12 | 3156 | 3156 | 3156 | 0.075143 | 1578 | 0.037571 | 3472 | 0.082667 | 1 | A17 | BASW0.03220011/05/DBE
Horizontal Wall | Basic | BASW.03220015/05 | 32 | 200 | 15 | 17 | 2676 | 2676 | 2676 | 0.063714 | 1036 | 0.024667 | 3051 | 0.072643 | 1.371 | A17 | BASW0.03220015/05
Horizontal Wall | Basic | BASW.03220016/05 | 32 | 200 | 16 | 17 | 2980 | 2980 | 2980 | 0.070952 | 1079 | 0.02569 | 3427 | 0.081595 | 1.464 | A17 | BASW0.03220016/05
Horizontal Wall | Basic | BASW.03220016/05/DBE | 32 | 200 | 16 | 17 | 4900 | 4900 | 4900 | 0.11667 | 2450 | 0.058333 | 5390 | 0.12833 | 1 | A17 | BASW0.03220016/05/DBE
Horizontal Wall | Basic | BASW.03220020/05 | 32 | 200 | 20 | 22 | 3730 | 3730 | 3730 | 0.08881 | 1473 | 0.035071 | 4237 | 0.10088 | 1.341 | A17 | BASW0.03220020/05
Horizontal Wall | Basic | BASW.03220021/05 | 32 | 200 | 21 | 22 | 4052 | 4052 | 4052 | 0.096476 | 1451 | 0.034548 | 4668 | 0.11114 | 1.482 | A17 | BASW0.03220021/05
Horizontal Wall | Basic | BASW.03220021/05/DBE | 32 | 200 | 21 | 22 | 5972 | 5972 | 5972 | 0.14219 | 2986 | 0.071095 | 6569 | 0.1564 | 1 | A17 | BASW0.03220021/05/DBE
Horizontal Wall | Basic | BASW.03224010/05 | 32 | 240 | 10 | 12 | 2014 | 2014 | 2014 | 0.047952 | 759 | 0.018071 | 2304 | 0.054857 | 1.407 | A17 | BASW0.03224010/05
Horizontal Wall | Basic | BASW.03224011/05 | 32 | 240 | 11 | 12 | 2347 | 2347 | 2347 | 0.055881 | 857 | 0.020405 | 2697 | 0.064214 | 1.454 | A17 | BASW0.03224011/05
Horizontal Wall | Basic | BASW.03224011/05/DBE | 32 | 240 | 11 | 12 | 4147 | 4147 | 4147 | 0.098738 | 2074 | 0.049381 | 4562 | 0.10862 | 1 | A17 | BASW0.03224011/05/DBE
Horizontal Wall | Basic | BASW.03224015/05 | 32 | 240 | 15 | 17 | 3211 | 3211 | 3211 | 0.076452 | 1243 | 0.029595 | 3661 | 0.087167 | 1.371 | A17 | BASW0.03224015/05
Horizontal Wall | Basic | BASW.03224016/05 | 32 | 240 | 16 | 17 | 3576 | 3576 | 3576 | 0.085143 | 1295 | 0.030833 | 4112 | 0.097905 | 1.464 | A17 | BASW0.03224016/05
Horizontal Wall | Basic | BASW.03224016/05/DBE | 32 | 240 | 16 | 17 | 6456 | 6456 | 6456 | 0.15371 | 3228 | 0.076857 | 7102 | 0.1691 | 1 | A17 | BASW0.03224016/05/DBE
Horizontal Wall | Basic | BASW.03224020/05 | 32 | 240 | 20 | 22 | 4476 | 4476 | 4476 | 0.10657 | 1768 | 0.042095 | 5085 | 0.12107 | 1.341 | A17 | BASW0.03224020/05
Horizontal Wall | Basic | BASW.03224021/05 | 32 | 240 | 21 | 22 | 4862 | 4862 | 4862 | 0.11576 | 1741 | 0.041452 | 5601 | 0.13336 | 1.482 | A17 | BASW0.03224021/05
Horizontal Wall | Basic | BASW.03224021/05/DBE | 32 | 240 | 21 | 22 | 7742 | 7742 | 7742 | 0.18433 | 3871 | 0.092167 | 8516 | 0.20276 | 1 | A17 | BASW0.03224021/05/DBE
Horizontal Wall | Basic | BASW.03228010/05 | 32 | 280 | 10 | 12 | 2349 | 2349 | 2349 | 0.055929 | 886 | 0.021095 | 2687 | 0.063976 | 1.407 | A17 | BASW0.03228010/05
Horizontal Wall | Basic | BASW.03228011/05 | 32 | 280 | 11 | 12 | 2738 | 2738 | 2738 | 0.06519 | 999 | 0.023786 | 3146 | 0.074905 | 1.454 | A17 | BASW0.03228011/05
Horizontal Wall | Basic | BASW.03228011/05/DBE | 32 | 280 | 11 | 12 | 4538 | 4538 | 4538 | 0.10805 | 2269 | 0.054024 | 4992 | 0.11886 | 1 | A17 | BASW0.03228011/05/DBE
Horizontal Wall | Basic | BASW.03228015/05 | 32 | 280 | 15 | 17 | 3746 | 3746 | 3746 | 0.08919 | 1450 | 0.034524 | 4270 | 0.10167 | 1.371 | A17 | BASW0.03228015/05
Horizontal Wall | Basic | BASW.03228016/05 | 32 | 280 | 16 | 17 | 4172 | 4172 | 4172 | 0.099333 | 1510 | 0.035952 | 4798 | 0.11424 | 1.464 | A17 | BASW0.03228016/05
Horizontal Wall | Basic | BASW.03228016/05/DBE | 32 | 280 | 16 | 17 | 7052 | 7052 | 7052 | 0.1679 | 3526 | 0.083952 | 7757 | 0.18469 | 1 | A17 | BASW0.03228016/05/DBE
Horizontal Wall | Basic | BASW.03228020/05 | 32 | 280 | 20 | 22 | 5222 | 5222 | 5222 | 0.12433 | 2063 | 0.049119 | 5932 | 0.14124 | 1.341 | A17 | BASW0.03228020/05
Horizontal Wall | Basic | BASW.03228021/05 | 32 | 280 | 21 | 22 | 5673 | 5673 | 5673 | 0.13507 | 2031 | 0.048357 | 6535 | 0.1556 | 1.482 | A17 | BASW0.03228021/05
Horizontal Wall | Basic | BASW.03228021/05/DBE | 32 | 280 | 21 | 22 | 8553 | 8553 | 8553 | 0.20364 | 4277 | 0.10183 | 9408 | 0.224 | 1 | A17 | BASW0.03228021/05/DBE
Horizontal Wall | Basic | BASW.04205010/05 | 42 | 50 | 10 | 12 | 463 | 463 | 463 | 0.011024 | 176 | 0.0041905 | 529 | 0.012595 | 1.396 | A17 | BASW0.04205010/05
Horizontal Wall | Basic | BASW.04205011/05 | 42 | 50 | 11 | 12 | 556 | 556 | 556 | 0.013238 | 204 | 0.0048571 | 638 | 0.01519 | 1.445 | A17 | BASW0.04205011/05
Horizontal Wall | Basic | BASW.04205015/05 | 42 | 50 | 15 | 17 | 745 | 745 | 745 | 0.017738 | 290 | 0.0069048 | 849 | 0.020214 | 1.362 | A17 | BASW0.04205015/05
Horizontal Wall | Basic | BASW.04205016/05 | 42 | 50 | 16 | 17 | 854 | 854 | 854 | 0.020333 | 311 | 0.0074048 | 981 | 0.023357 | 1.457 | A17 | BASW0.04205016/05
Horizontal Wall | Basic | BASW.04205020/05 | 42 | 50 | 20 | 22 | 1030 | 1030 | 1030 | 0.024524 | 410 | 0.0097619 | 1169 | 0.027833 | 1.33 | A17 | BASW0.04205020/05
Horizontal Wall | Basic | BASW.04205021/05 | 42 | 50 | 21 | 22 | 1161 | 1161 | 1161 | 0.027643 | 418 | 0.0099524 | 1336 | 0.03181 | 1.475 | A17 | BASW0.04205021/05
Horizontal Wall | Basic | BASW.04206010/05 | 42 | 60 | 10 | 12 | 556 | 556 | 556 | 0.013238 | 211 | 0.0050238 | 635 | 0.015119 | 1.396 | A17 | BASW0.04206010/05
Horizontal Wall | Basic | BASW.04206011/05 | 42 | 60 | 11 | 12 | 667 | 667 | 667 | 0.015881 | 245 | 0.0058333 | 766 | 0.018238 | 1.445 | A17 | BASW0.04206011/05
Horizontal Wall | Basic | BASW.04206011/05/DBE | 42 | 60 | 11 | 12 | 967 | 967 | 967 | 0.023024 | 484 | 0.011524 | 1064 | 0.025333 | 1 | A17 | BASW0.04206011/05/DBE
Horizontal Wall | Basic | BASW.04206015/05 | 42 | 60 | 15 | 17 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A17 | BASW0.04206015/05
Horizontal Wall | Basic | BASW.04206016/05 | 42 | 60 | 16 | 17 | 1024 | 1024 | 1024 | 0.024381 | 373 | 0.008881 | 1177 | 0.028024 | 1.457 | A17 | BASW0.04206016/05
Horizontal Wall | Basic | BASW.04206016/05/DBE | 42 | 60 | 16 | 17 | 1504 | 1504 | 1504 | 0.03581 | 752 | 0.017905 | 1654 | 0.039381 | 1 | A17 | BASW0.04206016/05/DBE
Horizontal Wall | Basic | BASW.04206020/05 | 42 | 60 | 20 | 22 | 1236 | 1236 | 1236 | 0.029429 | 492 | 0.011714 | 1403 | 0.033405 | 1.33 | A17 | BASW0.04206020/05
Horizontal Wall | Basic | BASW.04206021/05 | 42 | 60 | 21 | 22 | 1393 | 1393 | 1393 | 0.033167 | 501 | 0.011929 | 1603 | 0.038167 | 1.475 | A17 | BASW0.04206021/05
Horizontal Wall | Basic | BASW.04206021/05/DBE | 42 | 60 | 21 | 22 | 1873 | 1873 | 1873 | 0.044595 | 937 | 0.02231 | 2060 | 0.049048 | 1 | A17 | BASW0.04206021/05/DBE
Horizontal Wall | Basic | BASW.04207010/05 | 42 | 70 | 10 | 12 | 648 | 648 | 648 | 0.015429 | 246 | 0.0058571 | 740 | 0.017619 | 1.396 | A17 | BASW0.04207010/05
Horizontal Wall | Basic | BASW.04207011/05 | 42 | 70 | 11 | 12 | 778 | 778 | 778 | 0.018524 | 286 | 0.0068095 | 893 | 0.021262 | 1.445 | A17 | BASW0.04207011/05
Horizontal Wall | Basic | BASW.04207011/05/DBE | 42 | 70 | 11 | 12 | 1078 | 1078 | 1078 | 0.025667 | 539 | 0.012833 | 1186 | 0.028238 | 1 | A17 | BASW0.04207011/05/DBE
Horizontal Wall | Basic | BASW.04207015/05 | 42 | 70 | 15 | 17 | 1042 | 1042 | 1042 | 0.02481 | 405 | 0.0096429 | 1187 | 0.028262 | 1.362 | A17 | BASW0.04207015/05
Horizontal Wall | Basic | BASW.04207016/05 | 42 | 70 | 16 | 17 | 1195 | 1195 | 1195 | 0.028452 | 435 | 0.010357 | 1373 | 0.03269 | 1.457 | A17 | BASW0.04207016/05
Horizontal Wall | Basic | BASW.04207016/05/DBE | 42 | 70 | 16 | 17 | 1675 | 1675 | 1675 | 0.039881 | 838 | 0.019952 | 1843 | 0.043881 | 1 | A17 | BASW0.04207016/05/DBE
Horizontal Wall | Basic | BASW.04207020/05 | 42 | 70 | 20 | 22 | 1442 | 1442 | 1442 | 0.034333 | 574 | 0.013667 | 1637 | 0.038976 | 1.33 | A17 | BASW0.04207020/05
Horizontal Wall | Basic | BASW.04207021/05 | 42 | 70 | 21 | 22 | 1625 | 1625 | 1625 | 0.03869 | 585 | 0.013929 | 1870 | 0.044524 | 1.475 | A17 | BASW0.04207021/05
Horizontal Wall | Basic | BASW.04207021/05/DBE | 42 | 70 | 21 | 22 | 2105 | 2105 | 2105 | 0.050119 | 1053 | 0.025071 | 2316 | 0.055143 | 1 | A17 | BASW0.04207021/05/DBE
Horizontal Wall | Basic | BASW.04208010/05 | 42 | 80 | 10 | 12 | 741 | 741 | 741 | 0.017643 | 282 | 0.0067143 | 846 | 0.020143 | 1.396 | A17 | BASW0.04208010/05
Horizontal Wall | Basic | BASW.04208011/05 | 42 | 80 | 11 | 12 | 889 | 889 | 889 | 0.021167 | 326 | 0.0077619 | 1021 | 0.02431 | 1.445 | A17 | BASW0.04208011/05
Horizontal Wall | Basic | BASW.04208011/05/DBE | 42 | 80 | 11 | 12 | 1189 | 1189 | 1189 | 0.02831 | 595 | 0.014167 | 1308 | 0.031143 | 1 | A17 | BASW0.04208011/05/DBE
Horizontal Wall | Basic | BASW.04208015/05 | 42 | 80 | 15 | 17 | 1191 | 1191 | 1191 | 0.028357 | 463 | 0.011024 | 1357 | 0.03231 | 1.362 | A17 | BASW0.04208015/05
Horizontal Wall | Basic | BASW.04208016/05 | 42 | 80 | 16 | 17 | 1366 | 1366 | 1366 | 0.032524 | 497 | 0.011833 | 1570 | 0.037381 | 1.457 | A17 | BASW0.04208016/05
Horizontal Wall | Basic | BASW.04208016/05/DBE | 42 | 80 | 16 | 17 | 1846 | 1846 | 1846 | 0.043952 | 923 | 0.021976 | 2031 | 0.048357 | 1 | A17 | BASW0.04208016/05/DBE
Horizontal Wall | Basic | BASW.04208020/05 | 42 | 80 | 20 | 22 | 1648 | 1648 | 1648 | 0.039238 | 656 | 0.015619 | 1870 | 0.044524 | 1.33 | A17 | BASW0.04208020/05
Horizontal Wall | Basic | BASW.04208021/05 | 42 | 80 | 21 | 22 | 1857 | 1857 | 1857 | 0.044214 | 669 | 0.015929 | 2137 | 0.050881 | 1.475 | A17 | BASW0.04208021/05
Horizontal Wall | Basic | BASW.04208021/05/DBE | 42 | 80 | 21 | 22 | 2337 | 2337 | 2337 | 0.055643 | 1169 | 0.027833 | 2571 | 0.061214 | 1 | A17 | BASW0.04208021/05/DBE
Horizontal Wall | Basic | BASW.04209010/05 | 42 | 90 | 10 | 12 | 833 | 833 | 833 | 0.019833 | 317 | 0.0075476 | 951 | 0.022643 | 1.396 | A17 | BASW0.04209010/05
Horizontal Wall | Basic | BASW.04209011/05 | 42 | 90 | 11 | 12 | 1000 | 1000 | 1000 | 0.02381 | 367 | 0.0087381 | 1148 | 0.027333 | 1.445 | A17 | BASW0.04209011/05
Horizontal Wall | Basic | BASW.04209011/05/DBE | 42 | 90 | 11 | 12 | 1600 | 1600 | 1600 | 0.038095 | 800 | 0.019048 | 1760 | 0.041905 | 1 | A17 | BASW0.04209011/05/DBE
Horizontal Wall | Basic | BASW.04209015/05 | 42 | 90 | 15 | 17 | 1340 | 1340 | 1340 | 0.031905 | 521 | 0.012405 | 1526 | 0.036333 | 1.362 | A17 | BASW0.04209015/05
Horizontal Wall | Basic | BASW.04209016/05 | 42 | 90 | 16 | 17 | 1536 | 1536 | 1536 | 0.036571 | 559 | 0.01331 | 1765 | 0.042024 | 1.457 | A17 | BASW0.04209016/05
Horizontal Wall | Basic | BASW.04209016/05/DBE | 42 | 90 | 16 | 17 | 2496 | 2496 | 2496 | 0.059429 | 1248 | 0.029714 | 2746 | 0.065381 | 1 | A17 | BASW0.04209016/05/DBE
Horizontal Wall | Basic | BASW.04209020/05 | 42 | 90 | 20 | 22 | 1854 | 1854 | 1854 | 0.044143 | 738 | 0.017571 | 2104 | 0.050095 | 1.33 | A17 | BASW0.04209020/05
Horizontal Wall | Basic | BASW.04209021/05 | 42 | 90 | 21 | 22 | 2089 | 2089 | 2089 | 0.049738 | 752 | 0.017905 | 2404 | 0.057238 | 1.475 | A17 | BASW0.04209021/05
Horizontal Wall | Basic | BASW.04209021/05/DBE | 42 | 90 | 21 | 22 | 3049 | 3049 | 3049 | 0.072595 | 1525 | 0.03631 | 3354 | 0.079857 | 1 | A17 | BASW0.04209021/05/DBE
Horizontal Wall | Basic | BASW.04210010/05 | 42 | 100 | 10 | 12 | 926 | 926 | 926 | 0.022048 | 352 | 0.008381 | 1057 | 0.025167 | 1.396 | A17 | BASW0.04210010/05
Horizontal Wall | Basic | BASW.04210011/05 | 42 | 100 | 11 | 12 | 1111 | 1111 | 1111 | 0.026452 | 408 | 0.0097143 | 1275 | 0.030357 | 1.445 | A17 | BASW0.04210011/05
Horizontal Wall | Basic | BASW.04210011/05/DBE | 42 | 100 | 11 | 12 | 1711 | 1711 | 1711 | 0.040738 | 856 | 0.020381 | 1882 | 0.04481 | 1 | A17 | BASW0.04210011/05/DBE
Horizontal Wall | Basic | BASW.04210015/05 | 42 | 100 | 15 | 17 | 1489 | 1489 | 1489 | 0.035452 | 579 | 0.013786 | 1696 | 0.040381 | 1.362 | A17 | BASW0.04210015/05
Horizontal Wall | Basic | BASW.04210016/05 | 42 | 100 | 16 | 17 | 1707 | 1707 | 1707 | 0.040643 | 621 | 0.014786 | 1961 | 0.04669 | 1.457 | A17 | BASW0.04210016/05
Horizontal Wall | Basic | BASW.04210016/05/DBE | 42 | 100 | 16 | 17 | 2667 | 2667 | 2667 | 0.0635 | 1334 | 0.031762 | 2934 | 0.069857 | 1 | A17 | BASW0.04210016/05/DBE
Horizontal Wall | Basic | BASW.04210020/05 | 42 | 100 | 20 | 22 | 2060 | 2060 | 2060 | 0.049048 | 820 | 0.019524 | 2338 | 0.055667 | 1.33 | A17 | BASW0.04210020/05
Horizontal Wall | Basic | BASW.04210021/05 | 42 | 100 | 21 | 22 | 2321 | 2321 | 2321 | 0.055262 | 836 | 0.019905 | 2671 | 0.063595 | 1.475 | A17 | BASW0.04210021/05
Horizontal Wall | Basic | BASW.04210021/05/DBE | 42 | 100 | 21 | 22 | 3281 | 3281 | 3281 | 0.078119 | 1641 | 0.039071 | 3609 | 0.085929 | 1 | A17 | BASW0.04210021/05/DBE
Horizontal Wall | Basic | BASW.04211010/05 | 42 | 110 | 10 | 12 | 1019 | 1019 | 1019 | 0.024262 | 387 | 0.0092143 | 1164 | 0.027714 | 1.396 | A17 | BASW0.04211010/05
Horizontal Wall | Basic | BASW.04211011/05 | 42 | 110 | 11 | 12 | 1222 | 1222 | 1222 | 0.029095 | 448 | 0.010667 | 1403 | 0.033405 | 1.445 | A17 | BASW0.04211011/05
Horizontal Wall | Basic | BASW.04211011/05/DBE | 42 | 110 | 11 | 12 | 1822 | 1822 | 1822 | 0.043381 | 911 | 0.02169 | 2004 | 0.047714 | 1 | A17 | BASW0.04211011/05/DBE
Horizontal Wall | Basic | BASW.04211015/05 | 42 | 110 | 15 | 17 | 1638 | 1638 | 1638 | 0.039 | 637 | 0.015167 | 1866 | 0.044429 | 1.362 | A17 | BASW0.04211015/05
Horizontal Wall | Basic | BASW.04211016/05 | 42 | 110 | 16 | 17 | 1878 | 1878 | 1878 | 0.044714 | 684 | 0.016286 | 2158 | 0.051381 | 1.457 | A17 | BASW0.04211016/05
Horizontal Wall | Basic | BASW.04211016/05/DBE | 42 | 110 | 16 | 17 | 2838 | 2838 | 2838 | 0.067571 | 1419 | 0.033786 | 3122 | 0.074333 | 1 | A17 | BASW0.04211016/05/DBE
Horizontal Wall | Basic | BASW.04211020/05 | 42 | 110 | 20 | 22 | 2266 | 2266 | 2266 | 0.053952 | 902 | 0.021476 | 2572 | 0.061238 | 1.33 | A17 | BASW0.04211020/05
Horizontal Wall | Basic | BASW.04211021/05 | 42 | 110 | 21 | 22 | 2553 | 2553 | 2553 | 0.060786 | 919 | 0.021881 | 2939 | 0.069976 | 1.475 | A17 | BASW0.04211021/05
Horizontal Wall | Basic | BASW.04211021/05/DBE | 42 | 110 | 21 | 22 | 3513 | 3513 | 3513 | 0.083643 | 1757 | 0.041833 | 3864 | 0.092 | 1 | A17 | BASW0.04211021/05/DBE
Horizontal Wall | Basic | BASW.04212010/05 | 42 | 120 | 10 | 12 | 1111 | 1111 | 1111 | 0.026452 | 422 | 0.010048 | 1269 | 0.030214 | 1.396 | A17 | BASW0.04212010/05
Horizontal Wall | Basic | BASW.04212011/05 | 42 | 120 | 11 | 12 | 1333 | 1333 | 1333 | 0.031738 | 489 | 0.011643 | 1530 | 0.036429 | 1.445 | A17 | BASW0.04212011/05
Horizontal Wall | Basic | BASW.04212011/05/DBE | 42 | 120 | 11 | 12 | 1933 | 1933 | 1933 | 0.046024 | 967 | 0.023024 | 2126 | 0.050619 | 1 | A17 | BASW0.04212011/05/DBE
Horizontal Wall | Basic | BASW.04212015/05 | 42 | 120 | 15 | 17 | 1787 | 1787 | 1787 | 0.042548 | 695 | 0.016548 | 2035 | 0.048452 | 1.362 | A17 | BASW0.04212015/05
Horizontal Wall | Basic | BASW.04212016/05 | 42 | 120 | 16 | 17 | 2048 | 2048 | 2048 | 0.048762 | 745 | 0.017738 | 2353 | 0.056024 | 1.457 | A17 | BASW0.04212016/05
Horizontal Wall | Basic | BASW.04212016/05/DBE | 42 | 120 | 16 | 17 | 3008 | 3008 | 3008 | 0.071619 | 1504 | 0.03581 | 3309 | 0.078786 | 1 | A17 | BASW0.04212016/05/DBE
Horizontal Wall | Basic | BASW.04212020/05 | 42 | 120 | 20 | 22 | 2472 | 2472 | 2472 | 0.058857 | 984 | 0.023429 | 2806 | 0.06681 | 1.33 | A17 | BASW0.04212020/05
Horizontal Wall | Basic | BASW.04212021/05 | 42 | 120 | 21 | 22 | 2785 | 2785 | 2785 | 0.06631 | 1003 | 0.023881 | 3206 | 0.076333 | 1.475 | A17 | BASW0.04212021/05
Horizontal Wall | Basic | BASW.04212021/05/DBE | 42 | 120 | 21 | 22 | 3745 | 3745 | 3745 | 0.089167 | 1873 | 0.044595 | 4120 | 0.098095 | 1 | A17 | BASW0.04212021/05/DBE
Horizontal Wall | Basic | BASW.04214010/05 | 42 | 140 | 10 | 12 | 1296 | 1296 | 1296 | 0.030857 | 492 | 0.011714 | 1480 | 0.035238 | 1.396 | A17 | BASW0.04214010/05
Horizontal Wall | Basic | BASW.04214011/05 | 42 | 140 | 11 | 12 | 1555 | 1555 | 1555 | 0.037024 | 571 | 0.013595 | 1785 | 0.0425 | 1.445 | A17 | BASW0.04214011/05
Horizontal Wall | Basic | BASW.04214011/05/DBE | 42 | 140 | 11 | 12 | 2155 | 2155 | 2155 | 0.05131 | 1078 | 0.025667 | 2371 | 0.056452 | 1 | A17 | BASW0.04214011/05/DBE
Horizontal Wall | Basic | BASW.04214015/05 | 42 | 140 | 15 | 17 | 2085 | 2085 | 2085 | 0.049643 | 811 | 0.01931 | 2375 | 0.056548 | 1.362 | A17 | BASW0.04214015/05
Horizontal Wall | Basic | BASW.04214016/05 | 42 | 140 | 16 | 17 | 2390 | 2390 | 2390 | 0.056905 | 870 | 0.020714 | 2746 | 0.065381 | 1.457 | A17 | BASW0.04214016/05
Horizontal Wall | Basic | BASW.04214016/05/DBE | 42 | 140 | 16 | 17 | 3350 | 3350 | 3350 | 0.079762 | 1675 | 0.039881 | 3685 | 0.087738 | 1 | A17 | BASW0.04214016/05/DBE
Horizontal Wall | Basic | BASW.04214020/05 | 42 | 140 | 20 | 22 | 2884 | 2884 | 2884 | 0.068667 | 1148 | 0.027333 | 3273 | 0.077929 | 1.33 | A17 | BASW0.04214020/05
Horizontal Wall | Basic | BASW.04214021/05 | 42 | 140 | 21 | 22 | 3249 | 3249 | 3249 | 0.077357 | 1170 | 0.027857 | 3740 | 0.089048 | 1.475 | A17 | BASW0.04214021/05
Horizontal Wall | Basic | BASW.04214021/05/DBE | 42 | 140 | 21 | 22 | 4209 | 4209 | 4209 | 0.10021 | 2105 | 0.050119 | 4630 | 0.11024 | 1 | A17 | BASW0.04214021/05/DBE
Horizontal Wall | Basic | BASW.04216010/05 | 42 | 160 | 10 | 12 | 1482 | 1482 | 1482 | 0.035286 | 563 | 0.013405 | 1692 | 0.040286 | 1.396 | A17 | BASW0.04216010/05
Horizontal Wall | Basic | BASW.04216011/05 | 42 | 160 | 11 | 12 | 1778 | 1778 | 1778 | 0.042333 | 653 | 0.015548 | 2041 | 0.048595 | 1.445 | A17 | BASW0.04216011/05
Horizontal Wall | Basic | BASW.04216011/05/DBE | 42 | 160 | 11 | 12 | 2978 | 2978 | 2978 | 0.070905 | 1489 | 0.035452 | 3276 | 0.078 | 1 | A17 | BASW0.04216011/05/DBE
Horizontal Wall | Basic | BASW.04216015/05 | 42 | 160 | 15 | 17 | 2382 | 2382 | 2382 | 0.056714 | 927 | 0.022071 | 2713 | 0.064595 | 1.362 | A17 | BASW0.04216015/05
Horizontal Wall | Basic | BASW.04216016/05 | 42 | 160 | 16 | 17 | 2731 | 2731 | 2731 | 0.065024 | 994 | 0.023667 | 3138 | 0.074714 | 1.457 | A17 | BASW0.04216016/05
Horizontal Wall | Basic | BASW.04216016/05/DBE | 42 | 160 | 16 | 17 | 4651 | 4651 | 4651 | 0.11074 | 2326 | 0.055381 | 5116 | 0.12181 | 1 | A17 | BASW0.04216016/05/DBE
Horizontal Wall | Basic | BASW.04216020/05 | 42 | 160 | 20 | 22 | 3296 | 3296 | 3296 | 0.078476 | 1312 | 0.031238 | 3741 | 0.089071 | 1.33 | A17 | BASW0.04216020/05
Horizontal Wall | Basic | BASW.04216021/05 | 42 | 160 | 21 | 22 | 3714 | 3714 | 3714 | 0.088429 | 1337 | 0.031833 | 4275 | 0.10179 | 1.475 | A17 | BASW0.04216021/05
Horizontal Wall | Basic | BASW.04216021/05/DBE | 42 | 160 | 21 | 22 | 5634 | 5634 | 5634 | 0.13414 | 2817 | 0.067071 | 6197 | 0.14755 | 1 | A17 | BASW0.04216021/05/DBE
Horizontal Wall | Basic | BASW.04218010/05 | 42 | 180 | 10 | 12 | 1667 | 1667 | 1667 | 0.03969 | 633 | 0.015071 | 1904 | 0.045333 | 1.396 | A17 | BASW0.04218010/05
Horizontal Wall | Basic | BASW.04218011/05 | 42 | 180 | 11 | 12 | 2000 | 2000 | 2000 | 0.047619 | 734 | 0.017476 | 2296 | 0.054667 | 1.445 | A17 | BASW0.04218011/05
Horizontal Wall | Basic | BASW.04218011/05/DBE | 42 | 180 | 11 | 12 | 3200 | 3200 | 3200 | 0.07619 | 1600 | 0.038095 | 3520 | 0.08381 | 1 | A17 | BASW0.04218011/05/DBE
Horizontal Wall | Basic | BASW.04218015/05 | 42 | 180 | 15 | 17 | 2680 | 2680 | 2680 | 0.06381 | 1043 | 0.024833 | 3053 | 0.07269 | 1.362 | A17 | BASW0.04218015/05
Horizontal Wall | Basic | BASW.04218016/05 | 42 | 180 | 16 | 17 | 3073 | 3073 | 3073 | 0.073167 | 1119 | 0.026643 | 3531 | 0.084071 | 1.457 | A17 | BASW0.04218016/05
Horizontal Wall | Basic | BASW.04218016/05/DBE | 42 | 180 | 16 | 17 | 4993 | 4993 | 4993 | 0.11888 | 2497 | 0.059452 | 5492 | 0.13076 | 1 | A17 | BASW0.04218016/05/DBE
Horizontal Wall | Basic | BASW.04218020/05 | 42 | 180 | 20 | 22 | 3708 | 3708 | 3708 | 0.088286 | 1476 | 0.035143 | 4209 | 0.10021 | 1.33 | A17 | BASW0.04218020/05
Horizontal Wall | Basic | BASW.04218021/05 | 42 | 180 | 21 | 22 | 4178 | 4178 | 4178 | 0.099476 | 1504 | 0.03581 | 4809 | 0.1145 | 1.475 | A17 | BASW0.04218021/05
Horizontal Wall | Basic | BASW.04218021/05/DBE | 42 | 180 | 21 | 22 | 6098 | 6098 | 6098 | 0.14519 | 3049 | 0.072595 | 6708 | 0.15971 | 1 | A17 | BASW0.04218021/05/DBE
Horizontal Wall | Basic | BASW.04220010/05 | 42 | 200 | 10 | 12 | 1852 | 1852 | 1852 | 0.044095 | 704 | 0.016762 | 2115 | 0.050357 | 1.396 | A17 | BASW0.04220010/05
Horizontal Wall | Basic | BASW.04220011/05 | 42 | 200 | 11 | 12 | 2222 | 2222 | 2222 | 0.052905 | 815 | 0.019405 | 2551 | 0.060738 | 1.445 | A17 | BASW0.04220011/05
Horizontal Wall | Basic | BASW.04220011/05/DBE | 42 | 200 | 11 | 12 | 3422 | 3422 | 3422 | 0.081476 | 1711 | 0.040738 | 3764 | 0.089619 | 1 | A17 | BASW0.04220011/05/DBE
Horizontal Wall | Basic | BASW.04220015/05 | 42 | 200 | 15 | 17 | 2978 | 2978 | 2978 | 0.070905 | 1158 | 0.027571 | 3392 | 0.080762 | 1.362 | A17 | BASW0.04220015/05
Horizontal Wall | Basic | BASW.04220016/05 | 42 | 200 | 16 | 17 | 3414 | 3414 | 3414 | 0.081286 | 1243 | 0.029595 | 3923 | 0.093405 | 1.457 | A17 | BASW0.04220016/05
Horizontal Wall | Basic | BASW.04220016/05/DBE | 42 | 200 | 16 | 17 | 5334 | 5334 | 5334 | 0.127 | 2667 | 0.0635 | 5867 | 0.13969 | 1 | A17 | BASW0.04220016/05/DBE
Horizontal Wall | Basic | BASW.04220020/05 | 42 | 200 | 20 | 22 | 4120 | 4120 | 4120 | 0.098095 | 1640 | 0.039048 | 4676 | 0.11133 | 1.33 | A17 | BASW0.04220020/05
Horizontal Wall | Basic | BASW.04220021/05 | 42 | 200 | 21 | 22 | 4642 | 4642 | 4642 | 0.11052 | 1671 | 0.039786 | 5343 | 0.12721 | 1.475 | A17 | BASW0.04220021/05
Horizontal Wall | Basic | BASW.04220021/05/DBE | 42 | 200 | 21 | 22 | 6562 | 6562 | 6562 | 0.15624 | 3281 | 0.078119 | 7218 | 0.17186 | 1 | A17 | BASW0.04220021/05/DBE
Horizontal Wall | Basic | BASW.04224010/05 | 42 | 240 | 10 | 12 | 2222 | 2222 | 2222 | 0.052905 | 844 | 0.020095 | 2538 | 0.060429 | 1.396 | A17 | BASW0.04224010/05
Horizontal Wall | Basic | BASW.04224011/05 | 42 | 240 | 11 | 12 | 2666 | 2666 | 2666 | 0.063476 | 978 | 0.023286 | 3061 | 0.072881 | 1.445 | A17 | BASW0.04224011/05
Horizontal Wall | Basic | BASW.04224011/05/DBE | 42 | 240 | 11 | 12 | 4466 | 4466 | 4466 | 0.10633 | 2233 | 0.053167 | 4913 | 0.11698 | 1 | A17 | BASW0.04224011/05/DBE
Horizontal Wall | Basic | BASW.04224015/05 | 42 | 240 | 15 | 17 | 3574 | 3574 | 3574 | 0.085095 | 1390 | 0.033095 | 4071 | 0.096929 | 1.362 | A17 | BASW0.04224015/05
Horizontal Wall | Basic | BASW.04224016/05 | 42 | 240 | 16 | 17 | 4097 | 4097 | 4097 | 0.097548 | 1491 | 0.0355 | 4707 | 0.11207 | 1.457 | A17 | BASW0.04224016/05
Horizontal Wall | Basic | BASW.04224016/05/DBE | 42 | 240 | 16 | 17 | 6977 | 6977 | 6977 | 0.16612 | 3489 | 0.083071 | 7675 | 0.18274 | 1 | A17 | BASW0.04224016/05/DBE
Horizontal Wall | Basic | BASW.04224020/05 | 42 | 240 | 20 | 22 | 4944 | 4944 | 4944 | 0.11771 | 1968 | 0.046857 | 5611 | 0.1336 | 1.33 | A17 | BASW0.04224020/05
Horizontal Wall | Basic | BASW.04224021/05 | 42 | 240 | 21 | 22 | 5570 | 5570 | 5570 | 0.13262 | 2005 | 0.047738 | 6411 | 0.15264 | 1.475 | A17 | BASW0.04224021/05
Horizontal Wall | Basic | BASW.04224021/05/DBE | 42 | 240 | 21 | 22 | 8450 | 8450 | 8450 | 0.20119 | 4225 | 0.1006 | 9295 | 0.22131 | 1 | A17 | BASW0.04224021/05/DBE
Horizontal Wall | Basic | BASW.04228010/05 | 42 | 280 | 10 | 12 | 2593 | 2593 | 2593 | 0.061738 | 985 | 0.023452 | 2961 | 0.0705 | 1.396 | A17 | BASW0.04228010/05
Horizontal Wall | Basic | BASW.04228011/05 | 42 | 280 | 11 | 12 | 3111 | 3111 | 3111 | 0.074071 | 1142 | 0.02719 | 3571 | 0.085024 | 1.445 | A17 | BASW0.04228011/05
Horizontal Wall | Basic | BASW.04228011/05/DBE | 42 | 280 | 11 | 12 | 4911 | 4911 | 4911 | 0.11693 | 2456 | 0.058476 | 5402 | 0.12862 | 1 | A17 | BASW0.04228011/05/DBE
Horizontal Wall | Basic | BASW.04228015/05 | 42 | 280 | 15 | 17 | 4169 | 4169 | 4169 | 0.099262 | 1622 | 0.038619 | 4748 | 0.11305 | 1.362 | A17 | BASW0.04228015/05
Horizontal Wall | Basic | BASW.04228016/05 | 42 | 280 | 16 | 17 | 4780 | 4780 | 4780 | 0.11381 | 1740 | 0.041429 | 5492 | 0.13076 | 1.457 | A17 | BASW0.04228016/05
Horizontal Wall | Basic | BASW.04228016/05/DBE | 42 | 280 | 16 | 17 | 7660 | 7660 | 7660 | 0.18238 | 3830 | 0.09119 | 8426 | 0.20062 | 1 | A17 | BASW0.04228016/05/DBE
Horizontal Wall | Basic | BASW.04228020/05 | 42 | 280 | 20 | 22 | 5768 | 5768 | 5768 | 0.13733 | 2296 | 0.054667 | 6547 | 0.15588 | 1.33 | A17 | BASW0.04228020/05
Horizontal Wall | Basic | BASW.04228021/05 | 42 | 280 | 21 | 22 | 6499 | 6499 | 6499 | 0.15474 | 2340 | 0.055714 | 7480 | 0.1781 | 1.475 | A17 | BASW0.04228021/05
Horizontal Wall | Basic | BASW.04228021/05/DBE | 42 | 280 | 21 | 22 | 9379 | 9379 | 9379 | 0.22331 | 4690 | 0.11167 | 10317 | 0.24564 | 1 | A17 | BASW0.04228021/05/DBE
Horizontal Wall | Basic | BASW.05205010/05 | 52 | 50 | 10 | 12 | 496 | 496 | 496 | 0.01181 | 190 | 0.0045238 | 566 | 0.013476 | 1.385 | A17 | BASW0.05205010/05
Horizontal Wall | Basic | BASW.05205011/05 | 52 | 50 | 11 | 12 | 609 | 609 | 609 | 0.0145 | 225 | 0.0053571 | 699 | 0.016643 | 1.435 | A17 | BASW0.05205011/05
Horizontal Wall | Basic | BASW.05205015/05 | 52 | 50 | 15 | 17 | 804 | 804 | 804 | 0.019143 | 314 | 0.0074762 | 915 | 0.021786 | 1.354 | A17 | BASW0.05205015/05
Horizontal Wall | Basic | BASW.05205016/05 | 52 | 50 | 16 | 17 | 944 | 944 | 944 | 0.022476 | 346 | 0.0082381 | 1084 | 0.02581 | 1.45 | A17 | BASW0.05205016/05
Horizontal Wall | Basic | BASW.05205020/05 | 52 | 50 | 20 | 22 | 1104 | 1104 | 1104 | 0.026286 | 443 | 0.010548 | 1252 | 0.02981 | 1.319 | A17 | BASW0.05205020/05
Horizontal Wall | Basic | BASW.05205021/05 | 52 | 50 | 21 | 22 | 1284 | 1284 | 1284 | 0.030571 | 464 | 0.011048 | 1477 | 0.035167 | 1.469 | A17 | BASW0.05205021/05
Horizontal Wall | Basic | BASW.05206010/05 | 52 | 60 | 10 | 12 | 595 | 595 | 595 | 0.014167 | 228 | 0.0054286 | 679 | 0.016167 | 1.385 | A17 | BASW0.05206010/05
Horizontal Wall | Basic | BASW.05206011/05 | 52 | 60 | 11 | 12 | 731 | 731 | 731 | 0.017405 | 270 | 0.0064286 | 838 | 0.019952 | 1.435 | A17 | BASW0.05206011/05
Horizontal Wall | Basic | BASW.05206011/05/DBE | 52 | 60 | 11 | 12 | 1031 | 1031 | 1031 | 0.024548 | 516 | 0.012286 | 1134 | 0.027 | 1 | A17 | BASW0.05206011/05/DBE
Horizontal Wall | Basic | BASW.05206015/05 | 52 | 60 | 15 | 17 | 964 | 964 | 964 | 0.022952 | 377 | 0.0089762 | 1097 | 0.026119 | 1.354 | A17 | BASW0.05206015/05
Horizontal Wall | Basic | BASW.05206016/05 | 52 | 60 | 16 | 17 | 1132 | 1132 | 1132 | 0.026952 | 414 | 0.0098571 | 1300 | 0.030952 | 1.45 | A17 | BASW0.05206016/05
Horizontal Wall | Basic | BASW.05206016/05/DBE | 52 | 60 | 16 | 17 | 1612 | 1612 | 1612 | 0.038381 | 806 | 0.01919 | 1773 | 0.042214 | 1 | A17 | BASW0.05206016/05/DBE
Horizontal Wall | Basic | BASW.05206020/05 | 52 | 60 | 20 | 22 | 1324 | 1324 | 1324 | 0.031524 | 531 | 0.012643 | 1501 | 0.035738 | 1.319 | A17 | BASW0.05206020/05
Horizontal Wall | Basic | BASW.05206021/05 | 52 | 60 | 21 | 22 | 1541 | 1541 | 1541 | 0.03669 | 556 | 0.013238 | 1772 | 0.04219 | 1.469 | A17 | BASW0.05206021/05
Horizontal Wall | Basic | BASW.05206021/05/DBE | 52 | 60 | 21 | 22 | 2021 | 2021 | 2021 | 0.048119 | 1011 | 0.024071 | 2223 | 0.052929 | 1 | A17 | BASW0.05206021/05/DBE
Horizontal Wall | Basic | BASW.05207010/05 | 52 | 70 | 10 | 12 | 694 | 694 | 694 | 0.016524 | 266 | 0.0063333 | 792 | 0.018857 | 1.385 | A17 | BASW0.05207010/05
Horizontal Wall | Basic | BASW.05207011/05 | 52 | 70 | 11 | 12 | 853 | 853 | 853 | 0.02031 | 316 | 0.0075238 | 978 | 0.023286 | 1.435 | A17 | BASW0.05207011/05
Horizontal Wall | Basic | BASW.05207011/05/DBE | 52 | 70 | 11 | 12 | 1153 | 1153 | 1153 | 0.027452 | 577 | 0.013738 | 1268 | 0.03019 | 1 | A17 | BASW0.05207011/05/DBE
Horizontal Wall | Basic | BASW.05207015/05 | 52 | 70 | 15 | 17 | 1125 | 1125 | 1125 | 0.026786 | 440 | 0.010476 | 1280 | 0.030476 | 1.354 | A17 | BASW0.05207015/05
Horizontal Wall | Basic | BASW.05207016/05 | 52 | 70 | 16 | 17 | 1321 | 1321 | 1321 | 0.031452 | 483 | 0.0115 | 1517 | 0.036119 | 1.45 | A17 | BASW0.05207016/05
Horizontal Wall | Basic | BASW.05207016/05/DBE | 52 | 70 | 16 | 17 | 1801 | 1801 | 1801 | 0.042881 | 901 | 0.021452 | 1981 | 0.047167 | 1 | A17 | BASW0.05207016/05/DBE
Horizontal Wall | Basic | BASW.05207020/05 | 52 | 70 | 20 | 22 | 1545 | 1545 | 1545 | 0.036786 | 620 | 0.014762 | 1752 | 0.041714 | 1.319 | A17 | BASW0.05207020/05
Horizontal Wall | Basic | BASW.05207021/05 | 52 | 70 | 21 | 22 | 1798 | 1798 | 1798 | 0.04281 | 649 | 0.015452 | 2068 | 0.049238 | 1.469 | A17 | BASW0.05207021/05
Horizontal Wall | Basic | BASW.05207021/05/DBE | 52 | 70 | 21 | 22 | 2278 | 2278 | 2278 | 0.054238 | 1139 | 0.027119 | 2506 | 0.059667 | 1 | A17 | BASW0.05207021/05/DBE
Horizontal Wall | Basic | BASW.05208010/05 | 52 | 80 | 10 | 12 | 794 | 794 | 794 | 0.018905 | 304 | 0.0072381 | 906 | 0.021571 | 1.385 | A17 | BASW0.05208010/05
Horizontal Wall | Basic | BASW.05208011/05 | 52 | 80 | 11 | 12 | 974 | 974 | 974 | 0.02319 | 360 | 0.0085714 | 1117 | 0.026595 | 1.435 | A17 | BASW0.05208011/05
Horizontal Wall | Basic | BASW.05208011/05/DBE | 52 | 80 | 11 | 12 | 1274 | 1274 | 1274 | 0.030333 | 637 | 0.015167 | 1401 | 0.033357 | 1 | A17 | BASW0.05208011/05/DBE
Horizontal Wall | Basic | BASW.05208015/05 | 52 | 80 | 15 | 17 | 1286 | 1286 | 1286 | 0.030619 | 503 | 0.011976 | 1463 | 0.034833 | 1.354 | A17 | BASW0.05208015/05
Horizontal Wall | Basic | BASW.05208016/05 | 52 | 80 | 16 | 17 | 1510 | 1510 | 1510 | 0.035952 | 553 | 0.013167 | 1733 | 0.041262 | 1.45 | A17 | BASW0.05208016/05
Horizontal Wall | Basic | BASW.05208016/05/DBE | 52 | 80 | 16 | 17 | 1990 | 1990 | 1990 | 0.047381 | 995 | 0.02369 | 2189 | 0.052119 | 1 | A17 | BASW0.05208016/05/DBE
Horizontal Wall | Basic | BASW.05208020/05 | 52 | 80 | 20 | 22 | 1766 | 1766 | 1766 | 0.042048 | 708 | 0.016857 | 2003 | 0.04769 | 1.319 | A17 | BASW0.05208020/05
Horizontal Wall | Basic | BASW.05208021/05 | 52 | 80 | 21 | 22 | 2054 | 2054 | 2054 | 0.048905 | 741 | 0.017643 | 2362 | 0.056238 | 1.469 | A17 | BASW0.05208021/05
Horizontal Wall | Basic | BASW.05208021/05/DBE | 52 | 80 | 21 | 22 | 2534 | 2534 | 2534 | 0.060333 | 1267 | 0.030167 | 2787 | 0.066357 | 1 | A17 | BASW0.05208021/05/DBE
Horizontal Wall | Basic | BASW.05209010/05 | 52 | 90 | 10 | 12 | 893 | 893 | 893 | 0.021262 | 342 | 0.0081429 | 1019 | 0.024262 | 1.385 | A17 | BASW0.05209010/05
Horizontal Wall | Basic | BASW.05209011/05 | 52 | 90 | 11 | 12 | 1096 | 1096 | 1096 | 0.026095 | 406 | 0.0096667 | 1257 | 0.029929 | 1.435 | A17 | BASW0.05209011/05
Horizontal Wall | Basic | BASW.05209011/05/DBE | 52 | 90 | 11 | 12 | 1696 | 1696 | 1696 | 0.040381 | 848 | 0.02019 | 1866 | 0.044429 | 1 | A17 | BASW0.05209011/05/DBE
Horizontal Wall | Basic | BASW.05209015/05 | 52 | 90 | 15 | 17 | 1446 | 1446 | 1446 | 0.034429 | 565 | 0.013452 | 1646 | 0.03919 | 1.354 | A17 | BASW0.05209015/05
Horizontal Wall | Basic | BASW.05209016/05 | 52 | 90 | 16 | 17 | 1698 | 1698 | 1698 | 0.040429 | 621 | 0.014786 | 1949 | 0.046405 | 1.45 | A17 | BASW0.05209016/05
Horizontal Wall | Basic | BASW.05209016/05/DBE | 52 | 90 | 16 | 17 | 2658 | 2658 | 2658 | 0.063286 | 1329 | 0.031643 | 2924 | 0.069619 | 1 | A17 | BASW0.05209016/05/DBE
Horizontal Wall | Basic | BASW.05209020/05 | 52 | 90 | 20 | 22 | 1986 | 1986 | 1986 | 0.047286 | 796 | 0.018952 | 2252 | 0.053619 | 1.319 | A17 | BASW0.05209020/05
Horizontal Wall | Basic | BASW.05209021/05 | 52 | 90 | 21 | 22 | 2311 | 2311 | 2311 | 0.055024 | 834 | 0.019857 | 2658 | 0.063286 | 1.469 | A17 | BASW0.05209021/05
Horizontal Wall | Basic | BASW.05209021/05/DBE | 52 | 90 | 21 | 22 | 3271 | 3271 | 3271 | 0.077881 | 1636 | 0.038952 | 3598 | 0.085667 | 1 | A17 | BASW0.05209021/05/DBE
Horizontal Wall | Basic | BASW.05210010/05 | 52 | 100 | 10 | 12 | 992 | 992 | 992 | 0.023619 | 380 | 0.0090476 | 1132 | 0.026952 | 1.385 | A17 | BASW0.05210010/05
Horizontal Wall | Basic | BASW.05210011/05 | 52 | 100 | 11 | 12 | 1218 | 1218 | 1218 | 0.029 | 451 | 0.010738 | 1397 | 0.033262 | 1.435 | A17 | BASW0.05210011/05
Horizontal Wall | Basic | BASW.05210011/05/DBE | 52 | 100 | 11 | 12 | 1818 | 1818 | 1818 | 0.043286 | 909 | 0.021643 | 2000 | 0.047619 | 1 | A17 | BASW0.05210011/05/DBE
Horizontal Wall | Basic | BASW.05210015/05 | 52 | 100 | 15 | 17 | 1607 | 1607 | 1607 | 0.038262 | 628 | 0.014952 | 1829 | 0.043548 | 1.354 | A17 | BASW0.05210015/05
Horizontal Wall | Basic | BASW.05210016/05 | 52 | 100 | 16 | 17 | 1887 | 1887 | 1887 | 0.044929 | 691 | 0.016452 | 2166 | 0.051571 | 1.45 | A17 | BASW0.05210016/05
Horizontal Wall | Basic | BASW.05210016/05/DBE | 52 | 100 | 16 | 17 | 2847 | 2847 | 2847 | 0.067786 | 1424 | 0.033905 | 3132 | 0.074571 | 1 | A17 | BASW0.05210016/05/DBE
Horizontal Wall | Basic | BASW.05210020/05 | 52 | 100 | 20 | 22 | 2207 | 2207 | 2207 | 0.052548 | 885 | 0.021071 | 2503 | 0.059595 | 1.319 | A17 | BASW0.05210020/05
Horizontal Wall | Basic | BASW.05210021/05 | 52 | 100 | 21 | 22 | 2568 | 2568 | 2568 | 0.061143 | 927 | 0.022071 | 2953 | 0.07031 | 1.469 | A17 | BASW0.05210021/05
Horizontal Wall | Basic | BASW.05210021/05/DBE | 52 | 100 | 21 | 22 | 3528 | 3528 | 3528 | 0.084 | 1764 | 0.042 | 3881 | 0.092405 | 1 | A17 | BASW0.05210021/05/DBE
Horizontal Wall | Basic | BASW.05211010/05 | 52 | 110 | 10 | 12 | 1091 | 1091 | 1091 | 0.025976 | 418 | 0.0099524 | 1245 | 0.029643 | 1.385 | A17 | BASW0.05211010/05
Horizontal Wall | Basic | BASW.05211011/05 | 52 | 110 | 11 | 12 | 1340 | 1340 | 1340 | 0.031905 | 496 | 0.01181 | 1537 | 0.036595 | 1.435 | A17 | BASW0.05211011/05
Horizontal Wall | Basic | BASW.05211011/05/DBE | 52 | 110 | 11 | 12 | 1940 | 1940 | 1940 | 0.04619 | 970 | 0.023095 | 2134 | 0.05081 | 1 | A17 | BASW0.05211011/05/DBE
Horizontal Wall | Basic | BASW.05211015/05 | 52 | 110 | 15 | 17 | 1768 | 1768 | 1768 | 0.042095 | 691 | 0.016452 | 2012 | 0.047905 | 1.354 | A17 | BASW0.05211015/05
Horizontal Wall | Basic | BASW.05211016/05 | 52 | 110 | 16 | 17 | 2076 | 2076 | 2076 | 0.049429 | 760 | 0.018095 | 2383 | 0.056738 | 1.45 | A17 | BASW0.05211016/05
Horizontal Wall | Basic | BASW.05211016/05/DBE | 52 | 110 | 16 | 17 | 3036 | 3036 | 3036 | 0.072286 | 1518 | 0.036143 | 3340 | 0.079524 | 1 | A17 | BASW0.05211016/05/DBE
Horizontal Wall | Basic | BASW.05211020/05 | 52 | 110 | 20 | 22 | 2428 | 2428 | 2428 | 0.05781 | 974 | 0.02319 | 2753 | 0.065548 | 1.319 | A17 | BASW0.05211020/05
Horizontal Wall | Basic | BASW.05211021/05 | 52 | 110 | 21 | 22 | 2825 | 2825 | 2825 | 0.067262 | 1020 | 0.024286 | 3249 | 0.077357 | 1.469 | A17 | BASW0.05211021/05
Horizontal Wall | Basic | BASW.05211021/05/DBE | 52 | 110 | 21 | 22 | 3785 | 3785 | 3785 | 0.090119 | 1893 | 0.045071 | 4164 | 0.099143 | 1 | A17 | BASW0.05211021/05/DBE
Horizontal Wall | Basic | BASW.05212010/05 | 52 | 120 | 10 | 12 | 1190 | 1190 | 1190 | 0.028333 | 456 | 0.010857 | 1358 | 0.032333 | 1.385 | A17 | BASW0.05212010/05
Horizontal Wall | Basic | BASW.05212011/05 | 52 | 120 | 11 | 12 | 1462 | 1462 | 1462 | 0.03481 | 541 | 0.012881 | 1677 | 0.039929 | 1.435 | A17 | BASW0.05212011/05
Horizontal Wall | Basic | BASW.05212011/05/DBE | 52 | 120 | 11 | 12 | 2062 | 2062 | 2062 | 0.049095 | 1031 | 0.024548 | 2268 | 0.054 | 1 | A17 | BASW0.05212011/05/DBE
Horizontal Wall | Basic | BASW.05212015/05 | 52 | 120 | 15 | 17 | 1928 | 1928 | 1928 | 0.045905 | 754 | 0.017952 | 2194 | 0.052238 | 1.354 | A17 | BASW0.05212015/05
Horizontal Wall | Basic | BASW.05212016/05 | 52 | 120 | 16 | 17 | 2264 | 2264 | 2264 | 0.053905 | 829 | 0.019738 | 2599 | 0.061881 | 1.45 | A17 | BASW0.05212016/05
Horizontal Wall | Basic | BASW.05212016/05/DBE | 52 | 120 | 16 | 17 | 3224 | 3224 | 3224 | 0.076762 | 1612 | 0.038381 | 3546 | 0.084429 | 1 | A17 | BASW0.05212016/05/DBE
Horizontal Wall | Basic | BASW.05212020/05 | 52 | 120 | 20 | 22 | 2648 | 2648 | 2648 | 0.063048 | 1062 | 0.025286 | 3003 | 0.0715 | 1.319 | A17 | BASW0.05212020/05
Horizontal Wall | Basic | BASW.05212021/05 | 52 | 120 | 21 | 22 | 3082 | 3082 | 3082 | 0.073381 | 1113 | 0.0265 | 3544 | 0.084381 | 1.469 | A17 | BASW0.05212021/05
Horizontal Wall | Basic | BASW.05212021/05/DBE | 52 | 120 | 21 | 22 | 4042 | 4042 | 4042 | 0.096238 | 2021 | 0.048119 | 4446 | 0.10586 | 1 | A17 | BASW0.05212021/05/DBE
Horizontal Wall | Basic | BASW.05214010/05 | 52 | 140 | 10 | 12 | 1389 | 1389 | 1389 | 0.033071 | 532 | 0.012667 | 1585 | 0.037738 | 1.385 | A17 | BASW0.05214010/05
Horizontal Wall | Basic | BASW.05214011/05 | 52 | 140 | 11 | 12 | 1705 | 1705 | 1705 | 0.040595 | 631 | 0.015024 | 1956 | 0.046571 | 1.435 | A17 | BASW0.05214011/05
Horizontal Wall | Basic | BASW.05214011/05/DBE | 52 | 140 | 11 | 12 | 2305 | 2305 | 2305 | 0.054881 | 1153 | 0.027452 | 2536 | 0.060381 | 1 | A17 | BASW0.05214011/05/DBE
Horizontal Wall | Basic | BASW.05214015/05 | 52 | 140 | 15 | 17 | 2250 | 2250 | 2250 | 0.053571 | 880 | 0.020952 | 2561 | 0.060976 | 1.354 | A17 | BASW0.05214015/05
Horizontal Wall | Basic | BASW.05214016/05 | 52 | 140 | 16 | 17 | 2642 | 2642 | 2642 | 0.062905 | 967 | 0.023024 | 3033 | 0.072214 | 1.45 | A17 | BASW0.05214016/05
Horizontal Wall | Basic | BASW.05214016/05/DBE | 52 | 140 | 16 | 17 | 3602 | 3602 | 3602 | 0.085762 | 1801 | 0.042881 | 3962 | 0.094333 | 1 | A17 | BASW0.05214016/05/DBE
Horizontal Wall | Basic | BASW.05214020/05 | 52 | 140 | 20 | 22 | 3090 | 3090 | 3090 | 0.073571 | 1239 | 0.0295 | 3504 | 0.083429 | 1.319 | A17 | BASW0.05214020/05
Horizontal Wall | Basic | BASW.05214021/05 | 52 | 140 | 21 | 22 | 3595 | 3595 | 3595 | 0.085595 | 1298 | 0.030905 | 4134 | 0.098429 | 1.469 | A17 | BASW0.05214021/05
Horizontal Wall | Basic | BASW.05214021/05/DBE | 52 | 140 | 21 | 22 | 4555 | 4555 | 4555 | 0.10845 | 2278 | 0.054238 | 5011 | 0.11931 | 1 | A17 | BASW0.05214021/05/DBE
Horizontal Wall | Basic | BASW.05216010/05 | 52 | 160 | 10 | 12 | 1587 | 1587 | 1587 | 0.037786 | 608 | 0.014476 | 1811 | 0.043119 | 1.385 | A17 | BASW0.05216010/05
Horizontal Wall | Basic | BASW.05216011/05 | 52 | 160 | 11 | 12 | 1949 | 1949 | 1949 | 0.046405 | 721 | 0.017167 | 2236 | 0.053238 | 1.435 | A17 | BASW0.05216011/05
Horizontal Wall | Basic | BASW.05216011/05/DBE | 52 | 160 | 11 | 12 | 3149 | 3149 | 3149 | 0.074976 | 1575 | 0.0375 | 3464 | 0.082476 | 1 | A17 | BASW0.05216011/05/DBE
Horizontal Wall | Basic | BASW.05216015/05 | 52 | 160 | 15 | 17 | 2571 | 2571 | 2571 | 0.061214 | 1005 | 0.023929 | 2926 | 0.069667 | 1.354 | A17 | BASW0.05216015/05
Horizontal Wall | Basic | BASW.05216016/05 | 52 | 160 | 16 | 17 | 3019 | 3019 | 3019 | 0.071881 | 1105 | 0.02631 | 3466 | 0.082524 | 1.45 | A17 | BASW0.05216016/05
Horizontal Wall | Basic | BASW.05216016/05/DBE | 52 | 160 | 16 | 17 | 4939 | 4939 | 4939 | 0.1176 | 2470 | 0.05881 | 5433 | 0.12936 | 1 | A17 | BASW0.05216016/05/DBE
Horizontal Wall | Basic | BASW.05216020/05 | 52 | 160 | 20 | 22 | 3531 | 3531 | 3531 | 0.084071 | 1416 | 0.033714 | 4004 | 0.095333 | 1.319 | A17 | BASW0.05216020/05
Horizontal Wall | Basic | BASW.05216021/05 | 52 | 160 | 21 | 22 | 4109 | 4109 | 4109 | 0.097833 | 1483 | 0.03531 | 4725 | 0.1125 | 1.469 | A17 | BASW0.05216021/05
Horizontal Wall | Basic | BASW.05216021/05/DBE | 52 | 160 | 21 | 22 | 6029 | 6029 | 6029 | 0.14355 | 3015 | 0.071786 | 6632 | 0.1579 | 1 | A17 | BASW0.05216021/05/DBE
Horizontal Wall | Basic | BASW.05218010/05 | 52 | 180 | 10 | 12 | 1786 | 1786 | 1786 | 0.042524 | 684 | 0.016286 | 2038 | 0.048524 | 1.385 | A17 | BASW0.05218010/05
Horizontal Wall | Basic | BASW.05218011/05 | 52 | 180 | 11 | 12 | 2192 | 2192 | 2192 | 0.05219 | 811 | 0.01931 | 2514 | 0.059857 | 1.435 | A17 | BASW0.05218011/05
Horizontal Wall | Basic | BASW.05218011/05/DBE | 52 | 180 | 11 | 12 | 3392 | 3392 | 3392 | 0.080762 | 1696 | 0.040381 | 3731 | 0.088833 | 1 | A17 | BASW0.05218011/05/DBE
Horizontal Wall | Basic | BASW.05218015/05 | 52 | 180 | 15 | 17 | 2893 | 2893 | 2893 | 0.068881 | 1131 | 0.026929 | 3292 | 0.078381 | 1.354 | A17 | BASW0.05218015/05
Horizontal Wall | Basic | BASW.05218016/05 | 52 | 180 | 16 | 17 | 3397 | 3397 | 3397 | 0.080881 | 1243 | 0.029595 | 3900 | 0.092857 | 1.45 | A17 | BASW0.05218016/05
Horizontal Wall | Basic | BASW.05218016/05/DBE | 52 | 180 | 16 | 17 | 5317 | 5317 | 5317 | 0.1266 | 2659 | 0.06331 | 5849 | 0.13926 | 1 | A17 | BASW0.05218016/05/DBE
Horizontal Wall | Basic | BASW.05218020/05 | 52 | 180 | 20 | 22 | 3973 | 3973 | 3973 | 0.094595 | 1593 | 0.037929 | 4505 | 0.10726 | 1.319 | A17 | BASW0.05218020/05
Horizontal Wall | Basic | BASW.05218021/05 | 52 | 180 | 21 | 22 | 4622 | 4622 | 4622 | 0.11005 | 1669 | 0.039738 | 5315 | 0.12655 | 1.469 | A17 | BASW0.05218021/05
Horizontal Wall | Basic | BASW.05218021/05/DBE | 52 | 180 | 21 | 22 | 6542 | 6542 | 6542 | 0.15576 | 3271 | 0.077881 | 7196 | 0.17133 | 1 | A17 | BASW0.05218021/05/DBE
Horizontal Wall | Basic | BASW.05220010/05 | 52 | 200 | 10 | 12 | 1984 | 1984 | 1984 | 0.047238 | 760 | 0.018095 | 2264 | 0.053905 | 1.385 | A17 | BASW0.05220010/05
Horizontal Wall | Basic | BASW.05220011/05 | 52 | 200 | 11 | 12 | 2436 | 2436 | 2436 | 0.058 | 901 | 0.021452 | 2794 | 0.066524 | 1.435 | A17 | BASW0.05220011/05
Horizontal Wall | Basic | BASW.05220011/05/DBE | 52 | 200 | 11 | 12 | 3636 | 3636 | 3636 | 0.086571 | 1818 | 0.043286 | 4000 | 0.095238 | 1 | A17 | BASW0.05220011/05/DBE
Horizontal Wall | Basic | BASW.05220015/05 | 52 | 200 | 15 | 17 | 3214 | 3214 | 3214 | 0.076524 | 1257 | 0.029929 | 3658 | 0.087095 | 1.354 | A17 | BASW0.05220015/05
Horizontal Wall | Basic | BASW.05220016/05 | 52 | 200 | 16 | 17 | 3774 | 3774 | 3774 | 0.089857 | 1381 | 0.032881 | 4333 | 0.10317 | 1.45 | A17 | BASW0.05220016/05
Horizontal Wall | Basic | BASW.05220016/05/DBE | 52 | 200 | 16 | 17 | 5694 | 5694 | 5694 | 0.13557 | 2847 | 0.067786 | 6263 | 0.14912 | 1 | A17 | BASW0.05220016/05/DBE
Horizontal Wall | Basic | BASW.05220020/05 | 52 | 200 | 20 | 22 | 4414 | 4414 | 4414 | 0.1051 | 1770 | 0.042143 | 5005 | 0.11917 | 1.319 | A17 | BASW0.05220020/05
Horizontal Wall | Basic | BASW.05220021/05 | 52 | 200 | 21 | 22 | 5136 | 5136 | 5136 | 0.12229 | 1854 | 0.044143 | 5906 | 0.14062 | 1.469 | A17 | BASW0.05220021/05
Horizontal Wall | Basic | BASW.05220021/05/DBE | 52 | 200 | 21 | 22 | 7056 | 7056 | 7056 | 0.168 | 3528 | 0.084 | 7762 | 0.18481 | 1 | A17 | BASW0.05220021/05/DBE
Horizontal Wall | Basic | BASW.05224010/05 | 52 | 240 | 10 | 12 | 2381 | 2381 | 2381 | 0.05669 | 912 | 0.021714 | 2717 | 0.06469 | 1.385 | A17 | BASW0.05224010/05
Horizontal Wall | Basic | BASW.05224011/05 | 52 | 240 | 11 | 12 | 2923 | 2923 | 2923 | 0.069595 | 1082 | 0.025762 | 3353 | 0.079833 | 1.435 | A17 | BASW0.05224011/05
Horizontal Wall | Basic | BASW.05224011/05/DBE | 52 | 240 | 11 | 12 | 4723 | 4723 | 4723 | 0.11245 | 2362 | 0.056238 | 5195 | 0.12369 | 1 | A17 | BASW0.05224011/05/DBE
Horizontal Wall | Basic | BASW.05224015/05 | 52 | 240 | 15 | 17 | 3857 | 3857 | 3857 | 0.091833 | 1508 | 0.035905 | 4389 | 0.1045 | 1.354 | A17 | BASW0.05224015/05
Horizontal Wall | Basic | BASW.05224016/05 | 52 | 240 | 16 | 17 | 4529 | 4529 | 4529 | 0.10783 | 1658 | 0.039476 | 5199 | 0.12379 | 1.45 | A17 | BASW0.05224016/05
Horizontal Wall | Basic | BASW.05224016/05/DBE | 52 | 240 | 16 | 17 | 7409 | 7409 | 7409 | 0.1764 | 3705 | 0.088214 | 8150 | 0.19405 | 1 | A17 | BASW0.05224016/05/DBE
Horizontal Wall | Basic | BASW.05224020/05 | 52 | 240 | 20 | 22 | 5297 | 5297 | 5297 | 0.12612 | 2124 | 0.050571 | 6007 | 0.14302 | 1.319 | A17 | BASW0.05224020/05
Horizontal Wall | Basic | BASW.05224021/05 | 52 | 240 | 21 | 22 | 6163 | 6163 | 6163 | 0.14674 | 2225 | 0.052976 | 7087 | 0.16874 | 1.469 | A17 | BASW0.05224021/05
Horizontal Wall | Basic | BASW.05224021/05/DBE | 52 | 240 | 21 | 22 | 9043 | 9043 | 9043 | 0.21531 | 4522 | 0.10767 | 9947 | 0.23683 | 1 | A17 | BASW0.05224021/05/DBE
Horizontal Wall | Basic | BASW.05228010/05 | 52 | 280 | 10 | 12 | 2778 | 2778 | 2778 | 0.066143 | 1064 | 0.025333 | 3170 | 0.075476 | 1.385 | A17 | BASW0.05228010/05
Horizontal Wall | Basic | BASW.05228011/05 | 52 | 280 | 11 | 12 | 3410 | 3410 | 3410 | 0.08119 | 1262 | 0.030048 | 3911 | 0.093119 | 1.435 | A17 | BASW0.05228011/05
Horizontal Wall | Basic | BASW.05228011/05/DBE | 52 | 280 | 11 | 12 | 5210 | 5210 | 5210 | 0.12405 | 2605 | 0.062024 | 5731 | 0.13645 | 1 | A17 | BASW0.05228011/05/DBE
Horizontal Wall | Basic | BASW.05228015/05 | 52 | 280 | 15 | 17 | 4500 | 4500 | 4500 | 0.10714 | 1760 | 0.041905 | 5121 | 0.12193 | 1.354 | A17 | BASW0.05228015/05
Horizontal Wall | Basic | BASW.05228016/05 | 52 | 280 | 16 | 17 | 5284 | 5284 | 5284 | 0.12581 | 1934 | 0.046048 | 6066 | 0.14443 | 1.45 | A17 | BASW0.05228016/05
Horizontal Wall | Basic | BASW.05228016/05/DBE | 52 | 280 | 16 | 17 | 8164 | 8164 | 8164 | 0.19438 | 4082 | 0.09719 | 8980 | 0.21381 | 1 | A17 | BASW0.05228016/05/DBE
Horizontal Wall | Basic | BASW.05228020/05 | 52 | 280 | 20 | 22 | 6180 | 6180 | 6180 | 0.14714 | 2478 | 0.059 | 7008 | 0.16686 | 1.319 | A17 | BASW0.05228020/05
Horizontal Wall | Basic | BASW.05228021/05 | 52 | 280 | 21 | 22 | 7190 | 7190 | 7190 | 0.17119 | 2596 | 0.06181 | 8269 | 0.19688 | 1.469 | A17 | BASW0.05228021/05
Horizontal Wall | Basic | BASW.05228021/05/DBE | 52 | 280 | 21 | 22 | 10070 | 10070 | 10070 | 0.23976 | 5035 | 0.11988 | 11077 | 0.26374 | 1 | A17 | BASW0.05228021/05/DBE
Horizontal Wall | Basic | BASW.06205010/05 | 62 | 50 | 10 | 12 | 521 | 521 | 521 | 0.012405 | 201 | 0.0047857 | 594 | 0.014143 | 1.374 | A17 | BASW0.06205010/05
Horizontal Wall | Basic | BASW.06205011/05 | 62 | 50 | 11 | 12 | 653 | 653 | 653 | 0.015548 | 243 | 0.0057857 | 748 | 0.01781 | 1.426 | A17 | BASW0.06205011/05
Horizontal Wall | Basic | BASW.06205015/05 | 62 | 50 | 15 | 17 | 850 | 850 | 850 | 0.020238 | 335 | 0.0079762 | 966 | 0.023 | 1.345 | A17 | BASW0.06205015/05
Horizontal Wall | Basic | BASW.06205016/05 | 62 | 50 | 16 | 17 | 1020 | 1020 | 1020 | 0.024286 | 375 | 0.0089286 | 1170 | 0.027857 | 1.443 | A17 | BASW0.06205016/05
Horizontal Wall | Basic | BASW.06205020/05 | 62 | 50 | 20 | 22 | 1160 | 1160 | 1160 | 0.027619 | 469 | 0.011167 | 1314 | 0.031286 | 1.309 | A17 | BASW0.06205020/05
Horizontal Wall | Basic | BASW.06205021/05 | 62 | 50 | 21 | 22 | 1389 | 1389 | 1389 | 0.033071 | 504 | 0.012 | 1597 | 0.038024 | 1.462 | A17 | BASW0.06205021/05
Horizontal Wall | Basic | BASW.06206010/05 | 62 | 60 | 10 | 12 | 625 | 625 | 625 | 0.014881 | 241 | 0.0057381 | 713 | 0.016976 | 1.374 | A17 | BASW0.06206010/05
Horizontal Wall | Basic | BASW.06206011/05 | 62 | 60 | 11 | 12 | 784 | 784 | 784 | 0.018667 | 292 | 0.0069524 | 898 | 0.021381 | 1.426 | A17 | BASW0.06206011/05
Horizontal Wall | Basic | BASW.06206011/05/DBE | 62 | 60 | 11 | 12 | 1084 | 1084 | 1084 | 0.02581 | 542 | 0.012905 | 1192 | 0.028381 | 1 | A17 | BASW0.06206011/05/DBE
Horizontal Wall | Basic | BASW.06206015/05 | 62 | 60 | 15 | 17 | 1020 | 1020 | 1020 | 0.024286 | 402 | 0.0095714 | 1160 | 0.027619 | 1.345 | A17 | BASW0.06206015/05
Horizontal Wall | Basic | BASW.06206016/05 | 62 | 60 | 16 | 17 | 1224 | 1224 | 1224 | 0.029143 | 450 | 0.010714 | 1404 | 0.033429 | 1.443 | A17 | BASW0.06206016/05
Horizontal Wall | Basic | BASW.06206016/05/DBE | 62 | 60 | 16 | 17 | 1704 | 1704 | 1704 | 0.040571 | 852 | 0.020286 | 1874 | 0.044619 | 1 | A17 | BASW0.06206016/05/DBE
Horizontal Wall | Basic | BASW.06206020/05 | 62 | 60 | 20 | 22 | 1391 | 1391 | 1391 | 0.033119 | 562 | 0.013381 | 1576 | 0.037524 | 1.309 | A17 | BASW0.06206020/05
Horizontal Wall | Basic | BASW.06206021/05 | 62 | 60 | 21 | 22 | 1667 | 1667 | 1667 | 0.03969 | 605 | 0.014405 | 1917 | 0.045643 | 1.462 | A17 | BASW0.06206021/05
Horizontal Wall | Basic | BASW.06206021/05/DBE | 62 | 60 | 21 | 22 | 2147 | 2147 | 2147 | 0.051119 | 1074 | 0.025571 | 2362 | 0.056238 | 1 | A17 | BASW0.06206021/05/DBE
Horizontal Wall | Basic | BASW.06207010/05 | 62 | 70 | 10 | 12 | 729 | 729 | 729 | 0.017357 | 281 | 0.0066905 | 831 | 0.019786 | 1.374 | A17 | BASW0.06207010/05
Horizontal Wall | Basic | BASW.06207011/05 | 62 | 70 | 11 | 12 | 914 | 914 | 914 | 0.021762 | 340 | 0.0080952 | 1047 | 0.024929 | 1.426 | A17 | BASW0.06207011/05
Horizontal Wall | Basic | BASW.06207011/05/DBE | 62 | 70 | 11 | 12 | 1214 | 1214 | 1214 | 0.028905 | 607 | 0.014452 | 1335 | 0.031786 | 1 | A17 | BASW0.06207011/05/DBE
Horizontal Wall | Basic | BASW.06207015/05 | 62 | 70 | 15 | 17 | 1190 | 1190 | 1190 | 0.028333 | 469 | 0.011167 | 1353 | 0.032214 | 1.345 | A17 | BASW0.06207015/05
Horizontal Wall | Basic | BASW.06207016/05 | 62 | 70 | 16 | 17 | 1428 | 1428 | 1428 | 0.034 | 526 | 0.012524 | 1638 | 0.039 | 1.443 | A17 | BASW0.06207016/05
Horizontal Wall | Basic | BASW.06207016/05/DBE | 62 | 70 | 16 | 17 | 1908 | 1908 | 1908 | 0.045429 | 954 | 0.022714 | 2099 | 0.049976 | 1 | A17 | BASW0.06207016/05/DBE
Horizontal Wall | Basic | BASW.06207020/05 | 62 | 70 | 20 | 22 | 1623 | 1623 | 1623 | 0.038643 | 656 | 0.015619 | 1839 | 0.043786 | 1.309 | A17 | BASW0.06207020/05
Horizontal Wall | Basic | BASW.06207021/05 | 62 | 70 | 21 | 22 | 1945 | 1945 | 1945 | 0.04631 | 706 | 0.01681 | 2237 | 0.053262 | 1.462 | A17 | BASW0.06207021/05
Horizontal Wall | Basic | BASW.06207021/05/DBE | 62 | 70 | 21 | 22 | 2425 | 2425 | 2425 | 0.057738 | 1213 | 0.028881 | 2668 | 0.063524 | 1 | A17 | BASW0.06207021/05/DBE
Horizontal Wall | Basic | BASW.06208010/05 | 62 | 80 | 10 | 12 | 833 | 833 | 833 | 0.019833 | 322 | 0.0076667 | 950 | 0.022619 | 1.374 | A17 | BASW0.06208010/05
Horizontal Wall | Basic | BASW.06208011/05 | 62 | 80 | 11 | 12 | 1045 | 1045 | 1045 | 0.024881 | 389 | 0.0092619 | 1198 | 0.028524 | 1.426 | A17 | BASW0.06208011/05
Horizontal Wall | Basic | BASW.06208011/05/DBE | 62 | 80 | 11 | 12 | 1345 | 1345 | 1345 | 0.032024 | 673 | 0.016024 | 1480 | 0.035238 | 1 | A17 | BASW0.06208011/05/DBE
Horizontal Wall | Basic | BASW.06208015/05 | 62 | 80 | 15 | 17 | 1360 | 1360 | 1360 | 0.032381 | 536 | 0.012762 | 1546 | 0.03681 | 1.345 | A17 | BASW0.06208015/05
Horizontal Wall | Basic | BASW.06208016/05 | 62 | 80 | 16 | 17 | 1632 | 1632 | 1632 | 0.038857 | 601 | 0.01431 | 1872 | 0.044571 | 1.443 | A17 | BASW0.06208016/05
Horizontal Wall | Basic | BASW.06208016/05/DBE | 62 | 80 | 16 | 17 | 2112 | 2112 | 2112 | 0.050286 | 1056 | 0.025143 | 2323 | 0.05531 | 1 | A17 | BASW0.06208016/05/DBE
Horizontal Wall | Basic | BASW.06208020/05 | 62 | 80 | 20 | 22 | 1855 | 1855 | 1855 | 0.044167 | 749 | 0.017833 | 2102 | 0.050048 | 1.309 | A17 | BASW0.06208020/05
Horizontal Wall | Basic | BASW.06208021/05 | 62 | 80 | 21 | 22 | 2222 | 2222 | 2222 | 0.052905 | 807 | 0.019214 | 2555 | 0.060833 | 1.462 | A17 | BASW0.06208021/05
Horizontal Wall | Basic | BASW.06208021/05/DBE | 62 | 80 | 21 | 22 | 2702 | 2702 | 2702 | 0.064333 | 1351 | 0.032167 | 2972 | 0.070762 | 1 | A17 | BASW0.06208021/05/DBE
Horizontal Wall | Basic | BASW.06209010/05 | 62 | 90 | 10 | 12 | 937 | 937 | 937 | 0.02231 | 362 | 0.008619 | 1068 | 0.025429 | 1.374 | A17 | BASW0.06209010/05
Horizontal Wall | Basic | BASW.06209011/05 | 62 | 90 | 11 | 12 | 1175 | 1175 | 1175 | 0.027976 | 437 | 0.010405 | 1347 | 0.032071 | 1.426 | A17 | BASW0.06209011/05
Horizontal Wall | Basic | BASW.06209011/05/DBE | 62 | 90 | 11 | 12 | 1775 | 1775 | 1775 | 0.042262 | 888 | 0.021143 | 1953 | 0.0465 | 1 | A17 | BASW0.06209011/05/DBE
Horizontal Wall | Basic | BASW.06209015/05 | 62 | 90 | 15 | 17 | 1530 | 1530 | 1530 | 0.036429 | 603 | 0.014357 | 1740 | 0.041429 | 1.345 | A17 | BASW0.06209015/05
Horizontal Wall | Basic | BASW.06209016/05 | 62 | 90 | 16 | 17 | 1836 | 1836 | 1836 | 0.043714 | 676 | 0.016095 | 2106 | 0.050143 | 1.443 | A17 | BASW0.06209016/05
Horizontal Wall | Basic | BASW.06209016/05/DBE | 62 | 90 | 16 | 17 | 2796 | 2796 | 2796 | 0.066571 | 1398 | 0.033286 | 3076 | 0.073238 | 1 | A17 | BASW0.06209016/05/DBE
Horizontal Wall | Basic | BASW.06209020/05 | 62 | 90 | 20 | 22 | 2087 | 2087 | 2087 | 0.04969 | 843 | 0.020071 | 2365 | 0.05631 | 1.309 | A17 | BASW0.06209020/05
Horizontal Wall | Basic | BASW.06209021/05 | 62 | 90 | 21 | 22 | 2500 | 2500 | 2500 | 0.059524 | 908 | 0.021619 | 2875 | 0.068452 | 1.462 | A17 | BASW0.06209021/05
Horizontal Wall | Basic | BASW.06209021/05/DBE | 62 | 90 | 21 | 22 | 3460 | 3460 | 3460 | 0.082381 | 1730 | 0.04119 | 3806 | 0.090619 | 1 | A17 | BASW0.06209021/05/DBE
Horizontal Wall | Basic | BASW.06210010/05 | 62 | 100 | 10 | 12 | 1041 | 1041 | 1041 | 0.024786 | 402 | 0.0095714 | 1187 | 0.028262 | 1.374 | A17 | BASW0.06210010/05
Horizontal Wall | Basic | BASW.06210011/05 | 62 | 100 | 11 | 12 | 1306 | 1306 | 1306 | 0.031095 | 486 | 0.011571 | 1497 | 0.035643 | 1.426 | A17 | BASW0.06210011/05
Horizontal Wall | Basic | BASW.06210011/05/DBE | 62 | 100 | 11 | 12 | 1906 | 1906 | 1906 | 0.045381 | 953 | 0.02269 | 2097 | 0.049929 | 1 | A17 | BASW0.06210011/05/DBE
Horizontal Wall | Basic | BASW.06210015/05 | 62 | 100 | 15 | 17 | 1700 | 1700 | 1700 | 0.040476 | 670 | 0.015952 | 1933 | 0.046024 | 1.345 | A17 | BASW0.06210015/05
Horizontal Wall | Basic | BASW.06210016/05 | 62 | 100 | 16 | 17 | 2040 | 2040 | 2040 | 0.048571 | 751 | 0.017881 | 2340 | 0.055714 | 1.443 | A17 | BASW0.06210016/05
Horizontal Wall | Basic | BASW.06210016/05/DBE | 62 | 100 | 16 | 17 | 3000 | 3000 | 3000 | 0.071429 | 1500 | 0.035714 | 3300 | 0.078571 | 1 | A17 | BASW0.06210016/05/DBE
Horizontal Wall | Basic | BASW.06210020/05 | 62 | 100 | 20 | 22 | 2319 | 2319 | 2319 | 0.055214 | 937 | 0.02231 | 2627 | 0.062548 | 1.309 | A17 | BASW0.06210020/05
Horizontal Wall | Basic | BASW.06210021/05 | 62 | 100 | 21 | 22 | 2778 | 2778 | 2778 | 0.066143 | 1008 | 0.024 | 3195 | 0.076071 | 1.462 | A17 | BASW0.06210021/05
Horizontal Wall | Basic | BASW.06210021/05/DBE | 62 | 100 | 21 | 22 | 3738 | 3738 | 3738 | 0.089 | 1869 | 0.0445 | 4112 | 0.097905 | 1 | A17 | BASW0.06210021/05/DBE
Horizontal Wall | Basic | BASW.06211010/05 | 62 | 110 | 10 | 12 | 1145 | 1145 | 1145 | 0.027262 | 442 | 0.010524 | 1305 | 0.031071 | 1.374 | A17 | BASW0.06211010/05
Horizontal Wall | Basic | BASW.06211011/05 | 62 | 110 | 11 | 12 | 1437 | 1437 | 1437 | 0.034214 | 535 | 0.012738 | 1647 | 0.039214 | 1.426 | A17 | BASW0.06211011/05
Horizontal Wall | Basic | BASW.06211011/05/DBE | 62 | 110 | 11 | 12 | 2037 | 2037 | 2037 | 0.0485 | 1019 | 0.024262 | 2241 | 0.053357 | 1 | A17 | BASW0.06211011/05/DBE
Horizontal Wall | Basic | BASW.06211015/05 | 62 | 110 | 15 | 17 | 1870 | 1870 | 1870 | 0.044524 | 737 | 0.017548 | 2126 | 0.050619 | 1.345 | A17 | BASW0.06211015/05
Horizontal Wall | Basic | BASW.06211016/05 | 62 | 110 | 16 | 17 | 2244 | 2244 | 2244 | 0.053429 | 826 | 0.019667 | 2574 | 0.061286 | 1.443 | A17 | BASW0.06211016/05
Horizontal Wall | Basic | BASW.06211016/05/DBE | 62 | 110 | 16 | 17 | 3204 | 3204 | 3204 | 0.076286 | 1602 | 0.038143 | 3524 | 0.083905 | 1 | A17 | BASW0.06211016/05/DBE
Horizontal Wall | Basic | BASW.06211020/05 | 62 | 110 | 20 | 22 | 2551 | 2551 | 2551 | 0.060738 | 1031 | 0.024548 | 2890 | 0.06881 | 1.309 | A17 | BASW0.06211020/05
Horizontal Wall | Basic | BASW.06211021/05 | 62 | 110 | 21 | 22 | 3056 | 3056 | 3056 | 0.072762 | 1109 | 0.026405 | 3514 | 0.083667 | 1.462 | A17 | BASW0.06211021/05
Horizontal Wall | Basic | BASW.06211021/05/DBE | 62 | 110 | 21 | 22 | 4016 | 4016 | 4016 | 0.095619 | 2008 | 0.04781 | 4418 | 0.10519 | 1 | A17 | BASW0.06211021/05/DBE
Horizontal Wall | Basic | BASW.06212010/05 | 62 | 120 | 10 | 12 | 1249 | 1249 | 1249 | 0.029738 | 482 | 0.011476 | 1424 | 0.033905 | 1.374 | A17 | BASW0.06212010/05
Horizontal Wall | Basic | BASW.06212011/05 | 62 | 120 | 11 | 12 | 1567 | 1567 | 1567 | 0.03731 | 583 | 0.013881 | 1796 | 0.042762 | 1.426 | A17 | BASW0.06212011/05
Horizontal Wall | Basic | BASW.06212011/05/DBE | 62 | 120 | 11 | 12 | 2167 | 2167 | 2167 | 0.051595 | 1084 | 0.02581 | 2384 | 0.056762 | 1 | A17 | BASW0.06212011/05/DBE
Horizontal Wall | Basic | BASW.06212015/05 | 62 | 120 | 15 | 17 | 2040 | 2040 | 2040 | 0.048571 | 804 | 0.019143 | 2319 | 0.055214 | 1.345 | A17 | BASW0.06212015/05
Horizontal Wall | Basic | BASW.06212016/05 | 62 | 120 | 16 | 17 | 2448 | 2448 | 2448 | 0.058286 | 901 | 0.021452 | 2808 | 0.066857 | 1.443 | A17 | BASW0.06212016/05
Horizontal Wall | Basic | BASW.06212016/05/DBE | 62 | 120 | 16 | 17 | 3408 | 3408 | 3408 | 0.081143 | 1704 | 0.040571 | 3749 | 0.089262 | 1 | A17 | BASW0.06212016/05/DBE
Horizontal Wall | Basic | BASW.06212020/05 | 62 | 120 | 20 | 22 | 2783 | 2783 | 2783 | 0.066262 | 1124 | 0.026762 | 3153 | 0.075071 | 1.309 | A17 | BASW0.06212020/05
Horizontal Wall | Basic | BASW.06212021/05 | 62 | 120 | 21 | 22 | 3334 | 3334 | 3334 | 0.079381 | 1210 | 0.02881 | 3834 | 0.091286 | 1.462 | A17 | BASW0.06212021/05
Horizontal Wall | Basic | BASW.06212021/05/DBE | 62 | 120 | 21 | 22 | 4294 | 4294 | 4294 | 0.10224 | 2147 | 0.051119 | 4723 | 0.11245 | 1 | A17 | BASW0.06212021/05/DBE
Horizontal Wall | Basic | BASW.06214010/05 | 62 | 140 | 10 | 12 | 1457 | 1457 | 1457 | 0.03469 | 562 | 0.013381 | 1661 | 0.039548 | 1.374 | A17 | BASW0.06214010/05
Horizontal Wall | Basic | BASW.06214011/05 | 62 | 140 | 11 | 12 | 1828 | 1828 | 1828 | 0.043524 | 680 | 0.01619 | 2095 | 0.049881 | 1.426 | A17 | BASW0.06214011/05
Horizontal Wall | Basic | BASW.06214011/05/DBE | 62 | 140 | 11 | 12 | 2428 | 2428 | 2428 | 0.05781 | 1214 | 0.028905 | 2671 | 0.063595 | 1 | A17 | BASW0.06214011/05/DBE
Horizontal Wall | Basic | BASW.06214015/05 | 62 | 140 | 15 | 17 | 2380 | 2380 | 2380 | 0.056667 | 938 | 0.022333 | 2706 | 0.064429 | 1.345 | A17 | BASW0.06214015/05
Horizontal Wall | Basic | BASW.06214016/05 | 62 | 140 | 16 | 17 | 2856 | 2856 | 2856 | 0.068 | 1051 | 0.025024 | 3276 | 0.078 | 1.443 | A17 | BASW0.06214016/05
Horizontal Wall | Basic | BASW.06214016/05/DBE | 62 | 140 | 16 | 17 | 3816 | 3816 | 3816 | 0.090857 | 1908 | 0.045429 | 4198 | 0.099952 | 1 | A17 | BASW0.06214016/05/DBE
Horizontal Wall | Basic | BASW.06214020/05 | 62 | 140 | 20 | 22 | 3247 | 3247 | 3247 | 0.07731 | 1312 | 0.031238 | 3679 | 0.087595 | 1.309 | A17 | BASW0.06214020/05
Horizontal Wall | Basic | BASW.06214021/05 | 62 | 140 | 21 | 22 | 3889 | 3889 | 3889 | 0.092595 | 1412 | 0.033619 | 4472 | 0.10648 | 1.462 | A17 | BASW0.06214021/05
Horizontal Wall | Basic | BASW.06214021/05/DBE | 62 | 140 | 21 | 22 | 4849 | 4849 | 4849 | 0.11545 | 2425 | 0.057738 | 5334 | 0.127 | 1 | A17 | BASW0.06214021/05/DBE
Horizontal Wall | Basic | BASW.07205010/05 | 72 | 50 | 10 | 12 | 539 | 539 | 539 | 0.012833 | 210 | 0.005 | 614 | 0.014619 | 1.363 | A17 | BASW0.07205010/05
Horizontal Wall | Basic | BASW.07205011/05 | 72 | 50 | 11 | 12 | 689 | 689 | 689 | 0.016405 | 258 | 0.0061429 | 789 | 0.018786 | 1.417 | A17 | BASW0.07205011/05
Horizontal Wall | Basic | BASW.07205015/05 | 72 | 50 | 15 | 17 | 888 | 888 | 888 | 0.021143 | 352 | 0.008381 | 1009 | 0.024024 | 1.336 | A17 | BASW0.07205015/05
Horizontal Wall | Basic | BASW.07205016/05 | 72 | 50 | 16 | 17 | 1086 | 1086 | 1086 | 0.025857 | 402 | 0.0095714 | 1246 | 0.029667 | 1.436 | A17 | BASW0.07205016/05
Horizontal Wall | Basic | BASW.07205020/05 | 72 | 50 | 20 | 22 | 1201 | 1201 | 1201 | 0.028595 | 489 | 0.011643 | 1360 | 0.032381 | 1.298 | A17 | BASW0.07205020/05
Horizontal Wall | Basic | BASW.07205021/05 | 72 | 50 | 21 | 22 | 1479 | 1479 | 1479 | 0.035214 | 540 | 0.012857 | 1699 | 0.040452 | 1.455 | A17 | BASW0.07205021/05
Horizontal Wall | Basic | BASW.07206010/05 | 72 | 60 | 10 | 12 | 646 | 646 | 646 | 0.015381 | 251 | 0.0059762 | 736 | 0.017524 | 1.363 | A17 | BASW0.07206010/05
Horizontal Wall | Basic | BASW.07206011/05 | 72 | 60 | 11 | 12 | 827 | 827 | 827 | 0.01969 | 309 | 0.0073571 | 947 | 0.022548 | 1.417 | A17 | BASW0.07206011/05
Horizontal Wall | Basic | BASW.07206011/05/DBE | 72 | 60 | 11 | 12 | 1127 | 1127 | 1127 | 0.026833 | 564 | 0.013429 | 1240 | 0.029524 | 1 | A17 | BASW0.07206011/05/DBE
Horizontal Wall | Basic | BASW.07206015/05 | 72 | 60 | 15 | 17 | 1065 | 1065 | 1065 | 0.025357 | 422 | 0.010048 | 1210 | 0.02881 | 1.336 | A17 | BASW0.07206015/05
Horizontal Wall | Basic | BASW.07206016/05 | 72 | 60 | 16 | 17 | 1303 | 1303 | 1303 | 0.031024 | 482 | 0.011476 | 1495 | 0.035595 | 1.436 | A17 | BASW0.07206016/05
Horizontal Wall | Basic | BASW.07206016/05/DBE | 72 | 60 | 16 | 17 | 1783 | 1783 | 1783 | 0.042452 | 892 | 0.021238 | 1961 | 0.04669 | 1 | A17 | BASW0.07206016/05/DBE
Horizontal Wall | Basic | BASW.07206020/05 | 72 | 60 | 20 | 22 | 1441 | 1441 | 1441 | 0.03431 | 586 | 0.013952 | 1631 | 0.038833 | 1.298 | A17 | BASW0.07206020/05
Horizontal Wall | Basic | BASW.07206021/05 | 72 | 60 | 21 | 22 | 1775 | 1775 | 1775 | 0.042262 | 648 | 0.015429 | 2039 | 0.048548 | 1.455 | A17 | BASW0.07206021/05
Horizontal Wall | Basic | BASW.07206021/05/DBE | 72 | 60 | 21 | 22 | 2255 | 2255 | 2255 | 0.05369 | 1128 | 0.026857 | 2481 | 0.059071 | 1 | A17 | BASW0.07206021/05/DBE
Horizontal Wall | Basic | BASW.07207010/05 | 72 | 70 | 10 | 12 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.363 | A17 | BASW0.07207010/05
Horizontal Wall | Basic | BASW.07207011/05 | 72 | 70 | 11 | 12 | 965 | 965 | 965 | 0.022976 | 361 | 0.0085952 | 1105 | 0.02631 | 1.417 | A17 | BASW0.07207011/05
Horizontal Wall | Basic | BASW.07207011/05/DBE | 72 | 70 | 11 | 12 | 1265 | 1265 | 1265 | 0.030119 | 633 | 0.015071 | 1392 | 0.033143 | 1 | A17 | BASW0.07207011/05/DBE
Horizontal Wall | Basic | BASW.07207015/05 | 72 | 70 | 15 | 17 | 1243 | 1243 | 1243 | 0.029595 | 492 | 0.011714 | 1412 | 0.033619 | 1.336 | A17 | BASW0.07207015/05
Horizontal Wall | Basic | BASW.07207016/05 | 72 | 70 | 16 | 17 | 1520 | 1520 | 1520 | 0.03619 | 562 | 0.013381 | 1743 | 0.0415 | 1.436 | A17 | BASW0.07207016/05
Horizontal Wall | Basic | BASW.07207016/05/DBE | 72 | 70 | 16 | 17 | 2000 | 2000 | 2000 | 0.047619 | 1000 | 0.02381 | 2200 | 0.052381 | 1 | A17 | BASW0.07207016/05/DBE
Horizontal Wall | Basic | BASW.07207020/05 | 72 | 70 | 20 | 22 | 1681 | 1681 | 1681 | 0.040024 | 684 | 0.016286 | 1903 | 0.04531 | 1.298 | A17 | BASW0.07207020/05
Horizontal Wall | Basic | BASW.07207021/05 | 72 | 70 | 21 | 22 | 2071 | 2071 | 2071 | 0.04931 | 756 | 0.018 | 2380 | 0.056667 | 1.455 | A17 | BASW0.07207021/05
Horizontal Wall | Basic | BASW.07207021/05/DBE | 72 | 70 | 21 | 22 | 2551 | 2551 | 2551 | 0.060738 | 1276 | 0.030381 | 2806 | 0.06681 | 1 | A17 | BASW0.07207021/05/DBE
Horizontal Wall | Basic | BASW.07208010/05 | 72 | 80 | 10 | 12 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.363 | A17 | BASW0.07208010/05
Horizontal Wall | Basic | BASW.07208011/05 | 72 | 80 | 11 | 12 | 1102 | 1102 | 1102 | 0.026238 | 412 | 0.0098095 | 1262 | 0.030048 | 1.417 | A17 | BASW0.07208011/05
Horizontal Wall | Basic | BASW.07208011/05/DBE | 72 | 80 | 11 | 12 | 1402 | 1402 | 1402 | 0.033381 | 701 | 0.01669 | 1542 | 0.036714 | 1 | A17 | BASW0.07208011/05/DBE
Horizontal Wall | Basic | BASW.07208015/05 | 72 | 80 | 15 | 17 | 1420 | 1420 | 1420 | 0.03381 | 562 | 0.013381 | 1613 | 0.038405 | 1.336 | A17 | BASW0.07208015/05
Horizontal Wall | Basic | BASW.07208016/05 | 72 | 80 | 16 | 17 | 1737 | 1737 | 1737 | 0.041357 | 643 | 0.01531 | 1992 | 0.047429 | 1.436 | A17 | BASW0.07208016/05
Horizontal Wall | Basic | BASW.07208016/05/DBE | 72 | 80 | 16 | 17 | 2217 | 2217 | 2217 | 0.052786 | 1109 | 0.026405 | 2439 | 0.058071 | 1 | A17 | BASW0.07208016/05/DBE
Horizontal Wall | Basic | BASW.07208020/05 | 72 | 80 | 20 | 22 | 1922 | 1922 | 1922 | 0.045762 | 782 | 0.018619 | 2176 | 0.05181 | 1.298 | A17 | BASW0.07208020/05
Horizontal Wall | Basic | BASW.07208021/05 | 72 | 80 | 21 | 22 | 2366 | 2366 | 2366 | 0.056333 | 864 | 0.020571 | 2719 | 0.064738 | 1.455 | A17 | BASW0.07208021/05
Horizontal Wall | Basic | BASW.07208021/05/DBE | 72 | 80 | 21 | 22 | 2846 | 2846 | 2846 | 0.067762 | 1423 | 0.033881 | 3131 | 0.074548 | 1 | A17 | BASW0.07208021/05/DBE
Horizontal Wall | Basic | BASW.07209010/05 | 72 | 90 | 10 | 12 | 969 | 969 | 969 | 0.023071 | 377 | 0.0089762 | 1104 | 0.026286 | 1.363 | A17 | BASW0.07209010/05
Horizontal Wall | Basic | BASW.07209011/05 | 72 | 90 | 11 | 12 | 1240 | 1240 | 1240 | 0.029524 | 464 | 0.011048 | 1420 | 0.03381 | 1.417 | A17 | BASW0.07209011/05
Horizontal Wall | Basic | BASW.07209011/05/DBE | 72 | 90 | 11 | 12 | 1840 | 1840 | 1840 | 0.04381 | 920 | 0.021905 | 2024 | 0.04819 | 1 | A17 | BASW0.07209011/05/DBE
Horizontal Wall | Basic | BASW.07209015/05 | 72 | 90 | 15 | 17 | 1598 | 1598 | 1598 | 0.038048 | 633 | 0.015071 | 1815 | 0.043214 | 1.336 | A17 | BASW0.07209015/05
Horizontal Wall | Basic | BASW.07209016/05 | 72 | 90 | 16 | 17 | 1954 | 1954 | 1954 | 0.046524 | 723 | 0.017214 | 2241 | 0.053357 | 1.436 | A17 | BASW0.07209016/05
Horizontal Wall | Basic | BASW.07209016/05/DBE | 72 | 90 | 16 | 17 | 2914 | 2914 | 2914 | 0.069381 | 1457 | 0.03469 | 3205 | 0.07631 | 1 | A17 | BASW0.07209016/05/DBE
Horizontal Wall | Basic | BASW.07209020/05 | 72 | 90 | 20 | 22 | 2162 | 2162 | 2162 | 0.051476 | 880 | 0.020952 | 2447 | 0.058262 | 1.298 | A17 | BASW0.07209020/05
Horizontal Wall | Basic | BASW.07209021/05 | 72 | 90 | 21 | 22 | 2662 | 2662 | 2662 | 0.063381 | 972 | 0.023143 | 3059 | 0.072833 | 1.455 | A17 | BASW0.07209021/05
Horizontal Wall | Basic | BASW.07209021/05/DBE | 72 | 90 | 21 | 22 | 3622 | 3622 | 3622 | 0.086238 | 1811 | 0.043119 | 3984 | 0.094857 | 1 | A17 | BASW0.07209021/05/DBE
Horizontal Wall | Basic | BASW.07210010/05 | 72 | 100 | 10 | 12 | 1077 | 1077 | 1077 | 0.025643 | 419 | 0.0099762 | 1227 | 0.029214 | 1.363 | A17 | BASW0.07210010/05
Horizontal Wall | Basic | BASW.07210011/05 | 72 | 100 | 11 | 12 | 1378 | 1378 | 1378 | 0.03281 | 515 | 0.012262 | 1578 | 0.037571 | 1.417 | A17 | BASW0.07210011/05
Horizontal Wall | Basic | BASW.07210011/05/DBE | 72 | 100 | 11 | 12 | 1978 | 1978 | 1978 | 0.047095 | 989 | 0.023548 | 2176 | 0.05181 | 1 | A17 | BASW0.07210011/05/DBE
Horizontal Wall | Basic | BASW.07210015/05 | 72 | 100 | 15 | 17 | 1775 | 1775 | 1775 | 0.042262 | 703 | 0.016738 | 2016 | 0.048 | 1.336 | A17 | BASW0.07210015/05
Horizontal Wall | Basic | BASW.07210016/05 | 72 | 100 | 16 | 17 | 2171 | 2171 | 2171 | 0.05169 | 803 | 0.019119 | 2490 | 0.059286 | 1.436 | A17 | BASW0.07210016/05
Horizontal Wall | Basic | BASW.07210016/05/DBE | 72 | 100 | 16 | 17 | 3131 | 3131 | 3131 | 0.074548 | 1566 | 0.037286 | 3444 | 0.082 | 1 | A17 | BASW0.07210016/05/DBE
Horizontal Wall | Basic | BASW.07210020/05 | 72 | 100 | 20 | 22 | 2402 | 2402 | 2402 | 0.05719 | 978 | 0.023286 | 2719 | 0.064738 | 1.298 | A17 | BASW0.07210020/05
Horizontal Wall | Basic | BASW.07210021/05 | 72 | 100 | 21 | 22 | 2958 | 2958 | 2958 | 0.070429 | 1080 | 0.025714 | 3399 | 0.080929 | 1.455 | A17 | BASW0.07210021/05
Horizontal Wall | Basic | BASW.07210021/05/DBE | 72 | 100 | 21 | 22 | 3918 | 3918 | 3918 | 0.093286 | 1959 | 0.046643 | 4310 | 0.10262 | 1 | A17 | BASW0.07210021/05/DBE
Horizontal Wall | Basic | BASW.07211010/05 | 72 | 110 | 10 | 12 | 1185 | 1185 | 1185 | 0.028214 | 461 | 0.010976 | 1350 | 0.032143 | 1.363 | A17 | BASW0.07211010/05
Horizontal Wall | Basic | BASW.07211011/05 | 72 | 110 | 11 | 12 | 1516 | 1516 | 1516 | 0.036095 | 567 | 0.0135 | 1736 | 0.041333 | 1.417 | A17 | BASW0.07211011/05
Horizontal Wall | Basic | BASW.07211011/05/DBE | 72 | 110 | 11 | 12 | 2116 | 2116 | 2116 | 0.050381 | 1058 | 0.02519 | 2328 | 0.055429 | 1 | A17 | BASW0.07211011/05/DBE
Horizontal Wall | Basic | BASW.07211015/05 | 72 | 110 | 15 | 17 | 1953 | 1953 | 1953 | 0.0465 | 773 | 0.018405 | 2219 | 0.052833 | 1.336 | A17 | BASW0.07211015/05
Horizontal Wall | Basic | BASW.07211016/05 | 72 | 110 | 16 | 17 | 2388 | 2388 | 2388 | 0.056857 | 884 | 0.021048 | 2739 | 0.065214 | 1.436 | A17 | BASW0.07211016/05
Horizontal Wall | Basic | BASW.07211016/05/DBE | 72 | 110 | 16 | 17 | 3348 | 3348 | 3348 | 0.079714 | 1674 | 0.039857 | 3683 | 0.08769 | 1 | A17 | BASW0.07211016/05/DBE
Horizontal Wall | Basic | BASW.07211020/05 | 72 | 110 | 20 | 22 | 2642 | 2642 | 2642 | 0.062905 | 1075 | 0.025595 | 2991 | 0.071214 | 1.298 | A17 | BASW0.07211020/05
Horizontal Wall | Basic | BASW.07211021/05 | 72 | 110 | 21 | 22 | 3254 | 3254 | 3254 | 0.077476 | 1188 | 0.028286 | 3739 | 0.089024 | 1.455 | A17 | BASW0.07211021/05
Horizontal Wall | Basic | BASW.07211021/05/DBE | 72 | 110 | 21 | 22 | 4214 | 4214 | 4214 | 0.10033 | 2107 | 0.050167 | 4635 | 0.11036 | 1 | A17 | BASW0.07211021/05/DBE
Horizontal Wall | Basic | BASW.07212010/05 | 72 | 120 | 10 | 12 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.363 | A17 | BASW0.07212010/05
Horizontal Wall | Basic | BASW.07212011/05 | 72 | 120 | 11 | 12 | 1654 | 1654 | 1654 | 0.039381 | 619 | 0.014738 | 1894 | 0.045095 | 1.417 | A17 | BASW0.07212011/05
Horizontal Wall | Basic | BASW.07212011/05/DBE | 72 | 120 | 11 | 12 | 2254 | 2254 | 2254 | 0.053667 | 1127 | 0.026833 | 2479 | 0.059024 | 1 | A17 | BASW0.07212011/05/DBE
Horizontal Wall | Basic | BASW.07212015/05 | 72 | 120 | 15 | 17 | 2130 | 2130 | 2130 | 0.050714 | 843 | 0.020071 | 2420 | 0.057619 | 1.336 | A17 | BASW0.07212015/05
Horizontal Wall | Basic | BASW.07212016/05 | 72 | 120 | 16 | 17 | 2605 | 2605 | 2605 | 0.062024 | 964 | 0.022952 | 2988 | 0.071143 | 1.436 | A17 | BASW0.07212016/05
Horizontal Wall | Basic | BASW.07212016/05/DBE | 72 | 120 | 16 | 17 | 3565 | 3565 | 3565 | 0.084881 | 1783 | 0.042452 | 3922 | 0.093381 | 1 | A17 | BASW0.07212016/05/DBE
Horizontal Wall | Basic | BASW.07212020/05 | 72 | 120 | 20 | 22 | 2882 | 2882 | 2882 | 0.068619 | 1173 | 0.027929 | 3262 | 0.077667 | 1.298 | A17 | BASW0.07212020/05
Horizontal Wall | Basic | BASW.07212021/05 | 72 | 120 | 21 | 22 | 3550 | 3550 | 3550 | 0.084524 | 1296 | 0.030857 | 4079 | 0.097119 | 1.455 | A17 | BASW0.07212021/05
Horizontal Wall | Basic | BASW.07212021/05/DBE | 72 | 120 | 21 | 22 | 4510 | 4510 | 4510 | 0.10738 | 2255 | 0.05369 | 4961 | 0.11812 | 1 | A17 | BASW0.07212021/05/DBE
Horizontal Wall | Basic | BASW.07214010/05 | 72 | 140 | 10 | 12 | 1508 | 1508 | 1508 | 0.035905 | 587 | 0.013976 | 1718 | 0.040905 | 1.363 | A17 | BASW0.07214010/05
Horizontal Wall | Basic | BASW.07214011/05 | 72 | 140 | 11 | 12 | 1929 | 1929 | 1929 | 0.045929 | 721 | 0.017167 | 2209 | 0.052595 | 1.417 | A17 | BASW0.07214011/05
Horizontal Wall | Basic | BASW.07214011/05/DBE | 72 | 140 | 11 | 12 | 2529 | 2529 | 2529 | 0.060214 | 1265 | 0.030119 | 2782 | 0.066238 | 1 | A17 | BASW0.07214011/05/DBE
Horizontal Wall | Basic | BASW.07214015/05 | 72 | 140 | 15 | 17 | 2485 | 2485 | 2485 | 0.059167 | 984 | 0.023429 | 2823 | 0.067214 | 1.336 | A17 | BASW0.07214015/05
Horizontal Wall | Basic | BASW.07214016/05 | 72 | 140 | 16 | 17 | 3039 | 3039 | 3039 | 0.072357 | 1124 | 0.026762 | 3486 | 0.083 | 1.436 | A17 | BASW0.07214016/05
Horizontal Wall | Basic | BASW.07214016/05/DBE | 72 | 140 | 16 | 17 | 3999 | 3999 | 3999 | 0.095214 | 2000 | 0.047619 | 4399 | 0.10474 | 1 | A17 | BASW0.07214016/05/DBE
Horizontal Wall | Basic | BASW.07214020/05 | 72 | 140 | 20 | 22 | 3363 | 3363 | 3363 | 0.080071 | 1369 | 0.032595 | 3807 | 0.090643 | 1.298 | A17 | BASW0.07214020/05
Horizontal Wall | Basic | BASW.07214021/05 | 72 | 140 | 21 | 22 | 4141 | 4141 | 4141 | 0.098595 | 1511 | 0.035976 | 4758 | 0.11329 | 1.455 | A17 | BASW0.07214021/05
Horizontal Wall | Basic | BASW.07214021/05/DBE | 72 | 140 | 21 | 22 | 5101 | 5101 | 5101 | 0.12145 | 2551 | 0.060738 | 5611 | 0.1336 | 1 | A17 | BASW0.07214021/05/DBE
Horizontal Wall | Basic | BASW.08205010/05 | 82 | 50 | 10 | 12 | 552 | 552 | 552 | 0.013143 | 216 | 0.0051429 | 628 | 0.014952 | 1.352 | A17 | BASW0.08205010/05
Horizontal Wall | Basic | BASW.08205011/05 | 82 | 50 | 11 | 12 | 719 | 719 | 719 | 0.017119 | 271 | 0.0064524 | 823 | 0.019595 | 1.408 | A17 | BASW0.08205011/05
Horizontal Wall | Basic | BASW.08205015/05 | 82 | 50 | 15 | 17 | 918 | 918 | 918 | 0.021857 | 365 | 0.0086905 | 1042 | 0.02481 | 1.328 | A17 | BASW0.08205015/05
Horizontal Wall | Basic | BASW.08205016/05 | 82 | 50 | 16 | 17 | 1142 | 1142 | 1142 | 0.02719 | 424 | 0.010095 | 1309 | 0.031167 | 1.429 | A17 | BASW0.08205016/05
Horizontal Wall | Basic | BASW.08205020/05 | 82 | 50 | 20 | 22 | 1232 | 1232 | 1232 | 0.029333 | 505 | 0.012024 | 1393 | 0.033167 | 1.288 | A17 | BASW0.08205020/05
Horizontal Wall | Basic | BASW.08205021/05 | 82 | 50 | 21 | 22 | 1557 | 1557 | 1557 | 0.037071 | 571 | 0.013595 | 1787 | 0.042548 | 1.448 | A17 | BASW0.08205021/05
Horizontal Wall | Basic | BASW.08206010/05 | 82 | 60 | 10 | 12 | 662 | 662 | 662 | 0.015762 | 260 | 0.0061905 | 753 | 0.017929 | 1.352 | A17 | BASW0.08206010/05
Horizontal Wall | Basic | BASW.08206011/05 | 82 | 60 | 11 | 12 | 862 | 862 | 862 | 0.020524 | 325 | 0.0077381 | 986 | 0.023476 | 1.408 | A17 | BASW0.08206011/05
Horizontal Wall | Basic | BASW.08206011/05/DBE | 82 | 60 | 11 | 12 | 1162 | 1162 | 1162 | 0.027667 | 581 | 0.013833 | 1278 | 0.030429 | 1 | A17 | BASW0.08206011/05/DBE
Horizontal Wall | Basic | BASW.08206015/05 | 82 | 60 | 15 | 17 | 1101 | 1101 | 1101 | 0.026214 | 438 | 0.010429 | 1250 | 0.029762 | 1.328 | A17 | BASW0.08206015/05
Horizontal Wall | Basic | BASW.08206016/05 | 82 | 60 | 16 | 17 | 1370 | 1370 | 1370 | 0.032619 | 508 | 0.012095 | 1570 | 0.037381 | 1.429 | A17 | BASW0.08206016/05
Horizontal Wall | Basic | BASW.08206016/05/DBE | 82 | 60 | 16 | 17 | 1850 | 1850 | 1850 | 0.044048 | 925 | 0.022024 | 2035 | 0.048452 | 1 | A17 | BASW0.08206016/05/DBE
Horizontal Wall | Basic | BASW.08206020/05 | 82 | 60 | 20 | 22 | 1478 | 1478 | 1478 | 0.03519 | 606 | 0.014429 | 1672 | 0.03981 | 1.288 | A17 | BASW0.08206020/05
Horizontal Wall | Basic | BASW.08206021/05 | 82 | 60 | 21 | 22 | 1868 | 1868 | 1868 | 0.044476 | 686 | 0.016333 | 2144 | 0.051048 | 1.448 | A17 | BASW0.08206021/05
Horizontal Wall | Basic | BASW.08206021/05/DBE | 82 | 60 | 21 | 22 | 2348 | 2348 | 2348 | 0.055905 | 1174 | 0.027952 | 2583 | 0.0615 | 1 | A17 | BASW0.08206021/05/DBE
Horizontal Wall | Basic | BASW.08207010/05 | 82 | 70 | 10 | 12 | 773 | 773 | 773 | 0.018405 | 303 | 0.0072143 | 880 | 0.020952 | 1.352 | A17 | BASW0.08207010/05
Horizontal Wall | Basic | BASW.08207011/05 | 82 | 70 | 11 | 12 | 1006 | 1006 | 1006 | 0.023952 | 379 | 0.0090238 | 1151 | 0.027405 | 1.408 | A17 | BASW0.08207011/05
Horizontal Wall | Basic | BASW.08207011/05/DBE | 82 | 70 | 11 | 12 | 1306 | 1306 | 1306 | 0.031095 | 653 | 0.015548 | 1437 | 0.034214 | 1 | A17 | BASW0.08207011/05/DBE
Horizontal Wall | Basic | BASW.08207015/05 | 82 | 70 | 15 | 17 | 1285 | 1285 | 1285 | 0.030595 | 511 | 0.012167 | 1458 | 0.034714 | 1.328 | A17 | BASW0.08207015/05
Horizontal Wall | Basic | BASW.08207016/05 | 82 | 70 | 16 | 17 | 1598 | 1598 | 1598 | 0.038048 | 593 | 0.014119 | 1831 | 0.043595 | 1.429 | A17 | BASW0.08207016/05
Horizontal Wall | Basic | BASW.08207016/05/DBE | 82 | 70 | 16 | 17 | 2078 | 2078 | 2078 | 0.049476 | 1039 | 0.024738 | 2286 | 0.054429 | 1 | A17 | BASW0.08207016/05/DBE
Horizontal Wall | Basic | BASW.08207020/05 | 82 | 70 | 20 | 22 | 1725 | 1725 | 1725 | 0.041071 | 707 | 0.016833 | 1951 | 0.046452 | 1.288 | A17 | BASW0.08207020/05
Horizontal Wall | Basic | BASW.08207021/05 | 82 | 70 | 21 | 22 | 2179 | 2179 | 2179 | 0.051881 | 800 | 0.019048 | 2501 | 0.059548 | 1.448 | A17 | BASW0.08207021/05
Horizontal Wall | Basic | BASW.08207021/05/DBE | 82 | 70 | 21 | 22 | 2659 | 2659 | 2659 | 0.06331 | 1330 | 0.031667 | 2925 | 0.069643 | 1 | A17 | BASW0.08207021/05/DBE
Horizontal Wall | Basic | BASW.08208010/05 | 82 | 80 | 10 | 12 | 883 | 883 | 883 | 0.021024 | 346 | 0.0082381 | 1005 | 0.023929 | 1.352 | A17 | BASW0.08208010/05
Horizontal Wall | Basic | BASW.08208011/05 | 82 | 80 | 11 | 12 | 1150 | 1150 | 1150 | 0.027381 | 434 | 0.010333 | 1316 | 0.031333 | 1.408 | A17 | BASW0.08208011/05
Horizontal Wall | Basic | BASW.08208011/05/DBE | 82 | 80 | 11 | 12 | 1450 | 1450 | 1450 | 0.034524 | 725 | 0.017262 | 1595 | 0.037976 | 1 | A17 | BASW0.08208011/05/DBE
Horizontal Wall | Basic | BASW.08208015/05 | 82 | 80 | 15 | 17 | 1468 | 1468 | 1468 | 0.034952 | 584 | 0.013905 | 1666 | 0.039667 | 1.328 | A17 | BASW0.08208015/05
Horizontal Wall | Basic | BASW.08208016/05 | 82 | 80 | 16 | 17 | 1826 | 1826 | 1826 | 0.043476 | 677 | 0.016119 | 2093 | 0.049833 | 1.429 | A17 | BASW0.08208016/05
Horizontal Wall | Basic | BASW.08208016/05/DBE | 82 | 80 | 16 | 17 | 2306 | 2306 | 2306 | 0.054905 | 1153 | 0.027452 | 2537 | 0.060405 | 1 | A17 | BASW0.08208016/05/DBE
Horizontal Wall | Basic | BASW.08208020/05 | 82 | 80 | 20 | 22 | 1971 | 1971 | 1971 | 0.046929 | 808 | 0.019238 | 2229 | 0.053071 | 1.288 | A17 | BASW0.08208020/05
Horizontal Wall | Basic | BASW.08208021/05 | 82 | 80 | 21 | 22 | 2490 | 2490 | 2490 | 0.059286 | 914 | 0.021762 | 2859 | 0.068071 | 1.448 | A17 | BASW0.08208021/05
Horizontal Wall | Basic | BASW.08208021/05/DBE | 82 | 80 | 21 | 22 | 2970 | 2970 | 2970 | 0.070714 | 1485 | 0.035357 | 3267 | 0.077786 | 1 | A17 | BASW0.08208021/05/DBE
Horizontal Wall | Basic | BASW.08209010/05 | 82 | 90 | 10 | 12 | 994 | 994 | 994 | 0.023667 | 390 | 0.0092857 | 1131 | 0.026929 | 1.352 | A17 | BASW0.08209010/05
Horizontal Wall | Basic | BASW.08209011/05 | 82 | 90 | 11 | 12 | 1293 | 1293 | 1293 | 0.030786 | 487 | 0.011595 | 1479 | 0.035214 | 1.408 | A17 | BASW0.08209011/05
Horizontal Wall | Basic | BASW.08209011/05/DBE | 82 | 90 | 11 | 12 | 1893 | 1893 | 1893 | 0.045071 | 947 | 0.022548 | 2082 | 0.049571 | 1 | A17 | BASW0.08209011/05/DBE
Horizontal Wall | Basic | BASW.08209015/05 | 82 | 90 | 15 | 17 | 1652 | 1652 | 1652 | 0.039333 | 657 | 0.015643 | 1875 | 0.044643 | 1.328 | A17 | BASW0.08209015/05
Horizontal Wall | Basic | BASW.08209016/05 | 82 | 90 | 16 | 17 | 2055 | 2055 | 2055 | 0.048929 | 762 | 0.018143 | 2355 | 0.056071 | 1.429 | A17 | BASW0.08209016/05
Horizontal Wall | Basic | BASW.08209016/05/DBE | 82 | 90 | 16 | 17 | 3015 | 3015 | 3015 | 0.071786 | 1508 | 0.035905 | 3317 | 0.078976 | 1 | A17 | BASW0.08209016/05/DBE
Horizontal Wall | Basic | BASW.08209020/05 | 82 | 90 | 20 | 22 | 2218 | 2218 | 2218 | 0.05281 | 909 | 0.021643 | 2509 | 0.059738 | 1.288 | A17 | BASW0.08209020/05
Horizontal Wall | Basic | BASW.08209021/05 | 82 | 90 | 21 | 22 | 2802 | 2802 | 2802 | 0.066714 | 1028 | 0.024476 | 3217 | 0.076595 | 1.448 | A17 | BASW0.08209021/05
Horizontal Wall | Basic | BASW.08209021/05/DBE | 82 | 90 | 21 | 22 | 3762 | 3762 | 3762 | 0.089571 | 1881 | 0.044786 | 4138 | 0.098524 | 1 | A17 | BASW0.08209021/05/DBE
Horizontal Wall | Basic | BASW.08210010/05 | 82 | 100 | 10 | 12 | 1104 | 1104 | 1104 | 0.026286 | 433 | 0.01031 | 1256 | 0.029905 | 1.352 | A17 | BASW0.08210010/05
Horizontal Wall | Basic | BASW.08210011/05 | 82 | 100 | 11 | 12 | 1437 | 1437 | 1437 | 0.034214 | 542 | 0.012905 | 1644 | 0.039143 | 1.408 | A17 | BASW0.08210011/05
Horizontal Wall | Basic | BASW.08210011/05/DBE | 82 | 100 | 11 | 12 | 2037 | 2037 | 2037 | 0.0485 | 1019 | 0.024262 | 2241 | 0.053357 | 1 | A17 | BASW0.08210011/05/DBE
Horizontal Wall | Basic | BASW.08210015/05 | 82 | 100 | 15 | 17 | 1835 | 1835 | 1835 | 0.04369 | 730 | 0.017381 | 2083 | 0.049595 | 1.328 | A17 | BASW0.08210015/05
Horizontal Wall | Basic | BASW.08210016/05 | 82 | 100 | 16 | 17 | 2283 | 2283 | 2283 | 0.054357 | 847 | 0.020167 | 2616 | 0.062286 | 1.429 | A17 | BASW0.08210016/05
Horizontal Wall | Basic | BASW.08210016/05/DBE | 82 | 100 | 16 | 17 | 3243 | 3243 | 3243 | 0.077214 | 1622 | 0.038619 | 3567 | 0.084929 | 1 | A17 | BASW0.08210016/05/DBE
Horizontal Wall | Basic | BASW.08210020/05 | 82 | 100 | 20 | 22 | 2464 | 2464 | 2464 | 0.058667 | 1010 | 0.024048 | 2787 | 0.066357 | 1.288 | A17 | BASW0.08210020/05
Horizontal Wall | Basic | BASW.08210021/05 | 82 | 100 | 21 | 22 | 3113 | 3113 | 3113 | 0.074119 | 1142 | 0.02719 | 3574 | 0.085095 | 1.448 | A17 | BASW0.08210021/05
Horizontal Wall | Basic | BASW.08210021/05/DBE | 82 | 100 | 21 | 22 | 4073 | 4073 | 4073 | 0.096976 | 2037 | 0.0485 | 4480 | 0.10667 | 1 | A17 | BASW0.08210021/05/DBE
Horizontal Wall | Basic | BASW.08211010/05 | 82 | 110 | 10 | 12 | 1214 | 1214 | 1214 | 0.028905 | 476 | 0.011333 | 1382 | 0.032905 | 1.352 | A17 | BASW0.08211010/05
Horizontal Wall | Basic | BASW.08211011/05 | 82 | 110 | 11 | 12 | 1581 | 1581 | 1581 | 0.037643 | 596 | 0.01419 | 1809 | 0.043071 | 1.408 | A17 | BASW0.08211011/05
Horizontal Wall | Basic | BASW.08211011/05/DBE | 82 | 110 | 11 | 12 | 2181 | 2181 | 2181 | 0.051929 | 1091 | 0.025976 | 2399 | 0.057119 | 1 | A17 | BASW0.08211011/05/DBE
Horizontal Wall | Basic | BASW.08211015/05 | 82 | 110 | 15 | 17 | 2019 | 2019 | 2019 | 0.048071 | 804 | 0.019143 | 2292 | 0.054571 | 1.328 | A17 | BASW0.08211015/05
Horizontal Wall | Basic | BASW.08211016/05 | 82 | 110 | 16 | 17 | 2511 | 2511 | 2511 | 0.059786 | 932 | 0.02219 | 2878 | 0.068524 | 1.429 | A17 | BASW0.08211016/05
Horizontal Wall | Basic | BASW.08211016/05/DBE | 82 | 110 | 16 | 17 | 3471 | 3471 | 3471 | 0.082643 | 1736 | 0.041333 | 3818 | 0.090905 | 1 | A17 | BASW0.08211016/05/DBE
Horizontal Wall | Basic | BASW.08211020/05 | 82 | 110 | 20 | 22 | 2710 | 2710 | 2710 | 0.064524 | 1111 | 0.026452 | 3065 | 0.072976 | 1.288 | A17 | BASW0.08211020/05
Horizontal Wall | Basic | BASW.08211021/05 | 82 | 110 | 21 | 22 | 3424 | 3424 | 3424 | 0.081524 | 1257 | 0.029929 | 3931 | 0.093595 | 1.448 | A17 | BASW0.08211021/05
Horizontal Wall | Basic | BASW.08211021/05/DBE | 82 | 110 | 21 | 22 | 4384 | 4384 | 4384 | 0.10438 | 2192 | 0.05219 | 4822 | 0.11481 | 1 | A17 | BASW0.08211021/05/DBE
Horizontal Wall | Basic | BASW.08212010/05 | 82 | 120 | 10 | 12 | 1325 | 1325 | 1325 | 0.031548 | 519 | 0.012357 | 1508 | 0.035905 | 1.352 | A17 | BASW0.08212010/05
Horizontal Wall | Basic | BASW.08212011/05 | 82 | 120 | 11 | 12 | 1724 | 1724 | 1724 | 0.041048 | 650 | 0.015476 | 1972 | 0.046952 | 1.408 | A17 | BASW0.08212011/05
Horizontal Wall | Basic | BASW.08212011/05/DBE | 82 | 120 | 11 | 12 | 2324 | 2324 | 2324 | 0.055333 | 1162 | 0.027667 | 2556 | 0.060857 | 1 | A17 | BASW0.08212011/05/DBE
Horizontal Wall | Basic | BASW.08212015/05 | 82 | 120 | 15 | 17 | 2202 | 2202 | 2202 | 0.052429 | 876 | 0.020857 | 2499 | 0.0595 | 1.328 | A17 | BASW0.08212015/05
Horizontal Wall | Basic | BASW.08212016/05 | 82 | 120 | 16 | 17 | 2740 | 2740 | 2740 | 0.065238 | 1017 | 0.024214 | 3140 | 0.074762 | 1.429 | A17 | BASW0.08212016/05
Horizontal Wall | Basic | BASW.08212016/05/DBE | 82 | 120 | 16 | 17 | 3700 | 3700 | 3700 | 0.088095 | 1850 | 0.044048 | 4070 | 0.096905 | 1 | A17 | BASW0.08212016/05/DBE
Horizontal Wall | Basic | BASW.08212020/05 | 82 | 120 | 20 | 22 | 2957 | 2957 | 2957 | 0.070405 | 1212 | 0.028857 | 3344 | 0.079619 | 1.288 | A17 | BASW0.08212020/05
Horizontal Wall | Basic | BASW.08212021/05 | 82 | 120 | 21 | 22 | 3736 | 3736 | 3736 | 0.088952 | 1371 | 0.032643 | 4289 | 0.10212 | 1.448 | A17 | BASW0.08212021/05
Horizontal Wall | Basic | BASW.08212021/05/DBE | 82 | 120 | 21 | 22 | 4696 | 4696 | 4696 | 0.11181 | 2348 | 0.055905 | 5166 | 0.123 | 1 | A17 | BASW0.08212021/05/DBE
Horizontal Wall | Basic | BASW.08214010/05 | 82 | 140 | 10 | 12 | 1546 | 1546 | 1546 | 0.03681 | 606 | 0.014429 | 1759 | 0.041881 | 1.352 | A17 | BASW0.08214010/05
Horizontal Wall | Basic | BASW.08214011/05 | 82 | 140 | 11 | 12 | 2012 | 2012 | 2012 | 0.047905 | 759 | 0.018071 | 2302 | 0.05481 | 1.408 | A17 | BASW0.08214011/05
Horizontal Wall | Basic | BASW.08214011/05/DBE | 82 | 140 | 11 | 12 | 2612 | 2612 | 2612 | 0.06219 | 1306 | 0.031095 | 2873 | 0.068405 | 1 | A17 | BASW0.08214011/05/DBE
Horizontal Wall | Basic | BASW.08214015/05 | 82 | 140 | 15 | 17 | 2569 | 2569 | 2569 | 0.061167 | 1022 | 0.024333 | 2916 | 0.069429 | 1.328 | A17 | BASW0.08214015/05
Horizontal Wall | Basic | BASW.08214016/05 | 82 | 140 | 16 | 17 | 3196 | 3196 | 3196 | 0.076095 | 1186 | 0.028238 | 3663 | 0.087214 | 1.429 | A17 | BASW0.08214016/05
Horizontal Wall | Basic | BASW.08214016/05/DBE | 82 | 140 | 16 | 17 | 4156 | 4156 | 4156 | 0.098952 | 2078 | 0.049476 | 4572 | 0.10886 | 1 | A17 | BASW0.08214016/05/DBE
Horizontal Wall | Basic | BASW.08214020/05 | 82 | 140 | 20 | 22 | 3450 | 3450 | 3450 | 0.082143 | 1415 | 0.03369 | 3902 | 0.092905 | 1.288 | A17 | BASW0.08214020/05
Horizontal Wall | Basic | BASW.08214021/05 | 82 | 140 | 21 | 22 | 4358 | 4358 | 4358 | 0.10376 | 1599 | 0.038071 | 5003 | 0.11912 | 1.448 | A17 | BASW0.08214021/05
Horizontal Wall | Basic | BASW.08214021/05/DBE | 82 | 140 | 21 | 22 | 5318 | 5318 | 5318 | 0.12662 | 2659 | 0.06331 | 5850 | 0.13929 | 1 | A17 | BASW0.08214021/05/DBE
Horizontal Wall | Basic | BASW.09205010/05 | 92 | 50 | 10 | 12 | 561 | 561 | 561 | 0.013357 | 222 | 0.0052857 | 637 | 0.015167 | 1.341 | A17 | BASW0.09205010/05
Horizontal Wall | Basic | BASW.09205011/05 | 92 | 50 | 11 | 12 | 743 | 743 | 743 | 0.01769 | 282 | 0.0067143 | 849 | 0.020214 | 1.399 | A17 | BASW0.09205011/05
Horizontal Wall | Basic | BASW.09205015/05 | 92 | 50 | 15 | 17 | 941 | 941 | 941 | 0.022405 | 377 | 0.0089762 | 1067 | 0.025405 | 1.319 | A17 | BASW0.09205015/05
Horizontal Wall | Basic | BASW.09205016/05 | 92 | 50 | 16 | 17 | 1190 | 1190 | 1190 | 0.028333 | 444 | 0.010571 | 1363 | 0.032452 | 1.422 | A17 | BASW0.09205016/05
Horizontal Wall | Basic | BASW.09205020/05 | 92 | 50 | 20 | 22 | 1254 | 1254 | 1254 | 0.029857 | 518 | 0.012333 | 1416 | 0.033714 | 1.277 | A17 | BASW0.09205020/05
Horizontal Wall | Basic | BASW.09205021/05 | 92 | 50 | 21 | 22 | 1623 | 1623 | 1623 | 0.038643 | 597 | 0.014214 | 1862 | 0.044333 | 1.441 | A17 | BASW0.09205021/05
Horizontal Wall | Basic | BASW.09206010/05 | 92 | 60 | 10 | 12 | 673 | 673 | 673 | 0.016024 | 266 | 0.0063333 | 765 | 0.018214 | 1.341 | A17 | BASW0.09206010/05
Horizontal Wall | Basic | BASW.09206011/05 | 92 | 60 | 11 | 12 | 891 | 891 | 891 | 0.021214 | 338 | 0.0080476 | 1018 | 0.024238 | 1.399 | A17 | BASW0.09206011/05
Horizontal Wall | Basic | BASW.09206011/05/DBE | 92 | 60 | 11 | 12 | 1191 | 1191 | 1191 | 0.028357 | 596 | 0.01419 | 1310 | 0.03119 | 1 | A17 | BASW0.09206011/05/DBE
Horizontal Wall | Basic | BASW.09206015/05 | 92 | 60 | 15 | 17 | 1129 | 1129 | 1129 | 0.026881 | 453 | 0.010786 | 1280 | 0.030476 | 1.319 | A17 | BASW0.09206015/05
Horizontal Wall | Basic | BASW.09206016/05 | 92 | 60 | 16 | 17 | 1427 | 1427 | 1427 | 0.033976 | 532 | 0.012667 | 1634 | 0.038905 | 1.422 | A17 | BASW0.09206016/05
Horizontal Wall | Basic | BASW.09206016/05/DBE | 92 | 60 | 16 | 17 | 1907 | 1907 | 1907 | 0.045405 | 954 | 0.022714 | 2098 | 0.049952 | 1 | A17 | BASW0.09206016/05/DBE
Horizontal Wall | Basic | BASW.09206020/05 | 92 | 60 | 20 | 22 | 1505 | 1505 | 1505 | 0.035833 | 622 | 0.01481 | 1699 | 0.040452 | 1.277 | A17 | BASW0.09206020/05
Horizontal Wall | Basic | BASW.09206021/05 | 92 | 60 | 21 | 22 | 1948 | 1948 | 1948 | 0.046381 | 717 | 0.017071 | 2234 | 0.05319 | 1.441 | A17 | BASW0.09206021/05
Horizontal Wall | Basic | BASW.09206021/05/DBE | 92 | 60 | 21 | 22 | 2428 | 2428 | 2428 | 0.05781 | 1214 | 0.028905 | 2671 | 0.063595 | 1 | A17 | BASW0.09206021/05/DBE
Horizontal Wall | Basic | BASW.09207010/05 | 92 | 70 | 10 | 12 | 785 | 785 | 785 | 0.01869 | 310 | 0.007381 | 892 | 0.021238 | 1.341 | A17 | BASW0.09207010/05
Horizontal Wall | Basic | BASW.09207011/05 | 92 | 70 | 11 | 12 | 1040 | 1040 | 1040 | 0.024762 | 394 | 0.009381 | 1189 | 0.02831 | 1.399 | A17 | BASW0.09207011/05
Horizontal Wall | Basic | BASW.09207011/05/DBE | 92 | 70 | 11 | 12 | 1340 | 1340 | 1340 | 0.031905 | 670 | 0.015952 | 1474 | 0.035095 | 1 | A17 | BASW0.09207011/05/DBE
Horizontal Wall | Basic | BASW.09207015/05 | 92 | 70 | 15 | 17 | 1317 | 1317 | 1317 | 0.031357 | 528 | 0.012571 | 1493 | 0.035548 | 1.319 | A17 | BASW0.09207015/05
Horizontal Wall | Basic | BASW.09207016/05 | 92 | 70 | 16 | 17 | 1665 | 1665 | 1665 | 0.039643 | 621 | 0.014786 | 1906 | 0.045381 | 1.422 | A17 | BASW0.09207016/05
Horizontal Wall | Basic | BASW.09207016/05/DBE | 92 | 70 | 16 | 17 | 2145 | 2145 | 2145 | 0.051071 | 1073 | 0.025548 | 2360 | 0.05619 | 1 | A17 | BASW0.09207016/05/DBE
Horizontal Wall | Basic | BASW.09207020/05 | 92 | 70 | 20 | 22 | 1756 | 1756 | 1756 | 0.04181 | 725 | 0.017262 | 1983 | 0.047214 | 1.277 | A17 | BASW0.09207020/05
Horizontal Wall | Basic | BASW.09207021/05 | 92 | 70 | 21 | 22 | 2272 | 2272 | 2272 | 0.054095 | 836 | 0.019905 | 2606 | 0.062048 | 1.441 | A17 | BASW0.09207021/05
Horizontal Wall | Basic | BASW.09207021/05/DBE | 92 | 70 | 21 | 22 | 2752 | 2752 | 2752 | 0.065524 | 1376 | 0.032762 | 3027 | 0.072071 | 1 | A17 | BASW0.09207021/05/DBE
Horizontal Wall | Basic | BASW.09208010/05 | 92 | 80 | 10 | 12 | 898 | 898 | 898 | 0.021381 | 355 | 0.0084524 | 1020 | 0.024286 | 1.341 | A17 | BASW0.09208010/05
Horizontal Wall | Basic | BASW.09208011/05 | 92 | 80 | 11 | 12 | 1188 | 1188 | 1188 | 0.028286 | 450 | 0.010714 | 1358 | 0.032333 | 1.399 | A17 | BASW0.09208011/05
Horizontal Wall | Basic | BASW.09208011/05/DBE | 92 | 80 | 11 | 12 | 1488 | 1488 | 1488 | 0.035429 | 744 | 0.017714 | 1637 | 0.038976 | 1 | A17 | BASW0.09208011/05/DBE
Horizontal Wall | Basic | BASW.09208015/05 | 92 | 80 | 15 | 17 | 1505 | 1505 | 1505 | 0.035833 | 604 | 0.014381 | 1707 | 0.040643 | 1.319 | A17 | BASW0.09208015/05
Horizontal Wall | Basic | BASW.09208016/05 | 92 | 80 | 16 | 17 | 1903 | 1903 | 1903 | 0.04531 | 710 | 0.016905 | 2179 | 0.051881 | 1.422 | A17 | BASW0.09208016/05
Horizontal Wall | Basic | BASW.09208016/05/DBE | 92 | 80 | 16 | 17 | 2383 | 2383 | 2383 | 0.056738 | 1192 | 0.028381 | 2621 | 0.062405 | 1 | A17 | BASW0.09208016/05/DBE
Horizontal Wall | Basic | BASW.09208020/05 | 92 | 80 | 20 | 22 | 2006 | 2006 | 2006 | 0.047762 | 828 | 0.019714 | 2265 | 0.053929 | 1.277 | A17 | BASW0.09208020/05
Horizontal Wall | Basic | BASW.09208021/05 | 92 | 80 | 21 | 22 | 2597 | 2597 | 2597 | 0.061833 | 956 | 0.022762 | 2979 | 0.070929 | 1.441 | A17 | BASW0.09208021/05
Horizontal Wall | Basic | BASW.09208021/05/DBE | 92 | 80 | 21 | 22 | 3077 | 3077 | 3077 | 0.073262 | 1539 | 0.036643 | 3385 | 0.080595 | 1 | A17 | BASW0.09208021/05/DBE
Horizontal Wall | Basic | BASW.09209010/05 | 92 | 90 | 10 | 12 | 1010 | 1010 | 1010 | 0.024048 | 399 | 0.0095 | 1147 | 0.02731 | 1.341 | A17 | BASW0.09209010/05
Horizontal Wall | Basic | BASW.09209011/05 | 92 | 90 | 11 | 12 | 1337 | 1337 | 1337 | 0.031833 | 507 | 0.012071 | 1528 | 0.036381 | 1.399 | A17 | BASW0.09209011/05
Horizontal Wall | Basic | BASW.09209011/05/DBE | 92 | 90 | 11 | 12 | 1937 | 1937 | 1937 | 0.046119 | 969 | 0.023071 | 2131 | 0.050738 | 1 | A17 | BASW0.09209011/05/DBE
Horizontal Wall | Basic | BASW.09209015/05 | 92 | 90 | 15 | 17 | 1693 | 1693 | 1693 | 0.04031 | 679 | 0.016167 | 1920 | 0.045714 | 1.319 | A17 | BASW0.09209015/05
Horizontal Wall | Basic | BASW.09209016/05 | 92 | 90 | 16 | 17 | 2141 | 2141 | 2141 | 0.050976 | 799 | 0.019024 | 2451 | 0.058357 | 1.422 | A17 | BASW0.09209016/05
Horizontal Wall | Basic | BASW.09209016/05/DBE | 92 | 90 | 16 | 17 | 3101 | 3101 | 3101 | 0.073833 | 1551 | 0.036929 | 3411 | 0.081214 | 1 | A17 | BASW0.09209016/05/DBE
Horizontal Wall | Basic | BASW.09209020/05 | 92 | 90 | 20 | 22 | 2257 | 2257 | 2257 | 0.053738 | 932 | 0.02219 | 2548 | 0.060667 | 1.277 | A17 | BASW0.09209020/05
Horizontal Wall | Basic | BASW.09209021/05 | 92 | 90 | 21 | 22 | 2921 | 2921 | 2921 | 0.069548 | 1075 | 0.025595 | 3350 | 0.079762 | 1.441 | A17 | BASW0.09209021/05
Horizontal Wall | Basic | BASW.09209021/05/DBE | 92 | 90 | 21 | 22 | 3881 | 3881 | 3881 | 0.092405 | 1941 | 0.046214 | 4269 | 0.10164 | 1 | A17 | BASW0.09209021/05/DBE
Horizontal Wall | Basic | BASW.09210010/05 | 92 | 100 | 10 | 12 | 1122 | 1122 | 1122 | 0.026714 | 443 | 0.010548 | 1275 | 0.030357 | 1.341 | A17 | BASW0.09210010/05
Horizontal Wall | Basic | BASW.09210011/05 | 92 | 100 | 11 | 12 | 1485 | 1485 | 1485 | 0.035357 | 563 | 0.013405 | 1697 | 0.040405 | 1.399 | A17 | BASW0.09210011/05
Horizontal Wall | Basic | BASW.09210011/05/DBE | 92 | 100 | 11 | 12 | 2085 | 2085 | 2085 | 0.049643 | 1043 | 0.024833 | 2294 | 0.054619 | 1 | A17 | BASW0.09210011/05/DBE
Horizontal Wall | Basic | BASW.09210015/05 | 92 | 100 | 15 | 17 | 1881 | 1881 | 1881 | 0.044786 | 754 | 0.017952 | 2133 | 0.050786 | 1.319 | A17 | BASW0.09210015/05
Horizontal Wall | Basic | BASW.09210016/05 | 92 | 100 | 16 | 17 | 2379 | 2379 | 2379 | 0.056643 | 887 | 0.021119 | 2724 | 0.064857 | 1.422 | A17 | BASW0.09210016/05
Horizontal Wall | Basic | BASW.09210016/05/DBE | 92 | 100 | 16 | 17 | 3339 | 3339 | 3339 | 0.0795 | 1670 | 0.039762 | 3673 | 0.087452 | 1 | A17 | BASW0.09210016/05/DBE
Horizontal Wall | Basic | BASW.09210020/05 | 92 | 100 | 20 | 22 | 2508 | 2508 | 2508 | 0.059714 | 1036 | 0.024667 | 2832 | 0.067429 | 1.277 | A17 | BASW0.09210020/05
Horizontal Wall | Basic | BASW.09210021/05 | 92 | 100 | 21 | 22 | 3246 | 3246 | 3246 | 0.077286 | 1195 | 0.028452 | 3723 | 0.088643 | 1.441 | A17 | BASW0.09210021/05
Horizontal Wall | Basic | BASW.09210021/05/DBE | 92 | 100 | 21 | 22 | 4206 | 4206 | 4206 | 0.10014 | 2103 | 0.050071 | 4627 | 0.11017 | 1 | A17 | BASW0.09210021/05/DBE
Horizontal Wall | Basic | BASW.09211010/05 | 92 | 110 | 10 | 12 | 1234 | 1234 | 1234 | 0.029381 | 487 | 0.011595 | 1402 | 0.033381 | 1.341 | A17 | BASW0.09211010/05
Horizontal Wall | Basic | BASW.09211011/05 | 92 | 110 | 11 | 12 | 1634 | 1634 | 1634 | 0.038905 | 619 | 0.014738 | 1868 | 0.044476 | 1.399 | A17 | BASW0.09211011/05
Horizontal Wall | Basic | BASW.09211011/05/DBE | 92 | 110 | 11 | 12 | 2234 | 2234 | 2234 | 0.05319 | 1117 | 0.026595 | 2457 | 0.0585 | 1 | A17 | BASW0.09211011/05/DBE
Horizontal Wall | Basic | BASW.09211015/05 | 92 | 110 | 15 | 17 | 2069 | 2069 | 2069 | 0.049262 | 830 | 0.019762 | 2346 | 0.055857 | 1.319 | A17 | BASW0.09211015/05
Horizontal Wall | Basic | BASW.09211016/05 | 92 | 110 | 16 | 17 | 2617 | 2617 | 2617 | 0.06231 | 976 | 0.023238 | 2996 | 0.071333 | 1.422 | A17 | BASW0.09211016/05
Horizontal Wall | Basic | BASW.09211016/05/DBE | 92 | 110 | 16 | 17 | 3577 | 3577 | 3577 | 0.085167 | 1789 | 0.042595 | 3935 | 0.09369 | 1 | A17 | BASW0.09211016/05/DBE
Horizontal Wall | Basic | BASW.09211020/05 | 92 | 110 | 20 | 22 | 2759 | 2759 | 2759 | 0.06569 | 1139 | 0.027119 | 3115 | 0.074167 | 1.277 | A17 | BASW0.09211020/05
Horizontal Wall | Basic | BASW.09211021/05 | 92 | 110 | 21 | 22 | 3571 | 3571 | 3571 | 0.085024 | 1314 | 0.031286 | 4096 | 0.097524 | 1.441 | A17 | BASW0.09211021/05
Horizontal Wall | Basic | BASW.09211021/05/DBE | 92 | 110 | 21 | 22 | 4531 | 4531 | 4531 | 0.10788 | 2266 | 0.053952 | 4984 | 0.11867 | 1 | A17 | BASW0.09211021/05/DBE
Horizontal Wall | Basic | BASW.09212010/05 | 92 | 120 | 10 | 12 | 1346 | 1346 | 1346 | 0.032048 | 532 | 0.012667 | 1529 | 0.036405 | 1.341 | A17 | BASW0.09212010/05
Horizontal Wall | Basic | BASW.09212011/05 | 92 | 120 | 11 | 12 | 1782 | 1782 | 1782 | 0.042429 | 675 | 0.016071 | 2037 | 0.0485 | 1.399 | A17 | BASW0.09212011/05
Horizontal Wall | Basic | BASW.09212011/05/DBE | 92 | 120 | 11 | 12 | 2382 | 2382 | 2382 | 0.056714 | 1191 | 0.028357 | 2620 | 0.062381 | 1 | A17 | BASW0.09212011/05/DBE
Horizontal Wall | Basic | BASW.09212015/05 | 92 | 120 | 15 | 17 | 2257 | 2257 | 2257 | 0.053738 | 905 | 0.021548 | 2559 | 0.060929 | 1.319 | A17 | BASW0.09212015/05
Horizontal Wall | Basic | BASW.09212016/05 | 92 | 120 | 16 | 17 | 2855 | 2855 | 2855 | 0.067976 | 1065 | 0.025357 | 3269 | 0.077833 | 1.422 | A17 | BASW0.09212016/05
Horizontal Wall | Basic | BASW.09212016/05/DBE | 92 | 120 | 16 | 17 | 3815 | 3815 | 3815 | 0.090833 | 1908 | 0.045429 | 4197 | 0.099929 | 1 | A17 | BASW0.09212016/05/DBE
Horizontal Wall | Basic | BASW.09212020/05 | 92 | 120 | 20 | 22 | 3010 | 3010 | 3010 | 0.071667 | 1243 | 0.029595 | 3398 | 0.080905 | 1.277 | A17 | BASW0.09212020/05
Horizontal Wall | Basic | BASW.09212021/05 | 92 | 120 | 21 | 22 | 3895 | 3895 | 3895 | 0.092738 | 1433 | 0.034119 | 4468 | 0.10638 | 1.441 | A17 | BASW0.09212021/05
Horizontal Wall | Basic | BASW.09212021/05/DBE | 92 | 120 | 21 | 22 | 4855 | 4855 | 4855 | 0.1156 | 2428 | 0.05781 | 5341 | 0.12717 | 1 | A17 | BASW0.09212021/05/DBE
Horizontal Wall | Basic | BASW.09214010/05 | 92 | 140 | 10 | 12 | 1571 | 1571 | 1571 | 0.037405 | 621 | 0.014786 | 1785 | 0.0425 | 1.341 | A17 | BASW0.09214010/05
Horizontal Wall | Basic | BASW.09214011/05 | 92 | 140 | 11 | 12 | 2079 | 2079 | 2079 | 0.0495 | 788 | 0.018762 | 2376 | 0.056571 | 1.399 | A17 | BASW0.09214011/05
Horizontal Wall | Basic | BASW.09214011/05/DBE | 92 | 140 | 11 | 12 | 2679 | 2679 | 2679 | 0.063786 | 1340 | 0.031905 | 2947 | 0.070167 | 1 | A17 | BASW0.09214011/05/DBE
Horizontal Wall | Basic | BASW.09214015/05 | 92 | 140 | 15 | 17 | 2633 | 2633 | 2633 | 0.06269 | 1056 | 0.025143 | 2986 | 0.071095 | 1.319 | A17 | BASW0.09214015/05
Horizontal Wall | Basic | BASW.09214016/05 | 92 | 140 | 16 | 17 | 3331 | 3331 | 3331 | 0.07931 | 1242 | 0.029571 | 3814 | 0.09081 | 1.422 | A17 | BASW0.09214016/05
Horizontal Wall | Basic | BASW.09214016/05/DBE | 92 | 140 | 16 | 17 | 4291 | 4291 | 4291 | 0.10217 | 2146 | 0.051095 | 4720 | 0.11238 | 1 | A17 | BASW0.09214016/05/DBE
Horizontal Wall | Basic | BASW.09214020/05 | 92 | 140 | 20 | 22 | 3511 | 3511 | 3511 | 0.083595 | 1450 | 0.034524 | 3964 | 0.094381 | 1.277 | A17 | BASW0.09214020/05
Horizontal Wall | Basic | BASW.09214021/05 | 92 | 140 | 21 | 22 | 4544 | 4544 | 4544 | 0.10819 | 1672 | 0.03981 | 5212 | 0.1241 | 1.441 | A17 | BASW0.09214021/05
Horizontal Wall | Basic | BASW.09214021/05/DBE | 92 | 140 | 21 | 22 | 5504 | 5504 | 5504 | 0.13105 | 2752 | 0.065524 | 6054 | 0.14414 | 1 | A17 | BASW0.09214021/05/DBE
Build-In | Build-In Wall | BIWW.02004010 | 20 | 40 | 10 | 12 | 262 | 262 | 262 | 0.0062381 | 99 | 0.0023571 | 300 | 0.0071429 | 1.413 | A06 | BIWW0.02004010
Build-In | Build-In Wall | BIWW.02004015 | 20 | 40 | 15 | 17 | 436 | 436 | 436 | 0.010381 | 164 | 0.0039048 | 499 | 0.011881 | 1.408 | A06 | BIWW0.02004015
Build-In | Build-In Wall | BIWW.02004020 | 20 | 40 | 20 | 22 | 613 | 613 | 613 | 0.014595 | 231 | 0.0055 | 701 | 0.01669 | 1.408 | A06 | BIWW0.02004020
Build-In | Build-In Wall | BIWW.02005010 | 20 | 50 | 10 | 12 | 328 | 328 | 328 | 0.0078095 | 123 | 0.0029286 | 375 | 0.0089286 | 1.413 | A06 | BIWW0.02005010
Build-In | Build-In Wall | BIWW.02005015 | 20 | 50 | 15 | 17 | 545 | 545 | 545 | 0.012976 | 205 | 0.004881 | 623 | 0.014833 | 1.408 | A06 | BIWW0.02005015
Build-In | Build-In Wall | BIWW.02005020 | 20 | 50 | 20 | 22 | 766 | 766 | 766 | 0.018238 | 289 | 0.006881 | 876 | 0.020857 | 1.408 | A06 | BIWW0.02005020
Build-In | Build-In Wall | BIWW.02006010 | 20 | 60 | 10 | 12 | 393 | 393 | 393 | 0.0093571 | 148 | 0.0035238 | 450 | 0.010714 | 1.413 | A06 | BIWW0.02006010
Build-In | Build-In Wall | BIWW.02006015 | 20 | 60 | 15 | 17 | 654 | 654 | 654 | 0.015571 | 247 | 0.005881 | 748 | 0.01781 | 1.408 | A06 | BIWW0.02006015
Build-In | Build-In Wall | BIWW.02006020 | 20 | 60 | 20 | 22 | 919 | 919 | 919 | 0.021881 | 346 | 0.0082381 | 1051 | 0.025024 | 1.408 | A06 | BIWW0.02006020
Build-In | Build-In Wall | BIWW.02007010 | 20 | 70 | 10 | 12 | 459 | 459 | 459 | 0.010929 | 173 | 0.004119 | 525 | 0.0125 | 1.413 | A06 | BIWW0.02007010
Build-In | Build-In Wall | BIWW.02007015 | 20 | 70 | 15 | 17 | 763 | 763 | 763 | 0.018167 | 288 | 0.0068571 | 873 | 0.020786 | 1.408 | A06 | BIWW0.02007015
Build-In | Build-In Wall | BIWW.02007020 | 20 | 70 | 20 | 22 | 1072 | 1072 | 1072 | 0.025524 | 404 | 0.009619 | 1226 | 0.02919 | 1.408 | A06 | BIWW0.02007020
Build-In | Build-In Wall | BIWW.02008010 | 20 | 80 | 10 | 12 | 524 | 524 | 524 | 0.012476 | 197 | 0.0046905 | 599 | 0.014262 | 1.413 | A06 | BIWW0.02008010
Build-In | Build-In Wall | BIWW.02008015 | 20 | 80 | 15 | 17 | 872 | 872 | 872 | 0.020762 | 329 | 0.0078333 | 998 | 0.023762 | 1.408 | A06 | BIWW0.02008015
Build-In | Build-In Wall | BIWW.02008020 | 20 | 80 | 20 | 22 | 1226 | 1226 | 1226 | 0.02919 | 462 | 0.011 | 1403 | 0.033405 | 1.408 | A06 | BIWW0.02008020
Build-In | Build-In Wall | BIWW.02009010 | 20 | 90 | 10 | 12 | 590 | 590 | 590 | 0.014048 | 222 | 0.0052857 | 675 | 0.016071 | 1.413 | A06 | BIWW0.02009010
Build-In | Build-In Wall | BIWW.02009015 | 20 | 90 | 15 | 17 | 981 | 981 | 981 | 0.023357 | 370 | 0.0088095 | 1122 | 0.026714 | 1.408 | A06 | BIWW0.02009015
Build-In | Build-In Wall | BIWW.02009020 | 20 | 90 | 20 | 22 | 1379 | 1379 | 1379 | 0.032833 | 520 | 0.012381 | 1578 | 0.037571 | 1.408 | A06 | BIWW0.02009020
Build-In | Build-In Wall | BIWW.02010010 | 20 | 100 | 10 | 12 | 655 | 655 | 655 | 0.015595 | 246 | 0.0058571 | 749 | 0.017833 | 1.413 | A06 | BIWW0.02010010
Build-In | Build-In Wall | BIWW.02010015 | 20 | 100 | 15 | 17 | 1090 | 1090 | 1090 | 0.025952 | 411 | 0.0097857 | 1247 | 0.02969 | 1.408 | A06 | BIWW0.02010015
Build-In | Build-In Wall | BIWW.02010020 | 20 | 100 | 20 | 22 | 1532 | 1532 | 1532 | 0.036476 | 578 | 0.013762 | 1753 | 0.041738 | 1.408 | A06 | BIWW0.02010020
Build-In | Build-In Wall | BIWW.02011010 | 20 | 110 | 10 | 12 | 721 | 721 | 721 | 0.017167 | 271 | 0.0064524 | 825 | 0.019643 | 1.413 | A06 | BIWW0.02011010
Build-In | Build-In Wall | BIWW.02011015 | 20 | 110 | 15 | 17 | 1199 | 1199 | 1199 | 0.028548 | 452 | 0.010762 | 1372 | 0.032667 | 1.408 | A06 | BIWW0.02011015
Build-In | Build-In Wall | BIWW.02011020 | 20 | 110 | 20 | 22 | 1685 | 1685 | 1685 | 0.040119 | 635 | 0.015119 | 1928 | 0.045905 | 1.408 | A06 | BIWW0.02011020
Build-In | Build-In Wall | BIWW.02012010 | 20 | 120 | 10 | 12 | 786 | 786 | 786 | 0.018714 | 296 | 0.0070476 | 899 | 0.021405 | 1.413 | A06 | BIWW0.02012010
Build-In | Build-In Wall | BIWW.02012015 | 20 | 120 | 15 | 17 | 1308 | 1308 | 1308 | 0.031143 | 493 | 0.011738 | 1496 | 0.035619 | 1.408 | A06 | BIWW0.02012015
Build-In | Build-In Wall | BIWW.02012020 | 20 | 120 | 20 | 22 | 1838 | 1838 | 1838 | 0.043762 | 693 | 0.0165 | 2103 | 0.050071 | 1.408 | A06 | BIWW0.02012020
Build-In | Build-In Wall | BIWW.02014010 | 20 | 140 | 10 | 12 | 917 | 917 | 917 | 0.021833 | 345 | 0.0082143 | 1049 | 0.024976 | 1.413 | A06 | BIWW0.02014010
Build-In | Build-In Wall | BIWW.02014015 | 20 | 140 | 15 | 17 | 1526 | 1526 | 1526 | 0.036333 | 575 | 0.01369 | 1746 | 0.041571 | 1.408 | A06 | BIWW0.02014015
Build-In | Build-In Wall | BIWW.02014020 | 20 | 140 | 20 | 22 | 2145 | 2145 | 2145 | 0.051071 | 809 | 0.019262 | 2454 | 0.058429 | 1.408 | A06 | BIWW0.02014020
Build-In | Build-In Wall | BIWW.02016010 | 20 | 160 | 10 | 12 | 1048 | 1048 | 1048 | 0.024952 | 394 | 0.009381 | 1199 | 0.028548 | 1.413 | A06 | BIWW0.02016010
Build-In | Build-In Wall | BIWW.02016015 | 20 | 160 | 15 | 17 | 1744 | 1744 | 1744 | 0.041524 | 657 | 0.015643 | 1995 | 0.0475 | 1.408 | A06 | BIWW0.02016015
Build-In | Build-In Wall | BIWW.02016020 | 20 | 160 | 20 | 22 | 2451 | 2451 | 2451 | 0.058357 | 924 | 0.022 | 2804 | 0.066762 | 1.408 | A06 | BIWW0.02016020
Build-In | Build-In Wall | BIWW.02018010 | 20 | 180 | 10 | 12 | 1179 | 1179 | 1179 | 0.028071 | 443 | 0.010548 | 1349 | 0.032119 | 1.413 | A06 | BIWW0.02018010
Build-In | Build-In Wall | BIWW.02018015 | 20 | 180 | 15 | 17 | 1962 | 1962 | 1962 | 0.046714 | 740 | 0.017619 | 2245 | 0.053452 | 1.408 | A06 | BIWW0.02018015
Build-In | Build-In Wall | BIWW.02018020 | 20 | 180 | 20 | 22 | 2758 | 2758 | 2758 | 0.065667 | 1040 | 0.024762 | 3155 | 0.075119 | 1.408 | A06 | BIWW0.02018020
Build-In | Build-In Wall | BIWW.02020010 | 20 | 200 | 10 | 12 | 1310 | 1310 | 1310 | 0.03119 | 493 | 0.011738 | 1499 | 0.03569 | 1.413 | A06 | BIWW0.02020010
Build-In | Build-In Wall | BIWW.02020015 | 20 | 200 | 15 | 17 | 2180 | 2180 | 2180 | 0.051905 | 822 | 0.019571 | 2494 | 0.059381 | 1.408 | A06 | BIWW0.02020015
Build-In | Build-In Wall | BIWW.02020020 | 20 | 200 | 20 | 22 | 3064 | 3064 | 3064 | 0.072952 | 1155 | 0.0275 | 3505 | 0.083452 | 1.408 | A06 | BIWW0.02020020
Build-In | Build-In Wall | BIWW.02022010 | 20 | 220 | 10 | 12 | 1441 | 1441 | 1441 | 0.03431 | 542 | 0.012905 | 1649 | 0.039262 | 1.413 | A06 | BIWW0.02022010
Build-In | Build-In Wall | BIWW.02022015 | 20 | 220 | 15 | 17 | 2398 | 2398 | 2398 | 0.057095 | 904 | 0.021524 | 2743 | 0.06531 | 1.408 | A06 | BIWW0.02022015
Build-In | Build-In Wall | BIWW.02022020 | 20 | 220 | 20 | 22 | 3370 | 3370 | 3370 | 0.080238 | 1270 | 0.030238 | 3855 | 0.091786 | 1.408 | A06 | BIWW0.02022020
Build-In | Build-In Wall | BIWW.02024010 | 20 | 240 | 10 | 12 | 1572 | 1572 | 1572 | 0.037429 | 591 | 0.014071 | 1798 | 0.04281 | 1.413 | A06 | BIWW0.02024010
Build-In | Build-In Wall | BIWW.02024015 | 20 | 240 | 15 | 17 | 2616 | 2616 | 2616 | 0.062286 | 986 | 0.023476 | 2993 | 0.071262 | 1.408 | A06 | BIWW0.02024015
Build-In | Build-In Wall | BIWW.02024020 | 20 | 240 | 20 | 22 | 3677 | 3677 | 3677 | 0.087548 | 1386 | 0.033 | 4206 | 0.10014 | 1.408 | A06 | BIWW0.02024020
Build-In | Build-In Wall | BIWW.02026010 | 20 | 260 | 10 | 12 | 1703 | 1703 | 1703 | 0.040548 | 640 | 0.015238 | 1948 | 0.046381 | 1.413 | A06 | BIWW0.02026010
Build-In | Build-In Wall | BIWW.02026015 | 20 | 260 | 15 | 17 | 2834 | 2834 | 2834 | 0.067476 | 1068 | 0.025429 | 3242 | 0.07719 | 1.408 | A06 | BIWW0.02026015
Build-In | Build-In Wall | BIWW.02026020 | 20 | 260 | 20 | 22 | 3983 | 3983 | 3983 | 0.094833 | 1502 | 0.035762 | 4557 | 0.1085 | 1.408 | A06 | BIWW0.02026020
Build-In | Build-In Wall | BIWW.02028010 | 20 | 280 | 10 | 12 | 1834 | 1834 | 1834 | 0.043667 | 690 | 0.016429 | 2098 | 0.049952 | 1.413 | A06 | BIWW0.02028010
Build-In | Build-In Wall | BIWW.02028015 | 20 | 280 | 15 | 17 | 3052 | 3052 | 3052 | 0.072667 | 1151 | 0.027405 | 3491 | 0.083119 | 1.408 | A06 | BIWW0.02028015
Build-In | Build-In Wall | BIWW.02028020 | 20 | 280 | 20 | 22 | 4290 | 4290 | 4290 | 0.10214 | 1617 | 0.0385 | 4908 | 0.11686 | 1.408 | A06 | BIWW0.02028020
Build-In | Build-In Wall | BIWW.02030010 | 20 | 300 | 10 | 12 | 1965 | 1965 | 1965 | 0.046786 | 739 | 0.017595 | 2248 | 0.053524 | 1.413 | A06 | BIWW0.02030010
Build-In | Build-In Wall | BIWW.02030015 | 20 | 300 | 15 | 17 | 3270 | 3270 | 3270 | 0.077857 | 1233 | 0.029357 | 3741 | 0.089071 | 1.408 | A06 | BIWW0.02030015
Build-In | Build-In Wall | BIWW.02030020 | 20 | 300 | 20 | 22 | 4596 | 4596 | 4596 | 0.10943 | 1733 | 0.041262 | 5258 | 0.12519 | 1.408 | A06 | BIWW0.02030020
Build-In | Build-In Wall | BIWW.03004010 | 30 | 40 | 10 | 12 | 330 | 330 | 330 | 0.0078571 | 125 | 0.0029762 | 377 | 0.0089762 | 1.403 | A06 | BIWW0.03004010
Build-In | Build-In Wall | BIWW.03004011 | 30 | 40 | 11 | 12 | 448 | 448 | 448 | 0.010667 | 165 | 0.0039286 | 514 | 0.012238 | 1.44 | A06 | BIWW0.03004011
Build-In | Build-In Wall | BIWW.03004015 | 30 | 40 | 15 | 17 | 544 | 544 | 544 | 0.012952 | 207 | 0.0049286 | 621 | 0.014786 | 1.396 | A06 | BIWW0.03004015
Build-In | Build-In Wall | BIWW.03004016 | 30 | 40 | 16 | 17 | 592 | 592 | 592 | 0.014095 | 216 | 0.0051429 | 680 | 0.01619 | 1.456 | A06 | BIWW0.03004016
Build-In | Build-In Wall | BIWW.03004020 | 30 | 40 | 20 | 22 | 762 | 762 | 762 | 0.018143 | 290 | 0.0069048 | 870 | 0.020714 | 1.396 | A06 | BIWW0.03004020
Build-In | Build-In Wall | BIWW.03004021 | 30 | 40 | 21 | 22 | 779 | 779 | 779 | 0.018548 | 281 | 0.0066905 | 896 | 0.021333 | 1.468 | A06 | BIWW0.03004021
Build-In | Build-In Wall | BIWW.03005010 | 30 | 50 | 10 | 12 | 413 | 413 | 413 | 0.0098333 | 156 | 0.0037143 | 472 | 0.011238 | 1.403 | A06 | BIWW0.03005010
Build-In | Build-In Wall | BIWW.03005011 | 30 | 50 | 11 | 12 | 561 | 561 | 561 | 0.013357 | 207 | 0.0049286 | 643 | 0.01531 | 1.44 | A06 | BIWW0.03005011
Build-In | Build-In Wall | BIWW.03005015 | 30 | 50 | 15 | 17 | 680 | 680 | 680 | 0.01619 | 258 | 0.0061429 | 777 | 0.0185 | 1.396 | A06 | BIWW0.03005015
Build-In | Build-In Wall | BIWW.03005016 | 30 | 50 | 16 | 17 | 740 | 740 | 740 | 0.017619 | 270 | 0.0064286 | 850 | 0.020238 | 1.456 | A06 | BIWW0.03005016
Build-In | Build-In Wall | BIWW.03005020 | 30 | 50 | 20 | 22 | 953 | 953 | 953 | 0.02269 | 362 | 0.008619 | 1088 | 0.025905 | 1.396 | A06 | BIWW0.03005020
Build-In | Build-In Wall | BIWW.03005021 | 30 | 50 | 21 | 22 | 974 | 974 | 974 | 0.02319 | 352 | 0.008381 | 1120 | 0.026667 | 1.468 | A06 | BIWW0.03005021
Build-In | Build-In Wall | BIWW.03006010 | 30 | 60 | 10 | 12 | 496 | 496 | 496 | 0.01181 | 187 | 0.0044524 | 567 | 0.0135 | 1.403 | A06 | BIWW0.03006010
Build-In | Build-In Wall | BIWW.03006011 | 30 | 60 | 11 | 12 | 673 | 673 | 673 | 0.016024 | 248 | 0.0059048 | 772 | 0.018381 | 1.44 | A06 | BIWW0.03006011
Build-In | Build-In Wall | BIWW.03006011/DBE | 30 | 60 | 11 | #N/A | 973 | 973 | 973 | 0.023167 | 487 | 0.011595 | 1070 | 0.025476 | 1 | A06 | BIWW0.03006011/DBE
Build-In | Build-In Wall | BIWW.03006015 | 30 | 60 | 15 | 17 | 815 | 815 | 815 | 0.019405 | 310 | 0.007381 | 931 | 0.022167 | 1.396 | A06 | BIWW0.03006015
Build-In | Build-In Wall | BIWW.03006016 | 30 | 60 | 16 | 17 | 888 | 888 | 888 | 0.021143 | 324 | 0.0077143 | 1020 | 0.024286 | 1.456 | A06 | BIWW0.03006016
Build-In | Build-In Wall | BIWW.03006016/DBE | 30 | 60 | 16 | #N/A | 1368 | 1368 | 1368 | 0.032571 | 684 | 0.016286 | 1505 | 0.035833 | 1 | A06 | BIWW0.03006016/DBE
Build-In | Build-In Wall | BIWW.03006020 | 30 | 60 | 20 | 22 | 1144 | 1144 | 1144 | 0.027238 | 435 | 0.010357 | 1306 | 0.031095 | 1.396 | A06 | BIWW0.03006020
Build-In | Build-In Wall | BIWW.03006021 | 30 | 60 | 21 | 22 | 1169 | 1169 | 1169 | 0.027833 | 422 | 0.010048 | 1344 | 0.032 | 1.468 | A06 | BIWW0.03006021
Build-In | Build-In Wall | BIWW.03006021/DBE | 30 | 60 | 21 | #N/A | 1649 | 1649 | 1649 | 0.039262 | 825 | 0.019643 | 1814 | 0.04319 | 1 | A06 | BIWW0.03006021/DBE
Build-In | Build-In Wall | BIWW.03007010 | 30 | 70 | 10 | 12 | 578 | 578 | 578 | 0.013762 | 218 | 0.0051905 | 661 | 0.015738 | 1.403 | A06 | BIWW0.03007010
Build-In | Build-In Wall | BIWW.03007011 | 30 | 70 | 11 | 12 | 785 | 785 | 785 | 0.01869 | 290 | 0.0069048 | 900 | 0.021429 | 1.44 | A06 | BIWW0.03007011
Build-In | Build-In Wall | BIWW.03007011/DBE | 30 | 70 | 11 | #N/A | 1085 | 1085 | 1085 | 0.025833 | 543 | 0.012929 | 1194 | 0.028429 | 1 | A06 | BIWW0.03007011/DBE
Build-In | Build-In Wall | BIWW.03007015 | 30 | 70 | 15 | 17 | 951 | 951 | 951 | 0.022643 | 361 | 0.0085952 | 1086 | 0.025857 | 1.396 | A06 | BIWW0.03007015
Build-In | Build-In Wall | BIWW.03007016 | 30 | 70 | 16 | 17 | 1036 | 1036 | 1036 | 0.024667 | 378 | 0.009 | 1190 | 0.028333 | 1.456 | A06 | BIWW0.03007016
Build-In | Build-In Wall | BIWW.03007016/DBE | 30 | 70 | 16 | #N/A | 1516 | 1516 | 1516 | 0.036095 | 758 | 0.018048 | 1668 | 0.039714 | 1 | A06 | BIWW0.03007016/DBE
Build-In | Build-In Wall | BIWW.03007020 | 30 | 70 | 20 | 22 | 1334 | 1334 | 1334 | 0.031762 | 507 | 0.012071 | 1523 | 0.036262 | 1.396 | A06 | BIWW0.03007020
Build-In | Build-In Wall | BIWW.03007021 | 30 | 70 | 21 | 22 | 1364 | 1364 | 1364 | 0.032476 | 492 | 0.011714 | 1569 | 0.037357 | 1.468 | A06 | BIWW0.03007021
Build-In | Build-In Wall | BIWW.03007021/DBE | 30 | 70 | 21 | #N/A | 1844 | 1844 | 1844 | 0.043905 | 922 | 0.021952 | 2028 | 0.048286 | 1 | A06 | BIWW0.03007021/DBE
Build-In | Build-In Wall | BIWW.03008010 | 30 | 80 | 10 | 12 | 661 | 661 | 661 | 0.015738 | 250 | 0.0059524 | 756 | 0.018 | 1.403 | A06 | BIWW0.03008010
Build-In | Build-In Wall | BIWW.03008011 | 30 | 80 | 11 | 12 | 897 | 897 | 897 | 0.021357 | 331 | 0.007881 | 1029 | 0.0245 | 1.44 | A06 | BIWW0.03008011
Build-In | Build-In Wall | BIWW.03008011/DBE | 30 | 80 | 11 | #N/A | 1197 | 1197 | 1197 | 0.0285 | 599 | 0.014262 | 1317 | 0.031357 | 1 | A06 | BIWW0.03008011/DBE
Build-In | Build-In Wall | BIWW.03008015 | 30 | 80 | 15 | 17 | 1087 | 1087 | 1087 | 0.025881 | 413 | 0.0098333 | 1241 | 0.029548 | 1.396 | A06 | BIWW0.03008015
Build-In | Build-In Wall | BIWW.03008016 | 30 | 80 | 16 | 17 | 1184 | 1184 | 1184 | 0.02819 | 432 | 0.010286 | 1360 | 0.032381 | 1.456 | A06 | BIWW0.03008016
Build-In | Build-In Wall | BIWW.03008016/DBE | 30 | 80 | 16 | #N/A | 1664 | 1664 | 1664 | 0.039619 | 832 | 0.01981 | 1830 | 0.043571 | 1 | A06 | BIWW0.03008016/DBE
Build-In | Build-In Wall | BIWW.03008020 | 30 | 80 | 20 | 22 | 1525 | 1525 | 1525 | 0.03631 | 580 | 0.01381 | 1742 | 0.041476 | 1.396 | A06 | BIWW0.03008020
Build-In | Build-In Wall | BIWW.03008021 | 30 | 80 | 21 | 22 | 1558 | 1558 | 1558 | 0.037095 | 562 | 0.013381 | 1792 | 0.042667 | 1.468 | A06 | BIWW0.03008021
Build-In | Build-In Wall | BIWW.03008021/DBE | 30 | 80 | 21 | #N/A | 2038 | 2038 | 2038 | 0.048524 | 1019 | 0.024262 | 2242 | 0.053381 | 1 | A06 | BIWW0.03008021/DBE
Build-In | Build-In Wall | BIWW.03009010 | 30 | 90 | 10 | 12 | 743 | 743 | 743 | 0.01769 | 281 | 0.0066905 | 849 | 0.020214 | 1.403 | A06 | BIWW0.03009010
Build-In | Build-In Wall | BIWW.03009011 | 30 | 90 | 11 | 12 | 1009 | 1009 | 1009 | 0.024024 | 372 | 0.0088571 | 1157 | 0.027548 | 1.44 | A06 | BIWW0.03009011
Build-In | Build-In Wall | BIWW.03009011/DBE | 30 | 90 | 11 | #N/A | 1609 | 1609 | 1609 | 0.03831 | 805 | 0.019167 | 1770 | 0.042143 | 1 | A06 | BIWW0.03009011/DBE
Build-In | Build-In Wall | BIWW.03009015 | 30 | 90 | 15 | 17 | 1223 | 1223 | 1223 | 0.029119 | 465 | 0.011071 | 1397 | 0.033262 | 1.396 | A06 | BIWW0.03009015
Build-In | Build-In Wall | BIWW.03009016 | 30 | 90 | 16 | 17 | 1332 | 1332 | 1332 | 0.031714 | 486 | 0.011571 | 1530 | 0.036429 | 1.456 | A06 | BIWW0.03009016
Build-In | Build-In Wall | BIWW.03009016/DBE | 30 | 90 | 16 | #N/A | 2292 | 2292 | 2292 | 0.054571 | 1146 | 0.027286 | 2521 | 0.060024 | 1 | A06 | BIWW0.03009016/DBE
Build-In | Build-In Wall | BIWW.03009020 | 30 | 90 | 20 | 22 | 1715 | 1715 | 1715 | 0.040833 | 652 | 0.015524 | 1959 | 0.046643 | 1.396 | A06 | BIWW0.03009020
Build-In | Build-In Wall | BIWW.03009021 | 30 | 90 | 21 | 22 | 1753 | 1753 | 1753 | 0.041738 | 633 | 0.015071 | 2016 | 0.048 | 1.468 | A06 | BIWW0.03009021
Build-In | Build-In Wall | BIWW.03009021/DBE | 30 | 90 | 21 | #N/A | 2713 | 2713 | 2713 | 0.064595 | 1357 | 0.03231 | 2984 | 0.071048 | 1 | A06 | BIWW0.03009021/DBE
Build-In | Build-In Wall | BIWW.03010010 | 30 | 100 | 10 | 12 | 826 | 826 | 826 | 0.019667 | 312 | 0.0074286 | 944 | 0.022476 | 1.403 | A06 | BIWW0.03010010
Build-In | Build-In Wall | BIWW.03010011 | 30 | 100 | 11 | 12 | 1121 | 1121 | 1121 | 0.02669 | 414 | 0.0098571 | 1286 | 0.030619 | 1.44 | A06 | BIWW0.03010011
Build-In | Build-In Wall | BIWW.03010011/DBE | 30 | 100 | 11 | #N/A | 1721 | 1721 | 1721 | 0.040976 | 861 | 0.0205 | 1893 | 0.045071 | 1 | A06 | BIWW0.03010011/DBE
Build-In | Build-In Wall | BIWW.03010015 | 30 | 100 | 15 | 17 | 1359 | 1359 | 1359 | 0.032357 | 516 | 0.012286 | 1552 | 0.036952 | 1.396 | A06 | BIWW0.03010015
Build-In | Build-In Wall | BIWW.03010016 | 30 | 100 | 16 | 17 | 1480 | 1480 | 1480 | 0.035238 | 540 | 0.012857 | 1701 | 0.0405 | 1.456 | A06 | BIWW0.03010016
Build-In | Build-In Wall | BIWW.03010016/DBE | 30 | 100 | 16 | #N/A | 2440 | 2440 | 2440 | 0.058095 | 1220 | 0.029048 | 2684 | 0.063905 | 1 | A06 | BIWW0.03010016/DBE
Build-In | Build-In Wall | BIWW.03010020 | 30 | 100 | 20 | 22 | 1906 | 1906 | 1906 | 0.045381 | 724 | 0.017238 | 2177 | 0.051833 | 1.396 | A06 | BIWW0.03010020
Build-In | Build-In Wall | BIWW.03010021 | 30 | 100 | 21 | 22 | 1948 | 1948 | 1948 | 0.046381 | 703 | 0.016738 | 2240 | 0.053333 | 1.468 | A06 | BIWW0.03010021
Build-In | Build-In Wall | BIWW.03010021/DBE | 30 | 100 | 21 | #N/A | 2908 | 2908 | 2908 | 0.069238 | 1454 | 0.034619 | 3199 | 0.076167 | 1 | A06 | BIWW0.03010021/DBE
Build-In | Build-In Wall | BIWW.03011010 | 30 | 110 | 10 | 12 | 909 | 909 | 909 | 0.021643 | 344 | 0.0081905 | 1039 | 0.024738 | 1.403 | A06 | BIWW0.03011010
Build-In | Build-In Wall | BIWW.03011011 | 30 | 110 | 11 | 12 | 1233 | 1233 | 1233 | 0.029357 | 455 | 0.010833 | 1414 | 0.033667 | 1.44 | A06 | BIWW0.03011011
Build-In | Build-In Wall | BIWW.03011011/DBE | 30 | 110 | 11 | #N/A | 1833 | 1833 | 1833 | 0.043643 | 917 | 0.021833 | 2016 | 0.048 | 1 | A06 | BIWW0.03011011/DBE
Build-In | Build-In Wall | BIWW.03011015 | 30 | 110 | 15 | 17 | 1495 | 1495 | 1495 | 0.035595 | 568 | 0.013524 | 1707 | 0.040643 | 1.396 | A06 | BIWW0.03011015
Build-In | Build-In Wall | BIWW.03011016 | 30 | 110 | 16 | 17 | 1628 | 1628 | 1628 | 0.038762 | 594 | 0.014143 | 1871 | 0.044548 | 1.456 | A06 | BIWW0.03011016
Build-In | Build-In Wall | BIWW.03011016/DBE | 30 | 110 | 16 | #N/A | 2588 | 2588 | 2588 | 0.061619 | 1294 | 0.03081 | 2847 | 0.067786 | 1 | A06 | BIWW0.03011016/DBE
Build-In | Build-In Wall | BIWW.03011020 | 30 | 110 | 20 | 22 | 2097 | 2097 | 2097 | 0.049929 | 797 | 0.018976 | 2395 | 0.057024 | 1.396 | A06 | BIWW0.03011020
Build-In | Build-In Wall | BIWW.03011021 | 30 | 110 | 21 | 22 | 2143 | 2143 | 2143 | 0.051024 | 774 | 0.018429 | 2464 | 0.058667 | 1.468 | A06 | BIWW0.03011021
Build-In | Build-In Wall | BIWW.03011021/DBE | 30 | 110 | 21 | #N/A | 3103 | 3103 | 3103 | 0.073881 | 1552 | 0.036952 | 3413 | 0.081262 | 1 | A06 | BIWW0.03011021/DBE
Build-In | Build-In Wall | BIWW.03012010 | 30 | 120 | 10 | 12 | 991 | 991 | 991 | 0.023595 | 375 | 0.0089286 | 1133 | 0.026976 | 1.403 | A06 | BIWW0.03012010
Build-In | Build-In Wall | BIWW.03012011 | 30 | 120 | 11 | 12 | 1345 | 1345 | 1345 | 0.032024 | 496 | 0.01181 | 1543 | 0.036738 | 1.44 | A06 | BIWW0.03012011
Build-In | Build-In Wall | BIWW.03012011/DBE | 30 | 120 | 11 | #N/A | 1945 | 1945 | 1945 | 0.04631 | 973 | 0.023167 | 2140 | 0.050952 | 1 | A06 | BIWW0.03012011/DBE
Build-In | Build-In Wall | BIWW.03012015 | 30 | 120 | 15 | 17 | 1631 | 1631 | 1631 | 0.038833 | 620 | 0.014762 | 1863 | 0.044357 | 1.396 | A06 | BIWW0.03012015
Build-In | Build-In Wall | BIWW.03012016 | 30 | 120 | 16 | 17 | 1776 | 1776 | 1776 | 0.042286 | 648 | 0.015429 | 2041 | 0.048595 | 1.456 | A06 | BIWW0.03012016
Build-In | Build-In Wall | BIWW.03012016/DBE | 30 | 120 | 16 | #N/A | 2736 | 2736 | 2736 | 0.065143 | 1368 | 0.032571 | 3010 | 0.071667 | 1 | A06 | BIWW0.03012016/DBE
Build-In | Build-In Wall | BIWW.03012020 | 30 | 120 | 20 | 22 | 2287 | 2287 | 2287 | 0.054452 | 869 | 0.02069 | 2612 | 0.06219 | 1.396 | A06 | BIWW0.03012020
Build-In | Build-In Wall | BIWW.03012021 | 30 | 120 | 21 | 22 | 2338 | 2338 | 2338 | 0.055667 | 844 | 0.020095 | 2689 | 0.064024 | 1.468 | A06 | BIWW0.03012021
Build-In | Build-In Wall | BIWW.03012021/DBE | 30 | 120 | 21 | #N/A | 3298 | 3298 | 3298 | 0.078524 | 1649 | 0.039262 | 3628 | 0.086381 | 1 | A06 | BIWW0.03012021/DBE
Build-In | Build-In Wall | BIWW.03014010 | 30 | 140 | 10 | 12 | 1156 | 1156 | 1156 | 0.027524 | 437 | 0.010405 | 1321 | 0.031452 | 1.403 | A06 | BIWW0.03014010
Build-In | Build-In Wall | BIWW.03014011 | 30 | 140 | 11 | 12 | 1569 | 1569 | 1569 | 0.037357 | 579 | 0.013786 | 1800 | 0.042857 | 1.44 | A06 | BIWW0.03014011
Build-In | Build-In Wall | BIWW.03014011/DBE | 30 | 140 | 11 | #N/A | 2169 | 2169 | 2169 | 0.051643 | 1085 | 0.025833 | 2386 | 0.05681 | 1 | A06 | BIWW0.03014011/DBE
Build-In | Build-In Wall | BIWW.03014015 | 30 | 140 | 15 | 17 | 1903 | 1903 | 1903 | 0.04531 | 723 | 0.017214 | 2173 | 0.051738 | 1.396 | A06 | BIWW0.03014015
Build-In | Build-In Wall | BIWW.03014016 | 30 | 140 | 16 | 17 | 2072 | 2072 | 2072 | 0.049333 | 756 | 0.018 | 2381 | 0.05669 | 1.456 | A06 | BIWW0.03014016
Build-In | Build-In Wall | BIWW.03014016/DBE | 30 | 140 | 16 | #N/A | 3032 | 3032 | 3032 | 0.07219 | 1516 | 0.036095 | 3335 | 0.079405 | 1 | A06 | BIWW0.03014016/DBE
Build-In | Build-In Wall | BIWW.03014020 | 30 | 140 | 20 | 22 | 2668 | 2668 | 2668 | 0.063524 | 1014 | 0.024143 | 3047 | 0.072548 | 1.396 | A06 | BIWW0.03014020
Build-In | Build-In Wall | BIWW.03014021 | 30 | 140 | 21 | 22 | 2727 | 2727 | 2727 | 0.064929 | 984 | 0.023429 | 3136 | 0.074667 | 1.468 | A06 | BIWW0.03014021
Build-In | Build-In Wall | BIWW.03014021/DBE | 30 | 140 | 21 | #N/A | 3687 | 3687 | 3687 | 0.087786 | 1844 | 0.043905 | 4056 | 0.096571 | 1 | A06 | BIWW0.03014021/DBE
Build-In | Build-In Wall | BIWW.03016010 | 30 | 160 | 10 | 12 | 1322 | 1322 | 1322 | 0.031476 | 500 | 0.011905 | 1511 | 0.035976 | 1.403 | A06 | BIWW0.03016010
Build-In | Build-In Wall | BIWW.03016011 | 30 | 160 | 11 | 12 | 1794 | 1794 | 1794 | 0.042714 | 662 | 0.015762 | 2058 | 0.049 | 1.44 | A06 | BIWW0.03016011
Build-In | Build-In Wall | BIWW.03016011/DBE | 30 | 160 | 11 | #N/A | 2994 | 2994 | 2994 | 0.071286 | 1497 | 0.035643 | 3293 | 0.078405 | 1 | A06 | BIWW0.03016011/DBE
Build-In | Build-In Wall | BIWW.03016015 | 30 | 160 | 15 | 17 | 2174 | 2174 | 2174 | 0.051762 | 826 | 0.019667 | 2483 | 0.059119 | 1.396 | A06 | BIWW0.03016015
Build-In | Build-In Wall | BIWW.03016016 | 30 | 160 | 16 | 17 | 2368 | 2368 | 2368 | 0.056381 | 864 | 0.020571 | 2721 | 0.064786 | 1.456 | A06 | BIWW0.03016016
Build-In | Build-In Wall | BIWW.03016016/DBE | 30 | 160 | 16 | #N/A | 4288 | 4288 | 4288 | 0.1021 | 2144 | 0.051048 | 4717 | 0.11231 | 1 | A06 | BIWW0.03016016/DBE
Build-In | Build-In Wall | BIWW.03016020 | 30 | 160 | 20 | 22 | 3050 | 3050 | 3050 | 0.072619 | 1159 | 0.027595 | 3483 | 0.082929 | 1.396 | A06 | BIWW0.03016020
Build-In | Build-In Wall | BIWW.03016021 | 30 | 160 | 21 | 22 | 3117 | 3117 | 3117 | 0.074214 | 1125 | 0.026786 | 3585 | 0.085357 | 1.468 | A06 | BIWW0.03016021
Build-In | Build-In Wall | BIWW.03016021/DBE | 30 | 160 | 21 | #N/A | 5037 | 5037 | 5037 | 0.11993 | 2519 | 0.059976 | 5541 | 0.13193 | 1 | A06 | BIWW0.03016021/DBE
Build-In | Build-In Wall | BIWW.03018010 | 30 | 180 | 10 | 12 | 1487 | 1487 | 1487 | 0.035405 | 562 | 0.013381 | 1700 | 0.040476 | 1.403 | A06 | BIWW0.03018010
Build-In | Build-In Wall | BIWW.03018011 | 30 | 180 | 11 | 12 | 2018 | 2018 | 2018 | 0.048048 | 745 | 0.017738 | 2315 | 0.055119 | 1.44 | A06 | BIWW0.03018011
Build-In | Build-In Wall | BIWW.03018011/DBE | 30 | 180 | 11 | #N/A | 3218 | 3218 | 3218 | 0.076619 | 1609 | 0.03831 | 3540 | 0.084286 | 1 | A06 | BIWW0.03018011/DBE
Build-In | Build-In Wall | BIWW.03018015 | 30 | 180 | 15 | 17 | 2446 | 2446 | 2446 | 0.058238 | 929 | 0.022119 | 2793 | 0.0665 | 1.396 | A06 | BIWW0.03018015
Build-In | Build-In Wall | BIWW.03018016 | 30 | 180 | 16 | 17 | 2664 | 2664 | 2664 | 0.063429 | 972 | 0.023143 | 3061 | 0.072881 | 1.456 | A06 | BIWW0.03018016
Build-In | Build-In Wall | BIWW.03018016/DBE | 30 | 180 | 16 | #N/A | 4584 | 4584 | 4584 | 0.10914 | 2292 | 0.054571 | 5042 | 0.12005 | 1 | A06 | BIWW0.03018016/DBE
Build-In | Build-In Wall | BIWW.03018020 | 30 | 180 | 20 | 22 | 3431 | 3431 | 3431 | 0.08169 | 1304 | 0.031048 | 3918 | 0.093286 | 1.396 | A06 | BIWW0.03018020
Build-In | Build-In Wall | BIWW.03018021 | 30 | 180 | 21 | 22 | 3506 | 3506 | 3506 | 0.083476 | 1266 | 0.030143 | 4032 | 0.096 | 1.468 | A06 | BIWW0.03018021
Build-In | Build-In Wall | BIWW.03018021/DBE | 30 | 180 | 21 | #N/A | 5426 | 5426 | 5426 | 0.12919 | 2713 | 0.064595 | 5969 | 0.14212 | 1 | A06 | BIWW0.03018021/DBE
Build-In | Build-In Wall | BIWW.03020010 | 30 | 200 | 10 | 12 | 1652 | 1652 | 1652 | 0.039333 | 624 | 0.014857 | 1888 | 0.044952 | 1.403 | A06 | BIWW0.03020010
Build-In | Build-In Wall | BIWW.03020011 | 30 | 200 | 11 | 12 | 2242 | 2242 | 2242 | 0.053381 | 827 | 0.01969 | 2572 | 0.061238 | 1.44 | A06 | BIWW0.03020011
Build-In | Build-In Wall | BIWW.03020011/DBE | 30 | 200 | 11 | #N/A | 3442 | 3442 | 3442 | 0.081952 | 1721 | 0.040976 | 3786 | 0.090143 | 1 | A06 | BIWW0.03020011/DBE
Build-In | Build-In Wall | BIWW.03020015 | 30 | 200 | 15 | 17 | 2718 | 2718 | 2718 | 0.064714 | 1033 | 0.024595 | 3104 | 0.073905 | 1.396 | A06 | BIWW0.03020015
Build-In | Build-In Wall | BIWW.03020016 | 30 | 200 | 16 | 17 | 2960 | 2960 | 2960 | 0.070476 | 1080 | 0.025714 | 3401 | 0.080976 | 1.456 | A06 | BIWW0.03020016
Build-In | Build-In Wall | BIWW.03020016/DBE | 30 | 200 | 16 | #N/A | 4880 | 4880 | 4880 | 0.11619 | 2440 | 0.058095 | 5368 | 0.12781 | 1 | A06 | BIWW0.03020016/DBE
Build-In | Build-In Wall | BIWW.03020020 | 30 | 200 | 20 | 22 | 3812 | 3812 | 3812 | 0.090762 | 1449 | 0.0345 | 4353 | 0.10364 | 1.396 | A06 | BIWW0.03020020
Build-In | Build-In Wall | BIWW.03020021 | 30 | 200 | 21 | 22 | 3896 | 3896 | 3896 | 0.092762 | 1406 | 0.033476 | 4480 | 0.10667 | 1.468 | A06 | BIWW0.03020021
Build-In | Build-In Wall | BIWW.03020021/DBE | 30 | 200 | 21 | #N/A | 5816 | 5816 | 5816 | 0.13848 | 2908 | 0.069238 | 6398 | 0.15233 | 1 | A06 | BIWW0.03020021/DBE
Build-In | Build-In Wall | BIWW.03022010 | 30 | 220 | 10 | 12 | 1817 | 1817 | 1817 | 0.043262 | 687 | 0.016357 | 2077 | 0.049452 | 1.403 | A06 | BIWW0.03022010
Build-In | Build-In Wall | BIWW.03022011 | 30 | 220 | 11 | 12 | 2466 | 2466 | 2466 | 0.058714 | 910 | 0.021667 | 2829 | 0.067357 | 1.44 | A06 | BIWW0.03022011
Build-In | Build-In Wall | BIWW.03022011/DBE | 30 | 220 | 11 | #N/A | 3666 | 3666 | 3666 | 0.087286 | 1833 | 0.043643 | 4033 | 0.096024 | 1 | A06 | BIWW0.03022011/DBE
Build-In | Build-In Wall | BIWW.03022015 | 30 | 220 | 15 | 17 | 2990 | 2990 | 2990 | 0.07119 | 1136 | 0.027048 | 3415 | 0.08131 | 1.396 | A06 | BIWW0.03022015
Build-In | Build-In Wall | BIWW.03022016 | 30 | 220 | 16 | 17 | 3256 | 3256 | 3256 | 0.077524 | 1188 | 0.028286 | 3741 | 0.089071 | 1.456 | A06 | BIWW0.03022016
Build-In | Build-In Wall | BIWW.03022016/DBE | 30 | 220 | 16 | #N/A | 5176 | 5176 | 5176 | 0.12324 | 2588 | 0.061619 | 5694 | 0.13557 | 1 | A06 | BIWW0.03022016/DBE
Build-In | Build-In Wall | BIWW.03022020 | 30 | 220 | 20 | 22 | 4193 | 4193 | 4193 | 0.099833 | 1593 | 0.037929 | 4788 | 0.114 | 1.396 | A06 | BIWW0.03022020
Build-In | Build-In Wall | BIWW.03022021 | 30 | 220 | 21 | 22 | 4286 | 4286 | 4286 | 0.10205 | 1547 | 0.036833 | 4929 | 0.11736 | 1.468 | A06 | BIWW0.03022021
Build-In | Build-In Wall | BIWW.03022021/DBE | 30 | 220 | 21 | #N/A | 6206 | 6206 | 6206 | 0.14776 | 3103 | 0.073881 | 6827 | 0.16255 | 1 | A06 | BIWW0.03022021/DBE
Build-In | Build-In Wall | BIWW.03024010 | 30 | 240 | 10 | 12 | 1982 | 1982 | 1982 | 0.04719 | 749 | 0.017833 | 2265 | 0.053929 | 1.403 | A06 | BIWW0.03024010
Build-In | Build-In Wall | BIWW.03024011 | 30 | 240 | 11 | 12 | 2690 | 2690 | 2690 | 0.064048 | 993 | 0.023643 | 3085 | 0.073452 | 1.44 | A06 | BIWW0.03024011
Build-In | Build-In Wall | BIWW.03024011/DBE | 30 | 240 | 11 | #N/A | 4490 | 4490 | 4490 | 0.1069 | 2245 | 0.053452 | 4939 | 0.1176 | 1 | A06 | BIWW0.03024011/DBE
Build-In | Build-In Wall | BIWW.03024015 | 30 | 240 | 15 | 17 | 3262 | 3262 | 3262 | 0.077667 | 1240 | 0.029524 | 3725 | 0.08869 | 1.396 | A06 | BIWW0.03024015
Build-In | Build-In Wall | BIWW.03024016 | 30 | 240 | 16 | 17 | 3552 | 3552 | 3552 | 0.084571 | 1296 | 0.030857 | 4081 | 0.097167 | 1.456 | A06 | BIWW0.03024016
Build-In | Build-In Wall | BIWW.03024016/DBE | 30 | 240 | 16 | #N/A | 6432 | 6432 | 6432 | 0.15314 | 3216 | 0.076571 | 7075 | 0.16845 | 1 | A06 | BIWW0.03024016/DBE
Build-In | Build-In Wall | BIWW.03024020 | 30 | 240 | 20 | 22 | 4574 | 4574 | 4574 | 0.1089 | 1738 | 0.041381 | 5224 | 0.12438 | 1.396 | A06 | BIWW0.03024020
Build-In | Build-In Wall | BIWW.03024021 | 30 | 240 | 21 | 22 | 4675 | 4675 | 4675 | 0.11131 | 1688 | 0.04019 | 5376 | 0.128 | 1.468 | A06 | BIWW0.03024021
Build-In | Build-In Wall | BIWW.03024021/DBE | 30 | 240 | 21 | #N/A | 7555 | 7555 | 7555 | 0.17988 | 3778 | 0.089952 | 8311 | 0.19788 | 1 | A06 | BIWW0.03024021/DBE
Build-In | Build-In Wall | BIWW.03026010 | 30 | 260 | 10 | 12 | 2148 | 2148 | 2148 | 0.051143 | 812 | 0.019333 | 2455 | 0.058452 | 1.403 | A06 | BIWW0.03026010
Build-In | Build-In Wall | BIWW.03026011 | 30 | 260 | 11 | 12 | 2915 | 2915 | 2915 | 0.069405 | 1076 | 0.025619 | 3344 | 0.079619 | 1.44 | A06 | BIWW0.03026011
Build-In | Build-In Wall | BIWW.03026011/DBE | 30 | 260 | 11 | #N/A | 4715 | 4715 | 4715 | 0.11226 | 2358 | 0.056143 | 5187 | 0.1235 | 1 | A06 | BIWW0.03026011/DBE
Build-In | Build-In Wall | BIWW.03026015 | 30 | 260 | 15 | 17 | 3533 | 3533 | 3533 | 0.084119 | 1343 | 0.031976 | 4035 | 0.096071 | 1.396 | A06 | BIWW0.03026015
Build-In | Build-In Wall | BIWW.03026016 | 30 | 260 | 16 | 17 | 3848 | 3848 | 3848 | 0.091619 | 1405 | 0.033452 | 4421 | 0.10526 | 1.456 | A06 | BIWW0.03026016
Build-In | Build-In Wall | BIWW.03026016/DBE | 30 | 260 | 16 | #N/A | 6728 | 6728 | 6728 | 0.16019 | 3364 | 0.080095 | 7401 | 0.17621 | 1 | A06 | BIWW0.03026016/DBE
Build-In | Build-In Wall | BIWW.03026020 | 30 | 260 | 20 | 22 | 4956 | 4956 | 4956 | 0.118 | 1883 | 0.044833 | 5660 | 0.13476 | 1.396 | A06 | BIWW0.03026020
Build-In | Build-In Wall | BIWW.03026021 | 30 | 260 | 21 | 22 | 5065 | 5065 | 5065 | 0.1206 | 1828 | 0.043524 | 5825 | 0.13869 | 1.468 | A06 | BIWW0.03026021
Build-In | Build-In Wall | BIWW.03026021/DBE | 30 | 260 | 21 | #N/A | 7945 | 7945 | 7945 | 0.18917 | 3973 | 0.094595 | 8740 | 0.2081 | 1 | A06 | BIWW0.03026021/DBE
Build-In | Build-In Wall | BIWW.03028010 | 30 | 280 | 10 | 12 | 2313 | 2313 | 2313 | 0.055071 | 874 | 0.02081 | 2644 | 0.062952 | 1.403 | A06 | BIWW0.03028010
Build-In | Build-In Wall | BIWW.03028011 | 30 | 280 | 11 | 12 | 3139 | 3139 | 3139 | 0.074738 | 1158 | 0.027571 | 3600 | 0.085714 | 1.44 | A06 | BIWW0.03028011
Build-In | Build-In Wall | BIWW.03028011/DBE | 30 | 280 | 11 | #N/A | 4939 | 4939 | 4939 | 0.1176 | 2470 | 0.05881 | 5433 | 0.12936 | 1 | A06 | BIWW0.03028011/DBE
Build-In | Build-In Wall | BIWW.03028015 | 30 | 280 | 15 | 17 | 3805 | 3805 | 3805 | 0.090595 | 1446 | 0.034429 | 4345 | 0.10345 | 1.396 | A06 | BIWW0.03028015
Build-In | Build-In Wall | BIWW.03028016 | 30 | 280 | 16 | 17 | 4144 | 4144 | 4144 | 0.098667 | 1513 | 0.036024 | 4761 | 0.11336 | 1.456 | A06 | BIWW0.03028016
Build-In | Build-In Wall | BIWW.03028016/DBE | 30 | 280 | 16 | #N/A | 7024 | 7024 | 7024 | 0.16724 | 3512 | 0.083619 | 7726 | 0.18395 | 1 | A06 | BIWW0.03028016/DBE
Build-In | Build-In Wall | BIWW.03028020 | 30 | 280 | 20 | 22 | 5337 | 5337 | 5337 | 0.12707 | 2028 | 0.048286 | 6095 | 0.14512 | 1.396 | A06 | BIWW0.03028020
Build-In | Build-In Wall | BIWW.03028021 | 30 | 280 | 21 | 22 | 5454 | 5454 | 5454 | 0.12986 | 1969 | 0.046881 | 6272 | 0.14933 | 1.468 | A06 | BIWW0.03028021
Build-In | Build-In Wall | BIWW.03028021/DBE | 30 | 280 | 21 | #N/A | 8334 | 8334 | 8334 | 0.19843 | 4167 | 0.099214 | 9167 | 0.21826 | 1 | A06 | BIWW0.03028021/DBE
Build-In | Build-In Wall | BIWW.03030010 | 30 | 300 | 10 | 12 | 2478 | 2478 | 2478 | 0.059 | 937 | 0.02231 | 2832 | 0.067429 | 1.403 | A06 | BIWW0.03030010
Build-In | Build-In Wall | BIWW.03030011 | 30 | 300 | 11 | 12 | 3363 | 3363 | 3363 | 0.080071 | 1241 | 0.029548 | 3857 | 0.091833 | 1.44 | A06 | BIWW0.03030011
Build-In | Build-In Wall | BIWW.03030011/DBE | 30 | 300 | 11 | #N/A | 5163 | 5163 | 5163 | 0.12293 | 2582 | 0.061476 | 5679 | 0.13521 | 1 | A06 | BIWW0.03030011/DBE
Build-In | Build-In Wall | BIWW.03030015 | 30 | 300 | 15 | 17 | 4077 | 4077 | 4077 | 0.097071 | 1549 | 0.036881 | 4656 | 0.11086 | 1.396 | A06 | BIWW0.03030015
Build-In | Build-In Wall | BIWW.03030016 | 30 | 300 | 16 | 17 | 4440 | 4440 | 4440 | 0.10571 | 1621 | 0.038595 | 5102 | 0.12148 | 1.456 | A06 | BIWW0.03030016
Build-In | Build-In Wall | BIWW.03030016/DBE | 30 | 300 | 16 | #N/A | 7320 | 7320 | 7320 | 0.17429 | 3660 | 0.087143 | 8052 | 0.19171 | 1 | A06 | BIWW0.03030016/DBE
Build-In | Build-In Wall | BIWW.03030020 | 30 | 300 | 20 | 22 | 5718 | 5718 | 5718 | 0.13614 | 2173 | 0.051738 | 6530 | 0.15548 | 1.396 | A06 | BIWW0.03030020
Build-In | Build-In Wall | BIWW.03030021 | 30 | 300 | 21 | 22 | 5844 | 5844 | 5844 | 0.13914 | 2110 | 0.050238 | 6721 | 0.16002 | 1.468 | A06 | BIWW0.03030021
Build-In | Build-In Wall | BIWW.03030021/DBE | 30 | 300 | 21 | #N/A | 8724 | 8724 | 8724 | 0.20771 | 4362 | 0.10386 | 9596 | 0.22848 | 1 | A06 | BIWW0.03030021/DBE
Build-In | Build-In Wall | BIWW.04004010 | 40 | 40 | 10 | 12 | 385 | 385 | 385 | 0.0091667 | 147 | 0.0035 | 440 | 0.010476 | 1.394 | A06 | BIWW0.04004010
Build-In | Build-In Wall | BIWW.04004011 | 40 | 40 | 11 | 12 | 506 | 506 | 506 | 0.012048 | 187 | 0.0044524 | 580 | 0.01381 | 1.439 | A06 | BIWW0.04004011
Build-In | Build-In Wall | BIWW.04004015 | 40 | 40 | 15 | 17 | 627 | 627 | 627 | 0.014929 | 240 | 0.0057143 | 715 | 0.017024 | 1.385 | A06 | BIWW0.04004015
Build-In | Build-In Wall | BIWW.04004016 | 40 | 40 | 16 | 17 | 680 | 680 | 680 | 0.01619 | 247 | 0.005881 | 781 | 0.018595 | 1.46 | A06 | BIWW0.04004016
Build-In | Build-In Wall | BIWW.04004020 | 40 | 40 | 20 | 22 | 878 | 878 | 878 | 0.020905 | 336 | 0.008 | 1002 | 0.023857 | 1.384 | A06 | BIWW0.04004020
Build-In | Build-In Wall | BIWW.04004021 | 40 | 40 | 21 | 22 | 910 | 910 | 910 | 0.021667 | 327 | 0.0077857 | 1047 | 0.024929 | 1.477 | A06 | BIWW0.04004021
Build-In | Build-In Wall | BIWW.04005010 | 40 | 50 | 10 | 12 | 482 | 482 | 482 | 0.011476 | 184 | 0.004381 | 550 | 0.013095 | 1.394 | A06 | BIWW0.04005010
Build-In | Build-In Wall | BIWW.04005011 | 40 | 50 | 11 | 12 | 632 | 632 | 632 | 0.015048 | 233 | 0.0055476 | 725 | 0.017262 | 1.439 | A06 | BIWW0.04005011
Build-In | Build-In Wall | BIWW.04005015 | 40 | 50 | 15 | 17 | 784 | 784 | 784 | 0.018667 | 300 | 0.0071429 | 895 | 0.02131 | 1.385 | A06 | BIWW0.04005015
Build-In | Build-In Wall | BIWW.04005016 | 40 | 50 | 16 | 17 | 850 | 850 | 850 | 0.020238 | 309 | 0.0073571 | 977 | 0.023262 | 1.46 | A06 | BIWW0.04005016
Build-In | Build-In Wall | BIWW.04005020 | 40 | 50 | 20 | 22 | 1098 | 1098 | 1098 | 0.026143 | 421 | 0.010024 | 1253 | 0.029833 | 1.384 | A06 | BIWW0.04005020
Build-In | Build-In Wall | BIWW.04005021 | 40 | 50 | 21 | 22 | 1137 | 1137 | 1137 | 0.027071 | 408 | 0.0097143 | 1309 | 0.031167 | 1.477 | A06 | BIWW0.04005021
Build-In | Build-In Wall | BIWW.04006010 | 40 | 60 | 10 | 12 | 578 | 578 | 578 | 0.013762 | 220 | 0.0052381 | 660 | 0.015714 | 1.394 | A06 | BIWW0.04006010
Build-In | Build-In Wall | BIWW.04006011 | 40 | 60 | 11 | 12 | 758 | 758 | 758 | 0.018048 | 280 | 0.0066667 | 869 | 0.02069 | 1.439 | A06 | BIWW0.04006011
Build-In | Build-In Wall | BIWW.04006011/DBE | 40 | 60 | 11 | #N/A | 1058 | 1058 | 1058 | 0.02519 | 529 | 0.012595 | 1164 | 0.027714 | 1 | A06 | BIWW0.04006011/DBE
Build-In | Build-In Wall | BIWW.04006015 | 40 | 60 | 15 | 17 | 941 | 941 | 941 | 0.022405 | 360 | 0.0085714 | 1074 | 0.025571 | 1.385 | A06 | BIWW0.04006015
Build-In | Build-In Wall | BIWW.04006016 | 40 | 60 | 16 | 17 | 1020 | 1020 | 1020 | 0.024286 | 370 | 0.0088095 | 1172 | 0.027905 | 1.46 | A06 | BIWW0.04006016
Build-In | Build-In Wall | BIWW.04006016/DBE | 40 | 60 | 16 | #N/A | 1500 | 1500 | 1500 | 0.035714 | 750 | 0.017857 | 1650 | 0.039286 | 1 | A06 | BIWW0.04006016/DBE
Build-In | Build-In Wall | BIWW.04006020 | 40 | 60 | 20 | 22 | 1318 | 1318 | 1318 | 0.031381 | 505 | 0.012024 | 1504 | 0.03581 | 1.384 | A06 | BIWW0.04006020
Build-In | Build-In Wall | BIWW.04006021 | 40 | 60 | 21 | 22 | 1364 | 1364 | 1364 | 0.032476 | 490 | 0.011667 | 1570 | 0.037381 | 1.477 | A06 | BIWW0.04006021
Build-In | Build-In Wall | BIWW.04006021/DBE | 40 | 60 | 21 | #N/A | 1844 | 1844 | 1844 | 0.043905 | 922 | 0.021952 | 2028 | 0.048286 | 1 | A06 | BIWW0.04006021/DBE
Build-In | Build-In Wall | BIWW.04007010 | 40 | 70 | 10 | 12 | 674 | 674 | 674 | 0.016048 | 257 | 0.006119 | 770 | 0.018333 | 1.394 | A06 | BIWW0.04007010
Build-In | Build-In Wall | BIWW.04007011 | 40 | 70 | 11 | 12 | 885 | 885 | 885 | 0.021071 | 327 | 0.0077857 | 1015 | 0.024167 | 1.439 | A06 | BIWW0.04007011
Build-In | Build-In Wall | BIWW.04007011/DBE | 40 | 70 | 11 | #N/A | 1185 | 1185 | 1185 | 0.028214 | 593 | 0.014119 | 1304 | 0.031048 | 1 | A06 | BIWW0.04007011/DBE
Build-In | Build-In Wall | BIWW.04007015 | 40 | 70 | 15 | 17 | 1098 | 1098 | 1098 | 0.026143 | 421 | 0.010024 | 1253 | 0.029833 | 1.385 | A06 | BIWW0.04007015
Build-In | Build-In Wall | BIWW.04007016 | 40 | 70 | 16 | 17 | 1190 | 1190 | 1190 | 0.028333 | 432 | 0.010286 | 1367 | 0.032548 | 1.46 | A06 | BIWW0.04007016
Build-In | Build-In Wall | BIWW.04007016/DBE | 40 | 70 | 16 | #N/A | 1670 | 1670 | 1670 | 0.039762 | 835 | 0.019881 | 1837 | 0.043738 | 1 | A06 | BIWW0.04007016/DBE
Build-In | Build-In Wall | BIWW.04007020 | 40 | 70 | 20 | 22 | 1537 | 1537 | 1537 | 0.036595 | 589 | 0.014024 | 1754 | 0.041762 | 1.384 | A06 | BIWW0.04007020
Build-In | Build-In Wall | BIWW.04007021 | 40 | 70 | 21 | 22 | 1592 | 1592 | 1592 | 0.037905 | 572 | 0.013619 | 1832 | 0.043619 | 1.477 | A06 | BIWW0.04007021
Build-In | Build-In Wall | BIWW.04007021/DBE | 40 | 70 | 21 | #N/A | 2072 | 2072 | 2072 | 0.049333 | 1036 | 0.024667 | 2279 | 0.054262 | 1 | A06 | BIWW0.04007021/DBE
Build-In | Build-In Wall | BIWW.04008010 | 40 | 80 | 10 | 12 | 770 | 770 | 770 | 0.018333 | 293 | 0.0069762 | 879 | 0.020929 | 1.394 | A06 | BIWW0.04008010
Build-In | Build-In Wall | BIWW.04008011 | 40 | 80 | 11 | 12 | 1011 | 1011 | 1011 | 0.024071 | 373 | 0.008881 | 1160 | 0.027619 | 1.439 | A06 | BIWW0.04008011
Build-In | Build-In Wall | BIWW.04008011/DBE | 40 | 80 | 11 | #N/A | 1311 | 1311 | 1311 | 0.031214 | 656 | 0.015619 | 1442 | 0.034333 | 1 | A06 | BIWW0.04008011/DBE
Build-In | Build-In Wall | BIWW.04008015 | 40 | 80 | 15 | 17 | 1254 | 1254 | 1254 | 0.029857 | 480 | 0.011429 | 1431 | 0.034071 | 1.385 | A06 | BIWW0.04008015
Build-In | Build-In Wall | BIWW.04008016 | 40 | 80 | 16 | 17 | 1360 | 1360 | 1360 | 0.032381 | 494 | 0.011762 | 1563 | 0.037214 | 1.46 | A06 | BIWW0.04008016
Build-In | Build-In Wall | BIWW.04008016/DBE | 40 | 80 | 16 | #N/A | 1840 | 1840 | 1840 | 0.04381 | 920 | 0.021905 | 2024 | 0.04819 | 1 | A06 | BIWW0.04008016/DBE
Build-In | Build-In Wall | BIWW.04008020 | 40 | 80 | 20 | 22 | 1757 | 1757 | 1757 | 0.041833 | 673 | 0.016024 | 2005 | 0.047738 | 1.384 | A06 | BIWW0.04008020
Build-In | Build-In Wall | BIWW.04008021 | 40 | 80 | 21 | 22 | 1819 | 1819 | 1819 | 0.04331 | 653 | 0.015548 | 2094 | 0.049857 | 1.477 | A06 | BIWW0.04008021
Build-In | Build-In Wall | BIWW.04008021/DBE | 40 | 80 | 21 | #N/A | 2299 | 2299 | 2299 | 0.054738 | 1150 | 0.027381 | 2529 | 0.060214 | 1 | A06 | BIWW0.04008021/DBE
Build-In | Build-In Wall | BIWW.04009010 | 40 | 90 | 10 | 12 | 867 | 867 | 867 | 0.020643 | 330 | 0.0078571 | 990 | 0.023571 | 1.394 | A06 | BIWW0.04009010
Build-In | Build-In Wall | BIWW.04009011 | 40 | 90 | 11 | 12 | 1138 | 1138 | 1138 | 0.027095 | 420 | 0.01 | 1305 | 0.031071 | 1.439 | A06 | BIWW0.04009011
Build-In | Build-In Wall | BIWW.04009011/DBE | 40 | 90 | 11 | #N/A | 1738 | 1738 | 1738 | 0.041381 | 869 | 0.02069 | 1912 | 0.045524 | 1 | A06 | BIWW0.04009011/DBE
Build-In | Build-In Wall | BIWW.04009015 | 40 | 90 | 15 | 17 | 1411 | 1411 | 1411 | 0.033595 | 540 | 0.012857 | 1610 | 0.038333 | 1.385 | A06 | BIWW0.04009015
Build-In | Build-In Wall | BIWW.04009016 | 40 | 90 | 16 | 17 | 1530 | 1530 | 1530 | 0.036429 | 555 | 0.013214 | 1758 | 0.041857 | 1.46 | A06 | BIWW0.04009016
Build-In | Build-In Wall | BIWW.04009016/DBE | 40 | 90 | 16 | #N/A | 2490 | 2490 | 2490 | 0.059286 | 1245 | 0.029643 | 2739 | 0.065214 | 1 | A06 | BIWW0.04009016/DBE
Build-In | Build-In Wall | BIWW.04009020 | 40 | 90 | 20 | 22 | 1976 | 1976 | 1976 | 0.047048 | 757 | 0.018024 | 2255 | 0.05369 | 1.384 | A06 | BIWW0.04009020
Build-In | Build-In Wall | BIWW.04009021 | 40 | 90 | 21 | 22 | 2047 | 2047 | 2047 | 0.048738 | 735 | 0.0175 | 2356 | 0.056095 | 1.477 | A06 | BIWW0.04009021
Build-In | Build-In Wall | BIWW.04009021/DBE | 40 | 90 | 21 | #N/A | 3007 | 3007 | 3007 | 0.071595 | 1504 | 0.03581 | 3308 | 0.078762 | 1 | A06 | BIWW0.04009021/DBE
Build-In | Build-In Wall | BIWW.04010010 | 40 | 100 | 10 | 12 | 963 | 963 | 963 | 0.022929 | 367 | 0.0087381 | 1100 | 0.02619 | 1.394 | A06 | BIWW0.04010010
Build-In | Build-In Wall | BIWW.04010011 | 40 | 100 | 11 | 12 | 1264 | 1264 | 1264 | 0.030095 | 466 | 0.011095 | 1450 | 0.034524 | 1.439 | A06 | BIWW0.04010011
Build-In | Build-In Wall | BIWW.04010011/DBE | 40 | 100 | 11 | #N/A | 1864 | 1864 | 1864 | 0.044381 | 932 | 0.02219 | 2050 | 0.04881 | 1 | A06 | BIWW0.04010011/DBE
Build-In | Build-In Wall | BIWW.04010015 | 40 | 100 | 15 | 17 | 1568 | 1568 | 1568 | 0.037333 | 601 | 0.01431 | 1789 | 0.042595 | 1.385 | A06 | BIWW0.04010015
Build-In | Build-In Wall | BIWW.04010016 | 40 | 100 | 16 | 17 | 1700 | 1700 | 1700 | 0.040476 | 617 | 0.01469 | 1953 | 0.0465 | 1.46 | A06 | BIWW0.04010016
Build-In | Build-In Wall | BIWW.04010016/DBE | 40 | 100 | 16 | #N/A | 2660 | 2660 | 2660 | 0.063333 | 1330 | 0.031667 | 2926 | 0.069667 | 1 | A06 | BIWW0.04010016/DBE
Build-In | Build-In Wall | BIWW.04010020 | 40 | 100 | 20 | 22 | 2196 | 2196 | 2196 | 0.052286 | 841 | 0.020024 | 2506 | 0.059667 | 1.384 | A06 | BIWW0.04010020
Build-In | Build-In Wall | BIWW.04010021 | 40 | 100 | 21 | 22 | 2274 | 2274 | 2274 | 0.054143 | 816 | 0.019429 | 2617 | 0.06231 | 1.477 | A06 | BIWW0.04010021
Build-In | Build-In Wall | BIWW.04010021/DBE | 40 | 100 | 21 | #N/A | 3234 | 3234 | 3234 | 0.077 | 1617 | 0.0385 | 3557 | 0.08469 | 1 | A06 | BIWW0.04010021/DBE
Build-In | Build-In Wall | BIWW.04011010 | 40 | 110 | 10 | 12 | 1059 | 1059 | 1059 | 0.025214 | 403 | 0.0095952 | 1209 | 0.028786 | 1.394 | A06 | BIWW0.04011010
Build-In | Build-In Wall | BIWW.04011011 | 40 | 110 | 11 | 12 | 1390 | 1390 | 1390 | 0.033095 | 513 | 0.012214 | 1594 | 0.037952 | 1.439 | A06 | BIWW0.04011011
Build-In | Build-In Wall | BIWW.04011011/DBE | 40 | 110 | 11 | #N/A | 1990 | 1990 | 1990 | 0.047381 | 995 | 0.02369 | 2189 | 0.052119 | 1 | A06 | BIWW0.04011011/DBE
Build-In | Build-In Wall | BIWW.04011015 | 40 | 110 | 15 | 17 | 1725 | 1725 | 1725 | 0.041071 | 661 | 0.015738 | 1968 | 0.046857 | 1.385 | A06 | BIWW0.04011015
Build-In | Build-In Wall | BIWW.04011016 | 40 | 110 | 16 | 17 | 1870 | 1870 | 1870 | 0.044524 | 679 | 0.016167 | 2149 | 0.051167 | 1.46 | A06 | BIWW0.04011016
Build-In | Build-In Wall | BIWW.04011016/DBE | 40 | 110 | 16 | #N/A | 2830 | 2830 | 2830 | 0.067381 | 1415 | 0.03369 | 3113 | 0.074119 | 1 | A06 | BIWW0.04011016/DBE
Build-In | Build-In Wall | BIWW.04011020 | 40 | 110 | 20 | 22 | 2416 | 2416 | 2416 | 0.057524 | 925 | 0.022024 | 2757 | 0.065643 | 1.384 | A06 | BIWW0.04011020
Build-In | Build-In Wall | BIWW.04011021 | 40 | 110 | 21 | 22 | 2501 | 2501 | 2501 | 0.059548 | 898 | 0.021381 | 2879 | 0.068548 | 1.477 | A06 | BIWW0.04011021
Build-In | Build-In Wall | BIWW.04011021/DBE | 40 | 110 | 21 | #N/A | 3461 | 3461 | 3461 | 0.082405 | 1731 | 0.041214 | 3807 | 0.090643 | 1 | A06 | BIWW0.04011021/DBE
Build-In | Build-In Wall | BIWW.04012010 | 40 | 120 | 10 | 12 | 1156 | 1156 | 1156 | 0.027524 | 440 | 0.010476 | 1320 | 0.031429 | 1.394 | A06 | BIWW0.04012010
Build-In | Build-In Wall | BIWW.04012011 | 40 | 120 | 11 | 12 | 1517 | 1517 | 1517 | 0.036119 | 560 | 0.013333 | 1740 | 0.041429 | 1.439 | A06 | BIWW0.04012011
Build-In | Build-In Wall | BIWW.04012011/DBE | 40 | 120 | 11 | #N/A | 2117 | 2117 | 2117 | 0.050405 | 1059 | 0.025214 | 2329 | 0.055452 | 1 | A06 | BIWW0.04012011/DBE
Build-In | Build-In Wall | BIWW.04012015 | 40 | 120 | 15 | 17 | 1882 | 1882 | 1882 | 0.04481 | 721 | 0.017167 | 2147 | 0.051119 | 1.385 | A06 | BIWW0.04012015
Build-In | Build-In Wall | BIWW.04012016 | 40 | 120 | 16 | 17 | 2040 | 2040 | 2040 | 0.048571 | 741 | 0.017643 | 2344 | 0.05581 | 1.46 | A06 | BIWW0.04012016
Build-In | Build-In Wall | BIWW.04012016/DBE | 40 | 120 | 16 | #N/A | 3000 | 3000 | 3000 | 0.071429 | 1500 | 0.035714 | 3300 | 0.078571 | 1 | A06 | BIWW0.04012016/DBE
Build-In | Build-In Wall | BIWW.04012020 | 40 | 120 | 20 | 22 | 2635 | 2635 | 2635 | 0.062738 | 1009 | 0.024024 | 3007 | 0.071595 | 1.384 | A06 | BIWW0.04012020
Build-In | Build-In Wall | BIWW.04012021 | 40 | 120 | 21 | 22 | 2729 | 2729 | 2729 | 0.064976 | 980 | 0.023333 | 3141 | 0.074786 | 1.477 | A06 | BIWW0.04012021
Build-In | Build-In Wall | BIWW.04012021/DBE | 40 | 120 | 21 | #N/A | 3689 | 3689 | 3689 | 0.087833 | 1845 | 0.043929 | 4058 | 0.096619 | 1 | A06 | BIWW0.04012021/DBE
Build-In | Build-In Wall | BIWW.04014010 | 40 | 140 | 10 | 12 | 1348 | 1348 | 1348 | 0.032095 | 514 | 0.012238 | 1539 | 0.036643 | 1.394 | A06 | BIWW0.04014010
Build-In | Build-In Wall | BIWW.04014011 | 40 | 140 | 11 | 12 | 1770 | 1770 | 1770 | 0.042143 | 653 | 0.015548 | 2030 | 0.048333 | 1.439 | A06 | BIWW0.04014011
Build-In | Build-In Wall | BIWW.04014011/DBE | 40 | 140 | 11 | #N/A | 2370 | 2370 | 2370 | 0.056429 | 1185 | 0.028214 | 2607 | 0.062071 | 1 | A06 | BIWW0.04014011/DBE
Build-In | Build-In Wall | BIWW.04014015 | 40 | 140 | 15 | 17 | 2195 | 2195 | 2195 | 0.052262 | 841 | 0.020024 | 2504 | 0.059619 | 1.385 | A06 | BIWW0.04014015
Build-In | Build-In Wall | BIWW.04014016 | 40 | 140 | 16 | 17 | 2380 | 2380 | 2380 | 0.056667 | 864 | 0.020571 | 2735 | 0.065119 | 1.46 | A06 | BIWW0.04014016
Build-In | Build-In Wall | BIWW.04014016/DBE | 40 | 140 | 16 | #N/A | 3340 | 3340 | 3340 | 0.079524 | 1670 | 0.039762 | 3674 | 0.087476 | 1 | A06 | BIWW0.04014016/DBE
Build-In | Build-In Wall | BIWW.04014020 | 40 | 140 | 20 | 22 | 3074 | 3074 | 3074 | 0.07319 | 1177 | 0.028024 | 3507 | 0.0835 | 1.384 | A06 | BIWW0.04014020
Build-In | Build-In Wall | BIWW.04014021 | 40 | 140 | 21 | 22 | 3184 | 3184 | 3184 | 0.07581 | 1143 | 0.027214 | 3665 | 0.087262 | 1.477 | A06 | BIWW0.04014021
Build-In | Build-In Wall | BIWW.04014021/DBE | 40 | 140 | 21 | #N/A | 4144 | 4144 | 4144 | 0.098667 | 2072 | 0.049333 | 4558 | 0.10852 | 1 | A06 | BIWW0.04014021/DBE
Build-In | Build-In Wall | BIWW.04016010 | 40 | 160 | 10 | 12 | 1541 | 1541 | 1541 | 0.03669 | 587 | 0.013976 | 1760 | 0.041905 | 1.394 | A06 | BIWW0.04016010
Build-In | Build-In Wall | BIWW.04016011 | 40 | 160 | 11 | 12 | 2022 | 2022 | 2022 | 0.048143 | 746 | 0.017762 | 2319 | 0.055214 | 1.439 | A06 | BIWW0.04016011
Build-In | Build-In Wall | BIWW.04016011/DBE | 40 | 160 | 11 | #N/A | 3222 | 3222 | 3222 | 0.076714 | 1611 | 0.038357 | 3544 | 0.084381 | 1 | A06 | BIWW0.04016011/DBE
Build-In | Build-In Wall | BIWW.04016015 | 40 | 160 | 15 | 17 | 2509 | 2509 | 2509 | 0.059738 | 961 | 0.022881 | 2863 | 0.068167 | 1.385 | A06 | BIWW0.04016015
Build-In | Build-In Wall | BIWW.04016016 | 40 | 160 | 16 | 17 | 2720 | 2720 | 2720 | 0.064762 | 987 | 0.0235 | 3125 | 0.074405 | 1.46 | A06 | BIWW0.04016016
Build-In | Build-In Wall | BIWW.04016016/DBE | 40 | 160 | 16 | #N/A | 4640 | 4640 | 4640 | 0.11048 | 2320 | 0.055238 | 5104 | 0.12152 | 1 | A06 | BIWW0.04016016/DBE
Build-In | Build-In Wall | BIWW.04016020 | 40 | 160 | 20 | 22 | 3514 | 3514 | 3514 | 0.083667 | 1346 | 0.032048 | 4009 | 0.095452 | 1.384 | A06 | BIWW0.04016020
Build-In | Build-In Wall | BIWW.04016021 | 40 | 160 | 21 | 22 | 3638 | 3638 | 3638 | 0.086619 | 1306 | 0.031095 | 4187 | 0.09969 | 1.477 | A06 | BIWW0.04016021
Build-In | Build-In Wall | BIWW.04016021/DBE | 40 | 160 | 21 | #N/A | 5558 | 5558 | 5558 | 0.13233 | 2779 | 0.066167 | 6114 | 0.14557 | 1 | A06 | BIWW0.04016021/DBE
Build-In | Build-In Wall | BIWW.04018010 | 40 | 180 | 10 | 12 | 1733 | 1733 | 1733 | 0.041262 | 660 | 0.015714 | 1979 | 0.047119 | 1.394 | A06 | BIWW0.04018010
Build-In | Build-In Wall | BIWW.04018011 | 40 | 180 | 11 | 12 | 2275 | 2275 | 2275 | 0.054167 | 839 | 0.019976 | 2609 | 0.062119 | 1.439 | A06 | BIWW0.04018011
Build-In | Build-In Wall | BIWW.04018011/DBE | 40 | 180 | 11 | #N/A | 3475 | 3475 | 3475 | 0.082738 | 1738 | 0.041381 | 3823 | 0.091024 | 1 | A06 | BIWW0.04018011/DBE
Build-In | Build-In Wall | BIWW.04018015 | 40 | 180 | 15 | 17 | 2822 | 2822 | 2822 | 0.06719 | 1081 | 0.025738 | 3220 | 0.076667 | 1.385 | A06 | BIWW0.04018015
Build-In | Build-In Wall | BIWW.04018016 | 40 | 180 | 16 | 17 | 3060 | 3060 | 3060 | 0.072857 | 1111 | 0.026452 | 3516 | 0.083714 | 1.46 | A06 | BIWW0.04018016
Build-In | Build-In Wall | BIWW.04018016/DBE | 40 | 180 | 16 | #N/A | 4980 | 4980 | 4980 | 0.11857 | 2490 | 0.059286 | 5478 | 0.13043 | 1 | A06 | BIWW0.04018016/DBE
Build-In | Build-In Wall | BIWW.04018020 | 40 | 180 | 20 | 22 | 3953 | 3953 | 3953 | 0.094119 | 1514 | 0.036048 | 4510 | 0.10738 | 1.384 | A06 | BIWW0.04018020
Build-In | Build-In Wall | BIWW.04018021 | 40 | 180 | 21 | 22 | 4093 | 4093 | 4093 | 0.097452 | 1469 | 0.034976 | 4711 | 0.11217 | 1.477 | A06 | BIWW0.04018021
Build-In | Build-In Wall | BIWW.04018021/DBE | 40 | 180 | 21 | #N/A | 6013 | 6013 | 6013 | 0.14317 | 3007 | 0.071595 | 6614 | 0.15748 | 1 | A06 | BIWW0.04018021/DBE
Build-In | Build-In Wall | BIWW.04020010 | 40 | 200 | 10 | 12 | 1926 | 1926 | 1926 | 0.045857 | 734 | 0.017476 | 2199 | 0.052357 | 1.394 | A06 | BIWW0.04020010
Build-In | Build-In Wall | BIWW.04020011 | 40 | 200 | 11 | 12 | 2528 | 2528 | 2528 | 0.06019 | 933 | 0.022214 | 2900 | 0.069048 | 1.439 | A06 | BIWW0.04020011
Build-In | Build-In Wall | BIWW.04020011/DBE | 40 | 200 | 11 | #N/A | 3728 | 3728 | 3728 | 0.088762 | 1864 | 0.044381 | 4101 | 0.097643 | 1 | A06 | BIWW0.04020011/DBE
Build-In | Build-In Wall | BIWW.04020015 | 40 | 200 | 15 | 17 | 3136 | 3136 | 3136 | 0.074667 | 1201 | 0.028595 | 3578 | 0.08519 | 1.385 | A06 | BIWW0.04020015
Build-In | Build-In Wall | BIWW.04020016 | 40 | 200 | 16 | 17 | 3400 | 3400 | 3400 | 0.080952 | 1234 | 0.029381 | 3907 | 0.093024 | 1.46 | A06 | BIWW0.04020016
Build-In | Build-In Wall | BIWW.04020016/DBE | 40 | 200 | 16 | #N/A | 5320 | 5320 | 5320 | 0.12667 | 2660 | 0.063333 | 5852 | 0.13933 | 1 | A06 | BIWW0.04020016/DBE
Build-In | Build-In Wall | BIWW.04020020 | 40 | 200 | 20 | 22 | 4392 | 4392 | 4392 | 0.10457 | 1682 | 0.040048 | 5011 | 0.11931 | 1.384 | A06 | BIWW0.04020020
Build-In | Build-In Wall | BIWW.04020021 | 40 | 200 | 21 | 22 | 4548 | 4548 | 4548 | 0.10829 | 1633 | 0.038881 | 5235 | 0.12464 | 1.477 | A06 | BIWW0.04020021
Build-In | Build-In Wall | BIWW.04020021/DBE | 40 | 200 | 21 | #N/A | 6468 | 6468 | 6468 | 0.154 | 3234 | 0.077 | 7115 | 0.1694 | 1 | A06 | BIWW0.04020021/DBE
Build-In | Build-In Wall | BIWW.04022010 | 40 | 220 | 10 | 12 | 2119 | 2119 | 2119 | 0.050452 | 807 | 0.019214 | 2420 | 0.057619 | 1.394 | A06 | BIWW0.04022010
Build-In | Build-In Wall | BIWW.04022011 | 40 | 220 | 11 | 12 | 2781 | 2781 | 2781 | 0.066214 | 1026 | 0.024429 | 3190 | 0.075952 | 1.439 | A06 | BIWW0.04022011
Build-In | Build-In Wall | BIWW.04022011/DBE | 40 | 220 | 11 | #N/A | 3981 | 3981 | 3981 | 0.094786 | 1991 | 0.047405 | 4379 | 0.10426 | 1 | A06 | BIWW0.04022011/DBE
Build-In | Build-In Wall | BIWW.04022015 | 40 | 220 | 15 | 17 | 3450 | 3450 | 3450 | 0.082143 | 1321 | 0.031452 | 3936 | 0.093714 | 1.385 | A06 | BIWW0.04022015
Build-In | Build-In Wall | BIWW.04022016 | 40 | 220 | 16 | 17 | 3740 | 3740 | 3740 | 0.089048 | 1358 | 0.032333 | 4297 | 0.10231 | 1.46 | A06 | BIWW0.04022016
Build-In | Build-In Wall | BIWW.04022016/DBE | 40 | 220 | 16 | #N/A | 5660 | 5660 | 5660 | 0.13476 | 2830 | 0.067381 | 6226 | 0.14824 | 1 | A06 | BIWW0.04022016/DBE
Build-In | Build-In Wall | BIWW.04022020 | 40 | 220 | 20 | 22 | 4831 | 4831 | 4831 | 0.11502 | 1850 | 0.044048 | 5512 | 0.13124 | 1.384 | A06 | BIWW0.04022020
Build-In | Build-In Wall | BIWW.04022021 | 40 | 220 | 21 | 22 | 5003 | 5003 | 5003 | 0.11912 | 1796 | 0.042762 | 5758 | 0.1371 | 1.477 | A06 | BIWW0.04022021
Build-In | Build-In Wall | BIWW.04022021/DBE | 40 | 220 | 21 | #N/A | 6923 | 6923 | 6923 | 0.16483 | 3462 | 0.082429 | 7615 | 0.18131 | 1 | A06 | BIWW0.04022021/DBE
Build-In | Build-In Wall | BIWW.04024010 | 40 | 240 | 10 | 12 | 2311 | 2311 | 2311 | 0.055024 | 880 | 0.020952 | 2639 | 0.062833 | 1.394 | A06 | BIWW0.04024010
Build-In | Build-In Wall | BIWW.04024011 | 40 | 240 | 11 | 12 | 3034 | 3034 | 3034 | 0.072238 | 1120 | 0.026667 | 3480 | 0.082857 | 1.439 | A06 | BIWW0.04024011
Build-In | Build-In Wall | BIWW.04024011/DBE | 40 | 240 | 11 | #N/A | 4834 | 4834 | 4834 | 0.1151 | 2417 | 0.057548 | 5317 | 0.1266 | 1 | A06 | BIWW0.04024011/DBE
Build-In | Build-In Wall | BIWW.04024015 | 40 | 240 | 15 | 17 | 3763 | 3763 | 3763 | 0.089595 | 1441 | 0.03431 | 4294 | 0.10224 | 1.385 | A06 | BIWW0.04024015
Build-In | Build-In Wall | BIWW.04024016 | 40 | 240 | 16 | 17 | 4080 | 4080 | 4080 | 0.097143 | 1481 | 0.035262 | 4688 | 0.11162 | 1.46 | A06 | BIWW0.04024016
Build-In | Build-In Wall | BIWW.04024016/DBE | 40 | 240 | 16 | #N/A | 6960 | 6960 | 6960 | 0.16571 | 3480 | 0.082857 | 7656 | 0.18229 | 1 | A06 | BIWW0.04024016/DBE
Build-In | Build-In Wall | BIWW.04024020 | 40 | 240 | 20 | 22 | 5270 | 5270 | 5270 | 0.12548 | 2018 | 0.048048 | 6013 | 0.14317 | 1.384 | A06 | BIWW0.04024020
Build-In | Build-In Wall | BIWW.04024021 | 40 | 240 | 21 | 22 | 5458 | 5458 | 5458 | 0.12995 | 1959 | 0.046643 | 6282 | 0.14957 | 1.477 | A06 | BIWW0.04024021
Build-In | Build-In Wall | BIWW.04024021/DBE | 40 | 240 | 21 | #N/A | 8338 | 8338 | 8338 | 0.19852 | 4169 | 0.099262 | 9172 | 0.21838 | 1 | A06 | BIWW0.04024021/DBE
Build-In | Build-In Wall | BIWW.04026010 | 40 | 260 | 10 | 12 | 2504 | 2504 | 2504 | 0.059619 | 954 | 0.022714 | 2860 | 0.068095 | 1.394 | A06 | BIWW0.04026010
Build-In | Build-In Wall | BIWW.04026011 | 40 | 260 | 11 | 12 | 3286 | 3286 | 3286 | 0.078238 | 1213 | 0.028881 | 3769 | 0.089738 | 1.439 | A06 | BIWW0.04026011
Build-In | Build-In Wall | BIWW.04026011/DBE | 40 | 260 | 11 | #N/A | 5086 | 5086 | 5086 | 0.1211 | 2543 | 0.060548 | 5595 | 0.13321 | 1 | A06 | BIWW0.04026011/DBE
Build-In | Build-In Wall | BIWW.04026015 | 40 | 260 | 15 | 17 | 4077 | 4077 | 4077 | 0.097071 | 1561 | 0.037167 | 4652 | 0.11076 | 1.385 | A06 | BIWW0.04026015
Build-In | Build-In Wall | BIWW.04026016 | 40 | 260 | 16 | 17 | 4420 | 4420 | 4420 | 0.10524 | 1604 | 0.03819 | 5079 | 0.12093 | 1.46 | A06 | BIWW0.04026016
Build-In | Build-In Wall | BIWW.04026016/DBE | 40 | 260 | 16 | #N/A | 7300 | 7300 | 7300 | 0.17381 | 3650 | 0.086905 | 8030 | 0.19119 | 1 | A06 | BIWW0.04026016/DBE
Build-In | Build-In Wall | BIWW.04026020 | 40 | 260 | 20 | 22 | 5710 | 5710 | 5710 | 0.13595 | 2187 | 0.052071 | 6515 | 0.15512 | 1.384 | A06 | BIWW0.04026020
Build-In | Build-In Wall | BIWW.04026021 | 40 | 260 | 21 | 22 | 5912 | 5912 | 5912 | 0.14076 | 2122 | 0.050524 | 6805 | 0.16202 | 1.477 | A06 | BIWW0.04026021
Build-In | Build-In Wall | BIWW.04026021/DBE | 40 | 260 | 21 | #N/A | 8792 | 8792 | 8792 | 0.20933 | 4396 | 0.10467 | 9671 | 0.23026 | 1 | A06 | BIWW0.04026021/DBE
Build-In | Build-In Wall | BIWW.04028010 | 40 | 280 | 10 | 12 | 2696 | 2696 | 2696 | 0.06419 | 1027 | 0.024452 | 3079 | 0.07331 | 1.394 | A06 | BIWW0.04028010
Build-In | Build-In Wall | BIWW.04028011 | 40 | 280 | 11 | 12 | 3539 | 3539 | 3539 | 0.084262 | 1306 | 0.031095 | 4059 | 0.096643 | 1.439 | A06 | BIWW0.04028011
Build-In | Build-In Wall | BIWW.04028011/DBE | 40 | 280 | 11 | #N/A | 5339 | 5339 | 5339 | 0.12712 | 2670 | 0.063571 | 5873 | 0.13983 | 1 | A06 | BIWW0.04028011/DBE
Build-In | Build-In Wall | BIWW.04028015 | 40 | 280 | 15 | 17 | 4390 | 4390 | 4390 | 0.10452 | 1681 | 0.040024 | 5009 | 0.11926 | 1.385 | A06 | BIWW0.04028015
Build-In | Build-In Wall | BIWW.04028016 | 40 | 280 | 16 | 17 | 4760 | 4760 | 4760 | 0.11333 | 1728 | 0.041143 | 5469 | 0.13021 | 1.46 | A06 | BIWW0.04028016
Build-In | Build-In Wall | BIWW.04028016/DBE | 40 | 280 | 16 | #N/A | 7640 | 7640 | 7640 | 0.1819 | 3820 | 0.090952 | 8404 | 0.2001 | 1 | A06 | BIWW0.04028016/DBE
Build-In | Build-In Wall | BIWW.04028020 | 40 | 280 | 20 | 22 | 6149 | 6149 | 6149 | 0.1464 | 2355 | 0.056071 | 7016 | 0.16705 | 1.384 | A06 | BIWW0.04028020
Build-In | Build-In Wall | BIWW.04028021 | 40 | 280 | 21 | 22 | 6367 | 6367 | 6367 | 0.1516 | 2286 | 0.054429 | 7328 | 0.17448 | 1.477 | A06 | BIWW0.04028021
Build-In | Build-In Wall | BIWW.04028021/DBE | 40 | 280 | 21 | #N/A | 9247 | 9247 | 9247 | 0.22017 | 4624 | 0.1101 | 10172 | 0.24219 | 1 | A06 | BIWW0.04028021/DBE
Build-In | Build-In Wall | BIWW.04030010 | 40 | 300 | 10 | 12 | 2889 | 2889 | 2889 | 0.068786 | 1101 | 0.026214 | 3299 | 0.078548 | 1.394 | A06 | BIWW0.04030010
Build-In | Build-In Wall | BIWW.04030011 | 40 | 300 | 11 | 12 | 3792 | 3792 | 3792 | 0.090286 | 1399 | 0.03331 | 4349 | 0.10355 | 1.439 | A06 | BIWW0.04030011
Build-In | Build-In Wall | BIWW.04030011/DBE | 40 | 300 | 11 | #N/A | 5592 | 5592 | 5592 | 0.13314 | 2796 | 0.066571 | 6151 | 0.14645 | 1 | A06 | BIWW0.04030011/DBE
Build-In | Build-In Wall | BIWW.04030015 | 40 | 300 | 15 | 17 | 4704 | 4704 | 4704 | 0.112 | 1802 | 0.042905 | 5367 | 0.12779 | 1.385 | A06 | BIWW0.04030015
Build-In | Build-In Wall | BIWW.04030016 | 40 | 300 | 16 | 17 | 5100 | 5100 | 5100 | 0.12143 | 1851 | 0.044071 | 5860 | 0.13952 | 1.46 | A06 | BIWW0.04030016
Build-In | Build-In Wall | BIWW.04030016/DBE | 40 | 300 | 16 | #N/A | 7980 | 7980 | 7980 | 0.19 | 3990 | 0.095 | 8778 | 0.209 | 1 | A06 | BIWW0.04030016/DBE
Build-In | Build-In Wall | BIWW.04030020 | 40 | 300 | 20 | 22 | 6588 | 6588 | 6588 | 0.15686 | 2523 | 0.060071 | 7517 | 0.17898 | 1.384 | A06 | BIWW0.04030020
Build-In | Build-In Wall | BIWW.04030021 | 40 | 300 | 21 | 22 | 6822 | 6822 | 6822 | 0.16243 | 2449 | 0.05831 | 7852 | 0.18695 | 1.477 | A06 | BIWW0.04030021
Build-In | Build-In Wall | BIWW.04030021/DBE | 40 | 300 | 21 | #N/A | 9702 | 9702 | 9702 | 0.231 | 4851 | 0.1155 | 10672 | 0.2541 | 1 | A06 | BIWW0.04030021/DBE
Build-In | Build-In Wall | BIWW.05004010 | 50 | 40 | 10 | 12 | 430 | 430 | 430 | 0.010238 | 165 | 0.0039286 | 491 | 0.01169 | 1.385 | A06 | BIWW0.05004010
Build-In | Build-In Wall | BIWW.05004011 | 50 | 40 | 11 | 12 | 554 | 554 | 554 | 0.01319 | 204 | 0.0048571 | 635 | 0.015119 | 1.438 | A06 | BIWW0.05004011
Build-In | Build-In Wall | BIWW.05004015 | 50 | 40 | 15 | 17 | 694 | 694 | 694 | 0.016524 | 268 | 0.006381 | 791 | 0.018833 | 1.373 | A06 | BIWW0.05004015
Build-In | Build-In Wall | BIWW.05004016 | 50 | 40 | 16 | 17 | 759 | 759 | 759 | 0.018071 | 275 | 0.0065476 | 873 | 0.020786 | 1.464 | A06 | BIWW0.05004016
Build-In | Build-In Wall | BIWW.05004020 | 50 | 40 | 20 | 22 | 970 | 970 | 970 | 0.023095 | 374 | 0.0089048 | 1106 | 0.026333 | 1.373 | A06 | BIWW0.05004020
Build-In | Build-In Wall | BIWW.05004021 | 50 | 40 | 21 | 22 | 1033 | 1033 | 1033 | 0.024595 | 369 | 0.0087857 | 1190 | 0.028333 | 1.485 | A06 | BIWW0.05004021
Build-In | Build-In Wall | BIWW.05005010 | 50 | 50 | 10 | 12 | 538 | 538 | 538 | 0.01281 | 206 | 0.0049048 | 614 | 0.014619 | 1.385 | A06 | BIWW0.05005010
Build-In | Build-In Wall | BIWW.05005011 | 50 | 50 | 11 | 12 | 693 | 693 | 693 | 0.0165 | 256 | 0.0060952 | 795 | 0.018929 | 1.438 | A06 | BIWW0.05005011
Build-In | Build-In Wall | BIWW.05005015 | 50 | 50 | 15 | 17 | 867 | 867 | 867 | 0.020643 | 335 | 0.0079762 | 988 | 0.023524 | 1.373 | A06 | BIWW0.05005015
Build-In | Build-In Wall | BIWW.05005016 | 50 | 50 | 16 | 17 | 949 | 949 | 949 | 0.022595 | 344 | 0.0081905 | 1091 | 0.025976 | 1.464 | A06 | BIWW0.05005016
Build-In | Build-In Wall | BIWW.05005020 | 50 | 50 | 20 | 22 | 1213 | 1213 | 1213 | 0.028881 | 468 | 0.011143 | 1383 | 0.032929 | 1.373 | A06 | BIWW0.05005020
Build-In | Build-In Wall | BIWW.05005021 | 50 | 50 | 21 | 22 | 1291 | 1291 | 1291 | 0.030738 | 461 | 0.010976 | 1487 | 0.035405 | 1.485 | A06 | BIWW0.05005021
Build-In | Build-In Wall | BIWW.05006010 | 50 | 60 | 10 | 12 | 646 | 646 | 646 | 0.015381 | 247 | 0.005881 | 737 | 0.017548 | 1.385 | A06 | BIWW0.05006010
Build-In | Build-In Wall | BIWW.05006011 | 50 | 60 | 11 | 12 | 832 | 832 | 832 | 0.01981 | 307 | 0.0073095 | 954 | 0.022714 | 1.438 | A06 | BIWW0.05006011
Build-In | Build-In Wall | BIWW.05006011/DBE | 50 | 60 | 11 | #N/A | 1132 | 1132 | 1132 | 0.026952 | 566 | 0.013476 | 1245 | 0.029643 | 1 | A06 | BIWW0.05006011/DBE
Build-In | Build-In Wall | BIWW.05006015 | 50 | 60 | 15 | 17 | 1040 | 1040 | 1040 | 0.024762 | 401 | 0.0095476 | 1186 | 0.028238 | 1.373 | A06 | BIWW0.05006015
Build-In | Build-In Wall | BIWW.05006016 | 50 | 60 | 16 | 17 | 1139 | 1139 | 1139 | 0.027119 | 412 | 0.0098095 | 1310 | 0.03119 | 1.464 | A06 | BIWW0.05006016
Build-In | Build-In Wall | BIWW.05006016/DBE | 50 | 60 | 16 | #N/A | 1619 | 1619 | 1619 | 0.038548 | 810 | 0.019286 | 1781 | 0.042405 | 1 | A06 | BIWW0.05006016/DBE
Build-In | Build-In Wall | BIWW.05006020 | 50 | 60 | 20 | 22 | 1455 | 1455 | 1455 | 0.034643 | 562 | 0.013381 | 1659 | 0.0395 | 1.373 | A06 | BIWW0.05006020
Build-In | Build-In Wall | BIWW.05006021 | 50 | 60 | 21 | 22 | 1549 | 1549 | 1549 | 0.036881 | 553 | 0.013167 | 1784 | 0.042476 | 1.485 | A06 | BIWW0.05006021
Build-In | Build-In Wall | BIWW.05006021/DBE | 50 | 60 | 21 | #N/A | 2029 | 2029 | 2029 | 0.04831 | 1015 | 0.024167 | 2232 | 0.053143 | 1 | A06 | BIWW0.05006021/DBE
Build-In | Build-In Wall | BIWW.05007010 | 50 | 70 | 10 | 12 | 753 | 753 | 753 | 0.017929 | 288 | 0.0068571 | 859 | 0.020452 | 1.385 | A06 | BIWW0.05007010
Build-In | Build-In Wall | BIWW.05007011 | 50 | 70 | 11 | 12 | 970 | 970 | 970 | 0.023095 | 358 | 0.0085238 | 1113 | 0.0265 | 1.438 | A06 | BIWW0.05007011
Build-In | Build-In Wall | BIWW.05007011/DBE | 50 | 70 | 11 | #N/A | 1270 | 1270 | 1270 | 0.030238 | 635 | 0.015119 | 1397 | 0.033262 | 1 | A06 | BIWW0.05007011/DBE
Build-In | Build-In Wall | BIWW.05007015 | 50 | 70 | 15 | 17 | 1214 | 1214 | 1214 | 0.028905 | 469 | 0.011167 | 1384 | 0.032952 | 1.373 | A06 | BIWW0.05007015
Build-In | Build-In Wall | BIWW.05007016 | 50 | 70 | 16 | 17 | 1329 | 1329 | 1329 | 0.031643 | 481 | 0.011452 | 1528 | 0.036381 | 1.464 | A06 | BIWW0.05007016
Build-In | Build-In Wall | BIWW.05007016/DBE | 50 | 70 | 16 | #N/A | 1809 | 1809 | 1809 | 0.043071 | 905 | 0.021548 | 1990 | 0.047381 | 1 | A06 | BIWW0.05007016/DBE
Build-In | Build-In Wall | BIWW.05007020 | 50 | 70 | 20 | 22 | 1698 | 1698 | 1698 | 0.040429 | 655 | 0.015595 | 1936 | 0.046095 | 1.373 | A06 | BIWW0.05007020
Build-In | Build-In Wall | BIWW.05007021 | 50 | 70 | 21 | 22 | 1807 | 1807 | 1807 | 0.043024 | 645 | 0.015357 | 2082 | 0.049571 | 1.485 | A06 | BIWW0.05007021
Build-In | Build-In Wall | BIWW.05007021/DBE | 50 | 70 | 21 | #N/A | 2287 | 2287 | 2287 | 0.054452 | 1144 | 0.027238 | 2516 | 0.059905 | 1 | A06 | BIWW0.05007021/DBE
Build-In | Build-In Wall | BIWW.05008010 | 50 | 80 | 10 | 12 | 861 | 861 | 861 | 0.0205 | 330 | 0.0078571 | 982 | 0.023381 | 1.385 | A06 | BIWW0.05008010
Build-In | Build-In Wall | BIWW.05008011 | 50 | 80 | 11 | 12 | 1109 | 1109 | 1109 | 0.026405 | 409 | 0.0097381 | 1272 | 0.030286 | 1.438 | A06 | BIWW0.05008011
Build-In | Build-In Wall | BIWW.05008011/DBE | 50 | 80 | 11 | #N/A | 1409 | 1409 | 1409 | 0.033548 | 705 | 0.016786 | 1550 | 0.036905 | 1 | A06 | BIWW0.05008011/DBE
Build-In | Build-In Wall | BIWW.05008015 | 50 | 80 | 15 | 17 | 1387 | 1387 | 1387 | 0.033024 | 535 | 0.012738 | 1581 | 0.037643 | 1.373 | A06 | BIWW0.05008015
Build-In | Build-In Wall | BIWW.05008016 | 50 | 80 | 16 | 17 | 1518 | 1518 | 1518 | 0.036143 | 550 | 0.013095 | 1746 | 0.041571 | 1.464 | A06 | BIWW0.05008016
Build-In | Build-In Wall | BIWW.05008016/DBE | 50 | 80 | 16 | #N/A | 1998 | 1998 | 1998 | 0.047571 | 999 | 0.023786 | 2198 | 0.052333 | 1 | A06 | BIWW0.05008016/DBE
Build-In | Build-In Wall | BIWW.05008020 | 50 | 80 | 20 | 22 | 1940 | 1940 | 1940 | 0.04619 | 749 | 0.017833 | 2212 | 0.052667 | 1.373 | A06 | BIWW0.05008020
Build-In | Build-In Wall | BIWW.05008021 | 50 | 80 | 21 | 22 | 2066 | 2066 | 2066 | 0.04919 | 738 | 0.017571 | 2380 | 0.056667 | 1.485 | A06 | BIWW0.05008021
Build-In | Build-In Wall | BIWW.05008021/DBE | 50 | 80 | 21 | #N/A | 2546 | 2546 | 2546 | 0.060619 | 1273 | 0.03031 | 2801 | 0.06669 | 1 | A06 | BIWW0.05008021/DBE
Build-In | Build-In Wall | BIWW.05009010 | 50 | 90 | 10 | 12 | 968 | 968 | 968 | 0.023048 | 371 | 0.0088333 | 1104 | 0.026286 | 1.385 | A06 | BIWW0.05009010
Build-In | Build-In Wall | BIWW.05009011 | 50 | 90 | 11 | 12 | 1247 | 1247 | 1247 | 0.02969 | 460 | 0.010952 | 1430 | 0.034048 | 1.438 | A06 | BIWW0.05009011
Build-In | Build-In Wall | BIWW.05009011/DBE | 50 | 90 | 11 | #N/A | 1847 | 1847 | 1847 | 0.043976 | 924 | 0.022 | 2032 | 0.048381 | 1 | A06 | BIWW0.05009011/DBE
Build-In | Build-In Wall | BIWW.05009015 | 50 | 90 | 15 | 17 | 1561 | 1561 | 1561 | 0.037167 | 603 | 0.014357 | 1780 | 0.042381 | 1.373 | A06 | BIWW0.05009015
Build-In | Build-In Wall | BIWW.05009016 | 50 | 90 | 16 | 17 | 1708 | 1708 | 1708 | 0.040667 | 618 | 0.014714 | 1964 | 0.046762 | 1.464 | A06 | BIWW0.05009016
Build-In | Build-In Wall | BIWW.05009016/DBE | 50 | 90 | 16 | #N/A | 2668 | 2668 | 2668 | 0.063524 | 1334 | 0.031762 | 2935 | 0.069881 | 1 | A06 | BIWW0.05009016/DBE
Build-In | Build-In Wall | BIWW.05009020 | 50 | 90 | 20 | 22 | 2183 | 2183 | 2183 | 0.051976 | 843 | 0.020071 | 2489 | 0.059262 | 1.373 | A06 | BIWW0.05009020
Build-In | Build-In Wall | BIWW.05009021 | 50 | 90 | 21 | 22 | 2324 | 2324 | 2324 | 0.055333 | 830 | 0.019762 | 2677 | 0.063738 | 1.485 | A06 | BIWW0.05009021
Build-In | Build-In Wall | BIWW.05009021/DBE | 50 | 90 | 21 | #N/A | 3284 | 3284 | 3284 | 0.07819 | 1642 | 0.039095 | 3612 | 0.086 | 1 | A06 | BIWW0.05009021/DBE
Build-In | Build-In Wall | BIWW.05010010 | 50 | 100 | 10 | 12 | 1076 | 1076 | 1076 | 0.025619 | 412 | 0.0098095 | 1228 | 0.029238 | 1.385 | A06 | BIWW0.05010010
Build-In | Build-In Wall | BIWW.05010011 | 50 | 100 | 11 | 12 | 1386 | 1386 | 1386 | 0.033 | 511 | 0.012167 | 1590 | 0.037857 | 1.438 | A06 | BIWW0.05010011
Build-In | Build-In Wall | BIWW.05010011/DBE | 50 | 100 | 11 | #N/A | 1986 | 1986 | 1986 | 0.047286 | 993 | 0.023643 | 2185 | 0.052024 | 1 | A06 | BIWW0.05010011/DBE
Build-In | Build-In Wall | BIWW.05010015 | 50 | 100 | 15 | 17 | 1734 | 1734 | 1734 | 0.041286 | 669 | 0.015929 | 1977 | 0.047071 | 1.373 | A06 | BIWW0.05010015
Build-In | Build-In Wall | BIWW.05010016 | 50 | 100 | 16 | 17 | 1898 | 1898 | 1898 | 0.04519 | 687 | 0.016357 | 2183 | 0.051976 | 1.464 | A06 | BIWW0.05010016
Build-In | Build-In Wall | BIWW.05010016/DBE | 50 | 100 | 16 | #N/A | 2858 | 2858 | 2858 | 0.068048 | 1429 | 0.034024 | 3144 | 0.074857 | 1 | A06 | BIWW0.05010016/DBE
Build-In | Build-In Wall | BIWW.05010020 | 50 | 100 | 20 | 22 | 2425 | 2425 | 2425 | 0.057738 | 936 | 0.022286 | 2765 | 0.065833 | 1.373 | A06 | BIWW0.05010020
Build-In | Build-In Wall | BIWW.05010021 | 50 | 100 | 21 | 22 | 2582 | 2582 | 2582 | 0.061476 | 922 | 0.021952 | 2974 | 0.07081 | 1.485 | A06 | BIWW0.05010021
Build-In | Build-In Wall | BIWW.05010021/DBE | 50 | 100 | 21 | #N/A | 3542 | 3542 | 3542 | 0.084333 | 1771 | 0.042167 | 3896 | 0.092762 | 1 | A06 | BIWW0.05010021/DBE
Build-In | Build-In Wall | BIWW.05011010 | 50 | 110 | 10 | 12 | 1184 | 1184 | 1184 | 0.02819 | 453 | 0.010786 | 1351 | 0.032167 | 1.385 | A06 | BIWW0.05011010
Build-In | Build-In Wall | BIWW.05011011 | 50 | 110 | 11 | 12 | 1525 | 1525 | 1525 | 0.03631 | 563 | 0.013405 | 1749 | 0.041643 | 1.438 | A06 | BIWW0.05011011
Build-In | Build-In Wall | BIWW.05011011/DBE | 50 | 110 | 11 | #N/A | 2125 | 2125 | 2125 | 0.050595 | 1063 | 0.02531 | 2338 | 0.055667 | 1 | A06 | BIWW0.05011011/DBE
Build-In | Build-In Wall | BIWW.05011015 | 50 | 110 | 15 | 17 | 1907 | 1907 | 1907 | 0.045405 | 736 | 0.017524 | 2174 | 0.051762 | 1.373 | A06 | BIWW0.05011015
Build-In | Build-In Wall | BIWW.05011016 | 50 | 110 | 16 | 17 | 2088 | 2088 | 2088 | 0.049714 | 756 | 0.018 | 2401 | 0.057167 | 1.464 | A06 | BIWW0.05011016
Build-In | Build-In Wall | BIWW.05011016/DBE | 50 | 110 | 16 | #N/A | 3048 | 3048 | 3048 | 0.072571 | 1524 | 0.036286 | 3353 | 0.079833 | 1 | A06 | BIWW0.05011016/DBE
Build-In | Build-In Wall | BIWW.05011020 | 50 | 110 | 20 | 22 | 2668 | 2668 | 2668 | 0.063524 | 1030 | 0.024524 | 3042 | 0.072429 | 1.373 | A06 | BIWW0.05011020
Build-In | Build-In Wall | BIWW.05011021 | 50 | 110 | 21 | 22 | 2840 | 2840 | 2840 | 0.067619 | 1014 | 0.024143 | 3272 | 0.077905 | 1.485 | A06 | BIWW0.05011021
Build-In | Build-In Wall | BIWW.05011021/DBE | 50 | 110 | 21 | #N/A | 3800 | 3800 | 3800 | 0.090476 | 1900 | 0.045238 | 4180 | 0.099524 | 1 | A06 | BIWW0.05011021/DBE
Build-In | Build-In Wall | BIWW.05012010 | 50 | 120 | 10 | 12 | 1291 | 1291 | 1291 | 0.030738 | 494 | 0.011762 | 1473 | 0.035071 | 1.385 | A06 | BIWW0.05012010
Build-In | Build-In Wall | BIWW.05012011 | 50 | 120 | 11 | 12 | 1663 | 1663 | 1663 | 0.039595 | 614 | 0.014619 | 1907 | 0.045405 | 1.438 | A06 | BIWW0.05012011
Build-In | Build-In Wall | BIWW.05012011/DBE | 50 | 120 | 11 | #N/A | 2263 | 2263 | 2263 | 0.053881 | 1132 | 0.026952 | 2489 | 0.059262 | 1 | A06 | BIWW0.05012011/DBE
Build-In | Build-In Wall | BIWW.05012015 | 50 | 120 | 15 | 17 | 2081 | 2081 | 2081 | 0.049548 | 803 | 0.019119 | 2372 | 0.056476 | 1.373 | A06 | BIWW0.05012015
Build-In | Build-In Wall | BIWW.05012016 | 50 | 120 | 16 | 17 | 2278 | 2278 | 2278 | 0.054238 | 825 | 0.019643 | 2620 | 0.062381 | 1.464 | A06 | BIWW0.05012016
Build-In | Build-In Wall | BIWW.05012016/DBE | 50 | 120 | 16 | #N/A | 3238 | 3238 | 3238 | 0.077095 | 1619 | 0.038548 | 3562 | 0.08481 | 1 | A06 | BIWW0.05012016/DBE
Build-In | Build-In Wall | BIWW.05012020 | 50 | 120 | 20 | 22 | 2910 | 2910 | 2910 | 0.069286 | 1123 | 0.026738 | 3317 | 0.078976 | 1.373 | A06 | BIWW0.05012020
Build-In | Build-In Wall | BIWW.05012021 | 50 | 120 | 21 | 22 | 3098 | 3098 | 3098 | 0.073762 | 1106 | 0.026333 | 3569 | 0.084976 | 1.485 | A06 | BIWW0.05012021
Build-In | Build-In Wall | BIWW.05012021/DBE | 50 | 120 | 21 | #N/A | 4058 | 4058 | 4058 | 0.096619 | 2029 | 0.04831 | 4464 | 0.10629 | 1 | A06 | BIWW0.05012021/DBE
Build-In | Build-In Wall | BIWW.05014010 | 50 | 140 | 10 | 12 | 1506 | 1506 | 1506 | 0.035857 | 577 | 0.013738 | 1718 | 0.040905 | 1.385 | A06 | BIWW0.05014010
Build-In | Build-In Wall | BIWW.05014011 | 50 | 140 | 11 | 12 | 1940 | 1940 | 1940 | 0.04619 | 716 | 0.017048 | 2225 | 0.052976 | 1.438 | A06 | BIWW0.05014011
Build-In | Build-In Wall | BIWW.05014011/DBE | 50 | 140 | 11 | #N/A | 2540 | 2540 | 2540 | 0.060476 | 1270 | 0.030238 | 2794 | 0.066524 | 1 | A06 | BIWW0.05014011/DBE
Build-In | Build-In Wall | BIWW.05014015 | 50 | 140 | 15 | 17 | 2428 | 2428 | 2428 | 0.05781 | 937 | 0.02231 | 2768 | 0.065905 | 1.373 | A06 | BIWW0.05014015
Build-In | Build-In Wall | BIWW.05014016 | 50 | 140 | 16 | 17 | 2657 | 2657 | 2657 | 0.063262 | 962 | 0.022905 | 3056 | 0.072762 | 1.464 | A06 | BIWW0.05014016
Build-In | Build-In Wall | BIWW.05014016/DBE | 50 | 140 | 16 | #N/A | 3617 | 3617 | 3617 | 0.086119 | 1809 | 0.043071 | 3979 | 0.094738 | 1 | A06 | BIWW0.05014016/DBE
Build-In | Build-In Wall | BIWW.05014020 | 50 | 140 | 20 | 22 | 3395 | 3395 | 3395 | 0.080833 | 1310 | 0.03119 | 3870 | 0.092143 | 1.373 | A06 | BIWW0.05014020
Build-In | Build-In Wall | BIWW.05014021 | 50 | 140 | 21 | 22 | 3615 | 3615 | 3615 | 0.086071 | 1291 | 0.030738 | 4164 | 0.099143 | 1.485 | A06 | BIWW0.05014021
Build-In | Build-In Wall | BIWW.05014021/DBE | 50 | 140 | 21 | #N/A | 4575 | 4575 | 4575 | 0.10893 | 2288 | 0.054476 | 5033 | 0.11983 | 1 | A06 | BIWW0.05014021/DBE
Build-In | Build-In Wall | BIWW.05016010 | 50 | 160 | 10 | 12 | 1722 | 1722 | 1722 | 0.041 | 660 | 0.015714 | 1965 | 0.046786 | 1.385 | A06 | BIWW0.05016010
Build-In | Build-In Wall | BIWW.05016011 | 50 | 160 | 11 | 12 | 2218 | 2218 | 2218 | 0.05281 | 818 | 0.019476 | 2544 | 0.060571 | 1.438 | A06 | BIWW0.05016011
Build-In | Build-In Wall | BIWW.05016011/DBE | 50 | 160 | 11 | #N/A | 3418 | 3418 | 3418 | 0.081381 | 1709 | 0.04069 | 3760 | 0.089524 | 1 | A06 | BIWW0.05016011/DBE
Build-In | Build-In Wall | BIWW.05016015 | 50 | 160 | 15 | 17 | 2774 | 2774 | 2774 | 0.066048 | 1071 | 0.0255 | 3162 | 0.075286 | 1.373 | A06 | BIWW0.05016015
Build-In | Build-In Wall | BIWW.05016016 | 50 | 160 | 16 | 17 | 3037 | 3037 | 3037 | 0.07231 | 1099 | 0.026167 | 3493 | 0.083167 | 1.464 | A06 | BIWW0.05016016
Build-In | Build-In Wall | BIWW.05016016/DBE | 50 | 160 | 16 | #N/A | 4957 | 4957 | 4957 | 0.11802 | 2479 | 0.059024 | 5453 | 0.12983 | 1 | A06 | BIWW0.05016016/DBE
Build-In | Build-In Wall | BIWW.05016020 | 50 | 160 | 20 | 22 | 3880 | 3880 | 3880 | 0.092381 | 1498 | 0.035667 | 4423 | 0.10531 | 1.373 | A06 | BIWW0.05016020
Build-In | Build-In Wall | BIWW.05016021 | 50 | 160 | 21 | 22 | 4131 | 4131 | 4131 | 0.098357 | 1475 | 0.035119 | 4759 | 0.11331 | 1.485 | A06 | BIWW0.05016021
Build-In | Build-In Wall | BIWW.05016021/DBE | 50 | 160 | 21 | #N/A | 6051 | 6051 | 6051 | 0.14407 | 3026 | 0.072048 | 6656 | 0.15848 | 1 | A06 | BIWW0.05016021/DBE
Build-In | Build-In Wall | BIWW.05018010 | 50 | 180 | 10 | 12 | 1937 | 1937 | 1937 | 0.046119 | 742 | 0.017667 | 2210 | 0.052619 | 1.385 | A06 | BIWW0.05018010
Build-In | Build-In Wall | BIWW.05018011 | 50 | 180 | 11 | 12 | 2495 | 2495 | 2495 | 0.059405 | 921 | 0.021929 | 2862 | 0.068143 | 1.438 | A06 | BIWW0.05018011
Build-In | Build-In Wall | BIWW.05018011/DBE | 50 | 180 | 11 | #N/A | 3695 | 3695 | 3695 | 0.087976 | 1848 | 0.044 | 4065 | 0.096786 | 1 | A06 | BIWW0.05018011/DBE
Build-In | Build-In Wall | BIWW.05018015 | 50 | 180 | 15 | 17 | 3121 | 3121 | 3121 | 0.07431 | 1205 | 0.02869 | 3558 | 0.084714 | 1.373 | A06 | BIWW0.05018015
Build-In | Build-In Wall | BIWW.05018016 | 50 | 180 | 16 | 17 | 3416 | 3416 | 3416 | 0.081333 | 1237 | 0.029452 | 3928 | 0.093524 | 1.464 | A06 | BIWW0.05018016
Build-In | Build-In Wall | BIWW.05018016/DBE | 50 | 180 | 16 | #N/A | 5336 | 5336 | 5336 | 0.12705 | 2668 | 0.063524 | 5870 | 0.13976 | 1 | A06 | BIWW0.05018016/DBE
Build-In | Build-In Wall | BIWW.05018020 | 50 | 180 | 20 | 22 | 4365 | 4365 | 4365 | 0.10393 | 1685 | 0.040119 | 4976 | 0.11848 | 1.373 | A06 | BIWW0.05018020
Build-In | Build-In Wall | BIWW.05018021 | 50 | 180 | 21 | 22 | 4648 | 4648 | 4648 | 0.11067 | 1659 | 0.0395 | 5354 | 0.12748 | 1.485 | A06 | BIWW0.05018021
Build-In | Build-In Wall | BIWW.05018021/DBE | 50 | 180 | 21 | #N/A | 6568 | 6568 | 6568 | 0.15638 | 3284 | 0.07819 | 7225 | 0.17202 | 1 | A06 | BIWW0.05018021/DBE
Build-In | Build-In Wall | BIWW.05020010 | 50 | 200 | 10 | 12 | 2152 | 2152 | 2152 | 0.051238 | 824 | 0.019619 | 2455 | 0.058452 | 1.385 | A06 | BIWW0.05020010
Build-In | Build-In Wall | BIWW.05020011 | 50 | 200 | 11 | 12 | 2772 | 2772 | 2772 | 0.066 | 1023 | 0.024357 | 3179 | 0.07569 | 1.438 | A06 | BIWW0.05020011
Build-In | Build-In Wall | BIWW.05020011/DBE | 50 | 200 | 11 | #N/A | 3972 | 3972 | 3972 | 0.094571 | 1986 | 0.047286 | 4369 | 0.10402 | 1 | A06 | BIWW0.05020011/DBE
Build-In | Build-In Wall | BIWW.05020015 | 50 | 200 | 15 | 17 | 3468 | 3468 | 3468 | 0.082571 | 1339 | 0.031881 | 3954 | 0.094143 | 1.373 | A06 | BIWW0.05020015
Build-In | Build-In Wall | BIWW.05020016 | 50 | 200 | 16 | 17 | 3796 | 3796 | 3796 | 0.090381 | 1374 | 0.032714 | 4365 | 0.10393 | 1.464 | A06 | BIWW0.05020016
Build-In | Build-In Wall | BIWW.05020016/DBE | 50 | 200 | 16 | #N/A | 5716 | 5716 | 5716 | 0.1361 | 2858 | 0.068048 | 6288 | 0.14971 | 1 | A06 | BIWW0.05020016/DBE
Build-In | Build-In Wall | BIWW.05020020 | 50 | 200 | 20 | 22 | 4850 | 4850 | 4850 | 0.11548 | 1872 | 0.044571 | 5529 | 0.13164 | 1.373 | A06 | BIWW0.05020020
Build-In | Build-In Wall | BIWW.05020021 | 50 | 200 | 21 | 22 | 5164 | 5164 | 5164 | 0.12295 | 1844 | 0.043905 | 5949 | 0.14164 | 1.485 | A06 | BIWW0.05020021
Build-In | Build-In Wall | BIWW.05020021/DBE | 50 | 200 | 21 | #N/A | 7084 | 7084 | 7084 | 0.16867 | 3542 | 0.084333 | 7792 | 0.18552 | 1 | A06 | BIWW0.05020021/DBE
Build-In | Build-In Wall | BIWW.05022010 | 50 | 220 | 10 | 12 | 2367 | 2367 | 2367 | 0.056357 | 907 | 0.021595 | 2701 | 0.06431 | 1.385 | A06 | BIWW0.05022010
Build-In | Build-In Wall | BIWW.05022011 | 50 | 220 | 11 | 12 | 3049 | 3049 | 3049 | 0.072595 | 1125 | 0.026786 | 3497 | 0.083262 | 1.438 | A06 | BIWW0.05022011
Build-In | Build-In Wall | BIWW.05022011/DBE | 50 | 220 | 11 | #N/A | 4249 | 4249 | 4249 | 0.10117 | 2125 | 0.050595 | 4674 | 0.11129 | 1 | A06 | BIWW0.05022011/DBE
Build-In | Build-In Wall | BIWW.05022015 | 50 | 220 | 15 | 17 | 3815 | 3815 | 3815 | 0.090833 | 1473 | 0.035071 | 4349 | 0.10355 | 1.373 | A06 | BIWW0.05022015
Build-In | Build-In Wall | BIWW.05022016 | 50 | 220 | 16 | 17 | 4176 | 4176 | 4176 | 0.099429 | 1512 | 0.036 | 4802 | 0.11433 | 1.464 | A06 | BIWW0.05022016
Build-In | Build-In Wall | BIWW.05022016/DBE | 50 | 220 | 16 | #N/A | 6096 | 6096 | 6096 | 0.14514 | 3048 | 0.072571 | 6706 | 0.15967 | 1 | A06 | BIWW0.05022016/DBE
Build-In | Build-In Wall | BIWW.05022020 | 50 | 220 | 20 | 22 | 5335 | 5335 | 5335 | 0.12702 | 2059 | 0.049024 | 6082 | 0.14481 | 1.373 | A06 | BIWW0.05022020
Build-In | Build-In Wall | BIWW.05022021 | 50 | 220 | 21 | 22 | 5680 | 5680 | 5680 | 0.13524 | 2028 | 0.048286 | 6543 | 0.15579 | 1.485 | A06 | BIWW0.05022021
Build-In | Build-In Wall | BIWW.05022021/DBE | 50 | 220 | 21 | #N/A | 7600 | 7600 | 7600 | 0.18095 | 3800 | 0.090476 | 8360 | 0.19905 | 1 | A06 | BIWW0.05022021/DBE
Build-In | Build-In Wall | BIWW.05024010 | 50 | 240 | 10 | 12 | 2582 | 2582 | 2582 | 0.061476 | 989 | 0.023548 | 2946 | 0.070143 | 1.385 | A06 | BIWW0.05024010
Build-In | Build-In Wall | BIWW.05024011 | 50 | 240 | 11 | 12 | 3326 | 3326 | 3326 | 0.07919 | 1227 | 0.029214 | 3815 | 0.090833 | 1.438 | A06 | BIWW0.05024011
Build-In | Build-In Wall | BIWW.05024011/DBE | 50 | 240 | 11 | #N/A | 5126 | 5126 | 5126 | 0.12205 | 2563 | 0.061024 | 5639 | 0.13426 | 1 | A06 | BIWW0.05024011/DBE
Build-In | Build-In Wall | BIWW.05024015 | 50 | 240 | 15 | 17 | 4162 | 4162 | 4162 | 0.099095 | 1607 | 0.038262 | 4745 | 0.11298 | 1.373 | A06 | BIWW0.05024015
Build-In | Build-In Wall | BIWW.05024016 | 50 | 240 | 16 | 17 | 4555 | 4555 | 4555 | 0.10845 | 1649 | 0.039262 | 5238 | 0.12471 | 1.464 | A06 | BIWW0.05024016
Build-In | Build-In Wall | BIWW.05024016/DBE | 50 | 240 | 16 | #N/A | 7435 | 7435 | 7435 | 0.17702 | 3718 | 0.088524 | 8179 | 0.19474 | 1 | A06 | BIWW0.05024016/DBE
Build-In | Build-In Wall | BIWW.05024020 | 50 | 240 | 20 | 22 | 5820 | 5820 | 5820 | 0.13857 | 2247 | 0.0535 | 6635 | 0.15798 | 1.373 | A06 | BIWW0.05024020
Build-In | Build-In Wall | BIWW.05024021 | 50 | 240 | 21 | 22 | 6197 | 6197 | 6197 | 0.14755 | 2212 | 0.052667 | 7139 | 0.16998 | 1.485 | A06 | BIWW0.05024021
Build-In | Build-In Wall | BIWW.05024021/DBE | 50 | 240 | 21 | #N/A | 9077 | 9077 | 9077 | 0.21612 | 4539 | 0.10807 | 9985 | 0.23774 | 1 | A06 | BIWW0.05024021/DBE
Build-In | Build-In Wall | BIWW.05026010 | 50 | 260 | 10 | 12 | 2798 | 2798 | 2798 | 0.066619 | 1072 | 0.025524 | 3193 | 0.076024 | 1.385 | A06 | BIWW0.05026010
Build-In | Build-In Wall | BIWW.05026011 | 50 | 260 | 11 | 12 | 3604 | 3604 | 3604 | 0.08581 | 1330 | 0.031667 | 4134 | 0.098429 | 1.438 | A06 | BIWW0.05026011
Build-In | Build-In Wall | BIWW.05026011/DBE | 50 | 260 | 11 | #N/A | 5404 | 5404 | 5404 | 0.12867 | 2702 | 0.064333 | 5944 | 0.14152 | 1 | A06 | BIWW0.05026011/DBE
Build-In | Build-In Wall | BIWW.05026015 | 50 | 260 | 15 | 17 | 4508 | 4508 | 4508 | 0.10733 | 1740 | 0.041429 | 5139 | 0.12236 | 1.373 | A06 | BIWW0.05026015
Build-In | Build-In Wall | BIWW.05026016 | 50 | 260 | 16 | 17 | 4935 | 4935 | 4935 | 0.1175 | 1786 | 0.042524 | 5675 | 0.13512 | 1.464 | A06 | BIWW0.05026016
Build-In | Build-In Wall | BIWW.05026016/DBE | 50 | 260 | 16 | #N/A | 7815 | 7815 | 7815 | 0.18607 | 3908 | 0.093048 | 8597 | 0.20469 | 1 | A06 | BIWW0.05026016/DBE
Build-In | Build-In Wall | BIWW.05026020 | 50 | 260 | 20 | 22 | 6305 | 6305 | 6305 | 0.15012 | 2434 | 0.057952 | 7188 | 0.17114 | 1.373 | A06 | BIWW0.05026020
Build-In | Build-In Wall | BIWW.05026021 | 50 | 260 | 21 | 22 | 6713 | 6713 | 6713 | 0.15983 | 2397 | 0.057071 | 7733 | 0.18412 | 1.485 | A06 | BIWW0.05026021
Build-In | Build-In Wall | BIWW.05026021/DBE | 50 | 260 | 21 | #N/A | 9593 | 9593 | 9593 | 0.2284 | 4797 | 0.11421 | 10552 | 0.25124 | 1 | A06 | BIWW0.05026021/DBE
Build-In | Build-In Wall | BIWW.05028010 | 50 | 280 | 10 | 12 | 3013 | 3013 | 3013 | 0.071738 | 1154 | 0.027476 | 3438 | 0.081857 | 1.385 | A06 | BIWW0.05028010
Build-In | Build-In Wall | BIWW.05028011 | 50 | 280 | 11 | 12 | 3881 | 3881 | 3881 | 0.092405 | 1432 | 0.034095 | 4452 | 0.106 | 1.438 | A06 | BIWW0.05028011
Build-In | Build-In Wall | BIWW.05028011/DBE | 50 | 280 | 11 | #N/A | 5681 | 5681 | 5681 | 0.13526 | 2841 | 0.067643 | 6249 | 0.14879 | 1 | A06 | BIWW0.05028011/DBE
Build-In | Build-In Wall | BIWW.05028015 | 50 | 280 | 15 | 17 | 4855 | 4855 | 4855 | 0.1156 | 1874 | 0.044619 | 5535 | 0.13179 | 1.373 | A06 | BIWW0.05028015
Build-In | Build-In Wall | BIWW.05028016 | 50 | 280 | 16 | 17 | 5314 | 5314 | 5314 | 0.12652 | 1924 | 0.04581 | 6111 | 0.1455 | 1.464 | A06 | BIWW0.05028016
Build-In | Build-In Wall | BIWW.05028016/DBE | 50 | 280 | 16 | #N/A | 8194 | 8194 | 8194 | 0.1951 | 4097 | 0.097548 | 9013 | 0.2146 | 1 | A06 | BIWW0.05028016/DBE
Build-In | Build-In Wall | BIWW.05028020 | 50 | 280 | 20 | 22 | 6790 | 6790 | 6790 | 0.16167 | 2621 | 0.062405 | 7741 | 0.18431 | 1.373 | A06 | BIWW0.05028020
Build-In | Build-In Wall | BIWW.05028021 | 50 | 280 | 21 | 22 | 7230 | 7230 | 7230 | 0.17214 | 2581 | 0.061452 | 8329 | 0.19831 | 1.485 | A06 | BIWW0.05028021
Build-In | Build-In Wall | BIWW.05028021/DBE | 50 | 280 | 21 | #N/A | 10110 | 10110 | 10110 | 0.24071 | 5055 | 0.12036 | 11121 | 0.26479 | 1 | A06 | BIWW0.05028021/DBE
Build-In | Build-In Wall | BIWW.05030010 | 50 | 300 | 10 | 12 | 3228 | 3228 | 3228 | 0.076857 | 1236 | 0.029429 | 3683 | 0.08769 | 1.385 | A06 | BIWW0.05030010
Build-In | Build-In Wall | BIWW.05030011 | 50 | 300 | 11 | 12 | 4158 | 4158 | 4158 | 0.099 | 1534 | 0.036524 | 4769 | 0.11355 | 1.438 | A06 | BIWW0.05030011
Build-In | Build-In Wall | BIWW.05030011/DBE | 50 | 300 | 11 | #N/A | 5958 | 5958 | 5958 | 0.14186 | 2979 | 0.070929 | 6554 | 0.15605 | 1 | A06 | BIWW0.05030011/DBE
Build-In | Build-In Wall | BIWW.05030015 | 50 | 300 | 15 | 17 | 5202 | 5202 | 5202 | 0.12386 | 2008 | 0.04781 | 5930 | 0.14119 | 1.373 | A06 | BIWW0.05030015
Build-In | Build-In Wall | BIWW.05030016 | 50 | 300 | 16 | 17 | 5694 | 5694 | 5694 | 0.13557 | 2061 | 0.049071 | 6548 | 0.1559 | 1.464 | A06 | BIWW0.05030016
Build-In | Build-In Wall | BIWW.05030016/DBE | 50 | 300 | 16 | #N/A | 8574 | 8574 | 8574 | 0.20414 | 4287 | 0.10207 | 9431 | 0.22455 | 1 | A06 | BIWW0.05030016/DBE
Build-In | Build-In Wall | BIWW.05030020 | 50 | 300 | 20 | 22 | 7275 | 7275 | 7275 | 0.17321 | 2808 | 0.066857 | 8294 | 0.19748 | 1.373 | A06 | BIWW0.05030020
Build-In | Build-In Wall | BIWW.05030021 | 50 | 300 | 21 | 22 | 7746 | 7746 | 7746 | 0.18443 | 2765 | 0.065833 | 8923 | 0.21245 | 1.485 | A06 | BIWW0.05030021
Build-In | Build-In Wall | BIWW.05030021/DBE | 50 | 300 | 21 | #N/A | 10626 | 10626 | 10626 | 0.253 | 5313 | 0.1265 | 11689 | 0.27831 | 1 | A06 | BIWW0.05030021/DBE
Build-In | Build-In Wall | BIWW.06004010 | 60 | 40 | 10 | 12 | 468 | 468 | 468 | 0.011143 | 180 | 0.0042857 | 534 | 0.012714 | 1.376 | A06 | BIWW0.06004010
Build-In | Build-In Wall | BIWW.06004011 | 60 | 40 | 11 | 12 | 598 | 598 | 598 | 0.014238 | 221 | 0.0052619 | 686 | 0.016333 | 1.437 | A06 | BIWW0.06004011
Build-In | Build-In Wall | BIWW.06004015 | 60 | 40 | 15 | 17 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.361 | A06 | BIWW0.06004015
Build-In | Build-In Wall | BIWW.06004016 | 60 | 40 | 16 | 17 | 834 | 834 | 834 | 0.019857 | 301 | 0.0071667 | 959 | 0.022833 | 1.468 | A06 | BIWW0.06004016
Build-In | Build-In Wall | BIWW.06004020 | 60 | 40 | 20 | 22 | 1043 | 1043 | 1043 | 0.024833 | 406 | 0.0096667 | 1188 | 0.028286 | 1.361 | A06 | BIWW0.06004020
Build-In | Build-In Wall | BIWW.06004021 | 60 | 40 | 21 | 22 | 1153 | 1153 | 1153 | 0.027452 | 409 | 0.0097381 | 1329 | 0.031643 | 1.493 | A06 | BIWW0.06004021
Build-In | Build-In Wall | BIWW.06005010 | 60 | 50 | 10 | 12 | 585 | 585 | 585 | 0.013929 | 225 | 0.0053571 | 667 | 0.015881 | 1.376 | A06 | BIWW0.06005010
Build-In | Build-In Wall | BIWW.06005011 | 60 | 50 | 11 | 12 | 747 | 747 | 747 | 0.017786 | 276 | 0.0065714 | 857 | 0.020405 | 1.437 | A06 | BIWW0.06005011
Build-In | Build-In Wall | BIWW.06005015 | 60 | 50 | 15 | 17 | 933 | 933 | 933 | 0.022214 | 363 | 0.0086429 | 1063 | 0.02531 | 1.361 | A06 | BIWW0.06005015
Build-In | Build-In Wall | BIWW.06005016 | 60 | 50 | 16 | 17 | 1042 | 1042 | 1042 | 0.02481 | 376 | 0.0089524 | 1198 | 0.028524 | 1.468 | A06 | BIWW0.06005016
Build-In | Build-In Wall | BIWW.06005020 | 60 | 50 | 20 | 22 | 1304 | 1304 | 1304 | 0.031048 | 507 | 0.012071 | 1485 | 0.035357 | 1.361 | A06 | BIWW0.06005020
Build-In | Build-In Wall | BIWW.06005021 | 60 | 50 | 21 | 22 | 1441 | 1441 | 1441 | 0.03431 | 512 | 0.01219 | 1661 | 0.039548 | 1.493 | A06 | BIWW0.06005021
Build-In | Build-In Wall | BIWW.06006010 | 60 | 60 | 10 | 12 | 702 | 702 | 702 | 0.016714 | 270 | 0.0064286 | 800 | 0.019048 | 1.376 | A06 | BIWW0.06006010
Build-In | Build-In Wall | BIWW.06006011 | 60 | 60 | 11 | 12 | 896 | 896 | 896 | 0.021333 | 331 | 0.007881 | 1028 | 0.024476 | 1.437 | A06 | BIWW0.06006011
Build-In | Build-In Wall | BIWW.06006011/DBE | 60 | 60 | 11 | #N/A | 1196 | 1196 | 1196 | 0.028476 | 598 | 0.014238 | 1316 | 0.031333 | 1 | A06 | BIWW0.06006011/DBE
Build-In | Build-In Wall | BIWW.06006015 | 60 | 60 | 15 | 17 | 1120 | 1120 | 1120 | 0.026667 | 436 | 0.010381 | 1276 | 0.030381 | 1.361 | A06 | BIWW0.06006015
Build-In | Build-In Wall | BIWW.06006016 | 60 | 60 | 16 | 17 | 1250 | 1250 | 1250 | 0.029762 | 451 | 0.010738 | 1438 | 0.034238 | 1.468 | A06 | BIWW0.06006016
Build-In | Build-In Wall | BIWW.06006016/DBE | 60 | 60 | 16 | #N/A | 1730 | 1730 | 1730 | 0.04119 | 865 | 0.020595 | 1903 | 0.04531 | 1 | A06 | BIWW0.06006016/DBE
Build-In | Build-In Wall | BIWW.06006020 | 60 | 60 | 20 | 22 | 1565 | 1565 | 1565 | 0.037262 | 609 | 0.0145 | 1783 | 0.042452 | 1.361 | A06 | BIWW0.06006020
Build-In | Build-In Wall | BIWW.06006021 | 60 | 60 | 21 | 22 | 1729 | 1729 | 1729 | 0.041167 | 614 | 0.014619 | 1994 | 0.047476 | 1.493 | A06 | BIWW0.06006021
Build-In | Build-In Wall | BIWW.06006021/DBE | 60 | 60 | 21 | #N/A | 2209 | 2209 | 2209 | 0.052595 | 1105 | 0.02631 | 2430 | 0.057857 | 1 | A06 | BIWW0.06006021/DBE
Build-In | Build-In Wall | BIWW.06007010 | 60 | 70 | 10 | 12 | 819 | 819 | 819 | 0.0195 | 315 | 0.0075 | 934 | 0.022238 | 1.376 | A06 | BIWW0.06007010
Build-In | Build-In Wall | BIWW.06007011 | 60 | 70 | 11 | 12 | 1046 | 1046 | 1046 | 0.024905 | 386 | 0.0091905 | 1200 | 0.028571 | 1.437 | A06 | BIWW0.06007011
Build-In | Build-In Wall | BIWW.06007011/DBE | 60 | 70 | 11 | #N/A | 1346 | 1346 | 1346 | 0.032048 | 673 | 0.016024 | 1481 | 0.035262 | 1 | A06 | BIWW0.06007011/DBE
Build-In | Build-In Wall | BIWW.06007015 | 60 | 70 | 15 | 17 | 1306 | 1306 | 1306 | 0.031095 | 508 | 0.012095 | 1488 | 0.035429 | 1.361 | A06 | BIWW0.06007015
Build-In | Build-In Wall | BIWW.06007016 | 60 | 70 | 16 | 17 | 1459 | 1459 | 1459 | 0.034738 | 527 | 0.012548 | 1678 | 0.039952 | 1.468 | A06 | BIWW0.06007016
Build-In | Build-In Wall | BIWW.06007016/DBE | 60 | 70 | 16 | #N/A | 1939 | 1939 | 1939 | 0.046167 | 970 | 0.023095 | 2133 | 0.050786 | 1 | A06 | BIWW0.06007016/DBE
Build-In | Build-In Wall | BIWW.06007020 | 60 | 70 | 20 | 22 | 1826 | 1826 | 1826 | 0.043476 | 710 | 0.016905 | 2080 | 0.049524 | 1.361 | A06 | BIWW0.06007020
Build-In | Build-In Wall | BIWW.06007021 | 60 | 70 | 21 | 22 | 2017 | 2017 | 2017 | 0.048024 | 716 | 0.017048 | 2326 | 0.055381 | 1.493 | A06 | BIWW0.06007021
Build-In | Build-In Wall | BIWW.06007021/DBE | 60 | 70 | 21 | #N/A | 2497 | 2497 | 2497 | 0.059452 | 1249 | 0.029738 | 2747 | 0.065405 | 1 | A06 | BIWW0.06007021/DBE
Build-In | Build-In Wall | BIWW.06008010 | 60 | 80 | 10 | 12 | 936 | 936 | 936 | 0.022286 | 360 | 0.0085714 | 1067 | 0.025405 | 1.376 | A06 | BIWW0.06008010
Build-In | Build-In Wall | BIWW.06008011 | 60 | 80 | 11 | 12 | 1195 | 1195 | 1195 | 0.028452 | 441 | 0.0105 | 1371 | 0.032643 | 1.437 | A06 | BIWW0.06008011
Build-In | Build-In Wall | BIWW.06008011/DBE | 60 | 80 | 11 | #N/A | 1495 | 1495 | 1495 | 0.035595 | 748 | 0.01781 | 1645 | 0.039167 | 1 | A06 | BIWW0.06008011/DBE
Build-In | Build-In Wall | BIWW.06008015 | 60 | 80 | 15 | 17 | 1493 | 1493 | 1493 | 0.035548 | 581 | 0.013833 | 1701 | 0.0405 | 1.361 | A06 | BIWW0.06008015
Build-In | Build-In Wall | BIWW.06008016 | 60 | 80 | 16 | 17 | 1667 | 1667 | 1667 | 0.03969 | 602 | 0.014333 | 1917 | 0.045643 | 1.468 | A06 | BIWW0.06008016
Build-In | Build-In Wall | BIWW.06008016/DBE | 60 | 80 | 16 | #N/A | 2147 | 2147 | 2147 | 0.051119 | 1074 | 0.025571 | 2362 | 0.056238 | 1 | A06 | BIWW0.06008016/DBE
Build-In | Build-In Wall | BIWW.06008020 | 60 | 80 | 20 | 22 | 2086 | 2086 | 2086 | 0.049667 | 811 | 0.01931 | 2376 | 0.056571 | 1.361 | A06 | BIWW0.06008020
Build-In | Build-In Wall | BIWW.06008021 | 60 | 80 | 21 | 22 | 2306 | 2306 | 2306 | 0.054905 | 819 | 0.0195 | 2659 | 0.06331 | 1.493 | A06 | BIWW0.06008021
Build-In | Build-In Wall | BIWW.06008021/DBE | 60 | 80 | 21 | #N/A | 2786 | 2786 | 2786 | 0.066333 | 1393 | 0.033167 | 3065 | 0.072976 | 1 | A06 | BIWW0.06008021/DBE
Build-In | Build-In Wall | BIWW.06009010 | 60 | 90 | 10 | 12 | 1053 | 1053 | 1053 | 0.025071 | 405 | 0.0096429 | 1200 | 0.028571 | 1.376 | A06 | BIWW0.06009010
Build-In | Build-In Wall | BIWW.06009011 | 60 | 90 | 11 | 12 | 1345 | 1345 | 1345 | 0.032024 | 496 | 0.01181 | 1543 | 0.036738 | 1.437 | A06 | BIWW0.06009011
Build-In | Build-In Wall | BIWW.06009011/DBE | 60 | 90 | 11 | #N/A | 1945 | 1945 | 1945 | 0.04631 | 973 | 0.023167 | 2140 | 0.050952 | 1 | A06 | BIWW0.06009011/DBE
Build-In | Build-In Wall | BIWW.06009015 | 60 | 90 | 15 | 17 | 1679 | 1679 | 1679 | 0.039976 | 653 | 0.015548 | 1912 | 0.045524 | 1.361 | A06 | BIWW0.06009015
Build-In | Build-In Wall | BIWW.06009016 | 60 | 90 | 16 | 17 | 1876 | 1876 | 1876 | 0.044667 | 677 | 0.016119 | 2157 | 0.051357 | 1.468 | A06 | BIWW0.06009016
Build-In | Build-In Wall | BIWW.06009016/DBE | 60 | 90 | 16 | #N/A | 2836 | 2836 | 2836 | 0.067524 | 1418 | 0.033762 | 3120 | 0.074286 | 1 | A06 | BIWW0.06009016/DBE
Build-In | Build-In Wall | BIWW.06009020 | 60 | 90 | 20 | 22 | 2347 | 2347 | 2347 | 0.055881 | 913 | 0.021738 | 2673 | 0.063643 | 1.361 | A06 | BIWW0.06009020
Build-In | Build-In Wall | BIWW.06009021 | 60 | 90 | 21 | 22 | 2594 | 2594 | 2594 | 0.061762 | 921 | 0.021929 | 2991 | 0.071214 | 1.493 | A06 | BIWW0.06009021
Build-In | Build-In Wall | BIWW.06009021/DBE | 60 | 90 | 21 | #N/A | 3554 | 3554 | 3554 | 0.084619 | 1777 | 0.04231 | 3909 | 0.093071 | 1 | A06 | BIWW0.06009021/DBE
Build-In | Build-In Wall | BIWW.06010010 | 60 | 100 | 10 | 12 | 1170 | 1170 | 1170 | 0.027857 | 450 | 0.010714 | 1334 | 0.031762 | 1.376 | A06 | BIWW0.06010010
Build-In | Build-In Wall | BIWW.06010011 | 60 | 100 | 11 | 12 | 1494 | 1494 | 1494 | 0.035571 | 551 | 0.013119 | 1714 | 0.04081 | 1.437 | A06 | BIWW0.06010011
Build-In | Build-In Wall | BIWW.06010011/DBE | 60 | 100 | 11 | #N/A | 2094 | 2094 | 2094 | 0.049857 | 1047 | 0.024929 | 2303 | 0.054833 | 1 | A06 | BIWW0.06010011/DBE
Build-In | Build-In Wall | BIWW.06010015 | 60 | 100 | 15 | 17 | 1866 | 1866 | 1866 | 0.044429 | 726 | 0.017286 | 2125 | 0.050595 | 1.361 | A06 | BIWW0.06010015
Build-In | Build-In Wall | BIWW.06010016 | 60 | 100 | 16 | 17 | 2084 | 2084 | 2084 | 0.049619 | 752 | 0.017905 | 2397 | 0.057071 | 1.468 | A06 | BIWW0.06010016
Build-In | Build-In Wall | BIWW.06010016/DBE | 60 | 100 | 16 | #N/A | 3044 | 3044 | 3044 | 0.072476 | 1522 | 0.036238 | 3348 | 0.079714 | 1 | A06 | BIWW0.06010016/DBE
Build-In | Build-In Wall | BIWW.06010020 | 60 | 100 | 20 | 22 | 2608 | 2608 | 2608 | 0.062095 | 1015 | 0.024167 | 2971 | 0.070738 | 1.361 | A06 | BIWW0.06010020
Build-In | Build-In Wall | BIWW.06010021 | 60 | 100 | 21 | 22 | 2882 | 2882 | 2882 | 0.068619 | 1023 | 0.024357 | 3323 | 0.079119 | 1.493 | A06 | BIWW0.06010021
Build-In | Build-In Wall | BIWW.06010021/DBE | 60 | 100 | 21 | #N/A | 3842 | 3842 | 3842 | 0.091476 | 1921 | 0.045738 | 4226 | 0.10062 | 1 | A06 | BIWW0.06010021/DBE
Build-In | Build-In Wall | BIWW.06011010 | 60 | 110 | 10 | 12 | 1287 | 1287 | 1287 | 0.030643 | 495 | 0.011786 | 1467 | 0.034929 | 1.376 | A06 | BIWW0.06011010
Build-In | Build-In Wall | BIWW.06011011 | 60 | 110 | 11 | 12 | 1643 | 1643 | 1643 | 0.039119 | 606 | 0.014429 | 1885 | 0.044881 | 1.437 | A06 | BIWW0.06011011
Build-In | Build-In Wall | BIWW.06011011/DBE | 60 | 110 | 11 | #N/A | 2243 | 2243 | 2243 | 0.053405 | 1122 | 0.026714 | 2467 | 0.058738 | 1 | A06 | BIWW0.06011011/DBE
Build-In | Build-In Wall | BIWW.06011015 | 60 | 110 | 15 | 17 | 2053 | 2053 | 2053 | 0.048881 | 799 | 0.019024 | 2338 | 0.055667 | 1.361 | A06 | BIWW0.06011015
Build-In | Build-In Wall | BIWW.06011016 | 60 | 110 | 16 | 17 | 2292 | 2292 | 2292 | 0.054571 | 827 | 0.01969 | 2636 | 0.062762 | 1.468 | A06 | BIWW0.06011016
Build-In | Build-In Wall | BIWW.06011016/DBE | 60 | 110 | 16 | #N/A | 3252 | 3252 | 3252 | 0.077429 | 1626 | 0.038714 | 3577 | 0.085167 | 1 | A06 | BIWW0.06011016/DBE
Build-In | Build-In Wall | BIWW.06011020 | 60 | 110 | 20 | 22 | 2869 | 2869 | 2869 | 0.06831 | 1116 | 0.026571 | 3268 | 0.07781 | 1.361 | A06 | BIWW0.06011020
Build-In | Build-In Wall | BIWW.06011021 | 60 | 110 | 21 | 22 | 3170 | 3170 | 3170 | 0.075476 | 1125 | 0.026786 | 3655 | 0.087024 | 1.493 | A06 | BIWW0.06011021
Build-In | Build-In Wall | BIWW.06011021/DBE | 60 | 110 | 21 | #N/A | 4130 | 4130 | 4130 | 0.098333 | 2065 | 0.049167 | 4543 | 0.10817 | 1 | A06 | BIWW0.06011021/DBE
Build-In | Build-In Wall | BIWW.06012010 | 60 | 120 | 10 | 12 | 1404 | 1404 | 1404 | 0.033429 | 541 | 0.012881 | 1601 | 0.038119 | 1.376 | A06 | BIWW0.06012010
Build-In | Build-In Wall | BIWW.06012011 | 60 | 120 | 11 | 12 | 1793 | 1793 | 1793 | 0.04269 | 662 | 0.015762 | 2057 | 0.048976 | 1.437 | A06 | BIWW0.06012011
Build-In | Build-In Wall | BIWW.06012011/DBE | 60 | 120 | 11 | #N/A | 2393 | 2393 | 2393 | 0.056976 | 1197 | 0.0285 | 2632 | 0.062667 | 1 | A06 | BIWW0.06012011/DBE
Build-In | Build-In Wall | BIWW.06012015 | 60 | 120 | 15 | 17 | 2239 | 2239 | 2239 | 0.05331 | 871 | 0.020738 | 2550 | 0.060714 | 1.361 | A06 | BIWW0.06012015
Build-In | Build-In Wall | BIWW.06012016 | 60 | 120 | 16 | 17 | 2501 | 2501 | 2501 | 0.059548 | 903 | 0.0215 | 2876 | 0.068476 | 1.468 | A06 | BIWW0.06012016
Build-In | Build-In Wall | BIWW.06012016/DBE | 60 | 120 | 16 | #N/A | 3461 | 3461 | 3461 | 0.082405 | 1731 | 0.041214 | 3807 | 0.090643 | 1 | A06 | BIWW0.06012016/DBE
Build-In | Build-In Wall | BIWW.06012020 | 60 | 120 | 20 | 22 | 3130 | 3130 | 3130 | 0.074524 | 1218 | 0.029 | 3565 | 0.084881 | 1.361 | A06 | BIWW0.06012020
Build-In | Build-In Wall | BIWW.06012021 | 60 | 120 | 21 | 22 | 3458 | 3458 | 3458 | 0.082333 | 1228 | 0.029238 | 3987 | 0.094929 | 1.493 | A06 | BIWW0.06012021
Build-In | Build-In Wall | BIWW.06012021/DBE | 60 | 120 | 21 | #N/A | 4418 | 4418 | 4418 | 0.10519 | 2209 | 0.052595 | 4860 | 0.11571 | 1 | A06 | BIWW0.06012021/DBE
Build-In | Build-In Wall | BIWW.06014010 | 60 | 140 | 10 | 12 | 1638 | 1638 | 1638 | 0.039 | 631 | 0.015024 | 1867 | 0.044452 | 1.376 | A06 | BIWW0.06014010
Build-In | Build-In Wall | BIWW.06014011 | 60 | 140 | 11 | 12 | 2092 | 2092 | 2092 | 0.04981 | 772 | 0.018381 | 2400 | 0.057143 | 1.437 | A06 | BIWW0.06014011
Build-In | Build-In Wall | BIWW.06014011/DBE | 60 | 140 | 11 | #N/A | 2692 | 2692 | 2692 | 0.064095 | 1346 | 0.032048 | 2961 | 0.0705 | 1 | A06 | BIWW0.06014011/DBE
Build-In | Build-In Wall | BIWW.06014015 | 60 | 140 | 15 | 17 | 2612 | 2612 | 2612 | 0.06219 | 1016 | 0.02419 | 2975 | 0.070833 | 1.361 | A06 | BIWW0.06014015
Build-In | Build-In Wall | BIWW.06014016 | 60 | 140 | 16 | 17 | 2918 | 2918 | 2918 | 0.069476 | 1053 | 0.025071 | 3356 | 0.079905 | 1.468 | A06 | BIWW0.06014016
Build-In | Build-In Wall | BIWW.06014016/DBE | 60 | 140 | 16 | #N/A | 3878 | 3878 | 3878 | 0.092333 | 1939 | 0.046167 | 4266 | 0.10157 | 1 | A06 | BIWW0.06014016/DBE
Build-In | Build-In Wall | BIWW.06014020 | 60 | 140 | 20 | 22 | 3651 | 3651 | 3651 | 0.086929 | 1420 | 0.03381 | 4158 | 0.099 | 1.361 | A06 | BIWW0.06014020
Build-In | Build-In Wall | BIWW.06014021 | 60 | 140 | 21 | 22 | 4035 | 4035 | 4035 | 0.096071 | 1432 | 0.034095 | 4652 | 0.11076 | 1.493 | A06 | BIWW0.06014021
Build-In | Build-In Wall | BIWW.06014021/DBE | 60 | 140 | 21 | #N/A | 4995 | 4995 | 4995 | 0.11893 | 2498 | 0.059476 | 5495 | 0.13083 | 1 | A06 | BIWW0.06014021/DBE
Build-In | Build-In Wall | BIWW.06016010 | 60 | 160 | 10 | 12 | 1872 | 1872 | 1872 | 0.044571 | 721 | 0.017167 | 2134 | 0.05081 | 1.376 | A06 | BIWW0.06016010
Build-In | Build-In Wall | BIWW.06016011 | 60 | 160 | 11 | 12 | 2390 | 2390 | 2390 | 0.056905 | 882 | 0.021 | 2741 | 0.065262 | 1.437 | A06 | BIWW0.06016011
Build-In | Build-In Wall | BIWW.06016011/DBE | 60 | 160 | 11 | #N/A | 3590 | 3590 | 3590 | 0.085476 | 1795 | 0.042738 | 3949 | 0.094024 | 1 | A06 | BIWW0.06016011/DBE
Build-In | Build-In Wall | BIWW.06016015 | 60 | 160 | 15 | 17 | 2986 | 2986 | 2986 | 0.071095 | 1162 | 0.027667 | 3401 | 0.080976 | 1.361 | A06 | BIWW0.06016015
Build-In | Build-In Wall | BIWW.06016016 | 60 | 160 | 16 | 17 | 3334 | 3334 | 3334 | 0.079381 | 1204 | 0.028667 | 3834 | 0.091286 | 1.468 | A06 | BIWW0.06016016
Build-In | Build-In Wall | BIWW.06016016/DBE | 60 | 160 | 16 | #N/A | 5254 | 5254 | 5254 | 0.1251 | 2627 | 0.062548 | 5779 | 0.1376 | 1 | A06 | BIWW0.06016016/DBE
Build-In | Build-In Wall | BIWW.06016020 | 60 | 160 | 20 | 22 | 4173 | 4173 | 4173 | 0.099357 | 1623 | 0.038643 | 4753 | 0.11317 | 1.361 | A06 | BIWW0.06016020
Build-In | Build-In Wall | BIWW.06016021 | 60 | 160 | 21 | 22 | 4611 | 4611 | 4611 | 0.10979 | 1637 | 0.038976 | 5316 | 0.12657 | 1.493 | A06 | BIWW0.06016021
Build-In | Build-In Wall | BIWW.06016021/DBE | 60 | 160 | 21 | #N/A | 6531 | 6531 | 6531 | 0.1555 | 3266 | 0.077762 | 7184 | 0.17105 | 1 | A06 | BIWW0.06016021/DBE
Build-In | Build-In Wall | BIWW.06018010 | 60 | 180 | 10 | 12 | 2106 | 2106 | 2106 | 0.050143 | 811 | 0.01931 | 2401 | 0.057167 | 1.376 | A06 | BIWW0.06018010
Build-In | Build-In Wall | BIWW.06018011 | 60 | 180 | 11 | 12 | 2689 | 2689 | 2689 | 0.064024 | 992 | 0.023619 | 3084 | 0.073429 | 1.437 | A06 | BIWW0.06018011
Build-In | Build-In Wall | BIWW.06018011/DBE | 60 | 180 | 11 | #N/A | 3889 | 3889 | 3889 | 0.092595 | 1945 | 0.04631 | 4278 | 0.10186 | 1 | A06 | BIWW0.06018011/DBE
Build-In | Build-In Wall | BIWW.06018015 | 60 | 180 | 15 | 17 | 3359 | 3359 | 3359 | 0.079976 | 1307 | 0.031119 | 3826 | 0.091095 | 1.361 | A06 | BIWW0.06018015
Build-In | Build-In Wall | BIWW.06018016 | 60 | 180 | 16 | 17 | 3751 | 3751 | 3751 | 0.08931 | 1354 | 0.032238 | 4314 | 0.10271 | 1.468 | A06 | BIWW0.06018016
Build-In | Build-In Wall | BIWW.06018016/DBE | 60 | 180 | 16 | #N/A | 5671 | 5671 | 5671 | 0.13502 | 2836 | 0.067524 | 6238 | 0.14852 | 1 | A06 | BIWW0.06018016/DBE
Build-In | Build-In Wall | BIWW.06018020 | 60 | 180 | 20 | 22 | 4694 | 4694 | 4694 | 0.11176 | 1826 | 0.043476 | 5346 | 0.12729 | 1.361 | A06 | BIWW0.06018020
Build-In | Build-In Wall | BIWW.06018021 | 60 | 180 | 21 | 22 | 5188 | 5188 | 5188 | 0.12352 | 1842 | 0.043857 | 5982 | 0.14243 | 1.493 | A06 | BIWW0.06018021
Build-In | Build-In Wall | BIWW.06018021/DBE | 60 | 180 | 21 | #N/A | 7108 | 7108 | 7108 | 0.16924 | 3554 | 0.084619 | 7819 | 0.18617 | 1 | A06 | BIWW0.06018021/DBE
Build-In | Build-In Wall | BIWW.06020010 | 60 | 200 | 10 | 12 | 2340 | 2340 | 2340 | 0.055714 | 901 | 0.021452 | 2668 | 0.063524 | 1.376 | A06 | BIWW0.06020010
Build-In | Build-In Wall | BIWW.06020011 | 60 | 200 | 11 | 12 | 2988 | 2988 | 2988 | 0.071143 | 1103 | 0.026262 | 3427 | 0.081595 | 1.437 | A06 | BIWW0.06020011
Build-In | Build-In Wall | BIWW.06020011/DBE | 60 | 200 | 11 | #N/A | 4188 | 4188 | 4188 | 0.099714 | 2094 | 0.049857 | 4607 | 0.10969 | 1 | A06 | BIWW0.06020011/DBE
Build-In | Build-In Wall | BIWW.06020015 | 60 | 200 | 15 | 17 | 3732 | 3732 | 3732 | 0.088857 | 1452 | 0.034571 | 4251 | 0.10121 | 1.361 | A06 | BIWW0.06020015
Build-In | Build-In Wall | BIWW.06020016 | 60 | 200 | 16 | 17 | 4168 | 4168 | 4168 | 0.099238 | 1505 | 0.035833 | 4793 | 0.11412 | 1.468 | A06 | BIWW0.06020016
Build-In | Build-In Wall | BIWW.06020016/DBE | 60 | 200 | 16 | #N/A | 6088 | 6088 | 6088 | 0.14495 | 3044 | 0.072476 | 6697 | 0.15945 | 1 | A06 | BIWW0.06020016/DBE
Build-In | Build-In Wall | BIWW.06020020 | 60 | 200 | 20 | 22 | 5216 | 5216 | 5216 | 0.12419 | 2029 | 0.04831 | 5941 | 0.14145 | 1.361 | A06 | BIWW0.06020020
Build-In | Build-In Wall | BIWW.06020021 | 60 | 200 | 21 | 22 | 5764 | 5764 | 5764 | 0.13724 | 2046 | 0.048714 | 6646 | 0.15824 | 1.493 | A06 | BIWW0.06020021
Build-In | Build-In Wall | BIWW.06020021/DBE | 60 | 200 | 21 | #N/A | 7684 | 7684 | 7684 | 0.18295 | 3842 | 0.091476 | 8452 | 0.20124 | 1 | A06 | BIWW0.06020021/DBE
Build-In | Build-In Wall | BIWW.06022010 | 60 | 220 | 10 | 12 | 2574 | 2574 | 2574 | 0.061286 | 991 | 0.023595 | 2934 | 0.069857 | 1.376 | A06 | BIWW0.06022010
Build-In | Build-In Wall | BIWW.06022011 | 60 | 220 | 11 | 12 | 3287 | 3287 | 3287 | 0.078262 | 1213 | 0.028881 | 3770 | 0.089762 | 1.437 | A06 | BIWW0.06022011
Build-In | Build-In Wall | BIWW.06022011/DBE | 60 | 220 | 11 | #N/A | 4487 | 4487 | 4487 | 0.10683 | 2244 | 0.053429 | 4936 | 0.11752 | 1 | A06 | BIWW0.06022011/DBE
Build-In | Build-In Wall | BIWW.06022015 | 60 | 220 | 15 | 17 | 4105 | 4105 | 4105 | 0.097738 | 1597 | 0.038024 | 4676 | 0.11133 | 1.361 | A06 | BIWW0.06022015
Build-In | Build-In Wall | BIWW.06022016 | 60 | 220 | 16 | 17 | 4585 | 4585 | 4585 | 0.10917 | 1655 | 0.039405 | 5273 | 0.12555 | 1.468 | A06 | BIWW0.06022016
Build-In | Build-In Wall | BIWW.06022016/DBE | 60 | 220 | 16 | #N/A | 6505 | 6505 | 6505 | 0.15488 | 3253 | 0.077452 | 7156 | 0.17038 | 1 | A06 | BIWW0.06022016/DBE
Build-In | Build-In Wall | BIWW.06022020 | 60 | 220 | 20 | 22 | 5738 | 5738 | 5738 | 0.13662 | 2232 | 0.053143 | 6536 | 0.15562 | 1.361 | A06 | BIWW0.06022020
Build-In | Build-In Wall | BIWW.06022021 | 60 | 220 | 21 | 22 | 6340 | 6340 | 6340 | 0.15095 | 2251 | 0.053595 | 7310 | 0.17405 | 1.493 | A06 | BIWW0.06022021
Build-In | Build-In Wall | BIWW.06022021/DBE | 60 | 220 | 21 | #N/A | 8260 | 8260 | 8260 | 0.19667 | 4130 | 0.098333 | 9086 | 0.21633 | 1 | A06 | BIWW0.06022021/DBE
Build-In | Build-In Wall | BIWW.06024010 | 60 | 240 | 10 | 12 | 2808 | 2808 | 2808 | 0.066857 | 1081 | 0.025738 | 3201 | 0.076214 | 1.376 | A06 | BIWW0.06024010
Build-In | Build-In Wall | BIWW.06024011 | 60 | 240 | 11 | 12 | 3586 | 3586 | 3586 | 0.085381 | 1323 | 0.0315 | 4113 | 0.097929 | 1.437 | A06 | BIWW0.06024011
Build-In | Build-In Wall | BIWW.06024011/DBE | 60 | 240 | 11 | #N/A | 5386 | 5386 | 5386 | 0.12824 | 2693 | 0.064119 | 5925 | 0.14107 | 1 | A06 | BIWW0.06024011/DBE
Build-In | Build-In Wall | BIWW.06024015 | 60 | 240 | 15 | 17 | 4478 | 4478 | 4478 | 0.10662 | 1742 | 0.041476 | 5100 | 0.12143 | 1.361 | A06 | BIWW0.06024015
Build-In | Build-In Wall | BIWW.06024016 | 60 | 240 | 16 | 17 | 5002 | 5002 | 5002 | 0.1191 | 1806 | 0.043 | 5752 | 0.13695 | 1.468 | A06 | BIWW0.06024016
Build-In | Build-In Wall | BIWW.06024016/DBE | 60 | 240 | 16 | #N/A | 7882 | 7882 | 7882 | 0.18767 | 3941 | 0.093833 | 8670 | 0.20643 | 1 | A06 | BIWW0.06024016/DBE
Build-In | Build-In Wall | BIWW.06024020 | 60 | 240 | 20 | 22 | 6259 | 6259 | 6259 | 0.14902 | 2435 | 0.057976 | 7129 | 0.16974 | 1.361 | A06 | BIWW0.06024020
Build-In | Build-In Wall | BIWW.06024021 | 60 | 240 | 21 | 22 | 6917 | 6917 | 6917 | 0.16469 | 2456 | 0.058476 | 7975 | 0.18988 | 1.493 | A06 | BIWW0.06024021
Build-In | Build-In Wall | BIWW.06024021/DBE | 60 | 240 | 21 | #N/A | 9797 | 9797 | 9797 | 0.23326 | 4899 | 0.11664 | 10777 | 0.2566 | 1 | A06 | BIWW0.06024021/DBE
Build-In | Build-In Wall | BIWW.06026010 | 60 | 260 | 10 | 12 | 3042 | 3042 | 3042 | 0.072429 | 1171 | 0.027881 | 3468 | 0.082571 | 1.376 | A06 | BIWW0.06026010
Build-In | Build-In Wall | BIWW.06026011 | 60 | 260 | 11 | 12 | 3884 | 3884 | 3884 | 0.092476 | 1433 | 0.034119 | 4455 | 0.10607 | 1.437 | A06 | BIWW0.06026011
Build-In | Build-In Wall | BIWW.06026011/DBE | 60 | 260 | 11 | #N/A | 5684 | 5684 | 5684 | 0.13533 | 2842 | 0.067667 | 6252 | 0.14886 | 1 | A06 | BIWW0.06026011/DBE
Build-In | Build-In Wall | BIWW.06026015 | 60 | 260 | 15 | 17 | 4852 | 4852 | 4852 | 0.11552 | 1887 | 0.044929 | 5526 | 0.13157 | 1.361 | A06 | BIWW0.06026015
Build-In | Build-In Wall | BIWW.06026016 | 60 | 260 | 16 | 17 | 5418 | 5418 | 5418 | 0.129 | 1956 | 0.046571 | 6231 | 0.14836 | 1.468 | A06 | BIWW0.06026016
Build-In | Build-In Wall | BIWW.06026016/DBE | 60 | 260 | 16 | #N/A | 8298 | 8298 | 8298 | 0.19757 | 4149 | 0.098786 | 9128 | 0.21733 | 1 | A06 | BIWW0.06026016/DBE
Build-In | Build-In Wall | BIWW.06026020 | 60 | 260 | 20 | 22 | 6781 | 6781 | 6781 | 0.16145 | 2638 | 0.06281 | 7724 | 0.1839 | 1.361 | A06 | BIWW0.06026020
Build-In | Build-In Wall | BIWW.06026021 | 60 | 260 | 21 | 22 | 7493 | 7493 | 7493 | 0.1784 | 2660 | 0.063333 | 8639 | 0.20569 | 1.493 | A06 | BIWW0.06026021
Build-In | Build-In Wall | BIWW.06026021/DBE | 60 | 260 | 21 | #N/A | 10373 | 10373 | 10373 | 0.24698 | 5187 | 0.1235 | 11410 | 0.27167 | 1 | A06 | BIWW0.06026021/DBE
Build-In | Build-In Wall | BIWW.06028010 | 60 | 280 | 10 | 12 | 3276 | 3276 | 3276 | 0.078 | 1261 | 0.030024 | 3735 | 0.088929 | 1.376 | A06 | BIWW0.06028010
Build-In | Build-In Wall | BIWW.06028011 | 60 | 280 | 11 | 12 | 4183 | 4183 | 4183 | 0.099595 | 1544 | 0.036762 | 4798 | 0.11424 | 1.437 | A06 | BIWW0.06028011
Build-In | Build-In Wall | BIWW.06028011/DBE | 60 | 280 | 11 | #N/A | 5983 | 5983 | 5983 | 0.14245 | 2992 | 0.071238 | 6581 | 0.15669 | 1 | A06 | BIWW0.06028011/DBE
Build-In | Build-In Wall | BIWW.06028015 | 60 | 280 | 15 | 17 | 5225 | 5225 | 5225 | 0.1244 | 2033 | 0.048405 | 5951 | 0.14169 | 1.361 | A06 | BIWW0.06028015
Build-In | Build-In Wall | BIWW.06028016 | 60 | 280 | 16 | 17 | 5835 | 5835 | 5835 | 0.13893 | 2106 | 0.050143 | 6710 | 0.15976 | 1.468 | A06 | BIWW0.06028016
Build-In | Build-In Wall | BIWW.06028016/DBE | 60 | 280 | 16 | #N/A | 8715 | 8715 | 8715 | 0.2075 | 4358 | 0.10376 | 9587 | 0.22826 | 1 | A06 | BIWW0.06028016/DBE
Build-In | Build-In Wall | BIWW.06028020 | 60 | 280 | 20 | 22 | 7302 | 7302 | 7302 | 0.17386 | 2840 | 0.067619 | 8317 | 0.19802 | 1.361 | A06 | BIWW0.06028020
Build-In | Build-In Wall | BIWW.06028021 | 60 | 280 | 21 | 22 | 8070 | 8070 | 8070 | 0.19214 | 2865 | 0.068214 | 9305 | 0.22155 | 1.493 | A06 | BIWW0.06028021
Build-In | Build-In Wall | BIWW.06028021/DBE | 60 | 280 | 21 | #N/A | 10950 | 10950 | 10950 | 0.26071 | 5475 | 0.13036 | 12045 | 0.28679 | 1 | A06 | BIWW0.06028021/DBE
Build-In | Build-In Wall | BIWW.06030010 | 60 | 300 | 10 | 12 | 3510 | 3510 | 3510 | 0.083571 | 1351 | 0.032167 | 4001 | 0.095262 | 1.376 | A06 | BIWW0.06030010
Build-In | Build-In Wall | BIWW.06030011 | 60 | 300 | 11 | 12 | 4482 | 4482 | 4482 | 0.10671 | 1654 | 0.039381 | 5141 | 0.1224 | 1.437 | A06 | BIWW0.06030011
Build-In | Build-In Wall | BIWW.06030011/DBE | 60 | 300 | 11 | #N/A | 6282 | 6282 | 6282 | 0.14957 | 3141 | 0.074786 | 6910 | 0.16452 | 1 | A06 | BIWW0.06030011/DBE
Build-In | Build-In Wall | BIWW.06030015 | 60 | 300 | 15 | 17 | 5598 | 5598 | 5598 | 0.13329 | 2178 | 0.051857 | 6376 | 0.15181 | 1.361 | A06 | BIWW0.06030015
Build-In | Build-In Wall | BIWW.06030016 | 60 | 300 | 16 | 17 | 6252 | 6252 | 6252 | 0.14886 | 2257 | 0.053738 | 7190 | 0.17119 | 1.468 | A06 | BIWW0.06030016
Build-In | Build-In Wall | BIWW.06030016/DBE | 60 | 300 | 16 | #N/A | 9132 | 9132 | 9132 | 0.21743 | 4566 | 0.10871 | 10045 | 0.23917 | 1 | A06 | BIWW0.06030016/DBE
Build-In | Build-In Wall | BIWW.06030020 | 60 | 300 | 20 | 22 | 7824 | 7824 | 7824 | 0.18629 | 3044 | 0.072476 | 8912 | 0.21219 | 1.361 | A06 | BIWW0.06030020
Build-In | Build-In Wall | BIWW.06030021 | 60 | 300 | 21 | 22 | 8646 | 8646 | 8646 | 0.20586 | 3069 | 0.073071 | 9969 | 0.23736 | 1.493 | A06 | BIWW0.06030021
Build-In | Build-In Wall | BIWW.06030021/DBE | 60 | 300 | 21 | #N/A | 11526 | 11526 | 11526 | 0.27443 | 5763 | 0.13721 | 12679 | 0.30188 | 1 | A06 | BIWW0.06030021/DBE
Build-In | Build-In Wall | BIWW.07004010 | 70 | 40 | 10 | 12 | 499 | 499 | 499 | 0.011881 | 194 | 0.004619 | 568 | 0.013524 | 1.366 | A06 | BIWW0.07004010
Build-In | Build-In Wall | BIWW.07004011 | 70 | 40 | 11 | 12 | 636 | 636 | 636 | 0.015143 | 235 | 0.0055952 | 729 | 0.017357 | 1.436 | A06 | BIWW0.07004011
Build-In | Build-In Wall | BIWW.07004015 | 70 | 40 | 15 | 17 | 789 | 789 | 789 | 0.018786 | 309 | 0.0073571 | 897 | 0.021357 | 1.35 | A06 | BIWW0.07004015
Build-In | Build-In Wall | BIWW.07004016 | 70 | 40 | 16 | 17 | 904 | 904 | 904 | 0.021524 | 325 | 0.0077381 | 1041 | 0.024786 | 1.472 | A06 | BIWW0.07004016
Build-In | Build-In Wall | BIWW.07004020 | 70 | 40 | 20 | 22 | 1101 | 1101 | 1101 | 0.026214 | 433 | 0.01031 | 1252 | 0.02981 | 1.349 | A06 | BIWW0.07004020
Build-In | Build-In Wall | BIWW.07004021 | 70 | 40 | 21 | 22 | 1271 | 1271 | 1271 | 0.030262 | 449 | 0.01069 | 1467 | 0.034929 | 1.501 | A06 | BIWW0.07004021
Build-In | Build-In Wall | BIWW.07005010 | 70 | 50 | 10 | 12 | 624 | 624 | 624 | 0.014857 | 242 | 0.0057619 | 711 | 0.016929 | 1.366 | A06 | BIWW0.07005010
Build-In | Build-In Wall | BIWW.07005011 | 70 | 50 | 11 | 12 | 795 | 795 | 795 | 0.018929 | 294 | 0.007 | 912 | 0.021714 | 1.436 | A06 | BIWW0.07005011
Build-In | Build-In Wall | BIWW.07005015 | 70 | 50 | 15 | 17 | 986 | 986 | 986 | 0.023476 | 387 | 0.0092143 | 1121 | 0.02669 | 1.35 | A06 | BIWW0.07005015
Build-In | Build-In Wall | BIWW.07005016 | 70 | 50 | 16 | 17 | 1130 | 1130 | 1130 | 0.026905 | 407 | 0.0096905 | 1301 | 0.030976 | 1.472 | A06 | BIWW0.07005016
Build-In | Build-In Wall | BIWW.07005020 | 70 | 50 | 20 | 22 | 1377 | 1377 | 1377 | 0.032786 | 541 | 0.012881 | 1566 | 0.037286 | 1.349 | A06 | BIWW0.07005020
Build-In | Build-In Wall | BIWW.07005021 | 70 | 50 | 21 | 22 | 1589 | 1589 | 1589 | 0.037833 | 561 | 0.013357 | 1834 | 0.043667 | 1.501 | A06 | BIWW0.07005021
Build-In | Build-In Wall | BIWW.07006010 | 70 | 60 | 10 | 12 | 749 | 749 | 749 | 0.017833 | 291 | 0.0069286 | 853 | 0.02031 | 1.366 | A06 | BIWW0.07006010
Build-In | Build-In Wall | BIWW.07006011 | 70 | 60 | 11 | 12 | 954 | 954 | 954 | 0.022714 | 353 | 0.0084048 | 1094 | 0.026048 | 1.436 | A06 | BIWW0.07006011
Build-In | Build-In Wall | BIWW.07006011/DBE | 70 | 60 | 11 | #N/A | 1254 | 1254 | 1254 | 0.029857 | 627 | 0.014929 | 1379 | 0.032833 | 1 | A06 | BIWW0.07006011/DBE
Build-In | Build-In Wall | BIWW.07006015 | 70 | 60 | 15 | 17 | 1183 | 1183 | 1183 | 0.028167 | 464 | 0.011048 | 1345 | 0.032024 | 1.35 | A06 | BIWW0.07006015
Build-In | Build-In Wall | BIWW.07006016 | 70 | 60 | 16 | 17 | 1356 | 1356 | 1356 | 0.032286 | 488 | 0.011619 | 1561 | 0.037167 | 1.472 | A06 | BIWW0.07006016
Build-In | Build-In Wall | BIWW.07006016/DBE | 70 | 60 | 16 | #N/A | 1836 | 1836 | 1836 | 0.043714 | 918 | 0.021857 | 2020 | 0.048095 | 1 | A06 | BIWW0.07006016/DBE
Build-In | Build-In Wall | BIWW.07006020 | 70 | 60 | 20 | 22 | 1652 | 1652 | 1652 | 0.039333 | 649 | 0.015452 | 1878 | 0.044714 | 1.349 | A06 | BIWW0.07006020
Build-In | Build-In Wall | BIWW.07006021 | 70 | 60 | 21 | 22 | 1906 | 1906 | 1906 | 0.045381 | 673 | 0.016024 | 2200 | 0.052381 | 1.501 | A06 | BIWW0.07006021
Build-In | Build-In Wall | BIWW.07006021/DBE | 70 | 60 | 21 | #N/A | 2386 | 2386 | 2386 | 0.05681 | 1193 | 0.028405 | 2625 | 0.0625 | 1 | A06 | BIWW0.07006021/DBE
Build-In | Build-In Wall | BIWW.07007010 | 70 | 70 | 10 | 12 | 874 | 874 | 874 | 0.02081 | 339 | 0.0080714 | 995 | 0.02369 | 1.366 | A06 | BIWW0.07007010
Build-In | Build-In Wall | BIWW.07007011 | 70 | 70 | 11 | 12 | 1113 | 1113 | 1113 | 0.0265 | 412 | 0.0098095 | 1277 | 0.030405 | 1.436 | A06 | BIWW0.07007011
Build-In | Build-In Wall | BIWW.07007011/DBE | 70 | 70 | 11 | #N/A | 1413 | 1413 | 1413 | 0.033643 | 707 | 0.016833 | 1554 | 0.037 | 1 | A06 | BIWW0.07007011/DBE
Build-In | Build-In Wall | BIWW.07007015 | 70 | 70 | 15 | 17 | 1380 | 1380 | 1380 | 0.032857 | 541 | 0.012881 | 1569 | 0.037357 | 1.35 | A06 | BIWW0.07007015
Build-In | Build-In Wall | BIWW.07007016 | 70 | 70 | 16 | 17 | 1582 | 1582 | 1582 | 0.037667 | 570 | 0.013571 | 1821 | 0.043357 | 1.472 | A06 | BIWW0.07007016
Build-In | Build-In Wall | BIWW.07007016/DBE | 70 | 70 | 16 | #N/A | 2062 | 2062 | 2062 | 0.049095 | 1031 | 0.024548 | 2268 | 0.054 | 1 | A06 | BIWW0.07007016/DBE
Build-In | Build-In Wall | BIWW.07007020 | 70 | 70 | 20 | 22 | 1927 | 1927 | 1927 | 0.045881 | 757 | 0.018024 | 2191 | 0.052167 | 1.349 | A06 | BIWW0.07007020
Build-In | Build-In Wall | BIWW.07007021 | 70 | 70 | 21 | 22 | 2224 | 2224 | 2224 | 0.052952 | 785 | 0.01869 | 2566 | 0.061095 | 1.501 | A06 | BIWW0.07007021
Build-In | Build-In Wall | BIWW.07007021/DBE | 70 | 70 | 21 | #N/A | 2704 | 2704 | 2704 | 0.064381 | 1352 | 0.03219 | 2974 | 0.07081 | 1 | A06 | BIWW0.07007021/DBE
Build-In | Build-In Wall | BIWW.07008010 | 70 | 80 | 10 | 12 | 998 | 998 | 998 | 0.023762 | 387 | 0.0092143 | 1137 | 0.027071 | 1.366 | A06 | BIWW0.07008010
Build-In | Build-In Wall | BIWW.07008011 | 70 | 80 | 11 | 12 | 1272 | 1272 | 1272 | 0.030286 | 471 | 0.011214 | 1459 | 0.034738 | 1.436 | A06 | BIWW0.07008011
Build-In | Build-In Wall | BIWW.07008011/DBE | 70 | 80 | 11 | #N/A | 1572 | 1572 | 1572 | 0.037429 | 786 | 0.018714 | 1729 | 0.041167 | 1 | A06 | BIWW0.07008011/DBE
Build-In | Build-In Wall | BIWW.07008015 | 70 | 80 | 15 | 17 | 1578 | 1578 | 1578 | 0.037571 | 619 | 0.014738 | 1794 | 0.042714 | 1.35 | A06 | BIWW0.07008015
Build-In | Build-In Wall | BIWW.07008016 | 70 | 80 | 16 | 17 | 1808 | 1808 | 1808 | 0.043048 | 651 | 0.0155 | 2081 | 0.049548 | 1.472 | A06 | BIWW0.07008016
Build-In | Build-In Wall | BIWW.07008016/DBE | 70 | 80 | 16 | #N/A | 2288 | 2288 | 2288 | 0.054476 | 1144 | 0.027238 | 2517 | 0.059929 | 1 | A06 | BIWW0.07008016/DBE
Build-In | Build-In Wall | BIWW.07008020 | 70 | 80 | 20 | 22 | 2202 | 2202 | 2202 | 0.052429 | 865 | 0.020595 | 2504 | 0.059619 | 1.349 | A06 | BIWW0.07008020
Build-In | Build-In Wall | BIWW.07008021 | 70 | 80 | 21 | 22 | 2542 | 2542 | 2542 | 0.060524 | 897 | 0.021357 | 2933 | 0.069833 | 1.501 | A06 | BIWW0.07008021
Build-In | Build-In Wall | BIWW.07008021/DBE | 70 | 80 | 21 | #N/A | 3022 | 3022 | 3022 | 0.071952 | 1511 | 0.035976 | 3324 | 0.079143 | 1 | A06 | BIWW0.07008021/DBE
Build-In | Build-In Wall | BIWW.07009010 | 70 | 90 | 10 | 12 | 1123 | 1123 | 1123 | 0.026738 | 436 | 0.010381 | 1279 | 0.030452 | 1.366 | A06 | BIWW0.07009010
Build-In | Build-In Wall | BIWW.07009011 | 70 | 90 | 11 | 12 | 1431 | 1431 | 1431 | 0.034071 | 529 | 0.012595 | 1641 | 0.039071 | 1.436 | A06 | BIWW0.07009011
Build-In | Build-In Wall | BIWW.07009011/DBE | 70 | 90 | 11 | #N/A | 2031 | 2031 | 2031 | 0.048357 | 1016 | 0.02419 | 2234 | 0.05319 | 1 | A06 | BIWW0.07009011/DBE
Build-In | Build-In Wall | BIWW.07009015 | 70 | 90 | 15 | 17 | 1775 | 1775 | 1775 | 0.042262 | 696 | 0.016571 | 2018 | 0.048048 | 1.35 | A06 | BIWW0.07009015
Build-In | Build-In Wall | BIWW.07009016 | 70 | 90 | 16 | 17 | 2034 | 2034 | 2034 | 0.048429 | 732 | 0.017429 | 2341 | 0.055738 | 1.472 | A06 | BIWW0.07009016
Build-In | Build-In Wall | BIWW.07009016/DBE | 70 | 90 | 16 | #N/A | 2994 | 2994 | 2994 | 0.071286 | 1497 | 0.035643 | 3293 | 0.078405 | 1 | A06 | BIWW0.07009016/DBE
Build-In | Build-In Wall | BIWW.07009020 | 70 | 90 | 20 | 22 | 2478 | 2478 | 2478 | 0.059 | 974 | 0.02319 | 2817 | 0.067071 | 1.349 | A06 | BIWW0.07009020
Build-In | Build-In Wall | BIWW.07009021 | 70 | 90 | 21 | 22 | 2859 | 2859 | 2859 | 0.068071 | 1009 | 0.024024 | 3299 | 0.078548 | 1.501 | A06 | BIWW0.07009021
Build-In | Build-In Wall | BIWW.07009021/DBE | 70 | 90 | 21 | #N/A | 3819 | 3819 | 3819 | 0.090929 | 1910 | 0.045476 | 4201 | 0.10002 | 1 | A06 | BIWW0.07009021/DBE
Build-In | Build-In Wall | BIWW.07010010 | 70 | 100 | 10 | 12 | 1248 | 1248 | 1248 | 0.029714 | 484 | 0.011524 | 1421 | 0.033833 | 1.366 | A06 | BIWW0.07010010
Build-In | Build-In Wall | BIWW.07010011 | 70 | 100 | 11 | 12 | 1590 | 1590 | 1590 | 0.037857 | 588 | 0.014 | 1824 | 0.043429 | 1.436 | A06 | BIWW0.07010011
Build-In | Build-In Wall | BIWW.07010011/DBE | 70 | 100 | 11 | #N/A | 2190 | 2190 | 2190 | 0.052143 | 1095 | 0.026071 | 2409 | 0.057357 | 1 | A06 | BIWW0.07010011/DBE
Build-In | Build-In Wall | BIWW.07010015 | 70 | 100 | 15 | 17 | 1972 | 1972 | 1972 | 0.046952 | 773 | 0.018405 | 2242 | 0.053381 | 1.35 | A06 | BIWW0.07010015
Build-In | Build-In Wall | BIWW.07010016 | 70 | 100 | 16 | 17 | 2260 | 2260 | 2260 | 0.05381 | 814 | 0.019381 | 2601 | 0.061929 | 1.472 | A06 | BIWW0.07010016
Build-In | Build-In Wall | BIWW.07010016/DBE | 70 | 100 | 16 | #N/A | 3220 | 3220 | 3220 | 0.076667 | 1610 | 0.038333 | 3542 | 0.084333 | 1 | A06 | BIWW0.07010016/DBE
Build-In | Build-In Wall | BIWW.07010020 | 70 | 100 | 20 | 22 | 2753 | 2753 | 2753 | 0.065548 | 1082 | 0.025762 | 3130 | 0.074524 | 1.349 | A06 | BIWW0.07010020
Build-In | Build-In Wall | BIWW.07010021 | 70 | 100 | 21 | 22 | 3177 | 3177 | 3177 | 0.075643 | 1121 | 0.02669 | 3666 | 0.087286 | 1.501 | A06 | BIWW0.07010021
Build-In | Build-In Wall | BIWW.07010021/DBE | 70 | 100 | 21 | #N/A | 4137 | 4137 | 4137 | 0.0985 | 2069 | 0.049262 | 4551 | 0.10836 | 1 | A06 | BIWW0.07010021/DBE
Build-In | Build-In Wall | BIWW.07011010 | 70 | 110 | 10 | 12 | 1373 | 1373 | 1373 | 0.03269 | 533 | 0.01269 | 1564 | 0.037238 | 1.366 | A06 | BIWW0.07011010
Build-In | Build-In Wall | BIWW.07011011 | 70 | 110 | 11 | 12 | 1749 | 1749 | 1749 | 0.041643 | 647 | 0.015405 | 2006 | 0.047762 | 1.436 | A06 | BIWW0.07011011
Build-In | Build-In Wall | BIWW.07011011/DBE | 70 | 110 | 11 | #N/A | 2349 | 2349 | 2349 | 0.055929 | 1175 | 0.027976 | 2584 | 0.061524 | 1 | A06 | BIWW0.07011011/DBE
Build-In | Build-In Wall | BIWW.07011015 | 70 | 110 | 15 | 17 | 2169 | 2169 | 2169 | 0.051643 | 850 | 0.020238 | 2466 | 0.058714 | 1.35 | A06 | BIWW0.07011015
Build-In | Build-In Wall | BIWW.07011016 | 70 | 110 | 16 | 17 | 2486 | 2486 | 2486 | 0.05919 | 895 | 0.02131 | 2861 | 0.068119 | 1.472 | A06 | BIWW0.07011016
Build-In | Build-In Wall | BIWW.07011016/DBE | 70 | 110 | 16 | #N/A | 3446 | 3446 | 3446 | 0.082048 | 1723 | 0.041024 | 3791 | 0.090262 | 1 | A06 | BIWW0.07011016/DBE
Build-In | Build-In Wall | BIWW.07011020 | 70 | 110 | 20 | 22 | 3028 | 3028 | 3028 | 0.072095 | 1190 | 0.028333 | 3443 | 0.081976 | 1.349 | A06 | BIWW0.07011020
Build-In | Build-In Wall | BIWW.07011021 | 70 | 110 | 21 | 22 | 3495 | 3495 | 3495 | 0.083214 | 1234 | 0.029381 | 4033 | 0.096024 | 1.501 | A06 | BIWW0.07011021
Build-In | Build-In Wall | BIWW.07011021/DBE | 70 | 110 | 21 | #N/A | 4455 | 4455 | 4455 | 0.10607 | 2228 | 0.053048 | 4901 | 0.11669 | 1 | A06 | BIWW0.07011021/DBE
Build-In | Build-In Wall | BIWW.07012010 | 70 | 120 | 10 | 12 | 1498 | 1498 | 1498 | 0.035667 | 581 | 0.013833 | 1706 | 0.040619 | 1.366 | A06 | BIWW0.07012010
Build-In | Build-In Wall | BIWW.07012011 | 70 | 120 | 11 | 12 | 1908 | 1908 | 1908 | 0.045429 | 706 | 0.01681 | 2188 | 0.052095 | 1.436 | A06 | BIWW0.07012011
Build-In | Build-In Wall | BIWW.07012011/DBE | 70 | 120 | 11 | #N/A | 2508 | 2508 | 2508 | 0.059714 | 1254 | 0.029857 | 2759 | 0.06569 | 1 | A06 | BIWW0.07012011/DBE
Build-In | Build-In Wall | BIWW.07012015 | 70 | 120 | 15 | 17 | 2366 | 2366 | 2366 | 0.056333 | 927 | 0.022071 | 2690 | 0.064048 | 1.35 | A06 | BIWW0.07012015
Build-In | Build-In Wall | BIWW.07012016 | 70 | 120 | 16 | 17 | 2712 | 2712 | 2712 | 0.064571 | 976 | 0.023238 | 3122 | 0.074333 | 1.472 | A06 | BIWW0.07012016
Build-In | Build-In Wall | BIWW.07012016/DBE | 70 | 120 | 16 | #N/A | 3672 | 3672 | 3672 | 0.087429 | 1836 | 0.043714 | 4039 | 0.096167 | 1 | A06 | BIWW0.07012016/DBE
Build-In | Build-In Wall | BIWW.07012020 | 70 | 120 | 20 | 22 | 3304 | 3304 | 3304 | 0.078667 | 1298 | 0.030905 | 3757 | 0.089452 | 1.349 | A06 | BIWW0.07012020
Build-In | Build-In Wall | BIWW.07012021 | 70 | 120 | 21 | 22 | 3812 | 3812 | 3812 | 0.090762 | 1346 | 0.032048 | 4399 | 0.10474 | 1.501 | A06 | BIWW0.07012021
Build-In | Build-In Wall | BIWW.07012021/DBE | 70 | 120 | 21 | #N/A | 4772 | 4772 | 4772 | 0.11362 | 2386 | 0.05681 | 5249 | 0.12498 | 1 | A06 | BIWW0.07012021/DBE
Build-In | Build-In Wall | BIWW.07014010 | 70 | 140 | 10 | 12 | 1747 | 1747 | 1747 | 0.041595 | 678 | 0.016143 | 1990 | 0.047381 | 1.366 | A06 | BIWW0.07014010
Build-In | Build-In Wall | BIWW.07014011 | 70 | 140 | 11 | 12 | 2226 | 2226 | 2226 | 0.053 | 824 | 0.019619 | 2553 | 0.060786 | 1.436 | A06 | BIWW0.07014011
Build-In | Build-In Wall | BIWW.07014011/DBE | 70 | 140 | 11 | #N/A | 2826 | 2826 | 2826 | 0.067286 | 1413 | 0.033643 | 3109 | 0.074024 | 1 | A06 | BIWW0.07014011/DBE
Build-In | Build-In Wall | BIWW.07014015 | 70 | 140 | 15 | 17 | 2761 | 2761 | 2761 | 0.065738 | 1082 | 0.025762 | 3139 | 0.074738 | 1.35 | A06 | BIWW0.07014015
Build-In | Build-In Wall | BIWW.07014016 | 70 | 140 | 16 | 17 | 3164 | 3164 | 3164 | 0.075333 | 1139 | 0.027119 | 3642 | 0.086714 | 1.472 | A06 | BIWW0.07014016
Build-In | Build-In Wall | BIWW.07014016/DBE | 70 | 140 | 16 | #N/A | 4124 | 4124 | 4124 | 0.09819 | 2062 | 0.049095 | 4536 | 0.108 | 1 | A06 | BIWW0.07014016/DBE
Build-In | Build-In Wall | BIWW.07014020 | 70 | 140 | 20 | 22 | 3854 | 3854 | 3854 | 0.091762 | 1515 | 0.036071 | 4382 | 0.10433 | 1.349 | A06 | BIWW0.07014020
Build-In | Build-In Wall | BIWW.07014021 | 70 | 140 | 21 | 22 | 4448 | 4448 | 4448 | 0.1059 | 1570 | 0.037381 | 5133 | 0.12221 | 1.501 | A06 | BIWW0.07014021
Build-In | Build-In Wall | BIWW.07014021/DBE | 70 | 140 | 21 | #N/A | 5408 | 5408 | 5408 | 0.12876 | 2704 | 0.064381 | 5949 | 0.14164 | 1 | A06 | BIWW0.07014021/DBE
Build-In | Build-In Wall | BIWW.07016010 | 70 | 160 | 10 | 12 | 1997 | 1997 | 1997 | 0.047548 | 775 | 0.018452 | 2275 | 0.054167 | 1.366 | A06 | BIWW0.07016010
Build-In | Build-In Wall | BIWW.07016011 | 70 | 160 | 11 | 12 | 2544 | 2544 | 2544 | 0.060571 | 941 | 0.022405 | 2918 | 0.069476 | 1.436 | A06 | BIWW0.07016011
Build-In | Build-In Wall | BIWW.07016011/DBE | 70 | 160 | 11 | #N/A | 3744 | 3744 | 3744 | 0.089143 | 1872 | 0.044571 | 4118 | 0.098048 | 1 | A06 | BIWW0.07016011/DBE
Build-In | Build-In Wall | BIWW.07016015 | 70 | 160 | 15 | 17 | 3155 | 3155 | 3155 | 0.075119 | 1237 | 0.029452 | 3587 | 0.085405 | 1.35 | A06 | BIWW0.07016015
Build-In | Build-In Wall | BIWW.07016016 | 70 | 160 | 16 | 17 | 3616 | 3616 | 3616 | 0.086095 | 1302 | 0.031 | 4162 | 0.099095 | 1.472 | A06 | BIWW0.07016016
Build-In | Build-In Wall | BIWW.07016016/DBE | 70 | 160 | 16 | #N/A | 5536 | 5536 | 5536 | 0.13181 | 2768 | 0.065905 | 6090 | 0.145 | 1 | A06 | BIWW0.07016016/DBE
Build-In | Build-In Wall | BIWW.07016020 | 70 | 160 | 20 | 22 | 4405 | 4405 | 4405 | 0.10488 | 1731 | 0.041214 | 5008 | 0.11924 | 1.349 | A06 | BIWW0.07016020
Build-In | Build-In Wall | BIWW.07016021 | 70 | 160 | 21 | 22 | 5083 | 5083 | 5083 | 0.12102 | 1794 | 0.042714 | 5866 | 0.13967 | 1.501 | A06 | BIWW0.07016021
Build-In | Build-In Wall | BIWW.07016021/DBE | 70 | 160 | 21 | #N/A | 7003 | 7003 | 7003 | 0.16674 | 3502 | 0.083381 | 7703 | 0.1834 | 1 | A06 | BIWW0.07016021/DBE
Build-In | Build-In Wall | BIWW.07018010 | 70 | 180 | 10 | 12 | 2246 | 2246 | 2246 | 0.053476 | 871 | 0.020738 | 2558 | 0.060905 | 1.366 | A06 | BIWW0.07018010
Build-In | Build-In Wall | BIWW.07018011 | 70 | 180 | 11 | 12 | 2862 | 2862 | 2862 | 0.068143 | 1059 | 0.025214 | 3283 | 0.078167 | 1.436 | A06 | BIWW0.07018011
Build-In | Build-In Wall | BIWW.07018011/DBE | 70 | 180 | 11 | #N/A | 4062 | 4062 | 4062 | 0.096714 | 2031 | 0.048357 | 4468 | 0.10638 | 1 | A06 | BIWW0.07018011/DBE
Build-In | Build-In Wall | BIWW.07018015 | 70 | 180 | 15 | 17 | 3550 | 3550 | 3550 | 0.084524 | 1392 | 0.033143 | 4036 | 0.096095 | 1.35 | A06 | BIWW0.07018015
Build-In | Build-In Wall | BIWW.07018016 | 70 | 180 | 16 | 17 | 4068 | 4068 | 4068 | 0.096857 | 1464 | 0.034857 | 4682 | 0.11148 | 1.472 | A06 | BIWW0.07018016
Build-In | Build-In Wall | BIWW.07018016/DBE | 70 | 180 | 16 | #N/A | 5988 | 5988 | 5988 | 0.14257 | 2994 | 0.071286 | 6587 | 0.15683 | 1 | A06 | BIWW0.07018016/DBE
Build-In | Build-In Wall | BIWW.07018020 | 70 | 180 | 20 | 22 | 4955 | 4955 | 4955 | 0.11798 | 1947 | 0.046357 | 5634 | 0.13414 | 1.349 | A06 | BIWW0.07018020
Build-In | Build-In Wall | BIWW.07018021 | 70 | 180 | 21 | 22 | 5719 | 5719 | 5719 | 0.13617 | 2019 | 0.048071 | 6600 | 0.15714 | 1.501 | A06 | BIWW0.07018021
Build-In | Build-In Wall | BIWW.07018021/DBE | 70 | 180 | 21 | #N/A | 7639 | 7639 | 7639 | 0.18188 | 3820 | 0.090952 | 8403 | 0.20007 | 1 | A06 | BIWW0.07018021/DBE
Build-In | Build-In Wall | BIWW.07020010 | 70 | 200 | 10 | 12 | 2496 | 2496 | 2496 | 0.059429 | 968 | 0.023048 | 2843 | 0.06769 | 1.366 | A06 | BIWW0.07020010
Build-In | Build-In Wall | BIWW.07020011 | 70 | 200 | 11 | 12 | 3180 | 3180 | 3180 | 0.075714 | 1177 | 0.028024 | 3647 | 0.086833 | 1.436 | A06 | BIWW0.07020011
Build-In | Build-In Wall | BIWW.07020011/DBE | 70 | 200 | 11 | #N/A | 4380 | 4380 | 4380 | 0.10429 | 2190 | 0.052143 | 4818 | 0.11471 | 1 | A06 | BIWW0.07020011/DBE
Build-In | Build-In Wall | BIWW.07020015 | 70 | 200 | 15 | 17 | 3944 | 3944 | 3944 | 0.093905 | 1546 | 0.03681 | 4484 | 0.10676 | 1.35 | A06 | BIWW0.07020015
Build-In | Build-In Wall | BIWW.07020016 | 70 | 200 | 16 | 17 | 4520 | 4520 | 4520 | 0.10762 | 1627 | 0.038738 | 5203 | 0.12388 | 1.472 | A06 | BIWW0.07020016
Build-In | Build-In Wall | BIWW.07020016/DBE | 70 | 200 | 16 | #N/A | 6440 | 6440 | 6440 | 0.15333 | 3220 | 0.076667 | 7084 | 0.16867 | 1 | A06 | BIWW0.07020016/DBE
Build-In | Build-In Wall | BIWW.07020020 | 70 | 200 | 20 | 22 | 5506 | 5506 | 5506 | 0.1311 | 2164 | 0.051524 | 6260 | 0.14905 | 1.349 | A06 | BIWW0.07020020
Build-In | Build-In Wall | BIWW.07020021 | 70 | 200 | 21 | 22 | 6354 | 6354 | 6354 | 0.15129 | 2243 | 0.053405 | 7333 | 0.1746 | 1.501 | A06 | BIWW0.07020021
Build-In | Build-In Wall | BIWW.07020021/DBE | 70 | 200 | 21 | #N/A | 8274 | 8274 | 8274 | 0.197 | 4137 | 0.0985 | 9101 | 0.21669 | 1 | A06 | BIWW0.07020021/DBE
Build-In | Build-In Wall | BIWW.07022010 | 70 | 220 | 10 | 12 | 2746 | 2746 | 2746 | 0.065381 | 1065 | 0.025357 | 3128 | 0.074476 | 1.366 | A06 | BIWW0.07022010
Build-In | Build-In Wall | BIWW.07022011 | 70 | 220 | 11 | 12 | 3498 | 3498 | 3498 | 0.083286 | 1294 | 0.03081 | 4012 | 0.095524 | 1.436 | A06 | BIWW0.07022011
Build-In | Build-In Wall | BIWW.07022011/DBE | 70 | 220 | 11 | #N/A | 4698 | 4698 | 4698 | 0.11186 | 2349 | 0.055929 | 5168 | 0.12305 | 1 | A06 | BIWW0.07022011/DBE
Build-In | Build-In Wall | BIWW.07022015 | 70 | 220 | 15 | 17 | 4338 | 4338 | 4338 | 0.10329 | 1700 | 0.040476 | 4932 | 0.11743 | 1.35 | A06 | BIWW0.07022015
Build-In | Build-In Wall | BIWW.07022016 | 70 | 220 | 16 | 17 | 4972 | 4972 | 4972 | 0.11838 | 1790 | 0.042619 | 5723 | 0.13626 | 1.472 | A06 | BIWW0.07022016
Build-In | Build-In Wall | BIWW.07022016/DBE | 70 | 220 | 16 | #N/A | 6892 | 6892 | 6892 | 0.1641 | 3446 | 0.082048 | 7581 | 0.1805 | 1 | A06 | BIWW0.07022016/DBE
Build-In | Build-In Wall | BIWW.07022020 | 70 | 220 | 20 | 22 | 6057 | 6057 | 6057 | 0.14421 | 2380 | 0.056667 | 6887 | 0.16398 | 1.349 | A06 | BIWW0.07022020
Build-In | Build-In Wall | BIWW.07022021 | 70 | 220 | 21 | 22 | 6989 | 6989 | 6989 | 0.1664 | 2467 | 0.058738 | 8065 | 0.19202 | 1.501 | A06 | BIWW0.07022021
Build-In | Build-In Wall | BIWW.07022021/DBE | 70 | 220 | 21 | #N/A | 8909 | 8909 | 8909 | 0.21212 | 4455 | 0.10607 | 9800 | 0.23333 | 1 | A06 | BIWW0.07022021/DBE
Build-In | Build-In Wall | BIWW.07024010 | 70 | 240 | 10 | 12 | 2995 | 2995 | 2995 | 0.07131 | 1162 | 0.027667 | 3411 | 0.081214 | 1.366 | A06 | BIWW0.07024010
Build-In | Build-In Wall | BIWW.07024011 | 70 | 240 | 11 | 12 | 3816 | 3816 | 3816 | 0.090857 | 1412 | 0.033619 | 4377 | 0.10421 | 1.436 | A06 | BIWW0.07024011
Build-In | Build-In Wall | BIWW.07024011/DBE | 70 | 240 | 11 | #N/A | 5616 | 5616 | 5616 | 0.13371 | 2808 | 0.066857 | 6178 | 0.1471 | 1 | A06 | BIWW0.07024011/DBE
Build-In | Build-In Wall | BIWW.07024015 | 70 | 240 | 15 | 17 | 4733 | 4733 | 4733 | 0.11269 | 1855 | 0.044167 | 5381 | 0.12812 | 1.35 | A06 | BIWW0.07024015
Build-In | Build-In Wall | BIWW.07024016 | 70 | 240 | 16 | 17 | 5424 | 5424 | 5424 | 0.12914 | 1953 | 0.0465 | 6243 | 0.14864 | 1.472 | A06 | BIWW0.07024016
Build-In | Build-In Wall | BIWW.07024016/DBE | 70 | 240 | 16 | #N/A | 8304 | 8304 | 8304 | 0.19771 | 4152 | 0.098857 | 9134 | 0.21748 | 1 | A06 | BIWW0.07024016/DBE
Build-In | Build-In Wall | BIWW.07024020 | 70 | 240 | 20 | 22 | 6607 | 6607 | 6607 | 0.15731 | 2597 | 0.061833 | 7512 | 0.17886 | 1.349 | A06 | BIWW0.07024020
Build-In | Build-In Wall | BIWW.07024021 | 70 | 240 | 21 | 22 | 7625 | 7625 | 7625 | 0.18155 | 2692 | 0.064095 | 8799 | 0.2095 | 1.501 | A06 | BIWW0.07024021
Build-In | Build-In Wall | BIWW.07024021/DBE | 70 | 240 | 21 | #N/A | 10505 | 10505 | 10505 | 0.25012 | 5253 | 0.12507 | 11556 | 0.27514 | 1 | A06 | BIWW0.07024021/DBE
Build-In | Build-In Wall | BIWW.07026010 | 70 | 260 | 10 | 12 | 3245 | 3245 | 3245 | 0.077262 | 1259 | 0.029976 | 3696 | 0.088 | 1.366 | A06 | BIWW0.07026010
Build-In | Build-In Wall | BIWW.07026011 | 70 | 260 | 11 | 12 | 4134 | 4134 | 4134 | 0.098429 | 1530 | 0.036429 | 4742 | 0.1129 | 1.436 | A06 | BIWW0.07026011
Build-In | Build-In Wall | BIWW.07026011/DBE | 70 | 260 | 11 | #N/A | 5934 | 5934 | 5934 | 0.14129 | 2967 | 0.070643 | 6527 | 0.1554 | 1 | A06 | BIWW0.07026011/DBE
Build-In | Build-In Wall | BIWW.07026015 | 70 | 260 | 15 | 17 | 5127 | 5127 | 5127 | 0.12207 | 2010 | 0.047857 | 5829 | 0.13879 | 1.35 | A06 | BIWW0.07026015
Build-In | Build-In Wall | BIWW.07026016 | 70 | 260 | 16 | 17 | 5876 | 5876 | 5876 | 0.1399 | 2115 | 0.050357 | 6763 | 0.16102 | 1.472 | A06 | BIWW0.07026016
Build-In | Build-In Wall | BIWW.07026016/DBE | 70 | 260 | 16 | #N/A | 8756 | 8756 | 8756 | 0.20848 | 4378 | 0.10424 | 9632 | 0.22933 | 1 | A06 | BIWW0.07026016/DBE
Build-In | Build-In Wall | BIWW.07026020 | 70 | 260 | 20 | 22 | 7158 | 7158 | 7158 | 0.17043 | 2813 | 0.066976 | 8139 | 0.19379 | 1.349 | A06 | BIWW0.07026020
Build-In | Build-In Wall | BIWW.07026021 | 70 | 260 | 21 | 22 | 8260 | 8260 | 8260 | 0.19667 | 2916 | 0.069429 | 9532 | 0.22695 | 1.501 | A06 | BIWW0.07026021
Build-In | Build-In Wall | BIWW.07026021/DBE | 70 | 260 | 21 | #N/A | 11140 | 11140 | 11140 | 0.26524 | 5570 | 0.13262 | 12254 | 0.29176 | 1 | A06 | BIWW0.07026021/DBE
Build-In | Build-In Wall | BIWW.07028010 | 70 | 280 | 10 | 12 | 3494 | 3494 | 3494 | 0.08319 | 1356 | 0.032286 | 3980 | 0.094762 | 1.366 | A06 | BIWW0.07028010
Build-In | Build-In Wall | BIWW.07028011 | 70 | 280 | 11 | 12 | 4452 | 4452 | 4452 | 0.106 | 1647 | 0.039214 | 5106 | 0.12157 | 1.436 | A06 | BIWW0.07028011
Build-In | Build-In Wall | BIWW.07028011/DBE | 70 | 280 | 11 | #N/A | 6252 | 6252 | 6252 | 0.14886 | 3126 | 0.074429 | 6877 | 0.16374 | 1 | A06 | BIWW0.07028011/DBE
Build-In | Build-In Wall | BIWW.07028015 | 70 | 280 | 15 | 17 | 5522 | 5522 | 5522 | 0.13148 | 2165 | 0.051548 | 6279 | 0.1495 | 1.35 | A06 | BIWW0.07028015
Build-In | Build-In Wall | BIWW.07028016 | 70 | 280 | 16 | 17 | 6328 | 6328 | 6328 | 0.15067 | 2278 | 0.054238 | 7284 | 0.17343 | 1.472 | A06 | BIWW0.07028016
Build-In | Build-In Wall | BIWW.07028016/DBE | 70 | 280 | 16 | #N/A | 9208 | 9208 | 9208 | 0.21924 | 4604 | 0.10962 | 10129 | 0.24117 | 1 | A06 | BIWW0.07028016/DBE
Build-In | Build-In Wall | BIWW.07028020 | 70 | 280 | 20 | 22 | 7708 | 7708 | 7708 | 0.18352 | 3029 | 0.072119 | 8764 | 0.20867 | 1.349 | A06 | BIWW0.07028020
Build-In | Build-In Wall | BIWW.07028021 | 70 | 280 | 21 | 22 | 8896 | 8896 | 8896 | 0.21181 | 3140 | 0.074762 | 10266 | 0.24443 | 1.501 | A06 | BIWW0.07028021
Build-In | Build-In Wall | BIWW.07028021/DBE | 70 | 280 | 21 | #N/A | 11776 | 11776 | 11776 | 0.28038 | 5888 | 0.14019 | 12954 | 0.30843 | 1 | A06 | BIWW0.07028021/DBE
Build-In | Build-In Wall | BIWW.07030010 | 70 | 300 | 10 | 12 | 3744 | 3744 | 3744 | 0.089143 | 1453 | 0.034595 | 4264 | 0.10152 | 1.366 | A06 | BIWW0.07030010
Build-In | Build-In Wall | BIWW.07030011 | 70 | 300 | 11 | 12 | 4770 | 4770 | 4770 | 0.11357 | 1765 | 0.042024 | 5471 | 0.13026 | 1.436 | A06 | BIWW0.07030011
Build-In | Build-In Wall | BIWW.07030011/DBE | 70 | 300 | 11 | #N/A | 6570 | 6570 | 6570 | 0.15643 | 3285 | 0.078214 | 7227 | 0.17207 | 1 | A06 | BIWW0.07030011/DBE
Build-In | Build-In Wall | BIWW.07030015 | 70 | 300 | 15 | 17 | 5916 | 5916 | 5916 | 0.14086 | 2319 | 0.055214 | 6726 | 0.16014 | 1.35 | A06 | BIWW0.07030015
Build-In | Build-In Wall | BIWW.07030016 | 70 | 300 | 16 | 17 | 6780 | 6780 | 6780 | 0.16143 | 2441 | 0.058119 | 7804 | 0.18581 | 1.472 | A06 | BIWW0.07030016
Build-In | Build-In Wall | BIWW.07030016/DBE | 70 | 300 | 16 | #N/A | 9660 | 9660 | 9660 | 0.23 | 4830 | 0.115 | 10626 | 0.253 | 1 | A06 | BIWW0.07030016/DBE
Build-In | Build-In Wall | BIWW.07030020 | 70 | 300 | 20 | 22 | 8259 | 8259 | 8259 | 0.19664 | 3246 | 0.077286 | 9390 | 0.22357 | 1.349 | A06 | BIWW0.07030020
Build-In | Build-In Wall | BIWW.07030021 | 70 | 300 | 21 | 22 | 9531 | 9531 | 9531 | 0.22693 | 3364 | 0.080095 | 10999 | 0.26188 | 1.501 | A06 | BIWW0.07030021
Build-In | Build-In Wall | BIWW.07030021/DBE | 70 | 300 | 21 | #N/A | 12411 | 12411 | 12411 | 0.2955 | 6206 | 0.14776 | 13652 | 0.32505 | 1 | A06 | BIWW0.07030021/DBE
Build-In | Build-In Wall | BIWW.09004010 | 90 | 40 | 10 | 12 | 548 | 548 | 548 | 0.013048 | 215 | 0.005119 | 623 | 0.014833 | 1.348 | A06 | BIWW0.09004010
Build-In | Build-In Wall | BIWW.09004011 | 90 | 40 | 11 | 12 | 703 | 703 | 703 | 0.016738 | 260 | 0.0061905 | 806 | 0.01919 | 1.434 | A06 | BIWW0.09004011
Build-In | Build-In Wall | BIWW.09004015 | 90 | 40 | 15 | 17 | 848 | 848 | 848 | 0.02019 | 338 | 0.0080476 | 962 | 0.022905 | 1.326 | A06 | BIWW0.09004015
Build-In | Build-In Wall | BIWW.09004016 | 90 | 40 | 16 | 17 | 1038 | 1038 | 1038 | 0.024714 | 372 | 0.0088571 | 1195 | 0.028452 | 1.48 | A06 | BIWW0.09004016
Build-In | Build-In Wall | BIWW.09004020 | 90 | 40 | 20 | 22 | 1183 | 1183 | 1183 | 0.028167 | 472 | 0.011238 | 1343 | 0.031976 | 1.326 | A06 | BIWW0.09004020
Build-In | Build-In Wall | BIWW.09004021 | 90 | 40 | 21 | 22 | 1508 | 1508 | 1508 | 0.035905 | 526 | 0.012524 | 1743 | 0.0415 | 1.518 | A06 | BIWW0.09004021
Build-In | Build-In Wall | BIWW.09005010 | 90 | 50 | 10 | 12 | 685 | 685 | 685 | 0.01631 | 269 | 0.0064048 | 779 | 0.018548 | 1.348 | A06 | BIWW0.09005010
Build-In | Build-In Wall | BIWW.09005011 | 90 | 50 | 11 | 12 | 879 | 879 | 879 | 0.020929 | 325 | 0.0077381 | 1007 | 0.023976 | 1.434 | A06 | BIWW0.09005011
Build-In | Build-In Wall | BIWW.09005015 | 90 | 50 | 15 | 17 | 1060 | 1060 | 1060 | 0.025238 | 423 | 0.010071 | 1203 | 0.028643 | 1.326 | A06 | BIWW0.09005015
Build-In | Build-In Wall | BIWW.09005016 | 90 | 50 | 16 | 17 | 1298 | 1298 | 1298 | 0.030905 | 465 | 0.011071 | 1494 | 0.035571 | 1.48 | A06 | BIWW0.09005016
Build-In | Build-In Wall | BIWW.09005020 | 90 | 50 | 20 | 22 | 1479 | 1479 | 1479 | 0.035214 | 590 | 0.014048 | 1679 | 0.039976 | 1.326 | A06 | BIWW0.09005020
Build-In | Build-In Wall | BIWW.09005021 | 90 | 50 | 21 | 22 | 1885 | 1885 | 1885 | 0.044881 | 658 | 0.015667 | 2179 | 0.051881 | 1.518 | A06 | BIWW0.09005021
Build-In | Build-In Wall | BIWW.09006010 | 90 | 60 | 10 | 12 | 821 | 821 | 821 | 0.019548 | 323 | 0.0076905 | 933 | 0.022214 | 1.348 | A06 | BIWW0.09006010
Build-In | Build-In Wall | BIWW.09006011 | 90 | 60 | 11 | 12 | 1055 | 1055 | 1055 | 0.025119 | 390 | 0.0092857 | 1209 | 0.028786 | 1.434 | A06 | BIWW0.09006011
Build-In | Build-In Wall | BIWW.09006011/DBE | 90 | 60 | 11 | #N/A | 1355 | 1355 | 1355 | 0.032262 | 678 | 0.016143 | 1491 | 0.0355 | 1 | A06 | BIWW0.09006011/DBE
Build-In | Build-In Wall | BIWW.09006015 | 90 | 60 | 15 | 17 | 1272 | 1272 | 1272 | 0.030286 | 508 | 0.012095 | 1444 | 0.034381 | 1.326 | A06 | BIWW0.09006015
Build-In | Build-In Wall | BIWW.09006016 | 90 | 60 | 16 | 17 | 1558 | 1558 | 1558 | 0.037095 | 558 | 0.013286 | 1793 | 0.04269 | 1.48 | A06 | BIWW0.09006016
Build-In | Build-In Wall | BIWW.09006016/DBE | 90 | 60 | 16 | #N/A | 2038 | 2038 | 2038 | 0.048524 | 1019 | 0.024262 | 2242 | 0.053381 | 1 | A06 | BIWW0.09006016/DBE
Build-In | Build-In Wall | BIWW.09006020 | 90 | 60 | 20 | 22 | 1774 | 1774 | 1774 | 0.042238 | 708 | 0.016857 | 2013 | 0.047929 | 1.326 | A06 | BIWW0.09006020
Build-In | Build-In Wall | BIWW.09006021 | 90 | 60 | 21 | 22 | 2262 | 2262 | 2262 | 0.053857 | 789 | 0.018786 | 2615 | 0.062262 | 1.518 | A06 | BIWW0.09006021
Build-In | Build-In Wall | BIWW.09006021/DBE | 90 | 60 | 21 | #N/A | 2742 | 2742 | 2742 | 0.065286 | 1371 | 0.032643 | 3016 | 0.07181 | 1 | A06 | BIWW0.09006021/DBE
Build-In | Build-In Wall | BIWW.09007010 | 90 | 70 | 10 | 12 | 958 | 958 | 958 | 0.02281 | 376 | 0.0089524 | 1089 | 0.025929 | 1.348 | A06 | BIWW0.09007010
Build-In | Build-In Wall | BIWW.09007011 | 90 | 70 | 11 | 12 | 1231 | 1231 | 1231 | 0.02931 | 455 | 0.010833 | 1411 | 0.033595 | 1.434 | A06 | BIWW0.09007011
Build-In | Build-In Wall | BIWW.09007011/DBE | 90 | 70 | 11 | #N/A | 1531 | 1531 | 1531 | 0.036452 | 766 | 0.018238 | 1684 | 0.040095 | 1 | A06 | BIWW0.09007011/DBE
Build-In | Build-In Wall | BIWW.09007015 | 90 | 70 | 15 | 17 | 1484 | 1484 | 1484 | 0.035333 | 592 | 0.014095 | 1684 | 0.040095 | 1.326 | A06 | BIWW0.09007015
Build-In | Build-In Wall | BIWW.09007016 | 90 | 70 | 16 | 17 | 1817 | 1817 | 1817 | 0.043262 | 650 | 0.015476 | 2091 | 0.049786 | 1.48 | A06 | BIWW0.09007016
Build-In | Build-In Wall | BIWW.09007016/DBE | 90 | 70 | 16 | #N/A | 2297 | 2297 | 2297 | 0.05469 | 1149 | 0.027357 | 2527 | 0.060167 | 1 | A06 | BIWW0.09007016/DBE
Build-In | Build-In Wall | BIWW.09007020 | 90 | 70 | 20 | 22 | 2070 | 2070 | 2070 | 0.049286 | 826 | 0.019667 | 2349 | 0.055929 | 1.326 | A06 | BIWW0.09007020
Build-In | Build-In Wall | BIWW.09007021 | 90 | 70 | 21 | 22 | 2639 | 2639 | 2639 | 0.062833 | 921 | 0.021929 | 3051 | 0.072643 | 1.518 | A06 | BIWW0.09007021
Build-In | Build-In Wall | BIWW.09007021/DBE | 90 | 70 | 21 | #N/A | 3119 | 3119 | 3119 | 0.074262 | 1560 | 0.037143 | 3431 | 0.08169 | 1 | A06 | BIWW0.09007021/DBE
Build-In | Build-In Wall | BIWW.09008010 | 90 | 80 | 10 | 12 | 1095 | 1095 | 1095 | 0.026071 | 430 | 0.010238 | 1245 | 0.029643 | 1.348 | A06 | BIWW0.09008010
Build-In | Build-In Wall | BIWW.09008011 | 90 | 80 | 11 | 12 | 1406 | 1406 | 1406 | 0.033476 | 520 | 0.012381 | 1611 | 0.038357 | 1.434 | A06 | BIWW0.09008011
Build-In | Build-In Wall | BIWW.09008011/DBE | 90 | 80 | 11 | #N/A | 1706 | 1706 | 1706 | 0.040619 | 853 | 0.02031 | 1877 | 0.04469 | 1 | A06 | BIWW0.09008011/DBE
Build-In | Build-In Wall | BIWW.09008015 | 90 | 80 | 15 | 17 | 1696 | 1696 | 1696 | 0.040381 | 677 | 0.016119 | 1925 | 0.045833 | 1.326 | A06 | BIWW0.09008015
Build-In | Build-In Wall | BIWW.09008016 | 90 | 80 | 16 | 17 | 2077 | 2077 | 2077 | 0.049452 | 744 | 0.017714 | 2391 | 0.056929 | 1.48 | A06 | BIWW0.09008016
Build-In | Build-In Wall | BIWW.09008016/DBE | 90 | 80 | 16 | #N/A | 2557 | 2557 | 2557 | 0.060881 | 1279 | 0.030452 | 2813 | 0.066976 | 1 | A06 | BIWW0.09008016/DBE
Build-In | Build-In Wall | BIWW.09008020 | 90 | 80 | 20 | 22 | 2366 | 2366 | 2366 | 0.056333 | 944 | 0.022476 | 2685 | 0.063929 | 1.326 | A06 | BIWW0.09008020
Build-In | Build-In Wall | BIWW.09008021 | 90 | 80 | 21 | 22 | 3016 | 3016 | 3016 | 0.07181 | 1053 | 0.025071 | 3486 | 0.083 | 1.518 | A06 | BIWW0.09008021
Build-In | Build-In Wall | BIWW.09008021/DBE | 90 | 80 | 21 | #N/A | 3496 | 3496 | 3496 | 0.083238 | 1748 | 0.041619 | 3846 | 0.091571 | 1 | A06 | BIWW0.09008021/DBE
Build-In | Build-In Wall | BIWW.09009010 | 90 | 90 | 10 | 12 | 1232 | 1232 | 1232 | 0.029333 | 484 | 0.011524 | 1401 | 0.033357 | 1.348 | A06 | BIWW0.09009010
Build-In | Build-In Wall | BIWW.09009011 | 90 | 90 | 11 | 12 | 1582 | 1582 | 1582 | 0.037667 | 585 | 0.013929 | 1813 | 0.043167 | 1.434 | A06 | BIWW0.09009011
Build-In | Build-In Wall | BIWW.09009011/DBE | 90 | 90 | 11 | #N/A | 2182 | 2182 | 2182 | 0.051952 | 1091 | 0.025976 | 2400 | 0.057143 | 1 | A06 | BIWW0.09009011/DBE
Build-In | Build-In Wall | BIWW.09009015 | 90 | 90 | 15 | 17 | 1908 | 1908 | 1908 | 0.045429 | 761 | 0.018119 | 2166 | 0.051571 | 1.326 | A06 | BIWW0.09009015
Build-In | Build-In Wall | BIWW.09009016 | 90 | 90 | 16 | 17 | 2336 | 2336 | 2336 | 0.055619 | 836 | 0.019905 | 2689 | 0.064024 | 1.48 | A06 | BIWW0.09009016
Build-In | Build-In Wall | BIWW.09009016/DBE | 90 | 90 | 16 | #N/A | 3296 | 3296 | 3296 | 0.078476 | 1648 | 0.039238 | 3626 | 0.086333 | 1 | A06 | BIWW0.09009016/DBE
Build-In | Build-In Wall | BIWW.09009020 | 90 | 90 | 20 | 22 | 2661 | 2661 | 2661 | 0.063357 | 1062 | 0.025286 | 3020 | 0.071905 | 1.326 | A06 | BIWW0.09009020
Build-In | Build-In Wall | BIWW.09009021 | 90 | 90 | 21 | 22 | 3393 | 3393 | 3393 | 0.080786 | 1184 | 0.02819 | 3922 | 0.093381 | 1.518 | A06 | BIWW0.09009021
Build-In | Build-In Wall | BIWW.09009021/DBE | 90 | 90 | 21 | #N/A | 4353 | 4353 | 4353 | 0.10364 | 2177 | 0.051833 | 4788 | 0.114 | 1 | A06 | BIWW0.09009021/DBE
Build-In | Build-In Wall | BIWW.09010010 | 90 | 100 | 10 | 12 | 1369 | 1369 | 1369 | 0.032595 | 538 | 0.01281 | 1557 | 0.037071 | 1.348 | A06 | BIWW0.09010010
Build-In | Build-In Wall | BIWW.09010011 | 90 | 100 | 11 | 12 | 1758 | 1758 | 1758 | 0.041857 | 650 | 0.015476 | 2015 | 0.047976 | 1.434 | A06 | BIWW0.09010011
Build-In | Build-In Wall | BIWW.09010011/DBE | 90 | 100 | 11 | #N/A | 2358 | 2358 | 2358 | 0.056143 | 1179 | 0.028071 | 2594 | 0.061762 | 1 | A06 | BIWW0.09010011/DBE
Build-In | Build-In Wall | BIWW.09010015 | 90 | 100 | 15 | 17 | 2120 | 2120 | 2120 | 0.050476 | 846 | 0.020143 | 2406 | 0.057286 | 1.326 | A06 | BIWW0.09010015
Build-In | Build-In Wall | BIWW.09010016 | 90 | 100 | 16 | 17 | 2596 | 2596 | 2596 | 0.06181 | 929 | 0.022119 | 2988 | 0.071143 | 1.48 | A06 | BIWW0.09010016
Build-In | Build-In Wall | BIWW.09010016/DBE | 90 | 100 | 16 | #N/A | 3556 | 3556 | 3556 | 0.084667 | 1778 | 0.042333 | 3912 | 0.093143 | 1 | A06 | BIWW0.09010016/DBE
Build-In | Build-In Wall | BIWW.09010020 | 90 | 100 | 20 | 22 | 2957 | 2957 | 2957 | 0.070405 | 1180 | 0.028095 | 3356 | 0.079905 | 1.326 | A06 | BIWW0.09010020
Build-In | Build-In Wall | BIWW.09010021 | 90 | 100 | 21 | 22 | 3770 | 3770 | 3770 | 0.089762 | 1316 | 0.031333 | 4358 | 0.10376 | 1.518 | A06 | BIWW0.09010021
Build-In | Build-In Wall | BIWW.09010021/DBE | 90 | 100 | 21 | #N/A | 4730 | 4730 | 4730 | 0.11262 | 2365 | 0.05631 | 5203 | 0.12388 | 1 | A06 | BIWW0.09010021/DBE
Build-In | Build-In Wall | BIWW.09011010 | 90 | 110 | 10 | 12 | 1506 | 1506 | 1506 | 0.035857 | 592 | 0.014095 | 1712 | 0.040762 | 1.348 | A06 | BIWW0.09011010
Build-In | Build-In Wall | BIWW.09011011 | 90 | 110 | 11 | 12 | 1934 | 1934 | 1934 | 0.046048 | 716 | 0.017048 | 2216 | 0.052762 | 1.434 | A06 | BIWW0.09011011
Build-In | Build-In Wall | BIWW.09011011/DBE | 90 | 110 | 11 | #N/A | 2534 | 2534 | 2534 | 0.060333 | 1267 | 0.030167 | 2787 | 0.066357 | 1 | A06 | BIWW0.09011011/DBE
Build-In | Build-In Wall | BIWW.09011015 | 90 | 110 | 15 | 17 | 2332 | 2332 | 2332 | 0.055524 | 930 | 0.022143 | 2647 | 0.063024 | 1.326 | A06 | BIWW0.09011015
Build-In | Build-In Wall | BIWW.09011016 | 90 | 110 | 16 | 17 | 2856 | 2856 | 2856 | 0.068 | 1022 | 0.024333 | 3287 | 0.078262 | 1.48 | A06 | BIWW0.09011016
Build-In | Build-In Wall | BIWW.09011016/DBE | 90 | 110 | 16 | #N/A | 3816 | 3816 | 3816 | 0.090857 | 1908 | 0.045429 | 4198 | 0.099952 | 1 | A06 | BIWW0.09011016/DBE
Build-In | Build-In Wall | BIWW.09011020 | 90 | 110 | 20 | 22 | 3253 | 3253 | 3253 | 0.077452 | 1298 | 0.030905 | 3692 | 0.087905 | 1.326 | A06 | BIWW0.09011020
Build-In | Build-In Wall | BIWW.09011021 | 90 | 110 | 21 | 22 | 4147 | 4147 | 4147 | 0.098738 | 1447 | 0.034452 | 4794 | 0.11414 | 1.518 | A06 | BIWW0.09011021
Build-In | Build-In Wall | BIWW.09011021/DBE | 90 | 110 | 21 | #N/A | 5107 | 5107 | 5107 | 0.1216 | 2554 | 0.06081 | 5618 | 0.13376 | 1 | A06 | BIWW0.09011021/DBE
Build-In | Build-In Wall | BIWW.09012010 | 90 | 120 | 10 | 12 | 1643 | 1643 | 1643 | 0.039119 | 646 | 0.015381 | 1868 | 0.044476 | 1.348 | A06 | BIWW0.09012010
Build-In | Build-In Wall | BIWW.09012011 | 90 | 120 | 11 | 12 | 2110 | 2110 | 2110 | 0.050238 | 781 | 0.018595 | 2418 | 0.057571 | 1.434 | A06 | BIWW0.09012011
Build-In | Build-In Wall | BIWW.09012011/DBE | 90 | 120 | 11 | #N/A | 2710 | 2710 | 2710 | 0.064524 | 1355 | 0.032262 | 2981 | 0.070976 | 1 | A06 | BIWW0.09012011/DBE
Build-In | Build-In Wall | BIWW.09012015 | 90 | 120 | 15 | 17 | 2544 | 2544 | 2544 | 0.060571 | 1015 | 0.024167 | 2887 | 0.068738 | 1.326 | A06 | BIWW0.09012015
Build-In | Build-In Wall | BIWW.09012016 | 90 | 120 | 16 | 17 | 3115 | 3115 | 3115 | 0.074167 | 1115 | 0.026548 | 3585 | 0.085357 | 1.48 | A06 | BIWW0.09012016
Build-In | Build-In Wall | BIWW.09012016/DBE | 90 | 120 | 16 | #N/A | 4075 | 4075 | 4075 | 0.097024 | 2038 | 0.048524 | 4483 | 0.10674 | 1 | A06 | BIWW0.09012016/DBE
Build-In | Build-In Wall | BIWW.09012020 | 90 | 120 | 20 | 22 | 3548 | 3548 | 3548 | 0.084476 | 1416 | 0.033714 | 4027 | 0.095881 | 1.326 | A06 | BIWW0.09012020
Build-In | Build-In Wall | BIWW.09012021 | 90 | 120 | 21 | 22 | 4524 | 4524 | 4524 | 0.10771 | 1579 | 0.037595 | 5230 | 0.12452 | 1.518 | A06 | BIWW0.09012021
Build-In | Build-In Wall | BIWW.09012021/DBE | 90 | 120 | 21 | #N/A | 5484 | 5484 | 5484 | 0.13057 | 2742 | 0.065286 | 6032 | 0.14362 | 1 | A06 | BIWW0.09012021/DBE
Build-In | Build-In Wall | BIWW.09014010 | 90 | 140 | 10 | 12 | 1917 | 1917 | 1917 | 0.045643 | 753 | 0.017929 | 2180 | 0.051905 | 1.348 | A06 | BIWW0.09014010
Build-In | Build-In Wall | BIWW.09014011 | 90 | 140 | 11 | 12 | 2461 | 2461 | 2461 | 0.058595 | 911 | 0.02169 | 2820 | 0.067143 | 1.434 | A06 | BIWW0.09014011
Build-In | Build-In Wall | BIWW.09014011/DBE | 90 | 140 | 11 | #N/A | 3061 | 3061 | 3061 | 0.072881 | 1531 | 0.036452 | 3367 | 0.080167 | 1 | A06 | BIWW0.09014011/DBE
Build-In | Build-In Wall | BIWW.09014015 | 90 | 140 | 15 | 17 | 2968 | 2968 | 2968 | 0.070667 | 1184 | 0.02819 | 3369 | 0.080214 | 1.326 | A06 | BIWW0.09014015
Build-In | Build-In Wall | BIWW.09014016 | 90 | 140 | 16 | 17 | 3634 | 3634 | 3634 | 0.086524 | 1301 | 0.030976 | 4183 | 0.099595 | 1.48 | A06 | BIWW0.09014016
Build-In | Build-In Wall | BIWW.09014016/DBE | 90 | 140 | 16 | #N/A | 4594 | 4594 | 4594 | 0.10938 | 2297 | 0.05469 | 5053 | 0.12031 | 1 | A06 | BIWW0.09014016/DBE
Build-In | Build-In Wall | BIWW.09014020 | 90 | 140 | 20 | 22 | 4140 | 4140 | 4140 | 0.098571 | 1652 | 0.039333 | 4699 | 0.11188 | 1.326 | A06 | BIWW0.09014020
Build-In | Build-In Wall | BIWW.09014021 | 90 | 140 | 21 | 22 | 5278 | 5278 | 5278 | 0.12567 | 1842 | 0.043857 | 6101 | 0.14526 | 1.518 | A06 | BIWW0.09014021
Build-In | Build-In Wall | BIWW.09014021/DBE | 90 | 140 | 21 | #N/A | 6238 | 6238 | 6238 | 0.14852 | 3119 | 0.074262 | 6862 | 0.16338 | 1 | A06 | BIWW0.09014021/DBE
Build-In | Build-In Wall | BIWW.09016010 | 90 | 160 | 10 | 12 | 2190 | 2190 | 2190 | 0.052143 | 861 | 0.0205 | 2490 | 0.059286 | 1.348 | A06 | BIWW0.09016010
Build-In | Build-In Wall | BIWW.09016011 | 90 | 160 | 11 | 12 | 2813 | 2813 | 2813 | 0.066976 | 1041 | 0.024786 | 3224 | 0.076762 | 1.434 | A06 | BIWW0.09016011
Build-In | Build-In Wall | BIWW.09016011/DBE | 90 | 160 | 11 | #N/A | 4013 | 4013 | 4013 | 0.095548 | 2007 | 0.047786 | 4414 | 0.1051 | 1 | A06 | BIWW0.09016011/DBE
Build-In | Build-In Wall | BIWW.09016015 | 90 | 160 | 15 | 17 | 3392 | 3392 | 3392 | 0.080762 | 1353 | 0.032214 | 3850 | 0.091667 | 1.326 | A06 | BIWW0.09016015
Build-In | Build-In Wall | BIWW.09016016 | 90 | 160 | 16 | 17 | 4154 | 4154 | 4154 | 0.098905 | 1487 | 0.035405 | 4781 | 0.11383 | 1.48 | A06 | BIWW0.09016016
Build-In | Build-In Wall | BIWW.09016016/DBE | 90 | 160 | 16 | #N/A | 6074 | 6074 | 6074 | 0.14462 | 3037 | 0.07231 | 6681 | 0.15907 | 1 | A06 | BIWW0.09016016/DBE
Build-In | Build-In Wall | BIWW.09016020 | 90 | 160 | 20 | 22 | 4731 | 4731 | 4731 | 0.11264 | 1888 | 0.044952 | 5370 | 0.12786 | 1.326 | A06 | BIWW0.09016020
Build-In | Build-In Wall | BIWW.09016021 | 90 | 160 | 21 | 22 | 6032 | 6032 | 6032 | 0.14362 | 2105 | 0.050119 | 6973 | 0.16602 | 1.518 | A06 | BIWW0.09016021
Build-In | Build-In Wall | BIWW.09016021/DBE | 90 | 160 | 21 | #N/A | 7952 | 7952 | 7952 | 0.18933 | 3976 | 0.094667 | 8747 | 0.20826 | 1 | A06 | BIWW0.09016021/DBE
Build-In | Build-In Wall | BIWW.09018010 | 90 | 180 | 10 | 12 | 2464 | 2464 | 2464 | 0.058667 | 968 | 0.023048 | 2802 | 0.066714 | 1.348 | A06 | BIWW0.09018010
Build-In | Build-In Wall | BIWW.09018011 | 90 | 180 | 11 | 12 | 3164 | 3164 | 3164 | 0.075333 | 1171 | 0.027881 | 3626 | 0.086333 | 1.434 | A06 | BIWW0.09018011
Build-In | Build-In Wall | BIWW.09018011/DBE | 90 | 180 | 11 | #N/A | 4364 | 4364 | 4364 | 0.1039 | 2182 | 0.051952 | 4800 | 0.11429 | 1 | A06 | BIWW0.09018011/DBE
Build-In | Build-In Wall | BIWW.09018015 | 90 | 180 | 15 | 17 | 3816 | 3816 | 3816 | 0.090857 | 1523 | 0.036262 | 4331 | 0.10312 | 1.326 | A06 | BIWW0.09018015
Build-In | Build-In Wall | BIWW.09018016 | 90 | 180 | 16 | 17 | 4673 | 4673 | 4673 | 0.11126 | 1673 | 0.039833 | 5379 | 0.12807 | 1.48 | A06 | BIWW0.09018016
Build-In | Build-In Wall | BIWW.09018016/DBE | 90 | 180 | 16 | #N/A | 6593 | 6593 | 6593 | 0.15698 | 3297 | 0.0785 | 7252 | 0.17267 | 1 | A06 | BIWW0.09018016/DBE
Build-In | Build-In Wall | BIWW.09018020 | 90 | 180 | 20 | 22 | 5323 | 5323 | 5323 | 0.12674 | 2124 | 0.050571 | 6042 | 0.14386 | 1.326 | A06 | BIWW0.09018020
Build-In | Build-In Wall | BIWW.09018021 | 90 | 180 | 21 | 22 | 6786 | 6786 | 6786 | 0.16157 | 2368 | 0.056381 | 7845 | 0.18679 | 1.518 | A06 | BIWW0.09018021
Build-In | Build-In Wall | BIWW.09018021/DBE | 90 | 180 | 21 | #N/A | 8706 | 8706 | 8706 | 0.20729 | 4353 | 0.10364 | 9577 | 0.22802 | 1 | A06 | BIWW0.09018021/DBE
Build-In | Build-In Wall | BIWW.09020010 | 90 | 200 | 10 | 12 | 2738 | 2738 | 2738 | 0.06519 | 1076 | 0.025619 | 3113 | 0.074119 | 1.348 | A06 | BIWW0.09020010
Build-In | Build-In Wall | BIWW.09020011 | 90 | 200 | 11 | 12 | 3516 | 3516 | 3516 | 0.083714 | 1301 | 0.030976 | 4029 | 0.095929 | 1.434 | A06 | BIWW0.09020011
Build-In | Build-In Wall | BIWW.09020011/DBE | 90 | 200 | 11 | #N/A | 4716 | 4716 | 4716 | 0.11229 | 2358 | 0.056143 | 5188 | 0.12352 | 1 | A06 | BIWW0.09020011/DBE
Build-In | Build-In Wall | BIWW.09020015 | 90 | 200 | 15 | 17 | 4240 | 4240 | 4240 | 0.10095 | 1692 | 0.040286 | 4812 | 0.11457 | 1.326 | A06 | BIWW0.09020015
Build-In | Build-In Wall | BIWW.09020016 | 90 | 200 | 16 | 17 | 5192 | 5192 | 5192 | 0.12362 | 1859 | 0.044262 | 5976 | 0.14229 | 1.48 | A06 | BIWW0.09020016
Build-In | Build-In Wall | BIWW.09020016/DBE | 90 | 200 | 16 | #N/A | 7112 | 7112 | 7112 | 0.16933 | 3556 | 0.084667 | 7823 | 0.18626 | 1 | A06 | BIWW0.09020016/DBE
Build-In | Build-In Wall | BIWW.09020020 | 90 | 200 | 20 | 22 | 5914 | 5914 | 5914 | 0.14081 | 2360 | 0.05619 | 6712 | 0.15981 | 1.326 | A06 | BIWW0.09020020
Build-In | Build-In Wall | BIWW.09020021 | 90 | 200 | 21 | 22 | 7540 | 7540 | 7540 | 0.17952 | 2631 | 0.062643 | 8716 | 0.20752 | 1.518 | A06 | BIWW0.09020021
Build-In | Build-In Wall | BIWW.09020021/DBE | 90 | 200 | 21 | #N/A | 9460 | 9460 | 9460 | 0.22524 | 4730 | 0.11262 | 10406 | 0.24776 | 1 | A06 | BIWW0.09020021/DBE
Build-In | Build-In Wall | BIWW.09022010 | 90 | 220 | 10 | 12 | 3012 | 3012 | 3012 | 0.071714 | 1184 | 0.02819 | 3425 | 0.081548 | 1.348 | A06 | BIWW0.09022010
Build-In | Build-In Wall | BIWW.09022011 | 90 | 220 | 11 | 12 | 3868 | 3868 | 3868 | 0.092095 | 1431 | 0.034071 | 4433 | 0.10555 | 1.434 | A06 | BIWW0.09022011
Build-In | Build-In Wall | BIWW.09022011/DBE | 90 | 220 | 11 | #N/A | 5068 | 5068 | 5068 | 0.12067 | 2534 | 0.060333 | 5575 | 0.13274 | 1 | A06 | BIWW0.09022011/DBE
Build-In | Build-In Wall | BIWW.09022015 | 90 | 220 | 15 | 17 | 4664 | 4664 | 4664 | 0.11105 | 1861 | 0.04431 | 5294 | 0.12605 | 1.326 | A06 | BIWW0.09022015
Build-In | Build-In Wall | BIWW.09022016 | 90 | 220 | 16 | 17 | 5711 | 5711 | 5711 | 0.13598 | 2045 | 0.04869 | 6573 | 0.1565 | 1.48 | A06 | BIWW0.09022016
Build-In | Build-In Wall | BIWW.09022016/DBE | 90 | 220 | 16 | #N/A | 7631 | 7631 | 7631 | 0.18169 | 3816 | 0.090857 | 8394 | 0.19986 | 1 | A06 | BIWW0.09022016/DBE
Build-In | Build-In Wall | BIWW.09022020 | 90 | 220 | 20 | 22 | 6505 | 6505 | 6505 | 0.15488 | 2595 | 0.061786 | 7383 | 0.17579 | 1.326 | A06 | BIWW0.09022020
Build-In | Build-In Wall | BIWW.09022021 | 90 | 220 | 21 | 22 | 8294 | 8294 | 8294 | 0.19748 | 2895 | 0.068929 | 9588 | 0.22829 | 1.518 | A06 | BIWW0.09022021
Build-In | Build-In Wall | BIWW.09022021/DBE | 90 | 220 | 21 | #N/A | 10214 | 10214 | 10214 | 0.24319 | 5107 | 0.1216 | 11235 | 0.2675 | 1 | A06 | BIWW0.09022021/DBE
Build-In | Build-In Wall | BIWW.09024010 | 90 | 240 | 10 | 12 | 3286 | 3286 | 3286 | 0.078238 | 1291 | 0.030738 | 3736 | 0.088952 | 1.348 | A06 | BIWW0.09024010
Build-In | Build-In Wall | BIWW.09024011 | 90 | 240 | 11 | 12 | 4219 | 4219 | 4219 | 0.10045 | 1561 | 0.037167 | 4835 | 0.11512 | 1.434 | A06 | BIWW0.09024011
Build-In | Build-In Wall | BIWW.09024011/DBE | 90 | 240 | 11 | #N/A | 6019 | 6019 | 6019 | 0.14331 | 3010 | 0.071667 | 6621 | 0.15764 | 1 | A06 | BIWW0.09024011/DBE
Build-In | Build-In Wall | BIWW.09024015 | 90 | 240 | 15 | 17 | 5088 | 5088 | 5088 | 0.12114 | 2030 | 0.048333 | 5775 | 0.1375 | 1.326 | A06 | BIWW0.09024015
Build-In | Build-In Wall | BIWW.09024016 | 90 | 240 | 16 | 17 | 6230 | 6230 | 6230 | 0.14833 | 2230 | 0.053095 | 7171 | 0.17074 | 1.48 | A06 | BIWW0.09024016
Build-In | Build-In Wall | BIWW.09024016/DBE | 90 | 240 | 16 | #N/A | 9110 | 9110 | 9110 | 0.2169 | 4555 | 0.10845 | 10021 | 0.2386 | 1 | A06 | BIWW0.09024016/DBE
Build-In | Build-In Wall | BIWW.09024020 | 90 | 240 | 20 | 22 | 7097 | 7097 | 7097 | 0.16898 | 2832 | 0.067429 | 8055 | 0.19179 | 1.326 | A06 | BIWW0.09024020
Build-In | Build-In Wall | BIWW.09024021 | 90 | 240 | 21 | 22 | 9048 | 9048 | 9048 | 0.21543 | 3158 | 0.07519 | 10459 | 0.24902 | 1.518 | A06 | BIWW0.09024021
Build-In | Build-In Wall | BIWW.09024021/DBE | 90 | 240 | 21 | #N/A | 11928 | 11928 | 11928 | 0.284 | 5964 | 0.142 | 13121 | 0.3124 | 1 | A06 | BIWW0.09024021/DBE
Build-In | Build-In Wall | BIWW.09026010 | 90 | 260 | 10 | 12 | 3559 | 3559 | 3559 | 0.084738 | 1399 | 0.03331 | 4047 | 0.096357 | 1.348 | A06 | BIWW0.09026010
Build-In | Build-In Wall | BIWW.09026011 | 90 | 260 | 11 | 12 | 4571 | 4571 | 4571 | 0.10883 | 1691 | 0.040262 | 5238 | 0.12471 | 1.434 | A06 | BIWW0.09026011
Build-In | Build-In Wall | BIWW.09026011/DBE | 90 | 260 | 11 | #N/A | 6371 | 6371 | 6371 | 0.15169 | 3186 | 0.075857 | 7008 | 0.16686 | 1 | A06 | BIWW0.09026011/DBE
Build-In | Build-In Wall | BIWW.09026015 | 90 | 260 | 15 | 17 | 5512 | 5512 | 5512 | 0.13124 | 2199 | 0.052357 | 6256 | 0.14895 | 1.326 | A06 | BIWW0.09026015
Build-In | Build-In Wall | BIWW.09026016 | 90 | 260 | 16 | 17 | 6750 | 6750 | 6750 | 0.16071 | 2417 | 0.057548 | 7769 | 0.18498 | 1.48 | A06 | BIWW0.09026016
Build-In | Build-In Wall | BIWW.09026016/DBE | 90 | 260 | 16 | #N/A | 9630 | 9630 | 9630 | 0.22929 | 4815 | 0.11464 | 10593 | 0.25221 | 1 | A06 | BIWW0.09026016/DBE
Build-In | Build-In Wall | BIWW.09026020 | 90 | 260 | 20 | 22 | 7688 | 7688 | 7688 | 0.18305 | 3068 | 0.073048 | 8726 | 0.20776 | 1.326 | A06 | BIWW0.09026020
Build-In | Build-In Wall | BIWW.09026021 | 90 | 260 | 21 | 22 | 9802 | 9802 | 9802 | 0.23338 | 3421 | 0.081452 | 11331 | 0.26979 | 1.518 | A06 | BIWW0.09026021
Build-In | Build-In Wall | BIWW.09026021/DBE | 90 | 260 | 21 | #N/A | 12682 | 12682 | 12682 | 0.30195 | 6341 | 0.15098 | 13950 | 0.33214 | 1 | A06 | BIWW0.09026021/DBE
Build-In | Build-In Wall | BIWW.09028010 | 90 | 280 | 10 | 12 | 3833 | 3833 | 3833 | 0.091262 | 1506 | 0.035857 | 4358 | 0.10376 | 1.348 | A06 | BIWW0.09028010
Build-In | Build-In Wall | BIWW.09028011 | 90 | 280 | 11 | 12 | 4922 | 4922 | 4922 | 0.11719 | 1821 | 0.043357 | 5641 | 0.13431 | 1.434 | A06 | BIWW0.09028011
Build-In | Build-In Wall | BIWW.09028011/DBE | 90 | 280 | 11 | #N/A | 6722 | 6722 | 6722 | 0.16005 | 3361 | 0.080024 | 7394 | 0.17605 | 1 | A06 | BIWW0.09028011/DBE
Build-In | Build-In Wall | BIWW.09028015 | 90 | 280 | 15 | 17 | 5936 | 5936 | 5936 | 0.14133 | 2368 | 0.056381 | 6737 | 0.1604 | 1.326 | A06 | BIWW0.09028015
Build-In | Build-In Wall | BIWW.09028016 | 90 | 280 | 16 | 17 | 7269 | 7269 | 7269 | 0.17307 | 2602 | 0.061952 | 8367 | 0.19921 | 1.48 | A06 | BIWW0.09028016
Build-In | Build-In Wall | BIWW.09028016/DBE | 90 | 280 | 16 | #N/A | 10149 | 10149 | 10149 | 0.24164 | 5075 | 0.12083 | 11164 | 0.26581 | 1 | A06 | BIWW0.09028016/DBE
Build-In | Build-In Wall | BIWW.09028020 | 90 | 280 | 20 | 22 | 8280 | 8280 | 8280 | 0.19714 | 3304 | 0.078667 | 9398 | 0.22376 | 1.326 | A06 | BIWW0.09028020
Build-In | Build-In Wall | BIWW.09028021 | 90 | 280 | 21 | 22 | 10556 | 10556 | 10556 | 0.25133 | 3684 | 0.087714 | 12203 | 0.29055 | 1.518 | A06 | BIWW0.09028021
Build-In | Build-In Wall | BIWW.09028021/DBE | 90 | 280 | 21 | #N/A | 13436 | 13436 | 13436 | 0.3199 | 6718 | 0.15995 | 14780 | 0.3519 | 1 | A06 | BIWW0.09028021/DBE
Build-In | Build-In Wall | BIWW.09030010 | 90 | 300 | 10 | 12 | 4107 | 4107 | 4107 | 0.097786 | 1614 | 0.038429 | 4670 | 0.11119 | 1.348 | A06 | BIWW0.09030010
Build-In | Build-In Wall | BIWW.09030011 | 90 | 300 | 11 | 12 | 5274 | 5274 | 5274 | 0.12557 | 1951 | 0.046452 | 6044 | 0.1439 | 1.434 | A06 | BIWW0.09030011
Build-In | Build-In Wall | BIWW.09030011/DBE | 90 | 300 | 11 | #N/A | 7074 | 7074 | 7074 | 0.16843 | 3537 | 0.084214 | 7781 | 0.18526 | 1 | A06 | BIWW0.09030011/DBE
Build-In | Build-In Wall | BIWW.09030015 | 90 | 300 | 15 | 17 | 6360 | 6360 | 6360 | 0.15143 | 2538 | 0.060429 | 7219 | 0.17188 | 1.326 | A06 | BIWW0.09030015
Build-In | Build-In Wall | BIWW.09030016 | 90 | 300 | 16 | 17 | 7788 | 7788 | 7788 | 0.18543 | 2788 | 0.066381 | 8964 | 0.21343 | 1.48 | A06 | BIWW0.09030016
Build-In | Build-In Wall | BIWW.09030016/DBE | 90 | 300 | 16 | #N/A | 10668 | 10668 | 10668 | 0.254 | 5334 | 0.127 | 11735 | 0.2794 | 1 | A06 | BIWW0.09030016/DBE
Build-In | Build-In Wall | BIWW.09030020 | 90 | 300 | 20 | 22 | 8871 | 8871 | 8871 | 0.21121 | 3540 | 0.084286 | 10069 | 0.23974 | 1.326 | A06 | BIWW0.09030020
Build-In | Build-In Wall | BIWW.09030021 | 90 | 300 | 21 | 22 | 11310 | 11310 | 11310 | 0.26929 | 3947 | 0.093976 | 13074 | 0.31129 | 1.518 | A06 | BIWW0.09030021
Build-In | Build-In Wall | BIWW.09030021/DBE | 90 | 300 | 21 | #N/A | 14190 | 14190 | 14190 | 0.33786 | 7095 | 0.16893 | 15609 | 0.37164 | 1 | A06 | BIWW0.09030021/DBE
Horizontal Wall | Knockonwood | KNOW.03006006 | 30 | 60 | 06 | 11 | 416 | 416 | 416 | 0.0099048 | 151 | 0.0035952 | 478 | 0.011381 | 1.457 | A13 | KNOW0.03006006
Horizontal Wall | Knockonwood | KNOW.03006006/DBE | 30 | 60 | 06 | 11 | 551 | 551 | 551 | 0.013119 | 276 | 0.0065714 | 606 | 0.014429 | 1 | A13 | KNOW0.03006006/DBE
Horizontal Wall | Knockonwood | KNOW.03006010 | 30 | 60 | 10 | 13 | 452 | 452 | 452 | 0.010762 | 165 | 0.0039286 | 519 | 0.012357 | 1.453 | A13 | KNOW0.03006010
Horizontal Wall | Knockonwood | KNOW.03006011 | 30 | 60 | 11 | 13 | 515 | 515 | 515 | 0.012262 | 180 | 0.0042857 | 595 | 0.014167 | 1.516 | A13 | KNOW0.03006011
Horizontal Wall | Knockonwood | KNOW.03006011/DBE | 30 | 60 | 11 | 13 | 815 | 815 | 815 | 0.019405 | 408 | 0.0097143 | 897 | 0.021357 | 1 | A13 | KNOW0.03006011/DBE
Horizontal Wall | Knockonwood | KNOW.03006015 | 30 | 60 | 15 | 18 | 689 | 689 | 689 | 0.016405 | 254 | 0.0060476 | 790 | 0.01881 | 1.442 | A13 | KNOW0.03006015
Horizontal Wall | Knockonwood | KNOW.03006016 | 30 | 60 | 16 | 18 | 752 | 752 | 752 | 0.017905 | 267 | 0.0063571 | 867 | 0.020643 | 1.495 | A13 | KNOW0.03006016
Horizontal Wall | Knockonwood | KNOW.03006016/DBE | 30 | 60 | 16 | 18 | 1232 | 1232 | 1232 | 0.029333 | 616 | 0.014667 | 1355 | 0.032262 | 1 | A13 | KNOW0.03006016/DBE
Horizontal Wall | Knockonwood | KNOW.03008006 | 30 | 80 | 06 | 11 | 554 | 554 | 554 | 0.01319 | 202 | 0.0048095 | 637 | 0.015167 | 1.457 | A13 | KNOW0.03008006
Horizontal Wall | Knockonwood | KNOW.03008006/DBE | 30 | 80 | 06 | 11 | 689 | 689 | 689 | 0.016405 | 345 | 0.0082143 | 758 | 0.018048 | 1 | A13 | KNOW0.03008006/DBE
Horizontal Wall | Knockonwood | KNOW.03008010 | 30 | 80 | 10 | 13 | 603 | 603 | 603 | 0.014357 | 220 | 0.0052381 | 693 | 0.0165 | 1.453 | A13 | KNOW0.03008010
Horizontal Wall | Knockonwood | KNOW.03008011 | 30 | 80 | 11 | 13 | 687 | 687 | 687 | 0.016357 | 240 | 0.0057143 | 793 | 0.018881 | 1.516 | A13 | KNOW0.03008011
Horizontal Wall | Knockonwood | KNOW.03008011/DBE | 30 | 80 | 11 | 13 | 987 | 987 | 987 | 0.0235 | 494 | 0.011762 | 1086 | 0.025857 | 1 | A13 | KNOW0.03008011/DBE
Horizontal Wall | Knockonwood | KNOW.03008015 | 30 | 80 | 15 | 18 | 919 | 919 | 919 | 0.021881 | 338 | 0.0080476 | 1054 | 0.025095 | 1.442 | A13 | KNOW0.03008015
Horizontal Wall | Knockonwood | KNOW.03008016 | 30 | 80 | 16 | 18 | 1002 | 1002 | 1002 | 0.023857 | 356 | 0.0084762 | 1155 | 0.0275 | 1.495 | A13 | KNOW0.03008016
Horizontal Wall | Knockonwood | KNOW.03008016/DBE | 30 | 80 | 16 | 18 | 1482 | 1482 | 1482 | 0.035286 | 741 | 0.017643 | 1630 | 0.03881 | 1 | A13 | KNOW0.03008016/DBE
Horizontal Wall | Knockonwood | KNOW.03010006 | 30 | 100 | 06 | 11 | 693 | 693 | 693 | 0.0165 | 252 | 0.006 | 796 | 0.018952 | 1.457 | A13 | KNOW0.03010006
Horizontal Wall | Knockonwood | KNOW.03010006/DBE | 30 | 100 | 06 | 11 | 963 | 963 | 963 | 0.022929 | 482 | 0.011476 | 1059 | 0.025214 | 1 | A13 | KNOW0.03010006/DBE
Horizontal Wall | Knockonwood | KNOW.03010010 | 30 | 100 | 10 | 13 | 754 | 754 | 754 | 0.017952 | 275 | 0.0065476 | 866 | 0.020619 | 1.453 | A13 | KNOW0.03010010
Horizontal Wall | Knockonwood | KNOW.03010011 | 30 | 100 | 11 | 13 | 859 | 859 | 859 | 0.020452 | 301 | 0.0071667 | 992 | 0.023619 | 1.516 | A13 | KNOW0.03010011
Horizontal Wall | Knockonwood | KNOW.03010011/DBE | 30 | 100 | 11 | 13 | 1459 | 1459 | 1459 | 0.034738 | 730 | 0.017381 | 1605 | 0.038214 | 1 | A13 | KNOW0.03010011/DBE
Horizontal Wall | Knockonwood | KNOW.03010015 | 30 | 100 | 15 | 18 | 1149 | 1149 | 1149 | 0.027357 | 423 | 0.010071 | 1318 | 0.031381 | 1.442 | A13 | KNOW0.03010015
Horizontal Wall | Knockonwood | KNOW.03010016 | 30 | 100 | 16 | 18 | 1253 | 1253 | 1253 | 0.029833 | 445 | 0.010595 | 1445 | 0.034405 | 1.495 | A13 | KNOW0.03010016
Horizontal Wall | Knockonwood | KNOW.03010016/DBE | 30 | 100 | 16 | 18 | 2213 | 2213 | 2213 | 0.05269 | 1107 | 0.026357 | 2434 | 0.057952 | 1 | A13 | KNOW0.03010016/DBE
Horizontal Wall | Knockonwood | KNOW.03012006 | 30 | 120 | 06 | 11 | 832 | 832 | 832 | 0.01981 | 303 | 0.0072143 | 956 | 0.022762 | 1.457 | A13 | KNOW0.03012006
Horizontal Wall | Knockonwood | KNOW.03012006/DBE | 30 | 120 | 06 | 11 | 1102 | 1102 | 1102 | 0.026238 | 551 | 0.013119 | 1212 | 0.028857 | 1 | A13 | KNOW0.03012006/DBE
Horizontal Wall | Knockonwood | KNOW.03012010 | 30 | 120 | 10 | 13 | 905 | 905 | 905 | 0.021548 | 330 | 0.0078571 | 1040 | 0.024762 | 1.453 | A13 | KNOW0.03012010
Horizontal Wall | Knockonwood | KNOW.03012011 | 30 | 120 | 11 | 13 | 1031 | 1031 | 1031 | 0.024548 | 361 | 0.0085952 | 1191 | 0.028357 | 1.516 | A13 | KNOW0.03012011
Horizontal Wall | Knockonwood | KNOW.03012011/DBE | 30 | 120 | 11 | 13 | 1631 | 1631 | 1631 | 0.038833 | 816 | 0.019429 | 1794 | 0.042714 | 1 | A13 | KNOW0.03012011/DBE
Horizontal Wall | Knockonwood | KNOW.03012015 | 30 | 120 | 15 | 18 | 1379 | 1379 | 1379 | 0.032833 | 507 | 0.012071 | 1582 | 0.037667 | 1.442 | A13 | KNOW0.03012015
Horizontal Wall | Knockonwood | KNOW.03012016 | 30 | 120 | 16 | 18 | 1504 | 1504 | 1504 | 0.03581 | 534 | 0.012714 | 1734 | 0.041286 | 1.495 | A13 | KNOW0.03012016
Horizontal Wall | Knockonwood | KNOW.03012016/DBE | 30 | 120 | 16 | 18 | 2464 | 2464 | 2464 | 0.058667 | 1232 | 0.029333 | 2710 | 0.064524 | 1 | A13 | KNOW0.03012016/DBE
Horizontal Wall | Knockonwood | KNOW.03014006 | 30 | 140 | 06 | 11 | 970 | 970 | 970 | 0.023095 | 353 | 0.0084048 | 1115 | 0.026548 | 1.457 | A13 | KNOW0.03014006
Horizontal Wall | Knockonwood | KNOW.03014006/DBE | 30 | 140 | 06 | 11 | 1240 | 1240 | 1240 | 0.029524 | 620 | 0.014762 | 1364 | 0.032476 | 1 | A13 | KNOW0.03014006/DBE
Horizontal Wall | Knockonwood | KNOW.03014010 | 30 | 140 | 10 | 13 | 1056 | 1056 | 1056 | 0.025143 | 385 | 0.0091667 | 1213 | 0.028881 | 1.453 | A13 | KNOW0.03014010
Horizontal Wall | Knockonwood | KNOW.03014011 | 30 | 140 | 11 | 13 | 1203 | 1203 | 1203 | 0.028643 | 421 | 0.010024 | 1389 | 0.033071 | 1.516 | A13 | KNOW0.03014011
Horizontal Wall | Knockonwood | KNOW.03014011/DBE | 30 | 140 | 11 | 13 | 1803 | 1803 | 1803 | 0.042929 | 902 | 0.021476 | 1983 | 0.047214 | 1 | A13 | KNOW0.03014011/DBE
Horizontal Wall | Knockonwood | KNOW.03014015 | 30 | 140 | 15 | 18 | 1609 | 1609 | 1609 | 0.03831 | 592 | 0.014095 | 1846 | 0.043952 | 1.442 | A13 | KNOW0.03014015
Horizontal Wall | Knockonwood | KNOW.03014016 | 30 | 140 | 16 | 18 | 1754 | 1754 | 1754 | 0.041762 | 623 | 0.014833 | 2022 | 0.048143 | 1.495 | A13 | KNOW0.03014016
Horizontal Wall | Knockonwood | KNOW.03014016/DBE | 30 | 140 | 16 | 18 | 2714 | 2714 | 2714 | 0.064619 | 1357 | 0.03231 | 2985 | 0.071071 | 1 | A13 | KNOW0.03014016/DBE
Horizontal Wall | Knockonwood | KNOW.03018006 | 30 | 180 | 06 | 11 | 1247 | 1247 | 1247 | 0.02969 | 454 | 0.01081 | 1433 | 0.034119 | 1.457 | A13 | KNOW0.03018006
Horizontal Wall | Knockonwood | KNOW.03018006/DBE | 30 | 180 | 06 | 11 | 1787 | 1787 | 1787 | 0.042548 | 894 | 0.021286 | 1966 | 0.04681 | 1 | A13 | KNOW0.03018006/DBE
Horizontal Wall | Knockonwood | KNOW.03018010 | 30 | 180 | 10 | 13 | 1357 | 1357 | 1357 | 0.03231 | 495 | 0.011786 | 1559 | 0.037119 | 1.453 | A13 | KNOW0.03018010
Horizontal Wall | Knockonwood | KNOW.03018011 | 30 | 180 | 11 | 13 | 1546 | 1546 | 1546 | 0.03681 | 541 | 0.012881 | 1786 | 0.042524 | 1.516 | A13 | KNOW0.03018011
Horizontal Wall | Knockonwood | KNOW.03018011/DBE | 30 | 180 | 11 | 13 | 2746 | 2746 | 2746 | 0.065381 | 1373 | 0.03269 | 3021 | 0.071929 | 1 | A13 | KNOW0.03018011/DBE
Horizontal Wall | Knockonwood | KNOW.03018015 | 30 | 180 | 15 | 18 | 2068 | 2068 | 2068 | 0.049238 | 761 | 0.018119 | 2372 | 0.056476 | 1.442 | A13 | KNOW0.03018015
Horizontal Wall | Knockonwood | KNOW.03018016 | 30 | 180 | 16 | 18 | 2255 | 2255 | 2255 | 0.05369 | 801 | 0.019071 | 2600 | 0.061905 | 1.495 | A13 | KNOW0.03018016
Horizontal Wall | Knockonwood | KNOW.03018016/DBE | 30 | 180 | 16 | 18 | 4175 | 4175 | 4175 | 0.099405 | 2088 | 0.049714 | 4593 | 0.10936 | 1 | A13 | KNOW0.03018016/DBE
Horizontal Wall | Knockonwood | KNOW.03022006 | 30 | 220 | 06 | 11 | 1525 | 1525 | 1525 | 0.03631 | 555 | 0.013214 | 1752 | 0.041714 | 1.457 | A13 | KNOW0.03022006
Horizontal Wall | Knockonwood | KNOW.03022006/DBE | 30 | 220 | 06 | 11 | 2065 | 2065 | 2065 | 0.049167 | 1033 | 0.024595 | 2272 | 0.054095 | 1 | A13 | KNOW0.03022006/DBE
Horizontal Wall | Knockonwood | KNOW.03022010 | 30 | 220 | 10 | 13 | 1659 | 1659 | 1659 | 0.0395 | 606 | 0.014429 | 1906 | 0.045381 | 1.453 | A13 | KNOW0.03022010
Horizontal Wall | Knockonwood | KNOW.03022011 | 30 | 220 | 11 | 13 | 1890 | 1890 | 1890 | 0.045 | 662 | 0.015762 | 2183 | 0.051976 | 1.516 | A13 | KNOW0.03022011
Horizontal Wall | Knockonwood | KNOW.03022011/DBE | 30 | 220 | 11 | 13 | 3090 | 3090 | 3090 | 0.073571 | 1545 | 0.036786 | 3399 | 0.080929 | 1 | A13 | KNOW0.03022011/DBE
Horizontal Wall | Knockonwood | KNOW.03022015 | 30 | 220 | 15 | 18 | 2528 | 2528 | 2528 | 0.06019 | 930 | 0.022143 | 2900 | 0.069048 | 1.442 | A13 | KNOW0.03022015
Horizontal Wall | Knockonwood | KNOW.03022016 | 30 | 220 | 16 | 18 | 2757 | 2757 | 2757 | 0.065643 | 979 | 0.02331 | 3179 | 0.07569 | 1.495 | A13 | KNOW0.03022016
Horizontal Wall | Knockonwood | KNOW.03022016/DBE | 30 | 220 | 16 | 18 | 4677 | 4677 | 4677 | 0.11136 | 2339 | 0.05569 | 5145 | 0.1225 | 1 | A13 | KNOW0.03022016/DBE
Horizontal Wall | Knockonwood | KNOW.05506006 | 55 | 60 | 06 | 11 | 554 | 554 | 554 | 0.01319 | 204 | 0.0048571 | 635 | 0.015119 | 1.44 | A13 | KNOW0.05506006
Horizontal Wall | Knockonwood | KNOW.05506006/DBE | 55 | 60 | 06 | 11 | 689 | 689 | 689 | 0.016405 | 345 | 0.0082143 | 758 | 0.018048 | 1 | A13 | KNOW0.05506006/DBE
Horizontal Wall | Knockonwood | KNOW.05506010 | 55 | 60 | 10 | 13 | 660 | 660 | 660 | 0.015714 | 249 | 0.0059286 | 755 | 0.017976 | 1.407 | A13 | KNOW0.05506010
Horizontal Wall | Knockonwood | KNOW.05506011 | 55 | 60 | 11 | 13 | 718 | 718 | 718 | 0.017095 | 256 | 0.0060952 | 827 | 0.01969 | 1.487 | A13 | KNOW0.05506011
Horizontal Wall | Knockonwood | KNOW.05506011/DBE | 55 | 60 | 11 | 13 | 1018 | 1018 | 1018 | 0.024238 | 509 | 0.012119 | 1120 | 0.026667 | 1 | A13 | KNOW0.05506011/DBE
Horizontal Wall | Knockonwood | KNOW.05506015 | 55 | 60 | 15 | 18 | 1001 | 1001 | 1001 | 0.023833 | 382 | 0.0090952 | 1143 | 0.027214 | 1.389 | A13 | KNOW0.05506015
Horizontal Wall | Knockonwood | KNOW.05506016 | 55 | 60 | 16 | 18 | 1063 | 1063 | 1063 | 0.02531 | 381 | 0.0090714 | 1224 | 0.029143 | 1.48 | A13 | KNOW0.05506016
Horizontal Wall | Knockonwood | KNOW.05506016/DBE | 55 | 60 | 16 | 18 | 1543 | 1543 | 1543 | 0.036738 | 772 | 0.018381 | 1697 | 0.040405 | 1 | A13 | KNOW0.05506016/DBE
Horizontal Wall | Knockonwood | KNOW.05508006 | 55 | 80 | 06 | 11 | 739 | 739 | 739 | 0.017595 | 273 | 0.0065 | 848 | 0.02019 | 1.44 | A13 | KNOW0.05508006
Horizontal Wall | Knockonwood | KNOW.05508006/DBE | 55 | 80 | 06 | 11 | 874 | 874 | 874 | 0.02081 | 437 | 0.010405 | 961 | 0.022881 | 1 | A13 | KNOW0.05508006/DBE
Horizontal Wall | Knockonwood | KNOW.05508010 | 55 | 80 | 10 | 13 | 880 | 880 | 880 | 0.020952 | 332 | 0.0079048 | 1007 | 0.023976 | 1.407 | A13 | KNOW0.05508010
Horizontal Wall | Knockonwood | KNOW.05508011 | 55 | 80 | 11 | 13 | 958 | 958 | 958 | 0.02281 | 342 | 0.0081429 | 1104 | 0.026286 | 1.487 | A13 | KNOW0.05508011
Horizontal Wall | Knockonwood | KNOW.05508011/DBE | 55 | 80 | 11 | 13 | 1258 | 1258 | 1258 | 0.029952 | 629 | 0.014976 | 1384 | 0.032952 | 1 | A13 | KNOW0.05508011/DBE
Horizontal Wall | Knockonwood | KNOW.05508015 | 55 | 80 | 15 | 18 | 1335 | 1335 | 1335 | 0.031786 | 510 | 0.012143 | 1525 | 0.03631 | 1.389 | A13 | KNOW0.05508015
Horizontal Wall | Knockonwood | KNOW.05508016 | 55 | 80 | 16 | 18 | 1418 | 1418 | 1418 | 0.033762 | 508 | 0.012095 | 1632 | 0.038857 | 1.48 | A13 | KNOW0.05508016
Horizontal Wall | Knockonwood | KNOW.05508016/DBE | 55 | 80 | 16 | 18 | 1898 | 1898 | 1898 | 0.04519 | 949 | 0.022595 | 2088 | 0.049714 | 1 | A13 | KNOW0.05508016/DBE
Horizontal Wall | Knockonwood | KNOW.05510006 | 55 | 100 | 06 | 11 | 924 | 924 | 924 | 0.022 | 341 | 0.008119 | 1060 | 0.025238 | 1.44 | A13 | KNOW0.05510006
Horizontal Wall | Knockonwood | KNOW.05510006/DBE | 55 | 100 | 06 | 11 | 1194 | 1194 | 1194 | 0.028429 | 597 | 0.014214 | 1313 | 0.031262 | 1 | A13 | KNOW0.05510006/DBE
Horizontal Wall | Knockonwood | KNOW.05510010 | 55 | 100 | 10 | 13 | 1100 | 1100 | 1100 | 0.02619 | 415 | 0.009881 | 1258 | 0.029952 | 1.407 | A13 | KNOW0.05510010
Horizontal Wall | Knockonwood | KNOW.05510011 | 55 | 100 | 11 | 13 | 1197 | 1197 | 1197 | 0.0285 | 427 | 0.010167 | 1379 | 0.032833 | 1.487 | A13 | KNOW0.05510011
Horizontal Wall | Knockonwood | KNOW.05510011/DBE | 55 | 100 | 11 | 13 | 1797 | 1797 | 1797 | 0.042786 | 899 | 0.021405 | 1977 | 0.047071 | 1 | A13 | KNOW0.05510011/DBE
Horizontal Wall | Knockonwood | KNOW.05510015 | 55 | 100 | 15 | 18 | 1669 | 1669 | 1669 | 0.039738 | 638 | 0.01519 | 1906 | 0.045381 | 1.389 | A13 | KNOW0.05510015
Horizontal Wall | Knockonwood | KNOW.05510016 | 55 | 100 | 16 | 18 | 1772 | 1772 | 1772 | 0.04219 | 634 | 0.015095 | 2040 | 0.048571 | 1.48 | A13 | KNOW0.05510016
Horizontal Wall | Knockonwood | KNOW.05510016/DBE | 55 | 100 | 16 | 18 | 2732 | 2732 | 2732 | 0.065048 | 1366 | 0.032524 | 3005 | 0.071548 | 1 | A13 | KNOW0.05510016/DBE
Horizontal Wall | Knockonwood | KNOW.05512006 | 55 | 120 | 06 | 11 | 1109 | 1109 | 1109 | 0.026405 | 409 | 0.0097381 | 1272 | 0.030286 | 1.44 | A13 | KNOW0.05512006
Horizontal Wall | Knockonwood | KNOW.05512006/DBE | 55 | 120 | 06 | 11 | 1379 | 1379 | 1379 | 0.032833 | 690 | 0.016429 | 1517 | 0.036119 | 1 | A13 | KNOW0.05512006/DBE
Horizontal Wall | Knockonwood | KNOW.05512010 | 55 | 120 | 10 | 13 | 1320 | 1320 | 1320 | 0.031429 | 498 | 0.011857 | 1510 | 0.035952 | 1.407 | A13 | KNOW0.05512010
Horizontal Wall | Knockonwood | KNOW.05512011 | 55 | 120 | 11 | 13 | 1436 | 1436 | 1436 | 0.03419 | 513 | 0.012214 | 1654 | 0.039381 | 1.487 | A13 | KNOW0.05512011
Horizontal Wall | Knockonwood | KNOW.05512011/DBE | 55 | 120 | 11 | 13 | 2036 | 2036 | 2036 | 0.048476 | 1018 | 0.024238 | 2240 | 0.053333 | 1 | A13 | KNOW0.05512011/DBE
Horizontal Wall | Knockonwood | KNOW.05512015 | 55 | 120 | 15 | 18 | 2003 | 2003 | 2003 | 0.04769 | 765 | 0.018214 | 2287 | 0.054452 | 1.389 | A13 | KNOW0.05512015
Horizontal Wall | Knockonwood | KNOW.05512016 | 55 | 120 | 16 | 18 | 2126 | 2126 | 2126 | 0.050619 | 761 | 0.018119 | 2447 | 0.058262 | 1.48 | A13 | KNOW0.05512016
Horizontal Wall | Knockonwood | KNOW.05512016/DBE | 55 | 120 | 16 | 18 | 3086 | 3086 | 3086 | 0.073476 | 1543 | 0.036738 | 3395 | 0.080833 | 1 | A13 | KNOW0.05512016/DBE
Horizontal Wall | Knockonwood | KNOW.05514006 | 55 | 140 | 06 | 11 | 1294 | 1294 | 1294 | 0.03081 | 477 | 0.011357 | 1484 | 0.035333 | 1.44 | A13 | KNOW0.05514006
Horizontal Wall | Knockonwood | KNOW.05514006/DBE | 55 | 140 | 06 | 11 | 1564 | 1564 | 1564 | 0.037238 | 782 | 0.018619 | 1720 | 0.040952 | 1 | A13 | KNOW0.05514006/DBE
Horizontal Wall | Knockonwood | KNOW.05514010 | 55 | 140 | 10 | 13 | 1540 | 1540 | 1540 | 0.036667 | 581 | 0.013833 | 1762 | 0.041952 | 1.407 | A13 | KNOW0.05514010
Horizontal Wall | Knockonwood | KNOW.05514011 | 55 | 140 | 11 | 13 | 1676 | 1676 | 1676 | 0.039905 | 598 | 0.014238 | 1931 | 0.045976 | 1.487 | A13 | KNOW0.05514011
Horizontal Wall | Knockonwood | KNOW.05514011/DBE | 55 | 140 | 11 | 13 | 2276 | 2276 | 2276 | 0.05419 | 1138 | 0.027095 | 2504 | 0.059619 | 1 | A13 | KNOW0.05514011/DBE
Horizontal Wall | Knockonwood | KNOW.05514015 | 55 | 140 | 15 | 18 | 2337 | 2337 | 2337 | 0.055643 | 893 | 0.021262 | 2669 | 0.063548 | 1.389 | A13 | KNOW0.05514015
Horizontal Wall | Knockonwood | KNOW.05514016 | 55 | 140 | 16 | 18 | 2481 | 2481 | 2481 | 0.059071 | 888 | 0.021143 | 2856 | 0.068 | 1.48 | A13 | KNOW0.05514016
Horizontal Wall | Knockonwood | KNOW.05514016/DBE | 55 | 140 | 16 | 18 | 3441 | 3441 | 3441 | 0.081929 | 1721 | 0.040976 | 3785 | 0.090119 | 1 | A13 | KNOW0.05514016/DBE
Horizontal Wall | Knockonwood | KNOW.05518006 | 55 | 180 | 06 | 11 | 1663 | 1663 | 1663 | 0.039595 | 614 | 0.014619 | 1907 | 0.045405 | 1.44 | A13 | KNOW0.05518006
Horizontal Wall | Knockonwood | KNOW.05518006/DBE | 55 | 180 | 06 | 11 | 2203 | 2203 | 2203 | 0.052452 | 1102 | 0.026238 | 2423 | 0.05769 | 1 | A13 | KNOW0.05518006/DBE
Horizontal Wall | Knockonwood | KNOW.05518010 | 55 | 180 | 10 | 13 | 1980 | 1980 | 1980 | 0.047143 | 746 | 0.017762 | 2265 | 0.053929 | 1.407 | A13 | KNOW0.05518010
Horizontal Wall | Knockonwood | KNOW.05518011 | 55 | 180 | 11 | 13 | 2155 | 2155 | 2155 | 0.05131 | 769 | 0.01831 | 2483 | 0.059119 | 1.487 | A13 | KNOW0.05518011
Horizontal Wall | Knockonwood | KNOW.05518011/DBE | 55 | 180 | 11 | 13 | 3355 | 3355 | 3355 | 0.079881 | 1678 | 0.039952 | 3691 | 0.087881 | 1 | A13 | KNOW0.05518011/DBE
Horizontal Wall | Knockonwood | KNOW.05518015 | 55 | 180 | 15 | 18 | 3004 | 3004 | 3004 | 0.071524 | 1148 | 0.027333 | 3431 | 0.08169 | 1.389 | A13 | KNOW0.05518015
Horizontal Wall | Knockonwood | KNOW.05518016 | 55 | 180 | 16 | 18 | 3190 | 3190 | 3190 | 0.075952 | 1142 | 0.02719 | 3672 | 0.087429 | 1.48 | A13 | KNOW0.05518016
Horizontal Wall | Knockonwood | KNOW.05518016/DBE | 55 | 180 | 16 | 18 | 5110 | 5110 | 5110 | 0.12167 | 2555 | 0.060833 | 5621 | 0.13383 | 1 | A13 | KNOW0.05518016/DBE
Horizontal Wall | Knockonwood | KNOW.05522006 | 55 | 220 | 06 | 11 | 2033 | 2033 | 2033 | 0.048405 | 750 | 0.017857 | 2332 | 0.055524 | 1.44 | A13 | KNOW0.05522006
Horizontal Wall | Knockonwood | KNOW.05522006/DBE | 55 | 220 | 06 | 11 | 2573 | 2573 | 2573 | 0.061262 | 1287 | 0.030643 | 2830 | 0.067381 | 1 | A13 | KNOW0.05522006/DBE
Horizontal Wall | Knockonwood | KNOW.05522010 | 55 | 220 | 10 | 13 | 2420 | 2420 | 2420 | 0.057619 | 912 | 0.021714 | 2768 | 0.065905 | 1.407 | A13 | KNOW0.05522010
Horizontal Wall | Knockonwood | KNOW.05522011 | 55 | 220 | 11 | 13 | 2633 | 2633 | 2633 | 0.06269 | 940 | 0.022381 | 3033 | 0.072214 | 1.487 | A13 | KNOW0.05522011
Horizontal Wall | Knockonwood | KNOW.05522011/DBE | 55 | 220 | 11 | 13 | 3833 | 3833 | 3833 | 0.091262 | 1917 | 0.045643 | 4216 | 0.10038 | 1 | A13 | KNOW0.05522011/DBE
Horizontal Wall | Knockonwood | KNOW.05522015 | 55 | 220 | 15 | 18 | 3672 | 3672 | 3672 | 0.087429 | 1403 | 0.033405 | 4193 | 0.099833 | 1.389 | A13 | KNOW0.05522015
Horizontal Wall | Knockonwood | KNOW.05522016 | 55 | 220 | 16 | 18 | 3898 | 3898 | 3898 | 0.09281 | 1395 | 0.033214 | 4487 | 0.10683 | 1.48 | A13 | KNOW0.05522016
Horizontal Wall | Knockonwood | KNOW.05522016/DBE | 55 | 220 | 16 | 18 | 5818 | 5818 | 5818 | 0.13852 | 2909 | 0.069262 | 6400 | 0.15238 | 1 | A13 | KNOW0.05522016/DBE
Horizontal Wall | Knockonwood | KNOW.08006006 | 80 | 60 | 06 | 11 | 645 | 645 | 645 | 0.015357 | 241 | 0.0057381 | 739 | 0.017595 | 1.422 | A13 | KNOW0.08006006
Horizontal Wall | Knockonwood | KNOW.08006006/DBE | 80 | 60 | 06 | 11 | 780 | 780 | 780 | 0.018571 | 390 | 0.0092857 | 858 | 0.020429 | 1 | A13 | KNOW0.08006006/DBE
Horizontal Wall | Knockonwood | KNOW.08006010 | 80 | 60 | 10 | 13 | 778 | 778 | 778 | 0.018524 | 303 | 0.0072143 | 886 | 0.021095 | 1.361 | A13 | KNOW0.08006010
Horizontal Wall | Knockonwood | KNOW.08006011 | 80 | 60 | 11 | 13 | 845 | 845 | 845 | 0.020119 | 308 | 0.0073333 | 971 | 0.023119 | 1.458 | A13 | KNOW0.08006011
Horizontal Wall | Knockonwood | KNOW.08006011/DBE | 80 | 60 | 11 | 13 | 1145 | 1145 | 1145 | 0.027262 | 573 | 0.013643 | 1260 | 0.03 | 1 | A13 | KNOW0.08006011/DBE
Horizontal Wall | Knockonwood | KNOW.08006015 | 80 | 60 | 15 | 18 | 1165 | 1165 | 1165 | 0.027738 | 461 | 0.010976 | 1323 | 0.0315 | 1.337 | A13 | KNOW0.08006015
Horizontal Wall | Knockonwood | KNOW.08006016 | 80 | 60 | 16 | 18 | 1288 | 1288 | 1288 | 0.030667 | 466 | 0.011095 | 1481 | 0.035262 | 1.465 | A13 | KNOW0.08006016
Horizontal Wall | Knockonwood | KNOW.08006016/DBE | 80 | 60 | 16 | 18 | 1768 | 1768 | 1768 | 0.042095 | 884 | 0.021048 | 1945 | 0.04631 | 1 | A13 | KNOW0.08006016/DBE
Horizontal Wall | Knockonwood | KNOW.08008006 | 80 | 80 | 06 | 11 | 860 | 860 | 860 | 0.020476 | 321 | 0.0076429 | 985 | 0.023452 | 1.422 | A13 | KNOW0.08008006
Horizontal Wall | Knockonwood | KNOW.08008006/DBE | 80 | 80 | 06 | 11 | 995 | 995 | 995 | 0.02369 | 498 | 0.011857 | 1095 | 0.026071 | 1 | A13 | KNOW0.08008006/DBE
Horizontal Wall | Knockonwood | KNOW.08008010 | 80 | 80 | 10 | 13 | 1037 | 1037 | 1037 | 0.02469 | 403 | 0.0095952 | 1181 | 0.028119 | 1.361 | A13 | KNOW0.08008010
Horizontal Wall | Knockonwood | KNOW.08008011 | 80 | 80 | 11 | 13 | 1127 | 1127 | 1127 | 0.026833 | 410 | 0.0097619 | 1295 | 0.030833 | 1.458 | A13 | KNOW0.08008011
Horizontal Wall | Knockonwood | KNOW.08008011/DBE | 80 | 80 | 11 | 13 | 1427 | 1427 | 1427 | 0.033976 | 714 | 0.017 | 1570 | 0.037381 | 1 | A13 | KNOW0.08008011/DBE
Horizontal Wall | Knockonwood | KNOW.08008015 | 80 | 80 | 15 | 18 | 1553 | 1553 | 1553 | 0.036976 | 615 | 0.014643 | 1764 | 0.042 | 1.337 | A13 | KNOW0.08008015
Horizontal Wall | Knockonwood | KNOW.08008016 | 80 | 80 | 16 | 18 | 1718 | 1718 | 1718 | 0.040905 | 622 | 0.01481 | 1976 | 0.047048 | 1.465 | A13 | KNOW0.08008016
Horizontal Wall | Knockonwood | KNOW.08008016/DBE | 80 | 80 | 16 | 18 | 2198 | 2198 | 2198 | 0.052333 | 1099 | 0.026167 | 2418 | 0.057571 | 1 | A13 | KNOW0.08008016/DBE
Horizontal Wall | Knockonwood | KNOW.08010006 | 80 | 100 | 06 | 11 | 1075 | 1075 | 1075 | 0.025595 | 401 | 0.0095476 | 1231 | 0.02931 | 1.422 | A13 | KNOW0.08010006
Horizontal Wall | Knockonwood | KNOW.08010006/DBE | 80 | 100 | 06 | 11 | 1345 | 1345 | 1345 | 0.032024 | 673 | 0.016024 | 1480 | 0.035238 | 1 | A13 | KNOW0.08010006/DBE
Horizontal Wall | Knockonwood | KNOW.08010010 | 80 | 100 | 10 | 13 | 1296 | 1296 | 1296 | 0.030857 | 504 | 0.012 | 1476 | 0.035143 | 1.361 | A13 | KNOW0.08010010
Horizontal Wall | Knockonwood | KNOW.08010011 | 80 | 100 | 11 | 13 | 1409 | 1409 | 1409 | 0.033548 | 513 | 0.012214 | 1619 | 0.038548 | 1.458 | A13 | KNOW0.08010011
Horizontal Wall | Knockonwood | KNOW.08010011/DBE | 80 | 100 | 11 | 13 | 2009 | 2009 | 2009 | 0.047833 | 1005 | 0.023929 | 2210 | 0.052619 | 1 | A13 | KNOW0.08010011/DBE
Horizontal Wall | Knockonwood | KNOW.08010015 | 80 | 100 | 15 | 18 | 1941 | 1941 | 1941 | 0.046214 | 769 | 0.01831 | 2205 | 0.0525 | 1.337 | A13 | KNOW0.08010015
Horizontal Wall | Knockonwood | KNOW.08010016 | 80 | 100 | 16 | 18 | 2147 | 2147 | 2147 | 0.051119 | 777 | 0.0185 | 2469 | 0.058786 | 1.465 | A13 | KNOW0.08010016
Horizontal Wall | Knockonwood | KNOW.08010016/DBE | 80 | 100 | 16 | 18 | 3107 | 3107 | 3107 | 0.073976 | 1554 | 0.037 | 3418 | 0.081381 | 1 | A13 | KNOW0.08010016/DBE
Horizontal Wall | Knockonwood | KNOW.08012006 | 80 | 120 | 06 | 11 | 1290 | 1290 | 1290 | 0.030714 | 481 | 0.011452 | 1477 | 0.035167 | 1.422 | A13 | KNOW0.08012006
Horizontal Wall | Knockonwood | KNOW.08012006/DBE | 80 | 120 | 06 | 11 | 1560 | 1560 | 1560 | 0.037143 | 780 | 0.018571 | 1716 | 0.040857 | 1 | A13 | KNOW0.08012006/DBE
Horizontal Wall | Knockonwood | KNOW.08012010 | 80 | 120 | 10 | 13 | 1555 | 1555 | 1555 | 0.037024 | 605 | 0.014405 | 1771 | 0.042167 | 1.361 | A13 | KNOW0.08012010
Horizontal Wall | Knockonwood | KNOW.08012011 | 80 | 120 | 11 | 13 | 1691 | 1691 | 1691 | 0.040262 | 616 | 0.014667 | 1943 | 0.046262 | 1.458 | A13 | KNOW0.08012011
Horizontal Wall | Knockonwood | KNOW.08012011/DBE | 80 | 120 | 11 | 13 | 2291 | 2291 | 2291 | 0.054548 | 1146 | 0.027286 | 2520 | 0.06 | 1 | A13 | KNOW0.08012011/DBE
Horizontal Wall | Knockonwood | KNOW.08012015 | 80 | 120 | 15 | 18 | 2329 | 2329 | 2329 | 0.055452 | 922 | 0.021952 | 2646 | 0.063 | 1.337 | A13 | KNOW0.08012015
Horizontal Wall | Knockonwood | KNOW.08012016 | 80 | 120 | 16 | 18 | 2576 | 2576 | 2576 | 0.061333 | 933 | 0.022214 | 2962 | 0.070524 | 1.465 | A13 | KNOW0.08012016
Horizontal Wall | Knockonwood | KNOW.08012016/DBE | 80 | 120 | 16 | 18 | 3536 | 3536 | 3536 | 0.08419 | 1768 | 0.042095 | 3890 | 0.092619 | 1 | A13 | KNOW0.08012016/DBE
Freestanding | Knockonwood DBE | KNUF.02111015/DBE | 21 | 110 | 15 | 21 | 1678 | 1678 | 1678 | 0.039952 | 839 | 0.019976 | 1846 | 0.043952 | 1 | A13 | KNUF0.02111015/DBE
Freestanding | Knockonwood DBE | KNUF.02113015/DBE | 21 | 130 | 15 | 21 | 2164 | 2164 | 2164 | 0.051524 | 1082 | 0.025762 | 2380 | 0.056667 | 1 | A13 | KNUF0.02113015/DBE
Freestanding | Knockonwood DBE | KNUF.02117015/DBE | 21 | 170 | 15 | 21 | 2885 | 2885 | 2885 | 0.06869 | 1443 | 0.034357 | 3174 | 0.075571 | 1 | A13 | KNUF0.02117015/DBE
Freestanding | Knockonwood DBE | KNUF.02121015/DBE | 21 | 210 | 15 | 21 | 3606 | 3606 | 3606 | 0.085857 | 1803 | 0.042929 | 3967 | 0.094452 | 1 | A13 | KNUF0.02121015/DBE
Horizontal Wall | Linea Plus | LINW.02005010 | 20 | 50 | 10 | 12 | 284 | 284 | 284 | 0.0067619 | 105 | 0.0025 | 326 | 0.0077619 | 1.436 | A01 | LINW0.02005010
Horizontal Wall | Linea Plus | LINW.02005015 | 20 | 50 | 15 | 17 | 519 | 519 | 519 | 0.012357 | 194 | 0.004619 | 594 | 0.014143 | 1.424 | A01 | LINW0.02005015
Horizontal Wall | Linea Plus | LINW.02005020 | 20 | 50 | 20 | 22 | 697 | 697 | 697 | 0.016595 | 259 | 0.0061667 | 798 | 0.019 | 1.425 | A01 | LINW0.02005020
Horizontal Wall | Linea Plus | LINW.02006010 | 20 | 60 | 10 | 12 | 341 | 341 | 341 | 0.008119 | 126 | 0.003 | 391 | 0.0093095 | 1.436 | A01 | LINW0.02006010
Horizontal Wall | Linea Plus | LINW.02006015 | 20 | 60 | 15 | 17 | 623 | 623 | 623 | 0.014833 | 232 | 0.0055238 | 713 | 0.016976 | 1.424 | A01 | LINW0.02006015
Horizontal Wall | Linea Plus | LINW.02006020 | 20 | 60 | 20 | 22 | 836 | 836 | 836 | 0.019905 | 311 | 0.0074048 | 957 | 0.022786 | 1.425 | A01 | LINW0.02006020
Horizontal Wall | Linea Plus | LINW.02007010 | 20 | 70 | 10 | 12 | 398 | 398 | 398 | 0.0094762 | 147 | 0.0035 | 457 | 0.010881 | 1.436 | A01 | LINW0.02007010
Horizontal Wall | Linea Plus | LINW.02007015 | 20 | 70 | 15 | 17 | 727 | 727 | 727 | 0.01731 | 271 | 0.0064524 | 832 | 0.01981 | 1.424 | A01 | LINW0.02007015
Horizontal Wall | Linea Plus | LINW.02007020 | 20 | 70 | 20 | 22 | 976 | 976 | 976 | 0.023238 | 363 | 0.0086429 | 1118 | 0.026619 | 1.425 | A01 | LINW0.02007020
Horizontal Wall | Linea Plus | LINW.02008010 | 20 | 80 | 10 | 12 | 454 | 454 | 454 | 0.01081 | 168 | 0.004 | 521 | 0.012405 | 1.436 | A01 | LINW0.02008010
Horizontal Wall | Linea Plus | LINW.02008015 | 20 | 80 | 15 | 17 | 830 | 830 | 830 | 0.019762 | 310 | 0.007381 | 950 | 0.022619 | 1.424 | A01 | LINW0.02008015
Horizontal Wall | Linea Plus | LINW.02008020 | 20 | 80 | 20 | 22 | 1115 | 1115 | 1115 | 0.026548 | 415 | 0.009881 | 1277 | 0.030405 | 1.425 | A01 | LINW0.02008020
Horizontal Wall | Linea Plus | LINW.02009010 | 20 | 90 | 10 | 12 | 511 | 511 | 511 | 0.012167 | 189 | 0.0045 | 586 | 0.013952 | 1.436 | A01 | LINW0.02009010
Horizontal Wall | Linea Plus | LINW.02009015 | 20 | 90 | 15 | 17 | 934 | 934 | 934 | 0.022238 | 348 | 0.0082857 | 1069 | 0.025452 | 1.424 | A01 | LINW0.02009015
Horizontal Wall | Linea Plus | LINW.02009020 | 20 | 90 | 20 | 22 | 1255 | 1255 | 1255 | 0.029881 | 467 | 0.011119 | 1437 | 0.034214 | 1.425 | A01 | LINW0.02009020
Horizontal Wall | Linea Plus | LINW.02010010 | 20 | 100 | 10 | 12 | 568 | 568 | 568 | 0.013524 | 210 | 0.005 | 651 | 0.0155 | 1.436 | A01 | LINW0.02010010
Horizontal Wall | Linea Plus | LINW.02010015 | 20 | 100 | 15 | 17 | 1038 | 1038 | 1038 | 0.024714 | 387 | 0.0092143 | 1189 | 0.02831 | 1.424 | A01 | LINW0.02010015
Horizontal Wall | Linea Plus | LINW.02010020 | 20 | 100 | 20 | 22 | 1394 | 1394 | 1394 | 0.03319 | 519 | 0.012357 | 1596 | 0.038 | 1.425 | A01 | LINW0.02010020
Horizontal Wall | Linea Plus | LINW.02011010 | 20 | 110 | 10 | 12 | 625 | 625 | 625 | 0.014881 | 231 | 0.0055 | 717 | 0.017071 | 1.436 | A01 | LINW0.02011010
Horizontal Wall | Linea Plus | LINW.02011015 | 20 | 110 | 15 | 17 | 1142 | 1142 | 1142 | 0.02719 | 426 | 0.010143 | 1308 | 0.031143 | 1.424 | A01 | LINW0.02011015
Horizontal Wall | Linea Plus | LINW.02011020 | 20 | 110 | 20 | 22 | 1533 | 1533 | 1533 | 0.0365 | 570 | 0.013571 | 1755 | 0.041786 | 1.425 | A01 | LINW0.02011020
Horizontal Wall | Linea Plus | LINW.02012010 | 20 | 120 | 10 | 12 | 682 | 682 | 682 | 0.016238 | 252 | 0.006 | 782 | 0.018619 | 1.436 | A01 | LINW0.02012010
Horizontal Wall | Linea Plus | LINW.02012015 | 20 | 120 | 15 | 17 | 1246 | 1246 | 1246 | 0.029667 | 465 | 0.011071 | 1427 | 0.033976 | 1.424 | A01 | LINW0.02012015
Horizontal Wall | Linea Plus | LINW.02012020 | 20 | 120 | 20 | 22 | 1673 | 1673 | 1673 | 0.039833 | 622 | 0.01481 | 1916 | 0.045619 | 1.425 | A01 | LINW0.02012020
Horizontal Wall | Linea Plus | LINW.02014010 | 20 | 140 | 10 | 12 | 795 | 795 | 795 | 0.018929 | 294 | 0.007 | 912 | 0.021714 | 1.436 | A01 | LINW0.02014010
Horizontal Wall | Linea Plus | LINW.02014015 | 20 | 140 | 15 | 17 | 1453 | 1453 | 1453 | 0.034595 | 542 | 0.012905 | 1664 | 0.039619 | 1.424 | A01 | LINW0.02014015
Horizontal Wall | Linea Plus | LINW.02014020 | 20 | 140 | 20 | 22 | 1952 | 1952 | 1952 | 0.046476 | 726 | 0.017286 | 2235 | 0.053214 | 1.425 | A01 | LINW0.02014020
Horizontal Wall | Linea Plus | LINW.02016010 | 20 | 160 | 10 | 12 | 909 | 909 | 909 | 0.021643 | 336 | 0.008 | 1043 | 0.024833 | 1.436 | A01 | LINW0.02016010
Horizontal Wall | Linea Plus | LINW.02016015 | 20 | 160 | 15 | 17 | 1661 | 1661 | 1661 | 0.039548 | 620 | 0.014762 | 1902 | 0.045286 | 1.424 | A01 | LINW0.02016015
Horizontal Wall | Linea Plus | LINW.02016020 | 20 | 160 | 20 | 22 | 2230 | 2230 | 2230 | 0.053095 | 830 | 0.019762 | 2553 | 0.060786 | 1.425 | A01 | LINW0.02016020
Horizontal Wall | Linea Plus | LINW.02018010 | 20 | 180 | 10 | 12 | 1022 | 1022 | 1022 | 0.024333 | 378 | 0.009 | 1172 | 0.027905 | 1.436 | A01 | LINW0.02018010
Horizontal Wall | Linea Plus | LINW.02018015 | 20 | 180 | 15 | 17 | 1868 | 1868 | 1868 | 0.044476 | 697 | 0.016595 | 2139 | 0.050929 | 1.424 | A01 | LINW0.02018015
Horizontal Wall | Linea Plus | LINW.02018020 | 20 | 180 | 20 | 22 | 2509 | 2509 | 2509 | 0.059738 | 933 | 0.022214 | 2873 | 0.068405 | 1.425 | A01 | LINW0.02018020
Horizontal Wall | Linea Plus | LINW.02020010 | 20 | 200 | 10 | 12 | 1136 | 1136 | 1136 | 0.027048 | 420 | 0.01 | 1303 | 0.031024 | 1.436 | A01 | LINW0.02020010
Horizontal Wall | Linea Plus | LINW.02020015 | 20 | 200 | 15 | 17 | 2076 | 2076 | 2076 | 0.049429 | 774 | 0.018429 | 2377 | 0.056595 | 1.424 | A01 | LINW0.02020015
Horizontal Wall | Linea Plus | LINW.02020020 | 20 | 200 | 20 | 22 | 2788 | 2788 | 2788 | 0.066381 | 1037 | 0.02469 | 3192 | 0.076 | 1.425 | A01 | LINW0.02020020
Horizontal Wall | Linea Plus | LINW.02022010 | 20 | 220 | 10 | 12 | 1250 | 1250 | 1250 | 0.029762 | 463 | 0.011024 | 1434 | 0.034143 | 1.436 | A01 | LINW0.02022010
Horizontal Wall | Linea Plus | LINW.02022015 | 20 | 220 | 15 | 17 | 2284 | 2284 | 2284 | 0.054381 | 852 | 0.020286 | 2615 | 0.062262 | 1.424 | A01 | LINW0.02022015
Horizontal Wall | Linea Plus | LINW.02022020 | 20 | 220 | 20 | 22 | 3067 | 3067 | 3067 | 0.073024 | 1141 | 0.027167 | 3512 | 0.083619 | 1.425 | A01 | LINW0.02022020
Horizontal Wall | Linea Plus | LINW.02024010 | 20 | 240 | 10 | 12 | 1363 | 1363 | 1363 | 0.032452 | 504 | 0.012 | 1563 | 0.037214 | 1.436 | A01 | LINW0.02024010
Horizontal Wall | Linea Plus | LINW.02024015 | 20 | 240 | 15 | 17 | 2491 | 2491 | 2491 | 0.05931 | 929 | 0.022119 | 2852 | 0.067905 | 1.424 | A01 | LINW0.02024015
Horizontal Wall | Linea Plus | LINW.02024020 | 20 | 240 | 20 | 22 | 3346 | 3346 | 3346 | 0.079667 | 1245 | 0.029643 | 3831 | 0.091214 | 1.425 | A01 | LINW0.02024020
Horizontal Wall | Linea Plus | LINW.02026010 | 20 | 260 | 10 | 12 | 1477 | 1477 | 1477 | 0.035167 | 546 | 0.013 | 1694 | 0.040333 | 1.436 | A01 | LINW0.02026010
Horizontal Wall | Linea Plus | LINW.02026015 | 20 | 260 | 15 | 17 | 2699 | 2699 | 2699 | 0.064262 | 1007 | 0.023976 | 3090 | 0.073571 | 1.424 | A01 | LINW0.02026015
Horizontal Wall | Linea Plus | LINW.02026020 | 20 | 260 | 20 | 22 | 3624 | 3624 | 3624 | 0.086286 | 1348 | 0.032095 | 4149 | 0.098786 | 1.425 | A01 | LINW0.02026020
Horizontal Wall | Linea Plus | LINW.02028010 | 20 | 280 | 10 | 12 | 1590 | 1590 | 1590 | 0.037857 | 588 | 0.014 | 1824 | 0.043429 | 1.436 | A01 | LINW0.02028010
Horizontal Wall | Linea Plus | LINW.02028015 | 20 | 280 | 15 | 17 | 2906 | 2906 | 2906 | 0.06919 | 1084 | 0.02581 | 3327 | 0.079214 | 1.424 | A01 | LINW0.02028015
Horizontal Wall | Linea Plus | LINW.02028020 | 20 | 280 | 20 | 22 | 3903 | 3903 | 3903 | 0.092929 | 1452 | 0.034571 | 4469 | 0.1064 | 1.425 | A01 | LINW0.02028020
Horizontal Wall | Linea Plus | LINW.03505010 | 35 | 50 | 10 | 12 | 393 | 393 | 393 | 0.0093571 | 147 | 0.0035 | 450 | 0.010714 | 1.419 | A01 | LINW0.03505010
Horizontal Wall | Linea Plus | LINW.03505011 | 35 | 50 | 11 | 12 | 549 | 549 | 549 | 0.013071 | 199 | 0.0047381 | 631 | 0.015024 | 1.46 | A01 | LINW0.03505011
Horizontal Wall | Linea Plus | LINW.03505015 | 35 | 50 | 15 | 17 | 659 | 659 | 659 | 0.01569 | 250 | 0.0059524 | 753 | 0.017929 | 1.398 | A01 | LINW0.03505015
Horizontal Wall | Linea Plus | LINW.03505016 | 35 | 50 | 16 | 17 | 813 | 813 | 813 | 0.019357 | 294 | 0.007 | 935 | 0.022262 | 1.465 | A01 | LINW0.03505016
Horizontal Wall | Linea Plus | LINW.03505020 | 35 | 50 | 20 | 22 | 901 | 901 | 901 | 0.021452 | 341 | 0.008119 | 1030 | 0.024524 | 1.399 | A01 | LINW0.03505020
Horizontal Wall | Linea Plus | LINW.03505021 | 35 | 50 | 21 | 22 | 1039 | 1039 | 1039 | 0.024738 | 372 | 0.0088571 | 1197 | 0.0285 | 1.481 | A01 | LINW0.03505021
Horizontal Wall | Linea Plus | LINW.03506010 | 35 | 60 | 10 | 12 | 471 | 471 | 471 | 0.011214 | 176 | 0.0041905 | 539 | 0.012833 | 1.419 | A01 | LINW0.03506010
Horizontal Wall | Linea Plus | LINW.03506011 | 35 | 60 | 11 | 12 | 659 | 659 | 659 | 0.01569 | 239 | 0.0056905 | 757 | 0.018024 | 1.46 | A01 | LINW0.03506011
Horizontal Wall | Linea Plus | LINW.03506011/DBE | 35 | 60 | 11 | 12 | 959 | 959 | 959 | 0.022833 | 480 | 0.011429 | 1055 | 0.025119 | 1 | A01 | LINW0.03506011/DBE
Horizontal Wall | Linea Plus | LINW.03506015 | 35 | 60 | 15 | 17 | 790 | 790 | 790 | 0.01881 | 299 | 0.007119 | 903 | 0.0215 | 1.398 | A01 | LINW0.03506015
Horizontal Wall | Linea Plus | LINW.03506016 | 35 | 60 | 16 | 17 | 975 | 975 | 975 | 0.023214 | 353 | 0.0084048 | 1121 | 0.02669 | 1.465 | A01 | LINW0.03506016
Horizontal Wall | Linea Plus | LINW.03506016/DBE | 35 | 60 | 16 | 17 | 1455 | 1455 | 1455 | 0.034643 | 728 | 0.017333 | 1601 | 0.038119 | 1 | A01 | LINW0.03506016/DBE
Horizontal Wall | Linea Plus | LINW.03506020 | 35 | 60 | 20 | 22 | 1081 | 1081 | 1081 | 0.025738 | 410 | 0.0097619 | 1236 | 0.029429 | 1.399 | A01 | LINW0.03506020
Horizontal Wall | Linea Plus | LINW.03506021 | 35 | 60 | 21 | 22 | 1247 | 1247 | 1247 | 0.02969 | 446 | 0.010619 | 1437 | 0.034214 | 1.481 | A01 | LINW0.03506021
Horizontal Wall | Linea Plus | LINW.03506021/DBE | 35 | 60 | 21 | 22 | 1727 | 1727 | 1727 | 0.041119 | 864 | 0.020571 | 1900 | 0.045238 | 1 | A01 | LINW0.03506021/DBE
Horizontal Wall | Linea Plus | LINW.03507010 | 35 | 70 | 10 | 12 | 550 | 550 | 550 | 0.013095 | 206 | 0.0049048 | 630 | 0.015 | 1.419 | A01 | LINW0.03507010
Horizontal Wall | Linea Plus | LINW.03507011 | 35 | 70 | 11 | 12 | 769 | 769 | 769 | 0.01831 | 279 | 0.0066429 | 884 | 0.021048 | 1.46 | A01 | LINW0.03507011
Horizontal Wall | Linea Plus | LINW.03507011/DBE | 35 | 70 | 11 | 12 | 1069 | 1069 | 1069 | 0.025452 | 535 | 0.012738 | 1176 | 0.028 | 1 | A01 | LINW0.03507011/DBE
Horizontal Wall | Linea Plus | LINW.03507015 | 35 | 70 | 15 | 17 | 922 | 922 | 922 | 0.021952 | 349 | 0.0083095 | 1054 | 0.025095 | 1.398 | A01 | LINW0.03507015
Horizontal Wall | Linea Plus | LINW.03507016 | 35 | 70 | 16 | 17 | 1138 | 1138 | 1138 | 0.027095 | 412 | 0.0098095 | 1309 | 0.031167 | 1.465 | A01 | LINW0.03507016
Horizontal Wall | Linea Plus | LINW.03507016/DBE | 35 | 70 | 16 | 17 | 1618 | 1618 | 1618 | 0.038524 | 809 | 0.019262 | 1780 | 0.042381 | 1 | A01 | LINW0.03507016/DBE
Horizontal Wall | Linea Plus | LINW.03507020 | 35 | 70 | 20 | 22 | 1261 | 1261 | 1261 | 0.030024 | 478 | 0.011381 | 1441 | 0.03431 | 1.399 | A01 | LINW0.03507020
Horizontal Wall | Linea Plus | LINW.03507021 | 35 | 70 | 21 | 22 | 1455 | 1455 | 1455 | 0.034643 | 521 | 0.012405 | 1676 | 0.039905 | 1.481 | A01 | LINW0.03507021
Horizontal Wall | Linea Plus | LINW.03507021/DBE | 35 | 70 | 21 | 22 | 1935 | 1935 | 1935 | 0.046071 | 968 | 0.023048 | 2129 | 0.05069 | 1 | A01 | LINW0.03507021/DBE
Horizontal Wall | Linea Plus | LINW.03508010 | 35 | 80 | 10 | 12 | 628 | 628 | 628 | 0.014952 | 235 | 0.0055952 | 719 | 0.017119 | 1.419 | A01 | LINW0.03508010
Horizontal Wall | Linea Plus | LINW.03508011 | 35 | 80 | 11 | 12 | 878 | 878 | 878 | 0.020905 | 319 | 0.0075952 | 1009 | 0.024024 | 1.46 | A01 | LINW0.03508011
Horizontal Wall | Linea Plus | LINW.03508011/DBE | 35 | 80 | 11 | 12 | 1178 | 1178 | 1178 | 0.028048 | 589 | 0.014024 | 1296 | 0.030857 | 1 | A01 | LINW0.03508011/DBE
Horizontal Wall | Linea Plus | LINW.03508015 | 35 | 80 | 15 | 17 | 1054 | 1054 | 1054 | 0.025095 | 399 | 0.0095 | 1205 | 0.02869 | 1.398 | A01 | LINW0.03508015
Horizontal Wall | Linea Plus | LINW.03508016 | 35 | 80 | 16 | 17 | 1300 | 1300 | 1300 | 0.030952 | 471 | 0.011214 | 1495 | 0.035595 | 1.465 | A01 | LINW0.03508016
Horizontal Wall | Linea Plus | LINW.03508016/DBE | 35 | 80 | 16 | 17 | 1780 | 1780 | 1780 | 0.042381 | 890 | 0.02119 | 1958 | 0.046619 | 1 | A01 | LINW0.03508016/DBE
Horizontal Wall | Linea Plus | LINW.03508020 | 35 | 80 | 20 | 22 | 1441 | 1441 | 1441 | 0.03431 | 546 | 0.013 | 1647 | 0.039214 | 1.399 | A01 | LINW0.03508020
Horizontal Wall | Linea Plus | LINW.03508021 | 35 | 80 | 21 | 22 | 1662 | 1662 | 1662 | 0.039571 | 595 | 0.014167 | 1915 | 0.045595 | 1.481 | A01 | LINW0.03508021
Horizontal Wall | Linea Plus | LINW.03508021/DBE | 35 | 80 | 21 | 22 | 2142 | 2142 | 2142 | 0.051 | 1071 | 0.0255 | 2356 | 0.056095 | 1 | A01 | LINW0.03508021/DBE
Horizontal Wall | Linea Plus | LINW.03509010 | 35 | 90 | 10 | 12 | 707 | 707 | 707 | 0.016833 | 264 | 0.0062857 | 810 | 0.019286 | 1.419 | A01 | LINW0.03509010
Horizontal Wall | Linea Plus | LINW.03509011 | 35 | 90 | 11 | 12 | 988 | 988 | 988 | 0.023524 | 359 | 0.0085476 | 1135 | 0.027024 | 1.46 | A01 | LINW0.03509011
Horizontal Wall | Linea Plus | LINW.03509011/DBE | 35 | 90 | 11 | 12 | 1588 | 1588 | 1588 | 0.03781 | 794 | 0.018905 | 1747 | 0.041595 | 1 | A01 | LINW0.03509011/DBE
Horizontal Wall | Linea Plus | LINW.03509015 | 35 | 90 | 15 | 17 | 1185 | 1185 | 1185 | 0.028214 | 449 | 0.01069 | 1354 | 0.032238 | 1.398 | A01 | LINW0.03509015
Horizontal Wall | Linea Plus | LINW.03509016 | 35 | 90 | 16 | 17 | 1463 | 1463 | 1463 | 0.034833 | 530 | 0.012619 | 1682 | 0.040048 | 1.465 | A01 | LINW0.03509016
Horizontal Wall | Linea Plus | LINW.03509016/DBE | 35 | 90 | 16 | 17 | 2423 | 2423 | 2423 | 0.05769 | 1212 | 0.028857 | 2665 | 0.063452 | 1 | A01 | LINW0.03509016/DBE
Horizontal Wall | Linea Plus | LINW.03509020 | 35 | 90 | 20 | 22 | 1621 | 1621 | 1621 | 0.038595 | 614 | 0.014619 | 1853 | 0.044119 | 1.399 | A01 | LINW0.03509020
Horizontal Wall | Linea Plus | LINW.03509021 | 35 | 90 | 21 | 22 | 1870 | 1870 | 1870 | 0.044524 | 669 | 0.015929 | 2154 | 0.051286 | 1.481 | A01 | LINW0.03509021
Horizontal Wall | Linea Plus | LINW.03509021/DBE | 35 | 90 | 21 | 22 | 2830 | 2830 | 2830 | 0.067381 | 1415 | 0.03369 | 3113 | 0.074119 | 1 | A01 | LINW0.03509021/DBE
Horizontal Wall | Linea Plus | LINW.03510010 | 35 | 100 | 10 | 12 | 785 | 785 | 785 | 0.01869 | 294 | 0.007 | 899 | 0.021405 | 1.419 | A01 | LINW0.03510010
Horizontal Wall | Linea Plus | LINW.03510011 | 35 | 100 | 11 | 12 | 1098 | 1098 | 1098 | 0.026143 | 399 | 0.0095 | 1262 | 0.030048 | 1.46 | A01 | LINW0.03510011
Horizontal Wall | Linea Plus | LINW.03510011/DBE | 35 | 100 | 11 | 12 | 1698 | 1698 | 1698 | 0.040429 | 849 | 0.020214 | 1868 | 0.044476 | 1 | A01 | LINW0.03510011/DBE
Horizontal Wall | Linea Plus | LINW.03510015 | 35 | 100 | 15 | 17 | 1317 | 1317 | 1317 | 0.031357 | 499 | 0.011881 | 1505 | 0.035833 | 1.398 | A01 | LINW0.03510015
Horizontal Wall | Linea Plus | LINW.03510016 | 35 | 100 | 16 | 17 | 1625 | 1625 | 1625 | 0.03869 | 588 | 0.014 | 1869 | 0.0445 | 1.465 | A01 | LINW0.03510016
Horizontal Wall | Linea Plus | LINW.03510016/DBE | 35 | 100 | 16 | 17 | 2585 | 2585 | 2585 | 0.061548 | 1293 | 0.030786 | 2844 | 0.067714 | 1 | A01 | LINW0.03510016/DBE
Horizontal Wall | Linea Plus | LINW.03510020 | 35 | 100 | 20 | 22 | 1801 | 1801 | 1801 | 0.042881 | 683 | 0.016262 | 2059 | 0.049024 | 1.399 | A01 | LINW0.03510020
Horizontal Wall | Linea Plus | LINW.03510021 | 35 | 100 | 21 | 22 | 2078 | 2078 | 2078 | 0.049476 | 744 | 0.017714 | 2394 | 0.057 | 1.481 | A01 | LINW0.03510021
Horizontal Wall | Linea Plus | LINW.03510021/DBE | 35 | 100 | 21 | 22 | 3038 | 3038 | 3038 | 0.072333 | 1519 | 0.036167 | 3342 | 0.079571 | 1 | A01 | LINW0.03510021/DBE
Horizontal Wall | Linea Plus | LINW.03511010 | 35 | 110 | 10 | 12 | 864 | 864 | 864 | 0.020571 | 323 | 0.0076905 | 989 | 0.023548 | 1.419 | A01 | LINW0.03511010
Horizontal Wall | Linea Plus | LINW.03511011 | 35 | 110 | 11 | 12 | 1208 | 1208 | 1208 | 0.028762 | 439 | 0.010452 | 1388 | 0.033048 | 1.46 | A01 | LINW0.03511011
Horizontal Wall | Linea Plus | LINW.03511011/DBE | 35 | 110 | 11 | 12 | 1808 | 1808 | 1808 | 0.043048 | 904 | 0.021524 | 1989 | 0.047357 | 1 | A01 | LINW0.03511011/DBE
Horizontal Wall | Linea Plus | LINW.03511015 | 35 | 110 | 15 | 17 | 1449 | 1449 | 1449 | 0.0345 | 549 | 0.013071 | 1656 | 0.039429 | 1.398 | A01 | LINW0.03511015
Horizontal Wall | Linea Plus | LINW.03511016 | 35 | 110 | 16 | 17 | 1788 | 1788 | 1788 | 0.042571 | 647 | 0.015405 | 2056 | 0.048952 | 1.465 | A01 | LINW0.03511016
Horizontal Wall | Linea Plus | LINW.03511016/DBE | 35 | 110 | 16 | 17 | 2748 | 2748 | 2748 | 0.065429 | 1374 | 0.032714 | 3023 | 0.071976 | 1 | A01 | LINW0.03511016/DBE
Horizontal Wall | Linea Plus | LINW.03511020 | 35 | 110 | 20 | 22 | 1981 | 1981 | 1981 | 0.047167 | 751 | 0.017881 | 2264 | 0.053905 | 1.399 | A01 | LINW0.03511020
Horizontal Wall | Linea Plus | LINW.03511021 | 35 | 110 | 21 | 22 | 2286 | 2286 | 2286 | 0.054429 | 818 | 0.019476 | 2633 | 0.06269 | 1.481 | A01 | LINW0.03511021
Horizontal Wall | Linea Plus | LINW.03511021/DBE | 35 | 110 | 21 | 22 | 3246 | 3246 | 3246 | 0.077286 | 1623 | 0.038643 | 3571 | 0.085024 | 1 | A01 | LINW0.03511021/DBE
Horizontal Wall | Linea Plus | LINW.03512010 | 35 | 120 | 10 | 12 | 942 | 942 | 942 | 0.022429 | 352 | 0.008381 | 1079 | 0.02569 | 1.419 | A01 | LINW0.03512010
Horizontal Wall | Linea Plus | LINW.03512011 | 35 | 120 | 11 | 12 | 1318 | 1318 | 1318 | 0.031381 | 478 | 0.011381 | 1514 | 0.036048 | 1.46 | A01 | LINW0.03512011
Horizontal Wall | Linea Plus | LINW.03512011/DBE | 35 | 120 | 11 | 12 | 1918 | 1918 | 1918 | 0.045667 | 959 | 0.022833 | 2110 | 0.050238 | 1 | A01 | LINW0.03512011/DBE
Horizontal Wall | Linea Plus | LINW.03512015 | 35 | 120 | 15 | 17 | 1580 | 1580 | 1580 | 0.037619 | 599 | 0.014262 | 1806 | 0.043 | 1.398 | A01 | LINW0.03512015
Horizontal Wall | Linea Plus | LINW.03512016 | 35 | 120 | 16 | 17 | 1950 | 1950 | 1950 | 0.046429 | 706 | 0.01681 | 2243 | 0.053405 | 1.465 | A01 | LINW0.03512016
Horizontal Wall | Linea Plus | LINW.03512016/DBE | 35 | 120 | 16 | 17 | 2910 | 2910 | 2910 | 0.069286 | 1455 | 0.034643 | 3201 | 0.076214 | 1 | A01 | LINW0.03512016/DBE
Horizontal Wall | Linea Plus | LINW.03512020 | 35 | 120 | 20 | 22 | 2161 | 2161 | 2161 | 0.051452 | 819 | 0.0195 | 2470 | 0.05881 | 1.399 | A01 | LINW0.03512020
Horizontal Wall | Linea Plus | LINW.03512021 | 35 | 120 | 21 | 22 | 2494 | 2494 | 2494 | 0.059381 | 893 | 0.021262 | 2873 | 0.068405 | 1.481 | A01 | LINW0.03512021
Horizontal Wall | Linea Plus | LINW.03512021/DBE | 35 | 120 | 21 | 22 | 3454 | 3454 | 3454 | 0.082238 | 1727 | 0.041119 | 3799 | 0.090452 | 1 | A01 | LINW0.03512021/DBE
Horizontal Wall | Linea Plus | LINW.03514010 | 35 | 140 | 10 | 12 | 1099 | 1099 | 1099 | 0.026167 | 411 | 0.0097857 | 1258 | 0.029952 | 1.419 | A01 | LINW0.03514010
Horizontal Wall | Linea Plus | LINW.03514011 | 35 | 140 | 11 | 12 | 1537 | 1537 | 1537 | 0.036595 | 558 | 0.013286 | 1766 | 0.042048 | 1.46 | A01 | LINW0.03514011
Horizontal Wall | Linea Plus | LINW.03514011/DBE | 35 | 140 | 11 | 12 | 2137 | 2137 | 2137 | 0.050881 | 1069 | 0.025452 | 2351 | 0.055976 | 1 | A01 | LINW0.03514011/DBE
Horizontal Wall | Linea Plus | LINW.03514015 | 35 | 140 | 15 | 17 | 1844 | 1844 | 1844 | 0.043905 | 699 | 0.016643 | 2108 | 0.05019 | 1.398 | A01 | LINW0.03514015
Horizontal Wall | Linea Plus | LINW.03514016 | 35 | 140 | 16 | 17 | 2275 | 2275 | 2275 | 0.054167 | 824 | 0.019619 | 2616 | 0.062286 | 1.465 | A01 | LINW0.03514016
Horizontal Wall | Linea Plus | LINW.03514016/DBE | 35 | 140 | 16 | 17 | 3235 | 3235 | 3235 | 0.077024 | 1618 | 0.038524 | 3559 | 0.084738 | 1 | A01 | LINW0.03514016/DBE
Horizontal Wall | Linea Plus | LINW.03514020 | 35 | 140 | 20 | 22 | 2521 | 2521 | 2521 | 0.060024 | 955 | 0.022738 | 2882 | 0.068619 | 1.399 | A01 | LINW0.03514020
Horizontal Wall | Linea Plus | LINW.03514021 | 35 | 140 | 21 | 22 | 2909 | 2909 | 2909 | 0.069262 | 1041 | 0.024786 | 3351 | 0.079786 | 1.481 | A01 | LINW0.03514021
Horizontal Wall | Linea Plus | LINW.03514021/DBE | 35 | 140 | 21 | 22 | 3869 | 3869 | 3869 | 0.092119 | 1935 | 0.046071 | 4256 | 0.10133 | 1 | A01 | LINW0.03514021/DBE
Horizontal Wall | Linea Plus | LINW.03516010 | 35 | 160 | 10 | 12 | 1256 | 1256 | 1256 | 0.029905 | 470 | 0.01119 | 1438 | 0.034238 | 1.419 | A01 | LINW0.03516010
Horizontal Wall | Linea Plus | LINW.03516011 | 35 | 160 | 11 | 12 | 1757 | 1757 | 1757 | 0.041833 | 638 | 0.01519 | 2019 | 0.048071 | 1.46 | A01 | LINW0.03516011
Horizontal Wall | Linea Plus | LINW.03516011/DBE | 35 | 160 | 11 | 12 | 2957 | 2957 | 2957 | 0.070405 | 1479 | 0.035214 | 3253 | 0.077452 | 1 | A01 | LINW0.03516011/DBE
Horizontal Wall | Linea Plus | LINW.03516015 | 35 | 160 | 15 | 17 | 2107 | 2107 | 2107 | 0.050167 | 799 | 0.019024 | 2408 | 0.057333 | 1.398 | A01 | LINW0.03516015
Horizontal Wall | Linea Plus | LINW.03516016 | 35 | 160 | 16 | 17 | 2600 | 2600 | 2600 | 0.061905 | 941 | 0.022405 | 2990 | 0.07119 | 1.465 | A01 | LINW0.03516016
Horizontal Wall | Linea Plus | LINW.03516016/DBE | 35 | 160 | 16 | 17 | 4520 | 4520 | 4520 | 0.10762 | 2260 | 0.05381 | 4972 | 0.11838 | 1 | A01 | LINW0.03516016/DBE
Horizontal Wall | Linea Plus | LINW.03516020 | 35 | 160 | 20 | 22 | 2882 | 2882 | 2882 | 0.068619 | 1092 | 0.026 | 3294 | 0.078429 | 1.399 | A01 | LINW0.03516020
Horizontal Wall | Linea Plus | LINW.03516021 | 35 | 160 | 21 | 22 | 3325 | 3325 | 3325 | 0.079167 | 1190 | 0.028333 | 3830 | 0.09119 | 1.481 | A01 | LINW0.03516021
Horizontal Wall | Linea Plus | LINW.03516021/DBE | 35 | 160 | 21 | 22 | 5245 | 5245 | 5245 | 0.12488 | 2623 | 0.062452 | 5770 | 0.13738 | 1 | A01 | LINW0.03516021/DBE
Horizontal Wall | Linea Plus | LINW.03518010 | 35 | 180 | 10 | 12 | 1413 | 1413 | 1413 | 0.033643 | 528 | 0.012571 | 1618 | 0.038524 | 1.419 | A01 | LINW0.03518010
Horizontal Wall | Linea Plus | LINW.03518011 | 35 | 180 | 11 | 12 | 1976 | 1976 | 1976 | 0.047048 | 717 | 0.017071 | 2270 | 0.054048 | 1.46 | A01 | LINW0.03518011
Horizontal Wall | Linea Plus | LINW.03518011/DBE | 35 | 180 | 11 | 12 | 3176 | 3176 | 3176 | 0.075619 | 1588 | 0.03781 | 3494 | 0.08319 | 1 | A01 | LINW0.03518011/DBE
Horizontal Wall | Linea Plus | LINW.03518015 | 35 | 180 | 15 | 17 | 2371 | 2371 | 2371 | 0.056452 | 899 | 0.021405 | 2710 | 0.064524 | 1.398 | A01 | LINW0.03518015
Horizontal Wall | Linea Plus | LINW.03518016 | 35 | 180 | 16 | 17 | 2925 | 2925 | 2925 | 0.069643 | 1059 | 0.025214 | 3364 | 0.080095 | 1.465 | A01 | LINW0.03518016
Horizontal Wall | Linea Plus | LINW.03518016/DBE | 35 | 180 | 16 | 17 | 4845 | 4845 | 4845 | 0.11536 | 2423 | 0.05769 | 5330 | 0.1269 | 1 | A01 | LINW0.03518016/DBE
Horizontal Wall | Linea Plus | LINW.03518020 | 35 | 180 | 20 | 22 | 3242 | 3242 | 3242 | 0.07719 | 1229 | 0.029262 | 3706 | 0.088238 | 1.399 | A01 | LINW0.03518020
Horizontal Wall | Linea Plus | LINW.03518021 | 35 | 180 | 21 | 22 | 3740 | 3740 | 3740 | 0.089048 | 1339 | 0.031881 | 4308 | 0.10257 | 1.481 | A01 | LINW0.03518021
Horizontal Wall | Linea Plus | LINW.03518021/DBE | 35 | 180 | 21 | 22 | 5660 | 5660 | 5660 | 0.13476 | 2830 | 0.067381 | 6226 | 0.14824 | 1 | A01 | LINW0.03518021/DBE
Horizontal Wall | Linea Plus | LINW.03520010 | 35 | 200 | 10 | 12 | 1570 | 1570 | 1570 | 0.037381 | 587 | 0.013976 | 1798 | 0.04281 | 1.419 | A01 | LINW0.03520010
Horizontal Wall | Linea Plus | LINW.03520011 | 35 | 200 | 11 | 12 | 2196 | 2196 | 2196 | 0.052286 | 797 | 0.018976 | 2523 | 0.060071 | 1.46 | A01 | LINW0.03520011
Horizontal Wall | Linea Plus | LINW.03520011/DBE | 35 | 200 | 11 | 12 | 3396 | 3396 | 3396 | 0.080857 | 1698 | 0.040429 | 3736 | 0.088952 | 1 | A01 | LINW0.03520011/DBE
Horizontal Wall | Linea Plus | LINW.03520015 | 35 | 200 | 15 | 17 | 2634 | 2634 | 2634 | 0.062714 | 998 | 0.023762 | 3011 | 0.07169 | 1.398 | A01 | LINW0.03520015
Horizontal Wall | Linea Plus | LINW.03520016 | 35 | 200 | 16 | 17 | 3250 | 3250 | 3250 | 0.077381 | 1177 | 0.028024 | 3738 | 0.089 | 1.465 | A01 | LINW0.03520016
Horizontal Wall | Linea Plus | LINW.03520016/DBE | 35 | 200 | 16 | 17 | 5170 | 5170 | 5170 | 0.1231 | 2585 | 0.061548 | 5687 | 0.1354 | 1 | A01 | LINW0.03520016/DBE
Horizontal Wall | Linea Plus | LINW.03520020 | 35 | 200 | 20 | 22 | 3602 | 3602 | 3602 | 0.085762 | 1365 | 0.0325 | 4117 | 0.098024 | 1.399 | A01 | LINW0.03520020
Horizontal Wall | Linea Plus | LINW.03520021 | 35 | 200 | 21 | 22 | 4156 | 4156 | 4156 | 0.098952 | 1488 | 0.035429 | 4788 | 0.114 | 1.481 | A01 | LINW0.03520021
Horizontal Wall | Linea Plus | LINW.03520021/DBE | 35 | 200 | 21 | 22 | 6076 | 6076 | 6076 | 0.14467 | 3038 | 0.072333 | 6684 | 0.15914 | 1 | A01 | LINW0.03520021/DBE
Horizontal Wall | Linea Plus | LINW.03522010 | 35 | 220 | 10 | 12 | 1727 | 1727 | 1727 | 0.041119 | 646 | 0.015381 | 1977 | 0.047071 | 1.419 | A01 | LINW0.03522010
Horizontal Wall | Linea Plus | LINW.03522011 | 35 | 220 | 11 | 12 | 2416 | 2416 | 2416 | 0.057524 | 877 | 0.020881 | 2776 | 0.066095 | 1.46 | A01 | LINW0.03522011
Horizontal Wall | Linea Plus | LINW.03522011/DBE | 35 | 220 | 11 | 12 | 3616 | 3616 | 3616 | 0.086095 | 1808 | 0.043048 | 3978 | 0.094714 | 1 | A01 | LINW0.03522011/DBE
Horizontal Wall | Linea Plus | LINW.03522015 | 35 | 220 | 15 | 17 | 2897 | 2897 | 2897 | 0.068976 | 1098 | 0.026143 | 3311 | 0.078833 | 1.398 | A01 | LINW0.03522015
Horizontal Wall | Linea Plus | LINW.03522016 | 35 | 220 | 16 | 17 | 3575 | 3575 | 3575 | 0.085119 | 1294 | 0.03081 | 4111 | 0.097881 | 1.465 | A01 | LINW0.03522016
Horizontal Wall | Linea Plus | LINW.03522016/DBE | 35 | 220 | 16 | 17 | 5495 | 5495 | 5495 | 0.13083 | 2748 | 0.065429 | 6045 | 0.14393 | 1 | A01 | LINW0.03522016/DBE
Horizontal Wall | Linea Plus | LINW.03522020 | 35 | 220 | 20 | 22 | 3962 | 3962 | 3962 | 0.094333 | 1502 | 0.035762 | 4529 | 0.10783 | 1.399 | A01 | LINW0.03522020
Horizontal Wall | Linea Plus | LINW.03522021 | 35 | 220 | 21 | 22 | 4572 | 4572 | 4572 | 0.10886 | 1637 | 0.038976 | 5267 | 0.1254 | 1.481 | A01 | LINW0.03522021
Horizontal Wall | Linea Plus | LINW.03522021/DBE | 35 | 220 | 21 | 22 | 6492 | 6492 | 6492 | 0.15457 | 3246 | 0.077286 | 7141 | 0.17002 | 1 | A01 | LINW0.03522021/DBE
Horizontal Wall | Linea Plus | LINW.03524010 | 35 | 240 | 10 | 12 | 1884 | 1884 | 1884 | 0.044857 | 705 | 0.016786 | 2157 | 0.051357 | 1.419 | A01 | LINW0.03524010
Horizontal Wall | Linea Plus | LINW.03524011 | 35 | 240 | 11 | 12 | 2635 | 2635 | 2635 | 0.062738 | 957 | 0.022786 | 3028 | 0.072095 | 1.46 | A01 | LINW0.03524011
Horizontal Wall | Linea Plus | LINW.03524011/DBE | 35 | 240 | 11 | 12 | 4435 | 4435 | 4435 | 0.1056 | 2218 | 0.05281 | 4879 | 0.11617 | 1 | A01 | LINW0.03524011/DBE
Horizontal Wall | Linea Plus | LINW.03524015 | 35 | 240 | 15 | 17 | 3161 | 3161 | 3161 | 0.075262 | 1198 | 0.028524 | 3613 | 0.086024 | 1.398 | A01 | LINW0.03524015
Horizontal Wall | Linea Plus | LINW.03524016 | 35 | 240 | 16 | 17 | 3900 | 3900 | 3900 | 0.092857 | 1412 | 0.033619 | 4485 | 0.10679 | 1.465 | A01 | LINW0.03524016
Horizontal Wall | Linea Plus | LINW.03524016/DBE | 35 | 240 | 16 | 17 | 6780 | 6780 | 6780 | 0.16143 | 3390 | 0.080714 | 7458 | 0.17757 | 1 | A01 | LINW0.03524016/DBE
Horizontal Wall | Linea Plus | LINW.03524020 | 35 | 240 | 20 | 22 | 4322 | 4322 | 4322 | 0.1029 | 1638 | 0.039 | 4940 | 0.11762 | 1.399 | A01 | LINW0.03524020
Horizontal Wall | Linea Plus | LINW.03524021 | 35 | 240 | 21 | 22 | 4987 | 4987 | 4987 | 0.11874 | 1785 | 0.0425 | 5745 | 0.13679 | 1.481 | A01 | LINW0.03524021
Horizontal Wall | Linea Plus | LINW.03524021/DBE | 35 | 240 | 21 | 22 | 7867 | 7867 | 7867 | 0.18731 | 3934 | 0.093667 | 8654 | 0.20605 | 1 | A01 | LINW0.03524021/DBE
Horizontal Wall | Linea Plus | LINW.03526010 | 35 | 260 | 10 | 12 | 2041 | 2041 | 2041 | 0.048595 | 763 | 0.018167 | 2337 | 0.055643 | 1.419 | A01 | LINW0.03526010
Horizontal Wall | Linea Plus | LINW.03526011 | 35 | 260 | 11 | 12 | 2855 | 2855 | 2855 | 0.067976 | 1036 | 0.024667 | 3280 | 0.078095 | 1.46 | A01 | LINW0.03526011
Horizontal Wall | Linea Plus | LINW.03526011/DBE | 35 | 260 | 11 | 12 | 4655 | 4655 | 4655 | 0.11083 | 2328 | 0.055429 | 5121 | 0.12193 | 1 | A01 | LINW0.03526011/DBE
Horizontal Wall | Linea Plus | LINW.03526015 | 35 | 260 | 15 | 17 | 3424 | 3424 | 3424 | 0.081524 | 1298 | 0.030905 | 3914 | 0.09319 | 1.398 | A01 | LINW0.03526015
Horizontal Wall | Linea Plus | LINW.03526016 | 35 | 260 | 16 | 17 | 4225 | 4225 | 4225 | 0.1006 | 1529 | 0.036405 | 4859 | 0.11569 | 1.465 | A01 | LINW0.03526016
Horizontal Wall | Linea Plus | LINW.03526016/DBE | 35 | 260 | 16 | 17 | 7105 | 7105 | 7105 | 0.16917 | 3553 | 0.084595 | 7816 | 0.1861 | 1 | A01 | LINW0.03526016/DBE
Horizontal Wall | Linea Plus | LINW.03526020 | 35 | 260 | 20 | 22 | 4683 | 4683 | 4683 | 0.1115 | 1775 | 0.042262 | 5353 | 0.12745 | 1.399 | A01 | LINW0.03526020
Horizontal Wall | Linea Plus | LINW.03526021 | 35 | 260 | 21 | 22 | 5403 | 5403 | 5403 | 0.12864 | 1934 | 0.046048 | 6224 | 0.14819 | 1.481 | A01 | LINW0.03526021
Horizontal Wall | Linea Plus | LINW.03526021/DBE | 35 | 260 | 21 | 22 | 8283 | 8283 | 8283 | 0.19721 | 4142 | 0.098619 | 9111 | 0.21693 | 1 | A01 | LINW0.03526021/DBE
Horizontal Wall | Linea Plus | LINW.03528010 | 35 | 280 | 10 | 12 | 2198 | 2198 | 2198 | 0.052333 | 822 | 0.019571 | 2517 | 0.059929 | 1.419 | A01 | LINW0.03528010
Horizontal Wall | Linea Plus | LINW.03528011 | 35 | 280 | 11 | 12 | 3074 | 3074 | 3074 | 0.07319 | 1116 | 0.026571 | 3532 | 0.084095 | 1.46 | A01 | LINW0.03528011
Horizontal Wall | Linea Plus | LINW.03528011/DBE | 35 | 280 | 11 | 12 | 4874 | 4874 | 4874 | 0.11605 | 2437 | 0.058024 | 5361 | 0.12764 | 1 | A01 | LINW0.03528011/DBE
Horizontal Wall | Linea Plus | LINW.03528015 | 35 | 280 | 15 | 17 | 3688 | 3688 | 3688 | 0.08781 | 1398 | 0.033286 | 4215 | 0.10036 | 1.398 | A01 | LINW0.03528015
Horizontal Wall | Linea Plus | LINW.03528016 | 35 | 280 | 16 | 17 | 4550 | 4550 | 4550 | 0.10833 | 1647 | 0.039214 | 5233 | 0.1246 | 1.465 | A01 | LINW0.03528016
Horizontal Wall | Linea Plus | LINW.03528016/DBE | 35 | 280 | 16 | 17 | 7430 | 7430 | 7430 | 0.1769 | 3715 | 0.088452 | 8173 | 0.1946 | 1 | A01 | LINW0.03528016/DBE
Horizontal Wall | Linea Plus | LINW.03528020 | 35 | 280 | 20 | 22 | 5043 | 5043 | 5043 | 0.12007 | 1911 | 0.0455 | 5764 | 0.13724 | 1.399 | A01 | LINW0.03528020
Horizontal Wall | Linea Plus | LINW.03528021 | 35 | 280 | 21 | 22 | 5818 | 5818 | 5818 | 0.13852 | 2083 | 0.049595 | 6702 | 0.15957 | 1.481 | A01 | LINW0.03528021
Horizontal Wall | Linea Plus | LINW.03528021/DBE | 35 | 280 | 21 | 22 | 8698 | 8698 | 8698 | 0.2071 | 4349 | 0.10355 | 9568 | 0.22781 | 1 | A01 | LINW0.03528021/DBE
Horizontal Wall | Linea Plus | LINW.05005010 | 50 | 50 | 10 | 12 | 482 | 482 | 482 | 0.011476 | 182 | 0.0043333 | 551 | 0.013119 | 1.402 | A01 | LINW0.05005010
Horizontal Wall | Linea Plus | LINW.05005011 | 50 | 50 | 11 | 12 | 655 | 655 | 655 | 0.015595 | 239 | 0.0056905 | 753 | 0.017929 | 1.455 | A01 | LINW0.05005011
Horizontal Wall | Linea Plus | LINW.05005015 | 50 | 50 | 15 | 17 | 767 | 767 | 767 | 0.018262 | 296 | 0.0070476 | 874 | 0.02081 | 1.372 | A01 | LINW0.05005015
Horizontal Wall | Linea Plus | LINW.05005016 | 50 | 50 | 16 | 17 | 976 | 976 | 976 | 0.023238 | 354 | 0.0084286 | 1122 | 0.026714 | 1.463 | A01 | LINW0.05005016
Horizontal Wall | Linea Plus | LINW.05005020 | 50 | 50 | 20 | 22 | 1060 | 1060 | 1060 | 0.025238 | 409 | 0.0097381 | 1208 | 0.028762 | 1.373 | A01 | LINW0.05005020
Horizontal Wall | Linea Plus | LINW.05005021 | 50 | 50 | 21 | 22 | 1282 | 1282 | 1282 | 0.030524 | 458 | 0.010905 | 1477 | 0.035167 | 1.486 | A01 | LINW0.05005021
Horizontal Wall | Linea Plus | LINW.05006010 | 50 | 60 | 10 | 12 | 578 | 578 | 578 | 0.013762 | 218 | 0.0051905 | 661 | 0.015738 | 1.402 | A01 | LINW0.05006010
Horizontal Wall | Linea Plus | LINW.05006011 | 50 | 60 | 11 | 12 | 785 | 785 | 785 | 0.01869 | 287 | 0.0068333 | 902 | 0.021476 | 1.455 | A01 | LINW0.05006011
Horizontal Wall | Linea Plus | LINW.05006011/DBE | 50 | 60 | 11 | 12 | 1085 | 1085 | 1085 | 0.025833 | 543 | 0.012929 | 1194 | 0.028429 | 1 | A01 | LINW0.05006011/DBE
Horizontal Wall | Linea Plus | LINW.05006015 | 50 | 60 | 15 | 17 | 920 | 920 | 920 | 0.021905 | 355 | 0.0084524 | 1049 | 0.024976 | 1.372 | A01 | LINW0.05006015
Horizontal Wall | Linea Plus | LINW.05006016 | 50 | 60 | 16 | 17 | 1171 | 1171 | 1171 | 0.027881 | 425 | 0.010119 | 1347 | 0.032071 | 1.463 | A01 | LINW0.05006016
Horizontal Wall | Linea Plus | LINW.05006016/DBE | 50 | 60 | 16 | 17 | 1651 | 1651 | 1651 | 0.03931 | 826 | 0.019667 | 1816 | 0.043238 | 1 | A01 | LINW0.05006016/DBE
Horizontal Wall | Linea Plus | LINW.05006020 | 50 | 60 | 20 | 22 | 1272 | 1272 | 1272 | 0.030286 | 491 | 0.01169 | 1450 | 0.034524 | 1.373 | A01 | LINW0.05006020
Horizontal Wall | Linea Plus | LINW.05006021 | 50 | 60 | 21 | 22 | 1538 | 1538 | 1538 | 0.036619 | 549 | 0.013071 | 1772 | 0.04219 | 1.486 | A01 | LINW0.05006021
Horizontal Wall | Linea Plus | LINW.05006021/DBE | 50 | 60 | 21 | 22 | 2018 | 2018 | 2018 | 0.048048 | 1009 | 0.024024 | 2220 | 0.052857 | 1 | A01 | LINW0.05006021/DBE
Horizontal Wall | Linea Plus | LINW.05007010 | 50 | 70 | 10 | 12 | 675 | 675 | 675 | 0.016071 | 255 | 0.0060714 | 772 | 0.018381 | 1.402 | A01 | LINW0.05007010
Horizontal Wall | Linea Plus | LINW.05007011 | 50 | 70 | 11 | 12 | 916 | 916 | 916 | 0.02181 | 334 | 0.0079524 | 1052 | 0.025048 | 1.455 | A01 | LINW0.05007011
Horizontal Wall | Linea Plus | LINW.05007011/DBE | 50 | 70 | 11 | 12 | 1216 | 1216 | 1216 | 0.028952 | 608 | 0.014476 | 1338 | 0.031857 | 1 | A01 | LINW0.05007011/DBE
Horizontal Wall | Linea Plus | LINW.05007015 | 50 | 70 | 15 | 17 | 1073 | 1073 | 1073 | 0.025548 | 414 | 0.0098571 | 1223 | 0.029119 | 1.372 | A01 | LINW0.05007015
Horizontal Wall | Linea Plus | LINW.05007016 | 50 | 70 | 16 | 17 | 1366 | 1366 | 1366 | 0.032524 | 496 | 0.01181 | 1571 | 0.037405 | 1.463 | A01 | LINW0.05007016
Horizontal Wall | Linea Plus | LINW.05007016/DBE | 50 | 70 | 16 | 17 | 1846 | 1846 | 1846 | 0.043952 | 923 | 0.021976 | 2031 | 0.048357 | 1 | A01 | LINW0.05007016/DBE
Horizontal Wall | Linea Plus | LINW.05007020 | 50 | 70 | 20 | 22 | 1484 | 1484 | 1484 | 0.035333 | 573 | 0.013643 | 1692 | 0.040286 | 1.373 | A01 | LINW0.05007020
Horizontal Wall | Linea Plus | LINW.05007021 | 50 | 70 | 21 | 22 | 1795 | 1795 | 1795 | 0.042738 | 641 | 0.015262 | 2068 | 0.049238 | 1.486 | A01 | LINW0.05007021
Horizontal Wall | Linea Plus | LINW.05007021/DBE | 50 | 70 | 21 | 22 | 2275 | 2275 | 2275 | 0.054167 | 1138 | 0.027095 | 2503 | 0.059595 | 1 | A01 | LINW0.05007021/DBE
Horizontal Wall | Linea Plus | LINW.05008010 | 50 | 80 | 10 | 12 | 771 | 771 | 771 | 0.018357 | 291 | 0.0069286 | 881 | 0.020976 | 1.402 | A01 | LINW0.05008010
Horizontal Wall | Linea Plus | LINW.05008011 | 50 | 80 | 11 | 12 | 1047 | 1047 | 1047 | 0.024929 | 382 | 0.0090952 | 1203 | 0.028643 | 1.455 | A01 | LINW0.05008011
Horizontal Wall | Linea Plus | LINW.05008011/DBE | 50 | 80 | 11 | 12 | 1347 | 1347 | 1347 | 0.032071 | 674 | 0.016048 | 1482 | 0.035286 | 1 | A01 | LINW0.05008011/DBE
Horizontal Wall | Linea Plus | LINW.05008015 | 50 | 80 | 15 | 17 | 1226 | 1226 | 1226 | 0.02919 | 473 | 0.011262 | 1398 | 0.033286 | 1.372 | A01 | LINW0.05008015
Horizontal Wall | Linea Plus | LINW.05008016 | 50 | 80 | 16 | 17 | 1561 | 1561 | 1561 | 0.037167 | 567 | 0.0135 | 1795 | 0.042738 | 1.463 | A01 | LINW0.05008016
Horizontal Wall | Linea Plus | LINW.05008016/DBE | 50 | 80 | 16 | 17 | 2041 | 2041 | 2041 | 0.048595 | 1021 | 0.02431 | 2245 | 0.053452 | 1 | A01 | LINW0.05008016/DBE
Horizontal Wall | Linea Plus | LINW.05008020 | 50 | 80 | 20 | 22 | 1696 | 1696 | 1696 | 0.040381 | 655 | 0.015595 | 1933 | 0.046024 | 1.373 | A01 | LINW0.05008020
Horizontal Wall | Linea Plus | LINW.05008021 | 50 | 80 | 21 | 22 | 2051 | 2051 | 2051 | 0.048833 | 732 | 0.017429 | 2363 | 0.056262 | 1.486 | A01 | LINW0.05008021
Horizontal Wall | Linea Plus | LINW.05008021/DBE | 50 | 80 | 21 | 22 | 2531 | 2531 | 2531 | 0.060262 | 1266 | 0.030143 | 2784 | 0.066286 | 1 | A01 | LINW0.05008021/DBE
Horizontal Wall | Linea Plus | LINW.05009010 | 50 | 90 | 10 | 12 | 868 | 868 | 868 | 0.020667 | 328 | 0.0078095 | 992 | 0.023619 | 1.402 | A01 | LINW0.05009010
Horizontal Wall | Linea Plus | LINW.05009011 | 50 | 90 | 11 | 12 | 1178 | 1178 | 1178 | 0.028048 | 430 | 0.010238 | 1354 | 0.032238 | 1.455 | A01 | LINW0.05009011
Horizontal Wall | Linea Plus | LINW.05009011/DBE | 50 | 90 | 11 | 12 | 1778 | 1778 | 1778 | 0.042333 | 889 | 0.021167 | 1956 | 0.046571 | 1 | A01 | LINW0.05009011/DBE
Horizontal Wall | Linea Plus | LINW.05009015 | 50 | 90 | 15 | 17 | 1380 | 1380 | 1380 | 0.032857 | 533 | 0.01269 | 1573 | 0.037452 | 1.372 | A01 | LINW0.05009015
Horizontal Wall | Linea Plus | LINW.05009016 | 50 | 90 | 16 | 17 | 1756 | 1756 | 1756 | 0.04181 | 637 | 0.015167 | 2019 | 0.048071 | 1.463 | A01 | LINW0.05009016
Horizontal Wall | Linea Plus | LINW.05009016/DBE | 50 | 90 | 16 | 17 | 2716 | 2716 | 2716 | 0.064667 | 1358 | 0.032333 | 2988 | 0.071143 | 1 | A01 | LINW0.05009016/DBE
Horizontal Wall | Linea Plus | LINW.05009020 | 50 | 90 | 20 | 22 | 1908 | 1908 | 1908 | 0.045429 | 736 | 0.017524 | 2175 | 0.051786 | 1.373 | A01 | LINW0.05009020
Horizontal Wall | Linea Plus | LINW.05009021 | 50 | 90 | 21 | 22 | 2308 | 2308 | 2308 | 0.054952 | 824 | 0.019619 | 2659 | 0.06331 | 1.486 | A01 | LINW0.05009021
Horizontal Wall | Linea Plus | LINW.05009021/DBE | 50 | 90 | 21 | 22 | 3268 | 3268 | 3268 | 0.07781 | 1634 | 0.038905 | 3595 | 0.085595 | 1 | A01 | LINW0.05009021/DBE
Horizontal Wall | Linea Plus | LINW.05010010 | 50 | 100 | 10 | 12 | 964 | 964 | 964 | 0.022952 | 364 | 0.0086667 | 1102 | 0.026238 | 1.402 | A01 | LINW0.05010010
Horizontal Wall | Linea Plus | LINW.05010011 | 50 | 100 | 11 | 12 | 1309 | 1309 | 1309 | 0.031167 | 478 | 0.011381 | 1504 | 0.03581 | 1.455 | A01 | LINW0.05010011
Horizontal Wall | Linea Plus | LINW.05010011/DBE | 50 | 100 | 11 | 12 | 1909 | 1909 | 1909 | 0.045452 | 955 | 0.022738 | 2100 | 0.05 | 1 | A01 | LINW0.05010011/DBE
Horizontal Wall | Linea Plus | LINW.05010015 | 50 | 100 | 15 | 17 | 1533 | 1533 | 1533 | 0.0365 | 592 | 0.014095 | 1748 | 0.041619 | 1.372 | A01 | LINW0.05010015
Horizontal Wall | Linea Plus | LINW.05010016 | 50 | 100 | 16 | 17 | 1951 | 1951 | 1951 | 0.046452 | 708 | 0.016857 | 2244 | 0.053429 | 1.463 | A01 | LINW0.05010016
Horizontal Wall | Linea Plus | LINW.05010016/DBE | 50 | 100 | 16 | 17 | 2911 | 2911 | 2911 | 0.06931 | 1456 | 0.034667 | 3202 | 0.076238 | 1 | A01 | LINW0.05010016/DBE
Horizontal Wall | Linea Plus | LINW.05010020 | 50 | 100 | 20 | 22 | 2120 | 2120 | 2120 | 0.050476 | 818 | 0.019476 | 2417 | 0.057548 | 1.373 | A01 | LINW0.05010020
Horizontal Wall | Linea Plus | LINW.05010021 | 50 | 100 | 21 | 22 | 2564 | 2564 | 2564 | 0.061048 | 915 | 0.021786 | 2954 | 0.070333 | 1.486 | A01 | LINW0.05010021
Horizontal Wall | Linea Plus | LINW.05010021/DBE | 50 | 100 | 21 | 22 | 3524 | 3524 | 3524 | 0.083905 | 1762 | 0.041952 | 3876 | 0.092286 | 1 | A01 | LINW0.05010021/DBE
Horizontal Wall | Linea Plus | LINW.05011010 | 50 | 110 | 10 | 12 | 1060 | 1060 | 1060 | 0.025238 | 401 | 0.0095476 | 1212 | 0.028857 | 1.402 | A01 | LINW0.05011010
Horizontal Wall | Linea Plus | LINW.05011011 | 50 | 110 | 11 | 12 | 1440 | 1440 | 1440 | 0.034286 | 526 | 0.012524 | 1655 | 0.039405 | 1.455 | A01 | LINW0.05011011
Horizontal Wall | Linea Plus | LINW.05011011/DBE | 50 | 110 | 11 | 12 | 2040 | 2040 | 2040 | 0.048571 | 1020 | 0.024286 | 2244 | 0.053429 | 1 | A01 | LINW0.05011011/DBE
Horizontal Wall | Linea Plus | LINW.05011015 | 50 | 110 | 15 | 17 | 1686 | 1686 | 1686 | 0.040143 | 651 | 0.0155 | 1922 | 0.045762 | 1.372 | A01 | LINW0.05011015
Horizontal Wall | Linea Plus | LINW.05011016 | 50 | 110 | 16 | 17 | 2146 | 2146 | 2146 | 0.051095 | 779 | 0.018548 | 2468 | 0.058762 | 1.463 | A01 | LINW0.05011016
Horizontal Wall | Linea Plus | LINW.05011016/DBE | 50 | 110 | 16 | 17 | 3106 | 3106 | 3106 | 0.073952 | 1553 | 0.036976 | 3417 | 0.081357 | 1 | A01 | LINW0.05011016/DBE
Horizontal Wall | Linea Plus | LINW.05011020 | 50 | 110 | 20 | 22 | 2332 | 2332 | 2332 | 0.055524 | 900 | 0.021429 | 2658 | 0.063286 | 1.373 | A01 | LINW0.05011020
Horizontal Wall | Linea Plus | LINW.05011021 | 50 | 110 | 21 | 22 | 2820 | 2820 | 2820 | 0.067143 | 1007 | 0.023976 | 3249 | 0.077357 | 1.486 | A01 | LINW0.05011021
Horizontal Wall | Linea Plus | LINW.05011021/DBE | 50 | 110 | 21 | 22 | 3780 | 3780 | 3780 | 0.09 | 1890 | 0.045 | 4158 | 0.099 | 1 | A01 | LINW0.05011021/DBE
Horizontal Wall | Linea Plus | LINW.05012010 | 50 | 120 | 10 | 12 | 1157 | 1157 | 1157 | 0.027548 | 437 | 0.010405 | 1322 | 0.031476 | 1.402 | A01 | LINW0.05012010
Horizontal Wall | Linea Plus | LINW.05012011 | 50 | 120 | 11 | 12 | 1571 | 1571 | 1571 | 0.037405 | 573 | 0.013643 | 1805 | 0.042976 | 1.455 | A01 | LINW0.05012011
Horizontal Wall | Linea Plus | LINW.05012011/DBE | 50 | 120 | 11 | 12 | 2171 | 2171 | 2171 | 0.05169 | 1086 | 0.025857 | 2388 | 0.056857 | 1 | A01 | LINW0.05012011/DBE
Horizontal Wall | Linea Plus | LINW.05012015 | 50 | 120 | 15 | 17 | 1840 | 1840 | 1840 | 0.04381 | 710 | 0.016905 | 2098 | 0.049952 | 1.372 | A01 | LINW0.05012015
Horizontal Wall | Linea Plus | LINW.05012016 | 50 | 120 | 16 | 17 | 2341 | 2341 | 2341 | 0.055738 | 850 | 0.020238 | 2692 | 0.064095 | 1.463 | A01 | LINW0.05012016
Horizontal Wall | Linea Plus | LINW.05012016/DBE | 50 | 120 | 16 | 17 | 3301 | 3301 | 3301 | 0.078595 | 1651 | 0.03931 | 3631 | 0.086452 | 1 | A01 | LINW0.05012016/DBE
Horizontal Wall | Linea Plus | LINW.05012020 | 50 | 120 | 20 | 22 | 2544 | 2544 | 2544 | 0.060571 | 982 | 0.023381 | 2900 | 0.069048 | 1.373 | A01 | LINW0.05012020
Horizontal Wall | Linea Plus | LINW.05012021 | 50 | 120 | 21 | 22 | 3077 | 3077 | 3077 | 0.073262 | 1098 | 0.026143 | 3545 | 0.084405 | 1.486 | A01 | LINW0.05012021
Horizontal Wall | Linea Plus | LINW.05012021/DBE | 50 | 120 | 21 | 22 | 4037 | 4037 | 4037 | 0.096119 | 2019 | 0.048071 | 4441 | 0.10574 | 1 | A01 | LINW0.05012021/DBE
Horizontal Wall | Linea Plus | LINW.05014010 | 50 | 140 | 10 | 12 | 1350 | 1350 | 1350 | 0.032143 | 510 | 0.012143 | 1543 | 0.036738 | 1.402 | A01 | LINW0.05014010
Horizontal Wall | Linea Plus | LINW.05014011 | 50 | 140 | 11 | 12 | 1833 | 1833 | 1833 | 0.043643 | 669 | 0.015929 | 2106 | 0.050143 | 1.455 | A01 | LINW0.05014011
Horizontal Wall | Linea Plus | LINW.05014011/DBE | 50 | 140 | 11 | 12 | 2433 | 2433 | 2433 | 0.057929 | 1217 | 0.028976 | 2676 | 0.063714 | 1 | A01 | LINW0.05014011/DBE
Horizontal Wall | Linea Plus | LINW.05014015 | 50 | 140 | 15 | 17 | 2146 | 2146 | 2146 | 0.051095 | 828 | 0.019714 | 2446 | 0.058238 | 1.372 | A01 | LINW0.05014015
Horizontal Wall | Linea Plus | LINW.05014016 | 50 | 140 | 16 | 17 | 2731 | 2731 | 2731 | 0.065024 | 991 | 0.023595 | 3141 | 0.074786 | 1.463 | A01 | LINW0.05014016
Horizontal Wall | Linea Plus | LINW.05014016/DBE | 50 | 140 | 16 | 17 | 3691 | 3691 | 3691 | 0.087881 | 1846 | 0.043952 | 4060 | 0.096667 | 1 | A01 | LINW0.05014016/DBE
Horizontal Wall | Linea Plus | LINW.05014020 | 50 | 140 | 20 | 22 | 2968 | 2968 | 2968 | 0.070667 | 1146 | 0.027286 | 3384 | 0.080571 | 1.373 | A01 | LINW0.05014020
Horizontal Wall | Linea Plus | LINW.05014021 | 50 | 140 | 21 | 22 | 3590 | 3590 | 3590 | 0.085476 | 1282 | 0.030524 | 4136 | 0.098476 | 1.486 | A01 | LINW0.05014021
Horizontal Wall | Linea Plus | LINW.05014021/DBE | 50 | 140 | 21 | 22 | 4550 | 4550 | 4550 | 0.10833 | 2275 | 0.054167 | 5005 | 0.11917 | 1 | A01 | LINW0.05014021/DBE
Horizontal Wall | Linea Plus | LINW.05016010 | 50 | 160 | 10 | 12 | 1542 | 1542 | 1542 | 0.036714 | 583 | 0.013881 | 1763 | 0.041976 | 1.402 | A01 | LINW0.05016010
Horizontal Wall | Linea Plus | LINW.05016011 | 50 | 160 | 11 | 12 | 2094 | 2094 | 2094 | 0.049857 | 764 | 0.01819 | 2406 | 0.057286 | 1.455 | A01 | LINW0.05016011
Horizontal Wall | Linea Plus | LINW.05016011/DBE | 50 | 160 | 11 | 12 | 3294 | 3294 | 3294 | 0.078429 | 1647 | 0.039214 | 3623 | 0.086262 | 1 | A01 | LINW0.05016011/DBE
Horizontal Wall | Linea Plus | LINW.05016015 | 50 | 160 | 15 | 17 | 2453 | 2453 | 2453 | 0.058405 | 947 | 0.022548 | 2796 | 0.066571 | 1.372 | A01 | LINW0.05016015
Horizontal Wall | Linea Plus | LINW.05016016 | 50 | 160 | 16 | 17 | 3122 | 3122 | 3122 | 0.074333 | 1133 | 0.026976 | 3590 | 0.085476 | 1.463 | A01 | LINW0.05016016
Horizontal Wall | Linea Plus | LINW.05016016/DBE | 50 | 160 | 16 | 17 | 5042 | 5042 | 5042 | 0.12005 | 2521 | 0.060024 | 5546 | 0.13205 | 1 | A01 | LINW0.05016016/DBE
Horizontal Wall | Linea Plus | LINW.05016020 | 50 | 160 | 20 | 22 | 3392 | 3392 | 3392 | 0.080762 | 1309 | 0.031167 | 3867 | 0.092071 | 1.373 | A01 | LINW0.05016020
Horizontal Wall | Linea Plus | LINW.05016021 | 50 | 160 | 21 | 22 | 4102 | 4102 | 4102 | 0.097667 | 1464 | 0.034857 | 4726 | 0.11252 | 1.486 | A01 | LINW0.05016021
Horizontal Wall | Linea Plus | LINW.05016021/DBE | 50 | 160 | 21 | 22 | 6022 | 6022 | 6022 | 0.14338 | 3011 | 0.07169 | 6624 | 0.15771 | 1 | A01 | LINW0.05016021/DBE
Horizontal Wall | Linea Plus | LINW.05018010 | 50 | 180 | 10 | 12 | 1735 | 1735 | 1735 | 0.04131 | 656 | 0.015619 | 1983 | 0.047214 | 1.402 | A01 | LINW0.05018010
Horizontal Wall | Linea Plus | LINW.05018011 | 50 | 180 | 11 | 12 | 2356 | 2356 | 2356 | 0.056095 | 860 | 0.020476 | 2707 | 0.064452 | 1.455 | A01 | LINW0.05018011
Horizontal Wall | Linea Plus | LINW.05018011/DBE | 50 | 180 | 11 | 12 | 3556 | 3556 | 3556 | 0.084667 | 1778 | 0.042333 | 3912 | 0.093143 | 1 | A01 | LINW0.05018011/DBE
Horizontal Wall | Linea Plus | LINW.05018015 | 50 | 180 | 15 | 17 | 2759 | 2759 | 2759 | 0.06569 | 1065 | 0.025357 | 3145 | 0.074881 | 1.372 | A01 | LINW0.05018015
Horizontal Wall | Linea Plus | LINW.05018016 | 50 | 180 | 16 | 17 | 3512 | 3512 | 3512 | 0.083619 | 1275 | 0.030357 | 4039 | 0.096167 | 1.463 | A01 | LINW0.05018016
Horizontal Wall | Linea Plus | LINW.05018016/DBE | 50 | 180 | 16 | 17 | 5432 | 5432 | 5432 | 0.12933 | 2716 | 0.064667 | 5975 | 0.14226 | 1 | A01 | LINW0.05018016/DBE
Horizontal Wall | Linea Plus | LINW.05018020 | 50 | 180 | 20 | 22 | 3816 | 3816 | 3816 | 0.090857 | 1473 | 0.035071 | 4350 | 0.10357 | 1.373 | A01 | LINW0.05018020
Horizontal Wall | Linea Plus | LINW.05018021 | 50 | 180 | 21 | 22 | 4615 | 4615 | 4615 | 0.10988 | 1648 | 0.039238 | 5316 | 0.12657 | 1.486 | A01 | LINW0.05018021
Horizontal Wall | Linea Plus | LINW.05018021/DBE | 50 | 180 | 21 | 22 | 6535 | 6535 | 6535 | 0.1556 | 3268 | 0.07781 | 7189 | 0.17117 | 1 | A01 | LINW0.05018021/DBE
Horizontal Wall | Linea Plus | LINW.05020010 | 50 | 200 | 10 | 12 | 1928 | 1928 | 1928 | 0.045905 | 729 | 0.017357 | 2204 | 0.052476 | 1.402 | A01 | LINW0.05020010
Horizontal Wall | Linea Plus | LINW.05020011 | 50 | 200 | 11 | 12 | 2618 | 2618 | 2618 | 0.062333 | 956 | 0.022762 | 3008 | 0.071619 | 1.455 | A01 | LINW0.05020011
Horizontal Wall | Linea Plus | LINW.05020011/DBE | 50 | 200 | 11 | 12 | 3818 | 3818 | 3818 | 0.090905 | 1909 | 0.045452 | 4200 | 0.1 | 1 | A01 | LINW0.05020011/DBE
Horizontal Wall | Linea Plus | LINW.05020015 | 50 | 200 | 15 | 17 | 3066 | 3066 | 3066 | 0.073 | 1183 | 0.028167 | 3495 | 0.083214 | 1.372 | A01 | LINW0.05020015
Horizontal Wall | Linea Plus | LINW.05020016 | 50 | 200 | 16 | 17 | 3902 | 3902 | 3902 | 0.092905 | 1416 | 0.033714 | 4487 | 0.10683 | 1.463 | A01 | LINW0.05020016
Horizontal Wall | Linea Plus | LINW.05020016/DBE | 50 | 200 | 16 | 17 | 5822 | 5822 | 5822 | 0.13862 | 2911 | 0.06931 | 6404 | 0.15248 | 1 | A01 | LINW0.05020016/DBE
Horizontal Wall | Linea Plus | LINW.05020020 | 50 | 200 | 20 | 22 | 4240 | 4240 | 4240 | 0.10095 | 1637 | 0.038976 | 4834 | 0.1151 | 1.373 | A01 | LINW0.05020020
Horizontal Wall | Linea Plus | LINW.05020021 | 50 | 200 | 21 | 22 | 5128 | 5128 | 5128 | 0.1221 | 1831 | 0.043595 | 5907 | 0.14064 | 1.486 | A01 | LINW0.05020021
Horizontal Wall | Linea Plus | LINW.05020021/DBE | 50 | 200 | 21 | 22 | 7048 | 7048 | 7048 | 0.16781 | 3524 | 0.083905 | 7753 | 0.1846 | 1 | A01 | LINW0.05020021/DBE
Horizontal Wall | Linea Plus | LINW.05022010 | 50 | 220 | 10 | 12 | 2121 | 2121 | 2121 | 0.0505 | 802 | 0.019095 | 2424 | 0.057714 | 1.402 | A01 | LINW0.05022010
Horizontal Wall | Linea Plus | LINW.05022011 | 50 | 220 | 11 | 12 | 2880 | 2880 | 2880 | 0.068571 | 1051 | 0.025024 | 3309 | 0.078786 | 1.455 | A01 | LINW0.05022011
Horizontal Wall | Linea Plus | LINW.05022011/DBE | 50 | 220 | 11 | 12 | 4080 | 4080 | 4080 | 0.097143 | 2040 | 0.048571 | 4488 | 0.10686 | 1 | A01 | LINW0.05022011/DBE
Horizontal Wall | Linea Plus | LINW.05022015 | 50 | 220 | 15 | 17 | 3373 | 3373 | 3373 | 0.08031 | 1302 | 0.031 | 3845 | 0.091548 | 1.372 | A01 | LINW0.05022015
Horizontal Wall | Linea Plus | LINW.05022016 | 50 | 220 | 16 | 17 | 4292 | 4292 | 4292 | 0.10219 | 1558 | 0.037095 | 4936 | 0.11752 | 1.463 | A01 | LINW0.05022016
Horizontal Wall | Linea Plus | LINW.05022016/DBE | 50 | 220 | 16 | 17 | 6212 | 6212 | 6212 | 0.1479 | 3106 | 0.073952 | 6833 | 0.16269 | 1 | A01 | LINW0.05022016/DBE
Horizontal Wall | Linea Plus | LINW.05022020 | 50 | 220 | 20 | 22 | 4664 | 4664 | 4664 | 0.11105 | 1800 | 0.042857 | 5317 | 0.1266 | 1.373 | A01 | LINW0.05022020
Horizontal Wall | Linea Plus | LINW.05022021 | 50 | 220 | 21 | 22 | 5641 | 5641 | 5641 | 0.13431 | 2014 | 0.047952 | 6498 | 0.15471 | 1.486 | A01 | LINW0.05022021
Horizontal Wall | Linea Plus | LINW.05022021/DBE | 50 | 220 | 21 | 22 | 7561 | 7561 | 7561 | 0.18002 | 3781 | 0.090024 | 8317 | 0.19802 | 1 | A01 | LINW0.05022021/DBE
Horizontal Wall | Linea Plus | LINW.05024010 | 50 | 240 | 10 | 12 | 2314 | 2314 | 2314 | 0.055095 | 875 | 0.020833 | 2645 | 0.062976 | 1.402 | A01 | LINW0.05024010
Horizontal Wall | Linea Plus | LINW.05024011 | 50 | 240 | 11 | 12 | 3142 | 3142 | 3142 | 0.07481 | 1147 | 0.02731 | 3610 | 0.085952 | 1.455 | A01 | LINW0.05024011
Horizontal Wall | Linea Plus | LINW.05024011/DBE | 50 | 240 | 11 | 12 | 4942 | 4942 | 4942 | 0.11767 | 2471 | 0.058833 | 5436 | 0.12943 | 1 | A01 | LINW0.05024011/DBE
Horizontal Wall | Linea Plus | LINW.05024015 | 50 | 240 | 15 | 17 | 3679 | 3679 | 3679 | 0.087595 | 1420 | 0.03381 | 4194 | 0.099857 | 1.372 | A01 | LINW0.05024015
Horizontal Wall | Linea Plus | LINW.05024016 | 50 | 240 | 16 | 17 | 4682 | 4682 | 4682 | 0.11148 | 1700 | 0.040476 | 5384 | 0.12819 | 1.463 | A01 | LINW0.05024016
Horizontal Wall | Linea Plus | LINW.05024016/DBE | 50 | 240 | 16 | 17 | 7562 | 7562 | 7562 | 0.18005 | 3781 | 0.090024 | 8318 | 0.19805 | 1 | A01 | LINW0.05024016/DBE
Horizontal Wall | Linea Plus | LINW.05024020 | 50 | 240 | 20 | 22 | 5088 | 5088 | 5088 | 0.12114 | 1964 | 0.046762 | 5800 | 0.1381 | 1.373 | A01 | LINW0.05024020
Horizontal Wall | Linea Plus | LINW.05024021 | 50 | 240 | 21 | 22 | 6154 | 6154 | 6154 | 0.14652 | 2197 | 0.05231 | 7089 | 0.16879 | 1.486 | A01 | LINW0.05024021
Horizontal Wall | Linea Plus | LINW.05024021/DBE | 50 | 240 | 21 | 22 | 9034 | 9034 | 9034 | 0.2151 | 4517 | 0.10755 | 9937 | 0.2366 | 1 | A01 | LINW0.05024021/DBE
Horizontal Wall | Linea Plus | LINW.05026010 | 50 | 260 | 10 | 12 | 2506 | 2506 | 2506 | 0.059667 | 947 | 0.022548 | 2864 | 0.06819 | 1.402 | A01 | LINW0.05026010
Horizontal Wall | Linea Plus | LINW.05026011 | 50 | 260 | 11 | 12 | 3403 | 3403 | 3403 | 0.081024 | 1242 | 0.029571 | 3910 | 0.093095 | 1.455 | A01 | LINW0.05026011
Horizontal Wall | Linea Plus | LINW.05026011/DBE | 50 | 260 | 11 | 12 | 5203 | 5203 | 5203 | 0.12388 | 2602 | 0.061952 | 5723 | 0.13626 | 1 | A01 | LINW0.05026011/DBE
Horizontal Wall | Linea Plus | LINW.05026015 | 50 | 260 | 15 | 17 | 3986 | 3986 | 3986 | 0.094905 | 1539 | 0.036643 | 4544 | 0.10819 | 1.372 | A01 | LINW0.05026015
Horizontal Wall | Linea Plus | LINW.05026016 | 50 | 260 | 16 | 17 | 5073 | 5073 | 5073 | 0.12079 | 1841 | 0.043833 | 5834 | 0.1389 | 1.463 | A01 | LINW0.05026016
Horizontal Wall | Linea Plus | LINW.05026016/DBE | 50 | 260 | 16 | 17 | 7953 | 7953 | 7953 | 0.18936 | 3977 | 0.09469 | 8748 | 0.20829 | 1 | A01 | LINW0.05026016/DBE
Horizontal Wall | Linea Plus | LINW.05026020 | 50 | 260 | 20 | 22 | 5512 | 5512 | 5512 | 0.13124 | 2128 | 0.050667 | 6284 | 0.14962 | 1.373 | A01 | LINW0.05026020
Horizontal Wall | Linea Plus | LINW.05026021 | 50 | 260 | 21 | 22 | 6666 | 6666 | 6666 | 0.15871 | 2380 | 0.056667 | 7679 | 0.18283 | 1.486 | A01 | LINW0.05026021
Horizontal Wall | Linea Plus | LINW.05026021/DBE | 50 | 260 | 21 | 22 | 9546 | 9546 | 9546 | 0.22729 | 4773 | 0.11364 | 10501 | 0.25002 | 1 | A01 | LINW0.05026021/DBE
Horizontal Wall | Linea Plus | LINW.05028010 | 50 | 280 | 10 | 12 | 2699 | 2699 | 2699 | 0.064262 | 1020 | 0.024286 | 3085 | 0.073452 | 1.402 | A01 | LINW0.05028010
Horizontal Wall | Linea Plus | LINW.05028011 | 50 | 280 | 11 | 12 | 3665 | 3665 | 3665 | 0.087262 | 1338 | 0.031857 | 4211 | 0.10026 | 1.455 | A01 | LINW0.05028011
Horizontal Wall | Linea Plus | LINW.05028011/DBE | 50 | 280 | 11 | 12 | 5465 | 5465 | 5465 | 0.13012 | 2733 | 0.065071 | 6012 | 0.14314 | 1 | A01 | LINW0.05028011/DBE
Horizontal Wall | Linea Plus | LINW.05028015 | 50 | 280 | 15 | 17 | 4292 | 4292 | 4292 | 0.10219 | 1657 | 0.039452 | 4893 | 0.1165 | 1.372 | A01 | LINW0.05028015
Horizontal Wall | Linea Plus | LINW.05028016 | 50 | 280 | 16 | 17 | 5463 | 5463 | 5463 | 0.13007 | 1983 | 0.047214 | 6282 | 0.14957 | 1.463 | A01 | LINW0.05028016
Horizontal Wall | Linea Plus | LINW.05028016/DBE | 50 | 280 | 16 | 17 | 8343 | 8343 | 8343 | 0.19864 | 4172 | 0.099333 | 9177 | 0.2185 | 1 | A01 | LINW0.05028016/DBE
Horizontal Wall | Linea Plus | LINW.05028020 | 50 | 280 | 20 | 22 | 5936 | 5936 | 5936 | 0.14133 | 2291 | 0.054548 | 6767 | 0.16112 | 1.373 | A01 | LINW0.05028020
Horizontal Wall | Linea Plus | LINW.05028021 | 50 | 280 | 21 | 22 | 7179 | 7179 | 7179 | 0.17093 | 2563 | 0.061024 | 8270 | 0.1969 | 1.486 | A01 | LINW0.05028021
Horizontal Wall | Linea Plus | LINW.05028021/DBE | 50 | 280 | 21 | 22 | 10059 | 10059 | 10059 | 0.2395 | 5030 | 0.11976 | 11065 | 0.26345 | 1 | A01 | LINW0.05028021/DBE
Horizontal Wall | Linea Plus | LINW.06505010 | 65 | 50 | 10 | 12 | 561 | 561 | 561 | 0.013357 | 215 | 0.005119 | 640 | 0.015238 | 1.385 | A01 | LINW0.06505010
Horizontal Wall | Linea Plus | LINW.06505011 | 65 | 50 | 11 | 12 | 742 | 742 | 742 | 0.017667 | 272 | 0.0064762 | 852 | 0.020286 | 1.45 | A01 | LINW0.06505011
Horizontal Wall | Linea Plus | LINW.06505015 | 65 | 50 | 15 | 17 | 858 | 858 | 858 | 0.020429 | 338 | 0.0080476 | 976 | 0.023238 | 1.345 | A01 | LINW0.06505015
Horizontal Wall | Linea Plus | LINW.06505016 | 65 | 50 | 16 | 17 | 1114 | 1114 | 1114 | 0.026524 | 404 | 0.009619 | 1280 | 0.030476 | 1.46 | A01 | LINW0.06505016
Horizontal Wall | Linea Plus | LINW.06505020 | 65 | 50 | 20 | 22 | 1196 | 1196 | 1196 | 0.028476 | 470 | 0.01119 | 1360 | 0.032381 | 1.348 | A01 | LINW0.06505020
Horizontal Wall | Linea Plus | LINW.06505021 | 65 | 50 | 21 | 22 | 1503 | 1503 | 1503 | 0.035786 | 535 | 0.012738 | 1733 | 0.041262 | 1.49 | A01 | LINW0.06505021
Horizontal Wall | Linea Plus | LINW.06506010 | 65 | 60 | 10 | 12 | 673 | 673 | 673 | 0.016024 | 258 | 0.0061429 | 768 | 0.018286 | 1.385 | A01 | LINW0.06506010
Horizontal Wall | Linea Plus | LINW.06506011 | 65 | 60 | 11 | 12 | 890 | 890 | 890 | 0.02119 | 326 | 0.0077619 | 1022 | 0.024333 | 1.45 | A01 | LINW0.06506011
Horizontal Wall | Linea Plus | LINW.06506011/DBE | 65 | 60 | 11 | 12 | 1190 | 1190 | 1190 | 0.028333 | 595 | 0.014167 | 1309 | 0.031167 | 1 | A01 | LINW0.06506011/DBE
Horizontal Wall | Linea Plus | LINW.06506015 | 65 | 60 | 15 | 17 | 1029 | 1029 | 1029 | 0.0245 | 405 | 0.0096429 | 1170 | 0.027857 | 1.345 | A01 | LINW0.06506015
Horizontal Wall | Linea Plus | LINW.06506016 | 65 | 60 | 16 | 17 | 1336 | 1336 | 1336 | 0.03181 | 485 | 0.011548 | 1535 | 0.036548 | 1.46 | A01 | LINW0.06506016
Horizontal Wall | Linea Plus | LINW.06506016/DBE | 65 | 60 | 16 | 17 | 1816 | 1816 | 1816 | 0.043238 | 908 | 0.021619 | 1998 | 0.047571 | 1 | A01 | LINW0.06506016/DBE
Horizontal Wall | Linea Plus | LINW.06506020 | 65 | 60 | 20 | 22 | 1435 | 1435 | 1435 | 0.034167 | 564 | 0.013429 | 1632 | 0.038857 | 1.348 | A01 | LINW0.06506020
Horizontal Wall | Linea Plus | LINW.06506021 | 65 | 60 | 21 | 22 | 1803 | 1803 | 1803 | 0.042929 | 642 | 0.015286 | 2079 | 0.0495 | 1.49 | A01 | LINW0.06506021
Horizontal Wall | Linea Plus | LINW.06506021/DBE | 65 | 60 | 21 | 22 | 2283 | 2283 | 2283 | 0.054357 | 1142 | 0.02719 | 2511 | 0.059786 | 1 | A01 | LINW0.06506021/DBE
Horizontal Wall | Linea Plus | LINW.06507010 | 65 | 70 | 10 | 12 | 785 | 785 | 785 | 0.01869 | 301 | 0.0071667 | 896 | 0.021333 | 1.385 | A01 | LINW0.06507010
Horizontal Wall | Linea Plus | LINW.06507011 | 65 | 70 | 11 | 12 | 1038 | 1038 | 1038 | 0.024714 | 380 | 0.0090476 | 1192 | 0.028381 | 1.45 | A01 | LINW0.06507011
Horizontal Wall | Linea Plus | LINW.06507011/DBE | 65 | 70 | 11 | 12 | 1338 | 1338 | 1338 | 0.031857 | 669 | 0.015929 | 1472 | 0.035048 | 1 | A01 | LINW0.06507011/DBE
Horizontal Wall | Linea Plus | LINW.06507015 | 65 | 70 | 15 | 17 | 1201 | 1201 | 1201 | 0.028595 | 473 | 0.011262 | 1366 | 0.032524 | 1.345 | A01 | LINW0.06507015
Horizontal Wall | Linea Plus | LINW.06507016 | 65 | 70 | 16 | 17 | 1559 | 1559 | 1559 | 0.037119 | 566 | 0.013476 | 1791 | 0.042643 | 1.46 | A01 | LINW0.06507016
Horizontal Wall | Linea Plus | LINW.06507016/DBE | 65 | 70 | 16 | 17 | 2039 | 2039 | 2039 | 0.048548 | 1020 | 0.024286 | 2243 | 0.053405 | 1 | A01 | LINW0.06507016/DBE
Horizontal Wall | Linea Plus | LINW.06507020 | 65 | 70 | 20 | 22 | 1674 | 1674 | 1674 | 0.039857 | 658 | 0.015667 | 1903 | 0.04531 | 1.348 | A01 | LINW0.06507020
Horizontal Wall | Linea Plus | LINW.06507021 | 65 | 70 | 21 | 22 | 2104 | 2104 | 2104 | 0.050095 | 749 | 0.017833 | 2426 | 0.057762 | 1.49 | A01 | LINW0.06507021
Horizontal Wall | Linea Plus | LINW.06507021/DBE | 65 | 70 | 21 | 22 | 2584 | 2584 | 2584 | 0.061524 | 1292 | 0.030762 | 2842 | 0.067667 | 1 | A01 | LINW0.06507021/DBE
Horizontal Wall | Linea Plus | LINW.06508010 | 65 | 80 | 10 | 12 | 897 | 897 | 897 | 0.021357 | 344 | 0.0081905 | 1023 | 0.024357 | 1.385 | A01 | LINW0.06508010
Horizontal Wall | Linea Plus | LINW.06508011 | 65 | 80 | 11 | 12 | 1186 | 1186 | 1186 | 0.028238 | 434 | 0.010333 | 1362 | 0.032429 | 1.45 | A01 | LINW0.06508011
Horizontal Wall | Linea Plus | LINW.06508011/DBE | 65 | 80 | 11 | 12 | 1486 | 1486 | 1486 | 0.035381 | 743 | 0.01769 | 1635 | 0.038929 | 1 | A01 | LINW0.06508011/DBE
Horizontal Wall | Linea Plus | LINW.06508015 | 65 | 80 | 15 | 17 | 1372 | 1372 | 1372 | 0.032667 | 541 | 0.012881 | 1560 | 0.037143 | 1.345 | A01 | LINW0.06508015
Horizontal Wall | Linea Plus | LINW.06508016 | 65 | 80 | 16 | 17 | 1782 | 1782 | 1782 | 0.042429 | 647 | 0.015405 | 2048 | 0.048762 | 1.46 | A01 | LINW0.06508016
Horizontal Wall | Linea Plus | LINW.06508016/DBE | 65 | 80 | 16 | 17 | 2262 | 2262 | 2262 | 0.053857 | 1131 | 0.026929 | 2488 | 0.059238 | 1 | A01 | LINW0.06508016/DBE
Horizontal Wall | Linea Plus | LINW.06508020 | 65 | 80 | 20 | 22 | 1913 | 1913 | 1913 | 0.045548 | 752 | 0.017905 | 2175 | 0.051786 | 1.348 | A01 | LINW0.06508020
Horizontal Wall | Linea Plus | LINW.06508021 | 65 | 80 | 21 | 22 | 2404 | 2404 | 2404 | 0.057238 | 856 | 0.020381 | 2772 | 0.066 | 1.49 | A01 | LINW0.06508021
Horizontal Wall | Linea Plus | LINW.06508021/DBE | 65 | 80 | 21 | 22 | 2884 | 2884 | 2884 | 0.068667 | 1442 | 0.034333 | 3172 | 0.075524 | 1 | A01 | LINW0.06508021/DBE
Horizontal Wall | Linea Plus | LINW.06509010 | 65 | 90 | 10 | 12 | 1009 | 1009 | 1009 | 0.024024 | 386 | 0.0091905 | 1151 | 0.027405 | 1.385 | A01 | LINW0.06509010
Horizontal Wall | Linea Plus | LINW.06509011 | 65 | 90 | 11 | 12 | 1335 | 1335 | 1335 | 0.031786 | 489 | 0.011643 | 1533 | 0.0365 | 1.45 | A01 | LINW0.06509011
Horizontal Wall | Linea Plus | LINW.06509011/DBE | 65 | 90 | 11 | 12 | 1935 | 1935 | 1935 | 0.046071 | 968 | 0.023048 | 2129 | 0.05069 | 1 | A01 | LINW0.06509011/DBE
Horizontal Wall | Linea Plus | LINW.06509015 | 65 | 90 | 15 | 17 | 1544 | 1544 | 1544 | 0.036762 | 608 | 0.014476 | 1756 | 0.04181 | 1.345 | A01 | LINW0.06509015
Horizontal Wall | Linea Plus | LINW.06509016 | 65 | 90 | 16 | 17 | 2004 | 2004 | 2004 | 0.047714 | 727 | 0.01731 | 2303 | 0.054833 | 1.46 | A01 | LINW0.06509016
Horizontal Wall | Linea Plus | LINW.06509016/DBE | 65 | 90 | 16 | 17 | 2964 | 2964 | 2964 | 0.070571 | 1482 | 0.035286 | 3260 | 0.077619 | 1 | A01 | LINW0.06509016/DBE
Horizontal Wall | Linea Plus | LINW.06509020 | 65 | 90 | 20 | 22 | 2152 | 2152 | 2152 | 0.051238 | 846 | 0.020143 | 2447 | 0.058262 | 1.348 | A01 | LINW0.06509020
Horizontal Wall | Linea Plus | LINW.06509021 | 65 | 90 | 21 | 22 | 2705 | 2705 | 2705 | 0.064405 | 963 | 0.022929 | 3119 | 0.074262 | 1.49 | A01 | LINW0.06509021
Horizontal Wall | Linea Plus | LINW.06509021/DBE | 65 | 90 | 21 | 22 | 3665 | 3665 | 3665 | 0.087262 | 1833 | 0.043643 | 4032 | 0.096 | 1 | A01 | LINW0.06509021/DBE
Horizontal Wall | Linea Plus | LINW.06510010 | 65 | 100 | 10 | 12 | 1121 | 1121 | 1121 | 0.02669 | 429 | 0.010214 | 1279 | 0.030452 | 1.385 | A01 | LINW0.06510010
Horizontal Wall | Linea Plus | LINW.06510011 | 65 | 100 | 11 | 12 | 1483 | 1483 | 1483 | 0.03531 | 543 | 0.012929 | 1702 | 0.040524 | 1.45 | A01 | LINW0.06510011
Horizontal Wall | Linea Plus | LINW.06510011/DBE | 65 | 100 | 11 | 12 | 2083 | 2083 | 2083 | 0.049595 | 1042 | 0.02481 | 2291 | 0.054548 | 1 | A01 | LINW0.06510011/DBE
Horizontal Wall | Linea Plus | LINW.06510015 | 65 | 100 | 15 | 17 | 1715 | 1715 | 1715 | 0.040833 | 676 | 0.016095 | 1950 | 0.046429 | 1.345 | A01 | LINW0.06510015
Horizontal Wall | Linea Plus | LINW.06510016 | 65 | 100 | 16 | 17 | 2227 | 2227 | 2227 | 0.053024 | 808 | 0.019238 | 2559 | 0.060929 | 1.46 | A01 | LINW0.06510016
Horizontal Wall | Linea Plus | LINW.06510016/DBE | 65 | 100 | 16 | 17 | 3187 | 3187 | 3187 | 0.075881 | 1594 | 0.037952 | 3506 | 0.083476 | 1 | A01 | LINW0.06510016/DBE
Horizontal Wall | Linea Plus | LINW.06510020 | 65 | 100 | 20 | 22 | 2391 | 2391 | 2391 | 0.056929 | 940 | 0.022381 | 2719 | 0.064738 | 1.348 | A01 | LINW0.06510020
Horizontal Wall | Linea Plus | LINW.06510021 | 65 | 100 | 21 | 22 | 3005 | 3005 | 3005 | 0.071548 | 1070 | 0.025476 | 3465 | 0.0825 | 1.49 | A01 | LINW0.06510021
Horizontal Wall | Linea Plus | LINW.06510021/DBE | 65 | 100 | 21 | 22 | 3965 | 3965 | 3965 | 0.094405 | 1983 | 0.047214 | 4362 | 0.10386 | 1 | A01 | LINW0.06510021/DBE
Horizontal Wall | Linea Plus | LINW.06511010 | 65 | 110 | 10 | 12 | 1233 | 1233 | 1233 | 0.029357 | 472 | 0.011238 | 1407 | 0.0335 | 1.385 | A01 | LINW0.06511010
Horizontal Wall | Linea Plus | LINW.06511011 | 65 | 110 | 11 | 12 | 1631 | 1631 | 1631 | 0.038833 | 597 | 0.014214 | 1872 | 0.044571 | 1.45 | A01 | LINW0.06511011
Horizontal Wall | Linea Plus | LINW.06511011/DBE | 65 | 110 | 11 | 12 | 2231 | 2231 | 2231 | 0.053119 | 1116 | 0.026571 | 2454 | 0.058429 | 1 | A01 | LINW0.06511011/DBE
Horizontal Wall | Linea Plus | LINW.06511015 | 65 | 110 | 15 | 17 | 1887 | 1887 | 1887 | 0.044929 | 743 | 0.01769 | 2146 | 0.051095 | 1.345 | A01 | LINW0.06511015
Horizontal Wall | Linea Plus | LINW.06511016 | 65 | 110 | 16 | 17 | 2450 | 2450 | 2450 | 0.058333 | 889 | 0.021167 | 2815 | 0.067024 | 1.46 | A01 | LINW0.06511016
Horizontal Wall | Linea Plus | LINW.06511016/DBE | 65 | 110 | 16 | 17 | 3410 | 3410 | 3410 | 0.08119 | 1705 | 0.040595 | 3751 | 0.08931 | 1 | A01 | LINW0.06511016/DBE
Horizontal Wall | Linea Plus | LINW.06511020 | 65 | 110 | 20 | 22 | 2630 | 2630 | 2630 | 0.062619 | 1034 | 0.024619 | 2990 | 0.07119 | 1.348 | A01 | LINW0.06511020
Horizontal Wall | Linea Plus | LINW.06511021 | 65 | 110 | 21 | 22 | 3306 | 3306 | 3306 | 0.078714 | 1177 | 0.028024 | 3812 | 0.090762 | 1.49 | A01 | LINW0.06511021
Horizontal Wall | Linea Plus | LINW.06511021/DBE | 65 | 110 | 21 | 22 | 4266 | 4266 | 4266 | 0.10157 | 2133 | 0.050786 | 4693 | 0.11174 | 1 | A01 | LINW0.06511021/DBE
Horizontal Wall | Linea Plus | LINW.06512010 | 65 | 120 | 10 | 12 | 1345 | 1345 | 1345 | 0.032024 | 515 | 0.012262 | 1535 | 0.036548 | 1.385 | A01 | LINW0.06512010
Horizontal Wall | Linea Plus | LINW.06512011 | 65 | 120 | 11 | 12 | 1780 | 1780 | 1780 | 0.042381 | 651 | 0.0155 | 2043 | 0.048643 | 1.45 | A01 | LINW0.06512011
Horizontal Wall | Linea Plus | LINW.06512011/DBE | 65 | 120 | 11 | 12 | 2380 | 2380 | 2380 | 0.056667 | 1190 | 0.028333 | 2618 | 0.062333 | 1 | A01 | LINW0.06512011/DBE
Horizontal Wall | Linea Plus | LINW.06512015 | 65 | 120 | 15 | 17 | 2058 | 2058 | 2058 | 0.049 | 811 | 0.01931 | 2340 | 0.055714 | 1.345 | A01 | LINW0.06512015
Horizontal Wall | Linea Plus | LINW.06512016 | 65 | 120 | 16 | 17 | 2672 | 2672 | 2672 | 0.063619 | 970 | 0.023095 | 3070 | 0.073095 | 1.46 | A01 | LINW0.06512016
Horizontal Wall | Linea Plus | LINW.06512016/DBE | 65 | 120 | 16 | 17 | 3632 | 3632 | 3632 | 0.086476 | 1816 | 0.043238 | 3995 | 0.095119 | 1 | A01 | LINW0.06512016/DBE
Horizontal Wall | Linea Plus | LINW.06512020 | 65 | 120 | 20 | 22 | 2869 | 2869 | 2869 | 0.06831 | 1128 | 0.026857 | 3262 | 0.077667 | 1.348 | A01 | LINW0.06512020
Horizontal Wall | Linea Plus | LINW.06512021 | 65 | 120 | 21 | 22 | 3606 | 3606 | 3606 | 0.085857 | 1284 | 0.030571 | 4158 | 0.099 | 1.49 | A01 | LINW0.06512021
Horizontal Wall | Linea Plus | LINW.06512021/DBE | 65 | 120 | 21 | 22 | 4566 | 4566 | 4566 | 0.10871 | 2283 | 0.054357 | 5023 | 0.1196 | 1 | A01 | LINW0.06512021/DBE
Horizontal Wall | Linea Plus | LINW.06514010 | 65 | 140 | 10 | 12 | 1569 | 1569 | 1569 | 0.037357 | 601 | 0.01431 | 1790 | 0.042619 | 1.385 | A01 | LINW0.06514010
Horizontal Wall | Linea Plus | LINW.06514011 | 65 | 140 | 11 | 12 | 2076 | 2076 | 2076 | 0.049429 | 760 | 0.018095 | 2383 | 0.056738 | 1.45 | A01 | LINW0.06514011
Horizontal Wall | Linea Plus | LINW.06514011/DBE | 65 | 140 | 11 | 12 | 2676 | 2676 | 2676 | 0.063714 | 1338 | 0.031857 | 2944 | 0.070095 | 1 | A01 | LINW0.06514011/DBE
Horizontal Wall | Linea Plus | LINW.06514015 | 65 | 140 | 15 | 17 | 2401 | 2401 | 2401 | 0.057167 | 946 | 0.022524 | 2730 | 0.065 | 1.345 | A01 | LINW0.06514015
Horizontal Wall | Linea Plus | LINW.06514016 | 65 | 140 | 16 | 17 | 3118 | 3118 | 3118 | 0.074238 | 1132 | 0.026952 | 3583 | 0.08531 | 1.46 | A01 | LINW0.06514016
Horizontal Wall | Linea Plus | LINW.06514016/DBE | 65 | 140 | 16 | 17 | 4078 | 4078 | 4078 | 0.097095 | 2039 | 0.048548 | 4486 | 0.10681 | 1 | A01 | LINW0.06514016/DBE
Horizontal Wall | Linea Plus | LINW.06514020 | 65 | 140 | 20 | 22 | 3347 | 3347 | 3347 | 0.07969 | 1315 | 0.03131 | 3806 | 0.090619 | 1.348 | A01 | LINW0.06514020
Horizontal Wall | Linea Plus | LINW.06514021 | 65 | 140 | 21 | 22 | 4207 | 4207 | 4207 | 0.10017 | 1498 | 0.035667 | 4851 | 0.1155 | 1.49 | A01 | LINW0.06514021
Horizontal Wall | Linea Plus | LINW.06514021/DBE | 65 | 140 | 21 | 22 | 5167 | 5167 | 5167 | 0.12302 | 2584 | 0.061524 | 5684 | 0.13533 | 1 | A01 | LINW0.06514021/DBE
Horizontal Wall | Linea Plus | LINW.06516010 | 65 | 160 | 10 | 12 | 1794 | 1794 | 1794 | 0.042714 | 687 | 0.016357 | 2047 | 0.048738 | 1.385 | A01 | LINW0.06516010
Horizontal Wall | Linea Plus | LINW.06516011 | 65 | 160 | 11 | 12 | 2373 | 2373 | 2373 | 0.0565 | 869 | 0.02069 | 2724 | 0.064857 | 1.45 | A01 | LINW0.06516011
Horizontal Wall | Linea Plus | LINW.06516011/DBE | 65 | 160 | 11 | 12 | 3573 | 3573 | 3573 | 0.085071 | 1787 | 0.042548 | 3930 | 0.093571 | 1 | A01 | LINW0.06516011/DBE
Horizontal Wall | Linea Plus | LINW.06516015 | 65 | 160 | 15 | 17 | 2744 | 2744 | 2744 | 0.065333 | 1081 | 0.025738 | 3120 | 0.074286 | 1.345 | A01 | LINW0.06516015
Horizontal Wall | Linea Plus | LINW.06516016 | 65 | 160 | 16 | 17 | 3563 | 3563 | 3563 | 0.084833 | 1293 | 0.030786 | 4094 | 0.097476 | 1.46 | A01 | LINW0.06516016
Horizontal Wall | Linea Plus | LINW.06516016/DBE | 65 | 160 | 16 | 17 | 5483 | 5483 | 5483 | 0.13055 | 2742 | 0.065286 | 6031 | 0.1436 | 1 | A01 | LINW0.06516016/DBE
Horizontal Wall | Linea Plus | LINW.06516020 | 65 | 160 | 20 | 22 | 3826 | 3826 | 3826 | 0.091095 | 1504 | 0.03581 | 4350 | 0.10357 | 1.348 | A01 | LINW0.06516020
Horizontal Wall | Linea Plus | LINW.06516021 | 65 | 160 | 21 | 22 | 4808 | 4808 | 4808 | 0.11448 | 1712 | 0.040762 | 5544 | 0.132 | 1.49 | A01 | LINW0.06516021
Horizontal Wall | Linea Plus | LINW.06516021/DBE | 65 | 160 | 21 | 22 | 6728 | 6728 | 6728 | 0.16019 | 3364 | 0.080095 | 7401 | 0.17621 | 1 | A01 | LINW0.06516021/DBE
Horizontal Wall | Linea Plus | LINW.06518010 | 65 | 180 | 10 | 12 | 2018 | 2018 | 2018 | 0.048048 | 773 | 0.018405 | 2303 | 0.054833 | 1.385 | A01 | LINW0.06518010
Horizontal Wall | Linea Plus | LINW.06518011 | 65 | 180 | 11 | 12 | 2669 | 2669 | 2669 | 0.063548 | 977 | 0.023262 | 3064 | 0.072952 | 1.45 | A01 | LINW0.06518011
Horizontal Wall | Linea Plus | LINW.06518011/DBE | 65 | 180 | 11 | 12 | 3869 | 3869 | 3869 | 0.092119 | 1935 | 0.046071 | 4256 | 0.10133 | 1 | A01 | LINW0.06518011/DBE
Horizontal Wall | Linea Plus | LINW.06518015 | 65 | 180 | 15 | 17 | 3087 | 3087 | 3087 | 0.0735 | 1216 | 0.028952 | 3510 | 0.083571 | 1.345 | A01 | LINW0.06518015
Horizontal Wall | Linea Plus | LINW.06518016 | 65 | 180 | 16 | 17 | 4009 | 4009 | 4009 | 0.095452 | 1455 | 0.034643 | 4606 | 0.10967 | 1.46 | A01 | LINW0.06518016
Horizontal Wall | Linea Plus | LINW.06518016/DBE | 65 | 180 | 16 | 17 | 5929 | 5929 | 5929 | 0.14117 | 2965 | 0.070595 | 6522 | 0.15529 | 1 | A01 | LINW0.06518016/DBE
Horizontal Wall | Linea Plus | LINW.06518020 | 65 | 180 | 20 | 22 | 4304 | 4304 | 4304 | 0.10248 | 1691 | 0.040262 | 4894 | 0.11652 | 1.348 | A01 | LINW0.06518020
Horizontal Wall | Linea Plus | LINW.06518021 | 65 | 180 | 21 | 22 | 5409 | 5409 | 5409 | 0.12879 | 1926 | 0.045857 | 6237 | 0.1485 | 1.49 | A01 | LINW0.06518021
Horizontal Wall | Linea Plus | LINW.06518021/DBE | 65 | 180 | 21 | 22 | 7329 | 7329 | 7329 | 0.1745 | 3665 | 0.087262 | 8062 | 0.19195 | 1 | A01 | LINW0.06518021/DBE
Horizontal Wall | Linea Plus | LINW.06520010 | 65 | 200 | 10 | 12 | 2242 | 2242 | 2242 | 0.053381 | 859 | 0.020452 | 2558 | 0.060905 | 1.385 | A01 | LINW0.06520010
Horizontal Wall | Linea Plus | LINW.06520011 | 65 | 200 | 11 | 12 | 2966 | 2966 | 2966 | 0.070619 | 1086 | 0.025857 | 3405 | 0.081071 | 1.45 | A01 | LINW0.06520011
Horizontal Wall | Linea Plus | LINW.06520011/DBE | 65 | 200 | 11 | 12 | 4166 | 4166 | 4166 | 0.09919 | 2083 | 0.049595 | 4583 | 0.10912 | 1 | A01 | LINW0.06520011/DBE
Horizontal Wall | Linea Plus | LINW.06520015 | 65 | 200 | 15 | 17 | 3430 | 3430 | 3430 | 0.081667 | 1351 | 0.032167 | 3900 | 0.092857 | 1.345 | A01 | LINW0.06520015
Horizontal Wall | Linea Plus | LINW.06520016 | 65 | 200 | 16 | 17 | 4454 | 4454 | 4454 | 0.10605 | 1617 | 0.0385 | 5118 | 0.12186 | 1.46 | A01 | LINW0.06520016
Horizontal Wall | Linea Plus | LINW.06520016/DBE | 65 | 200 | 16 | 17 | 6374 | 6374 | 6374 | 0.15176 | 3187 | 0.075881 | 7011 | 0.16693 | 1 | A01 | LINW0.06520016/DBE
Horizontal Wall | Linea Plus | LINW.06520020 | 65 | 200 | 20 | 22 | 4782 | 4782 | 4782 | 0.11386 | 1879 | 0.044738 | 5437 | 0.12945 | 1.348 | A01 | LINW0.06520020
Horizontal Wall | Linea Plus | LINW.06520021 | 65 | 200 | 21 | 22 | 6010 | 6010 | 6010 | 0.1431 | 2140 | 0.050952 | 6930 | 0.165 | 1.49 | A01 | LINW0.06520021
Horizontal Wall | Linea Plus | LINW.06520021/DBE | 65 | 200 | 21 | 22 | 7930 | 7930 | 7930 | 0.18881 | 3965 | 0.094405 | 8723 | 0.20769 | 1 | A01 | LINW0.06520021/DBE
Horizontal Wall | Linea Plus | LINW.06522010 | 65 | 220 | 10 | 12 | 2466 | 2466 | 2466 | 0.058714 | 944 | 0.022476 | 2814 | 0.067 | 1.385 | A01 | LINW0.06522010
Horizontal Wall | Linea Plus | LINW.06522011 | 65 | 220 | 11 | 12 | 3263 | 3263 | 3263 | 0.07769 | 1194 | 0.028429 | 3746 | 0.08919 | 1.45 | A01 | LINW0.06522011
Horizontal Wall | Linea Plus | LINW.06522011/DBE | 65 | 220 | 11 | 12 | 4463 | 4463 | 4463 | 0.10626 | 2232 | 0.053143 | 4909 | 0.11688 | 1 | A01 | LINW0.06522011/DBE
Horizontal Wall | Linea Plus | LINW.06522015 | 65 | 220 | 15 | 17 | 3773 | 3773 | 3773 | 0.089833 | 1487 | 0.035405 | 4290 | 0.10214 | 1.345 | A01 | LINW0.06522015
Horizontal Wall | Linea Plus | LINW.06522016 | 65 | 220 | 16 | 17 | 4899 | 4899 | 4899 | 0.11664 | 1778 | 0.042333 | 5629 | 0.13402 | 1.46 | A01 | LINW0.06522016
Horizontal Wall | Linea Plus | LINW.06522016/DBE | 65 | 220 | 16 | 17 | 6819 | 6819 | 6819 | 0.16236 | 3410 | 0.08119 | 7501 | 0.1786 | 1 | A01 | LINW0.06522016/DBE
Horizontal Wall | Linea Plus | LINW.06522020 | 65 | 220 | 20 | 22 | 5260 | 5260 | 5260 | 0.12524 | 2067 | 0.049214 | 5981 | 0.1424 | 1.348 | A01 | LINW0.06522020
Horizontal Wall | Linea Plus | LINW.06522021 | 65 | 220 | 21 | 22 | 6611 | 6611 | 6611 | 0.1574 | 2354 | 0.056048 | 7622 | 0.18148 | 1.49 | A01 | LINW0.06522021
Horizontal Wall | Linea Plus | LINW.06522021/DBE | 65 | 220 | 21 | 22 | 8531 | 8531 | 8531 | 0.20312 | 4266 | 0.10157 | 9384 | 0.22343 | 1 | A01 | LINW0.06522021/DBE
Horizontal Wall | Linea Plus | LINW.06524010 | 65 | 240 | 10 | 12 | 2690 | 2690 | 2690 | 0.064048 | 1030 | 0.024524 | 3069 | 0.073071 | 1.385 | A01 | LINW0.06524010
Horizontal Wall | Linea Plus | LINW.06524011 | 65 | 240 | 11 | 12 | 3559 | 3559 | 3559 | 0.084738 | 1303 | 0.031024 | 4086 | 0.097286 | 1.45 | A01 | LINW0.06524011
Horizontal Wall | Linea Plus | LINW.06524011/DBE | 65 | 240 | 11 | 12 | 5359 | 5359 | 5359 | 0.1276 | 2680 | 0.06381 | 5895 | 0.14036 | 1 | A01 | LINW0.06524011/DBE
Horizontal Wall | Linea Plus | LINW.06524015 | 65 | 240 | 15 | 17 | 4116 | 4116 | 4116 | 0.098 | 1622 | 0.038619 | 4680 | 0.11143 | 1.345 | A01 | LINW0.06524015
Horizontal Wall | Linea Plus | LINW.06524016 | 65 | 240 | 16 | 17 | 5345 | 5345 | 5345 | 0.12726 | 1940 | 0.04619 | 6141 | 0.14621 | 1.46 | A01 | LINW0.06524016
Horizontal Wall | Linea Plus | LINW.06524016/DBE | 65 | 240 | 16 | 17 | 8225 | 8225 | 8225 | 0.19583 | 4113 | 0.097929 | 9048 | 0.21543 | 1 | A01 | LINW0.06524016/DBE
Horizontal Wall | Linea Plus | LINW.06524020 | 65 | 240 | 20 | 22 | 5738 | 5738 | 5738 | 0.13662 | 2255 | 0.05369 | 6524 | 0.15533 | 1.348 | A01 | LINW0.06524020
Horizontal Wall | Linea Plus | LINW.06524021 | 65 | 240 | 21 | 22 | 7212 | 7212 | 7212 | 0.17171 | 2567 | 0.061119 | 8315 | 0.19798 | 1.49 | A01 | LINW0.06524021
Horizontal Wall | Linea Plus | LINW.06524021/DBE | 65 | 240 | 21 | 22 | 10092 | 10092 | 10092 | 0.24029 | 5046 | 0.12014 | 11101 | 0.26431 | 1 | A01 | LINW0.06524021/DBE
Horizontal Wall | Linea Plus | LINW.06526010 | 65 | 260 | 10 | 12 | 2915 | 2915 | 2915 | 0.069405 | 1116 | 0.026571 | 3326 | 0.07919 | 1.385 | A01 | LINW0.06526010
Horizontal Wall | Linea Plus | LINW.06526011 | 65 | 260 | 11 | 12 | 3856 | 3856 | 3856 | 0.09181 | 1411 | 0.033595 | 4427 | 0.1054 | 1.45 | A01 | LINW0.06526011
Horizontal Wall | Linea Plus | LINW.06526011/DBE | 65 | 260 | 11 | 12 | 5656 | 5656 | 5656 | 0.13467 | 2828 | 0.067333 | 6222 | 0.14814 | 1 | A01 | LINW0.06526011/DBE
Horizontal Wall | Linea Plus | LINW.06526015 | 65 | 260 | 15 | 17 | 4459 | 4459 | 4459 | 0.10617 | 1757 | 0.041833 | 5070 | 0.12071 | 1.345 | A01 | LINW0.06526015
Horizontal Wall | Linea Plus | LINW.06526016 | 65 | 260 | 16 | 17 | 5790 | 5790 | 5790 | 0.13786 | 2102 | 0.050048 | 6653 | 0.1584 | 1.46 | A01 | LINW0.06526016
Horizontal Wall | Linea Plus | LINW.06526016/DBE | 65 | 260 | 16 | 17 | 8670 | 8670 | 8670 | 0.20643 | 4335 | 0.10321 | 9537 | 0.22707 | 1 | A01 | LINW0.06526016/DBE
Horizontal Wall | Linea Plus | LINW.06526020 | 65 | 260 | 20 | 22 | 6217 | 6217 | 6217 | 0.14802 | 2443 | 0.058167 | 7069 | 0.16831 | 1.348 | A01 | LINW0.06526020
Horizontal Wall | Linea Plus | LINW.06526021 | 65 | 260 | 21 | 22 | 7813 | 7813 | 7813 | 0.18602 | 2781 | 0.066214 | 9008 | 0.21448 | 1.49 | A01 | LINW0.06526021
Horizontal Wall | Linea Plus | LINW.06526021/DBE | 65 | 260 | 21 | 22 | 10693 | 10693 | 10693 | 0.2546 | 5347 | 0.12731 | 11762 | 0.28005 | 1 | A01 | LINW0.06526021/DBE
Horizontal Wall | Linea Plus | LINW.06528010 | 65 | 280 | 10 | 12 | 3139 | 3139 | 3139 | 0.074738 | 1202 | 0.028619 | 3582 | 0.085286 | 1.385 | A01 | LINW0.06528010
Horizontal Wall | Linea Plus | LINW.06528011 | 65 | 280 | 11 | 12 | 4152 | 4152 | 4152 | 0.098857 | 1520 | 0.03619 | 4766 | 0.11348 | 1.45 | A01 | LINW0.06528011
Horizontal Wall | Linea Plus | LINW.06528011/DBE | 65 | 280 | 11 | 12 | 5952 | 5952 | 5952 | 0.14171 | 2976 | 0.070857 | 6547 | 0.15588 | 1 | A01 | LINW0.06528011/DBE
Horizontal Wall | Linea Plus | LINW.06528015 | 65 | 280 | 15 | 17 | 4802 | 4802 | 4802 | 0.11433 | 1892 | 0.045048 | 5460 | 0.13 | 1.345 | A01 | LINW0.06528015
Horizontal Wall | Linea Plus | LINW.06528016 | 65 | 280 | 16 | 17 | 6236 | 6236 | 6236 | 0.14848 | 2264 | 0.053905 | 7165 | 0.1706 | 1.46 | A01 | LINW0.06528016
Horizontal Wall | Linea Plus | LINW.06528016/DBE | 65 | 280 | 16 | 17 | 9116 | 9116 | 9116 | 0.21705 | 4558 | 0.10852 | 10028 | 0.23876 | 1 | A01 | LINW0.06528016/DBE
Horizontal Wall | Linea Plus | LINW.06528020 | 65 | 280 | 20 | 22 | 6695 | 6695 | 6695 | 0.1594 | 2631 | 0.062643 | 7612 | 0.18124 | 1.348 | A01 | LINW0.06528020
Horizontal Wall | Linea Plus | LINW.06528021 | 65 | 280 | 21 | 22 | 8414 | 8414 | 8414 | 0.20033 | 2995 | 0.07131 | 9701 | 0.23098 | 1.49 | A01 | LINW0.06528021
Horizontal Wall | Linea Plus | LINW.06528021/DBE | 65 | 280 | 21 | 22 | 11294 | 11294 | 11294 | 0.2689 | 5647 | 0.13445 | 12423 | 0.29579 | 1 | A01 | LINW0.06528021/DBE
Horizontal Wall | Linea Plus | LINW.09506010 | 95 | 60 | 10 | 12 | 838 | 838 | 838 | 0.019952 | 328 | 0.0078095 | 953 | 0.02269 | 1.35 | A01 | LINW0.09506010
Horizontal Wall | Linea Plus | LINW.09506011 | 95 | 60 | 11 | 12 | 1055 | 1055 | 1055 | 0.025119 | 388 | 0.0092381 | 1210 | 0.02881 | 1.441 | A01 | LINW0.09506011
Horizontal Wall | Linea Plus | LINW.09506011/DBE | 95 | 60 | 11 | 12 | 1355 | 1355 | 1355 | 0.032262 | 678 | 0.016143 | 1491 | 0.0355 | 1 | A01 | LINW0.09506011/DBE
Horizontal Wall | Linea Plus | LINW.09506015 | 95 | 60 | 15 | 17 | 1210 | 1210 | 1210 | 0.02881 | 494 | 0.011762 | 1369 | 0.032595 | 1.293 | A01 | LINW0.09506015
Horizontal Wall | Linea Plus | LINW.09506016 | 95 | 60 | 16 | 17 | 1608 | 1608 | 1608 | 0.038286 | 587 | 0.013976 | 1848 | 0.044 | 1.455 | A01 | LINW0.09506016
Horizontal Wall | Linea Plus | LINW.09506016/DBE | 95 | 60 | 16 | 17 | 2088 | 2088 | 2088 | 0.049714 | 1044 | 0.024857 | 2297 | 0.05469 | 1 | A01 | LINW0.09506016/DBE
Horizontal Wall | Linea Plus | LINW.09506020 | 95 | 60 | 20 | 22 | 1706 | 1706 | 1706 | 0.040619 | 694 | 0.016524 | 1929 | 0.045929 | 1.296 | A01 | LINW0.09506020
Horizontal Wall | Linea Plus | LINW.09506021 | 95 | 60 | 21 | 22 | 2290 | 2290 | 2290 | 0.054524 | 811 | 0.01931 | 2643 | 0.062929 | 1.499 | A01 | LINW0.09506021
Horizontal Wall | Linea Plus | LINW.09506021/DBE | 95 | 60 | 21 | 22 | 2770 | 2770 | 2770 | 0.065952 | 1385 | 0.032976 | 3047 | 0.072548 | 1 | A01 | LINW0.09506021/DBE
Horizontal Wall | Linea Plus | LINW.09507010 | 95 | 70 | 10 | 12 | 977 | 977 | 977 | 0.023262 | 383 | 0.009119 | 1111 | 0.026452 | 1.35 | A01 | LINW0.09507010
Horizontal Wall | Linea Plus | LINW.09507011 | 95 | 70 | 11 | 12 | 1231 | 1231 | 1231 | 0.02931 | 453 | 0.010786 | 1412 | 0.033619 | 1.441 | A01 | LINW0.09507011
Horizontal Wall | Linea Plus | LINW.09507011/DBE | 95 | 70 | 11 | 12 | 1531 | 1531 | 1531 | 0.036452 | 766 | 0.018238 | 1684 | 0.040095 | 1 | A01 | LINW0.09507011/DBE
Horizontal Wall | Linea Plus | LINW.09507015 | 95 | 70 | 15 | 17 | 1411 | 1411 | 1411 | 0.033595 | 576 | 0.013714 | 1596 | 0.038 | 1.293 | A01 | LINW0.09507015
Horizontal Wall | Linea Plus | LINW.09507016 | 95 | 70 | 16 | 17 | 1876 | 1876 | 1876 | 0.044667 | 685 | 0.01631 | 2156 | 0.051333 | 1.455 | A01 | LINW0.09507016
Horizontal Wall | Linea Plus | LINW.09507016/DBE | 95 | 70 | 16 | 17 | 2356 | 2356 | 2356 | 0.056095 | 1178 | 0.028048 | 2592 | 0.061714 | 1 | A01 | LINW0.09507016/DBE
Horizontal Wall | Linea Plus | LINW.09507020 | 95 | 70 | 20 | 22 | 1991 | 1991 | 1991 | 0.047405 | 810 | 0.019286 | 2252 | 0.053619 | 1.296 | A01 | LINW0.09507020
Horizontal Wall | Linea Plus | LINW.09507021 | 95 | 70 | 21 | 22 | 2671 | 2671 | 2671 | 0.063595 | 946 | 0.022524 | 3082 | 0.073381 | 1.499 | A01 | LINW0.09507021
Horizontal Wall | Linea Plus | LINW.09507021/DBE | 95 | 70 | 21 | 22 | 3151 | 3151 | 3151 | 0.075024 | 1576 | 0.037524 | 3466 | 0.082524 | 1 | A01 | LINW0.09507021/DBE
Horizontal Wall | Linea Plus | LINW.09508010 | 95 | 80 | 10 | 12 | 1117 | 1117 | 1117 | 0.026595 | 438 | 0.010429 | 1270 | 0.030238 | 1.35 | A01 | LINW0.09508010
Horizontal Wall | Linea Plus | LINW.09508011 | 95 | 80 | 11 | 12 | 1406 | 1406 | 1406 | 0.033476 | 517 | 0.01231 | 1613 | 0.038405 | 1.441 | A01 | LINW0.09508011
Horizontal Wall | Linea Plus | LINW.09508011/DBE | 95 | 80 | 11 | 12 | 1706 | 1706 | 1706 | 0.040619 | 853 | 0.02031 | 1877 | 0.04469 | 1 | A01 | LINW0.09508011/DBE
Horizontal Wall | Linea Plus | LINW.09508015 | 95 | 80 | 15 | 17 | 1613 | 1613 | 1613 | 0.038405 | 658 | 0.015667 | 1824 | 0.043429 | 1.293 | A01 | LINW0.09508015
Horizontal Wall | Linea Plus | LINW.09508016 | 95 | 80 | 16 | 17 | 2144 | 2144 | 2144 | 0.051048 | 783 | 0.018643 | 2463 | 0.058643 | 1.455 | A01 | LINW0.09508016
Horizontal Wall | Linea Plus | LINW.09508016/DBE | 95 | 80 | 16 | 17 | 2624 | 2624 | 2624 | 0.062476 | 1312 | 0.031238 | 2886 | 0.068714 | 1 | A01 | LINW0.09508016/DBE
Horizontal Wall | Linea Plus | LINW.09508020 | 95 | 80 | 20 | 22 | 2275 | 2275 | 2275 | 0.054167 | 926 | 0.022048 | 2573 | 0.061262 | 1.296 | A01 | LINW0.09508020
Horizontal Wall | Linea Plus | LINW.09508021 | 95 | 80 | 21 | 22 | 3053 | 3053 | 3053 | 0.07269 | 1081 | 0.025738 | 3523 | 0.083881 | 1.499 | A01 | LINW0.09508021
Horizontal Wall | Linea Plus | LINW.09508021/DBE | 95 | 80 | 21 | 22 | 3533 | 3533 | 3533 | 0.084119 | 1767 | 0.042071 | 3886 | 0.092524 | 1 | A01 | LINW0.09508021/DBE
Horizontal Wall | Linea Plus | LINW.09509010 | 95 | 90 | 10 | 12 | 1256 | 1256 | 1256 | 0.029905 | 492 | 0.011714 | 1428 | 0.034 | 1.35 | A01 | LINW0.09509010
Horizontal Wall | Linea Plus | LINW.09509011 | 95 | 90 | 11 | 12 | 1582 | 1582 | 1582 | 0.037667 | 582 | 0.013857 | 1815 | 0.043214 | 1.441 | A01 | LINW0.09509011
Horizontal Wall | Linea Plus | LINW.09509011/DBE | 95 | 90 | 11 | 12 | 2182 | 2182 | 2182 | 0.051952 | 1091 | 0.025976 | 2400 | 0.057143 | 1 | A01 | LINW0.09509011/DBE
Horizontal Wall | Linea Plus | LINW.09509015 | 95 | 90 | 15 | 17 | 1814 | 1814 | 1814 | 0.04319 | 740 | 0.017619 | 2052 | 0.048857 | 1.293 | A01 | LINW0.09509015
Horizontal Wall | Linea Plus | LINW.09509016 | 95 | 90 | 16 | 17 | 2412 | 2412 | 2412 | 0.057429 | 880 | 0.020952 | 2771 | 0.065976 | 1.455 | A01 | LINW0.09509016
Horizontal Wall | Linea Plus | LINW.09509016/DBE | 95 | 90 | 16 | 17 | 3372 | 3372 | 3372 | 0.080286 | 1686 | 0.040143 | 3709 | 0.08831 | 1 | A01 | LINW0.09509016/DBE
Horizontal Wall | Linea Plus | LINW.09509020 | 95 | 90 | 20 | 22 | 2560 | 2560 | 2560 | 0.060952 | 1042 | 0.02481 | 2895 | 0.068929 | 1.296 | A01 | LINW0.09509020
Horizontal Wall | Linea Plus | LINW.09509021 | 95 | 90 | 21 | 22 | 3434 | 3434 | 3434 | 0.081762 | 1216 | 0.028952 | 3963 | 0.094357 | 1.499 | A01 | LINW0.09509021
Horizontal Wall | Linea Plus | LINW.09509021/DBE | 95 | 90 | 21 | 22 | 4394 | 4394 | 4394 | 0.10462 | 2197 | 0.05231 | 4833 | 0.11507 | 1 | A01 | LINW0.09509021/DBE
Horizontal Wall | Linea Plus | LINW.09510010 | 95 | 100 | 10 | 12 | 1396 | 1396 | 1396 | 0.033238 | 547 | 0.013024 | 1587 | 0.037786 | 1.35 | A01 | LINW0.09510010
Horizontal Wall | Linea Plus | LINW.09510011 | 95 | 100 | 11 | 12 | 1758 | 1758 | 1758 | 0.041857 | 647 | 0.015405 | 2016 | 0.048 | 1.441 | A01 | LINW0.09510011
Horizontal Wall | Linea Plus | LINW.09510011/DBE | 95 | 100 | 11 | 12 | 2358 | 2358 | 2358 | 0.056143 | 1179 | 0.028071 | 2594 | 0.061762 | 1 | A01 | LINW0.09510011/DBE
Horizontal Wall | Linea Plus | LINW.09510015 | 95 | 100 | 15 | 17 | 2016 | 2016 | 2016 | 0.048 | 823 | 0.019595 | 2280 | 0.054286 | 1.293 | A01 | LINW0.09510015
Horizontal Wall | Linea Plus | LINW.09510016 | 95 | 100 | 16 | 17 | 2680 | 2680 | 2680 | 0.06381 | 978 | 0.023286 | 3079 | 0.07331 | 1.455 | A01 | LINW0.09510016
Horizontal Wall | Linea Plus | LINW.09510016/DBE | 95 | 100 | 16 | 17 | 3640 | 3640 | 3640 | 0.086667 | 1820 | 0.043333 | 4004 | 0.095333 | 1 | A01 | LINW0.09510016/DBE
Horizontal Wall | Linea Plus | LINW.09510020 | 95 | 100 | 20 | 22 | 2844 | 2844 | 2844 | 0.067714 | 1158 | 0.027571 | 3217 | 0.076595 | 1.296 | A01 | LINW0.09510020
Horizontal Wall | Linea Plus | LINW.09510021 | 95 | 100 | 21 | 22 | 3816 | 3816 | 3816 | 0.090857 | 1351 | 0.032167 | 4404 | 0.10486 | 1.499 | A01 | LINW0.09510021
Horizontal Wall | Linea Plus | LINW.09510021/DBE | 95 | 100 | 21 | 22 | 4776 | 4776 | 4776 | 0.11371 | 2388 | 0.056857 | 5254 | 0.1251 | 1 | A01 | LINW0.09510021/DBE
Horizontal Wall | Linea Plus | LINW.09511010 | 95 | 110 | 10 | 12 | 1536 | 1536 | 1536 | 0.036571 | 602 | 0.014333 | 1746 | 0.041571 | 1.35 | A01 | LINW0.09511010
Horizontal Wall | Linea Plus | LINW.09511011 | 95 | 110 | 11 | 12 | 1934 | 1934 | 1934 | 0.046048 | 712 | 0.016952 | 2218 | 0.05281 | 1.441 | A01 | LINW0.09511011
Horizontal Wall | Linea Plus | LINW.09511011/DBE | 95 | 110 | 11 | 12 | 2534 | 2534 | 2534 | 0.060333 | 1267 | 0.030167 | 2787 | 0.066357 | 1 | A01 | LINW0.09511011/DBE
Horizontal Wall | Linea Plus | LINW.09511015 | 95 | 110 | 15 | 17 | 2218 | 2218 | 2218 | 0.05281 | 905 | 0.021548 | 2509 | 0.059738 | 1.293 | A01 | LINW0.09511015
Horizontal Wall | Linea Plus | LINW.09511016 | 95 | 110 | 16 | 17 | 2948 | 2948 | 2948 | 0.07019 | 1076 | 0.025619 | 3387 | 0.080643 | 1.455 | A01 | LINW0.09511016
Horizontal Wall | Linea Plus | LINW.09511016/DBE | 95 | 110 | 16 | 17 | 3908 | 3908 | 3908 | 0.093048 | 1954 | 0.046524 | 4299 | 0.10236 | 1 | A01 | LINW0.09511016/DBE
Horizontal Wall | Linea Plus | LINW.09511020 | 95 | 110 | 20 | 22 | 3128 | 3128 | 3128 | 0.074476 | 1273 | 0.03031 | 3538 | 0.084238 | 1.296 | A01 | LINW0.09511020
Horizontal Wall | Linea Plus | LINW.09511021 | 95 | 110 | 21 | 22 | 4198 | 4198 | 4198 | 0.099952 | 1486 | 0.035381 | 4844 | 0.11533 | 1.499 | A01 | LINW0.09511021
Horizontal Wall | Linea Plus | LINW.09511021/DBE | 95 | 110 | 21 | 22 | 5158 | 5158 | 5158 | 0.12281 | 2579 | 0.061405 | 5674 | 0.1351 | 1 | A01 | LINW0.09511021/DBE
Horizontal Wall | Linea Plus | LINW.09512010 | 95 | 120 | 10 | 12 | 1675 | 1675 | 1675 | 0.039881 | 657 | 0.015643 | 1904 | 0.045333 | 1.35 | A01 | LINW0.09512010
Horizontal Wall | Linea Plus | LINW.09512011 | 95 | 120 | 11 | 12 | 2110 | 2110 | 2110 | 0.050238 | 776 | 0.018476 | 2420 | 0.057619 | 1.441 | A01 | LINW0.09512011
Horizontal Wall | Linea Plus | LINW.09512011/DBE | 95 | 120 | 11 | 12 | 2710 | 2710 | 2710 | 0.064524 | 1355 | 0.032262 | 2981 | 0.070976 | 1 | A01 | LINW0.09512011/DBE
Horizontal Wall | Linea Plus | LINW.09512015 | 95 | 120 | 15 | 17 | 2419 | 2419 | 2419 | 0.057595 | 987 | 0.0235 | 2736 | 0.065143 | 1.293 | A01 | LINW0.09512015
Horizontal Wall | Linea Plus | LINW.09512016 | 95 | 120 | 16 | 17 | 3216 | 3216 | 3216 | 0.076571 | 1174 | 0.027952 | 3695 | 0.087976 | 1.455 | A01 | LINW0.09512016
Horizontal Wall | Linea Plus | LINW.09512016/DBE | 95 | 120 | 16 | 17 | 4176 | 4176 | 4176 | 0.099429 | 2088 | 0.049714 | 4594 | 0.10938 | 1 | A01 | LINW0.09512016/DBE
Horizontal Wall | Linea Plus | LINW.09512020 | 95 | 120 | 20 | 22 | 3413 | 3413 | 3413 | 0.081262 | 1389 | 0.033071 | 3860 | 0.091905 | 1.296 | A01 | LINW0.09512020
Horizontal Wall | Linea Plus | LINW.09512021 | 95 | 120 | 21 | 22 | 4579 | 4579 | 4579 | 0.10902 | 1621 | 0.038595 | 5284 | 0.12581 | 1.499 | A01 | LINW0.09512021
Horizontal Wall | Linea Plus | LINW.09512021/DBE | 95 | 120 | 21 | 22 | 5539 | 5539 | 5539 | 0.13188 | 2770 | 0.065952 | 6093 | 0.14507 | 1 | A01 | LINW0.09512021/DBE
Horizontal Wall | Linea Plus | LINW.09514010 | 95 | 140 | 10 | 12 | 1954 | 1954 | 1954 | 0.046524 | 766 | 0.018238 | 2222 | 0.052905 | 1.35 | A01 | LINW0.09514010
Horizontal Wall | Linea Plus | LINW.09514011 | 95 | 140 | 11 | 12 | 2461 | 2461 | 2461 | 0.058595 | 906 | 0.021571 | 2823 | 0.067214 | 1.441 | A01 | LINW0.09514011
Horizontal Wall | Linea Plus | LINW.09514011/DBE | 95 | 140 | 11 | 12 | 3061 | 3061 | 3061 | 0.072881 | 1531 | 0.036452 | 3367 | 0.080167 | 1 | A01 | LINW0.09514011/DBE
Horizontal Wall | Linea Plus | LINW.09514015 | 95 | 140 | 15 | 17 | 2822 | 2822 | 2822 | 0.06719 | 1151 | 0.027405 | 3192 | 0.076 | 1.293 | A01 | LINW0.09514015
Horizontal Wall | Linea Plus | LINW.09514016 | 95 | 140 | 16 | 17 | 3752 | 3752 | 3752 | 0.089333 | 1369 | 0.032595 | 4311 | 0.10264 | 1.455 | A01 | LINW0.09514016
Horizontal Wall | Linea Plus | LINW.09514016/DBE | 95 | 140 | 16 | 17 | 4712 | 4712 | 4712 | 0.11219 | 2356 | 0.056095 | 5183 | 0.1234 | 1 | A01 | LINW0.09514016/DBE
Horizontal Wall | Linea Plus | LINW.09514020 | 95 | 140 | 20 | 22 | 3982 | 3982 | 3982 | 0.09481 | 1621 | 0.038595 | 4504 | 0.10724 | 1.296 | A01 | LINW0.09514020
Horizontal Wall | Linea Plus | LINW.09514021 | 95 | 140 | 21 | 22 | 5342 | 5342 | 5342 | 0.12719 | 1891 | 0.045024 | 6165 | 0.14679 | 1.499 | A01 | LINW0.09514021
Horizontal Wall | Linea Plus | LINW.09514021/DBE | 95 | 140 | 21 | 22 | 6302 | 6302 | 6302 | 0.15005 | 3151 | 0.075024 | 6932 | 0.16505 | 1 | A01 | LINW0.09514021/DBE
Horizontal Wall | Maxi | MAXW.04406310/FF | 44 | 63 | 10 | 13 | 401 | 401 | 401 | 0.0095476 | 150 | 0.0035714 | 459 | 0.010929 | 1.414 | A10 | MAXW0.04406310/FF
Horizontal Wall | Maxi | MAXW.04406310/FT | 44 | 63 | 10 | 13 | 511 | 511 | 511 | 0.012167 | 193 | 0.0045952 | 584 | 0.013905 | 1.404 | A10 | MAXW0.04406310/FT
Horizontal Wall | Maxi | MAXW.04406310/WF | 44 | 63 | 10 | 13 | 557 | 557 | 557 | 0.013262 | 211 | 0.0050238 | 637 | 0.015167 | 1.4 | A10 | MAXW0.04406310/WF
Horizontal Wall | Maxi | MAXW.04406310/WT | 44 | 63 | 10 | 13 | 637 | 637 | 637 | 0.015167 | 243 | 0.0057857 | 727 | 0.01731 | 1.391 | A10 | MAXW0.04406310/WT
Horizontal Wall | Maxi | MAXW.04406311/FT | 44 | 63 | 11 | 13 | 696 | 696 | 696 | 0.016571 | 257 | 0.006119 | 798 | 0.019 | 1.44 | A10 | MAXW0.04406311/FT
Horizontal Wall | Maxi | MAXW.04406311/FT/DBE | 44 | 63 | 11 | 13 | 996 | 996 | 996 | 0.023714 | 498 | 0.011857 | 1096 | 0.026095 | 1 | A10 | MAXW0.04406311/FT/DBE
Horizontal Wall | Maxi | MAXW.04406311/WF | 44 | 63 | 11 | 13 | 744 | 744 | 744 | 0.017714 | 275 | 0.0065476 | 853 | 0.02031 | 1.44 | A10 | MAXW0.04406311/WF
Horizontal Wall | Maxi | MAXW.04406311/WF/DBE | 44 | 63 | 11 | 13 | 1044 | 1044 | 1044 | 0.024857 | 522 | 0.012429 | 1148 | 0.027333 | 1 | A10 | MAXW0.04406311/WF/DBE
Horizontal Wall | Maxi | MAXW.04406311/WT | 44 | 63 | 11 | 13 | 828 | 828 | 828 | 0.019714 | 306 | 0.0072857 | 950 | 0.022619 | 1.439 | A10 | MAXW0.04406311/WT
Horizontal Wall | Maxi | MAXW.04406311/WT/DBE | 44 | 63 | 11 | 13 | 1128 | 1128 | 1128 | 0.026857 | 564 | 0.013429 | 1241 | 0.029548 | 1 | A10 | MAXW0.04406311/WT/DBE
Horizontal Wall | Maxi | MAXW.04406315/FF | 44 | 63 | 15 | 18 | 585 | 585 | 585 | 0.013929 | 221 | 0.0052619 | 669 | 0.015929 | 1.409 | A10 | MAXW0.04406315/FF
Horizontal Wall | Maxi | MAXW.04406315/FT | 44 | 63 | 15 | 18 | 790 | 790 | 790 | 0.01881 | 300 | 0.0071429 | 902 | 0.021476 | 1.397 | A10 | MAXW0.04406315/FT
Horizontal Wall | Maxi | MAXW.04406315/WF | 44 | 63 | 15 | 18 | 834 | 834 | 834 | 0.019857 | 318 | 0.0075714 | 952 | 0.022667 | 1.392 | A10 | MAXW0.04406315/WF
Horizontal Wall | Maxi | MAXW.04406315/WT | 44 | 63 | 15 | 18 | 1034 | 1034 | 1034 | 0.024619 | 397 | 0.0094524 | 1180 | 0.028095 | 1.38 | A10 | MAXW0.04406315/WT
Horizontal Wall | Maxi | MAXW.04406316/FT | 44 | 63 | 16 | 18 | 864 | 864 | 864 | 0.020571 | 315 | 0.0075 | 993 | 0.023643 | 1.455 | A10 | MAXW0.04406316/FT
Horizontal Wall | Maxi | MAXW.04406316/FT/DBE | 44 | 63 | 16 | 18 | 1344 | 1344 | 1344 | 0.032 | 672 | 0.016 | 1478 | 0.03519 | 1 | A10 | MAXW0.04406316/FT/DBE
Horizontal Wall | Maxi | MAXW.04406316/WF | 44 | 63 | 16 | 18 | 907 | 907 | 907 | 0.021595 | 330 | 0.0078571 | 1042 | 0.02481 | 1.457 | A10 | MAXW0.04406316/WF
Horizontal Wall | Maxi | MAXW.04406316/WF/DBE | 44 | 63 | 16 | 18 | 1387 | 1387 | 1387 | 0.033024 | 694 | 0.016524 | 1526 | 0.036333 | 1 | A10 | MAXW0.04406316/WF/DBE
Horizontal Wall | Maxi | MAXW.04406316/WT | 44 | 63 | 16 | 18 | 1121 | 1121 | 1121 | 0.02669 | 407 | 0.0096905 | 1289 | 0.03069 | 1.462 | A10 | MAXW0.04406316/WT
Horizontal Wall | Maxi | MAXW.04406316/WT/DBE | 44 | 63 | 16 | 18 | 1601 | 1601 | 1601 | 0.038119 | 801 | 0.019071 | 1761 | 0.041929 | 1 | A10 | MAXW0.04406316/WT/DBE
Horizontal Wall | Maxi | MAXW.04406320/FF | 44 | 63 | 20 | 23 | 748 | 748 | 748 | 0.01781 | 282 | 0.0067143 | 856 | 0.020381 | 1.409 | A10 | MAXW0.04406320/FF
Horizontal Wall | Maxi | MAXW.04406320/FT | 44 | 63 | 20 | 23 | 1073 | 1073 | 1073 | 0.025548 | 408 | 0.0097143 | 1225 | 0.029167 | 1.397 | A10 | MAXW0.04406320/FT
Horizontal Wall | Maxi | MAXW.04406320/WF | 44 | 63 | 20 | 23 | 1111 | 1111 | 1111 | 0.026452 | 423 | 0.010071 | 1269 | 0.030214 | 1.391 | A10 | MAXW0.04406320/WF
Horizontal Wall | Maxi | MAXW.04406320/WT | 44 | 63 | 20 | 23 | 1446 | 1446 | 1446 | 0.034429 | 555 | 0.013214 | 1650 | 0.039286 | 1.38 | A10 | MAXW0.04406320/WT
Horizontal Wall | Maxi | MAXW.04406321/FT | 44 | 63 | 21 | 23 | 1099 | 1099 | 1099 | 0.026167 | 398 | 0.0094762 | 1264 | 0.030095 | 1.467 | A10 | MAXW0.04406321/FT
Horizontal Wall | Maxi | MAXW.04406321/FT/DBE | 44 | 63 | 21 | 23 | 1579 | 1579 | 1579 | 0.037595 | 790 | 0.01881 | 1737 | 0.041357 | 1 | A10 | MAXW0.04406321/FT/DBE
Horizontal Wall | Maxi | MAXW.04406321/WF | 44 | 63 | 21 | 23 | 1143 | 1143 | 1143 | 0.027214 | 411 | 0.0097857 | 1316 | 0.031333 | 1.472 | A10 | MAXW0.04406321/WF
Horizontal Wall | Maxi | MAXW.04406321/WF/DBE | 44 | 63 | 21 | 23 | 1623 | 1623 | 1623 | 0.038643 | 812 | 0.019333 | 1785 | 0.0425 | 1 | A10 | MAXW0.04406321/WF/DBE
Horizontal Wall | Maxi | MAXW.04406321/WT | 44 | 63 | 21 | 23 | 1510 | 1510 | 1510 | 0.035952 | 541 | 0.012881 | 1738 | 0.041381 | 1.48 | A10 | MAXW0.04406321/WT
Horizontal Wall | Maxi | MAXW.04406321/WT/DBE | 44 | 63 | 21 | 23 | 1990 | 1990 | 1990 | 0.047381 | 995 | 0.02369 | 2189 | 0.052119 | 1 | A10 | MAXW0.04406321/WT/DBE
Horizontal Wall | Maxi | MAXW.04408310/FF | 44 | 83 | 10 | 13 | 528 | 528 | 528 | 0.012571 | 198 | 0.0047143 | 604 | 0.014381 | 1.414 | A10 | MAXW0.04408310/FF
Horizontal Wall | Maxi | MAXW.04408310/FT | 44 | 83 | 10 | 13 | 673 | 673 | 673 | 0.016024 | 254 | 0.0060476 | 769 | 0.01831 | 1.404 | A10 | MAXW0.04408310/FT
Horizontal Wall | Maxi | MAXW.04408310/WF | 44 | 83 | 10 | 13 | 734 | 734 | 734 | 0.017476 | 278 | 0.006619 | 839 | 0.019976 | 1.4 | A10 | MAXW0.04408310/WF
Horizontal Wall | Maxi | MAXW.04408310/WT | 44 | 83 | 10 | 13 | 840 | 840 | 840 | 0.02 | 320 | 0.007619 | 959 | 0.022833 | 1.391 | A10 | MAXW0.04408310/WT
Horizontal Wall | Maxi | MAXW.04408311/FT | 44 | 83 | 11 | 13 | 917 | 917 | 917 | 0.021833 | 338 | 0.0080476 | 1052 | 0.025048 | 1.44 | A10 | MAXW0.04408311/FT
Horizontal Wall | Maxi | MAXW.04408311/FT/DBE | 44 | 83 | 11 | 13 | 1217 | 1217 | 1217 | 0.028976 | 609 | 0.0145 | 1339 | 0.031881 | 1 | A10 | MAXW0.04408311/FT/DBE
Horizontal Wall | Maxi | MAXW.04408311/WF | 44 | 83 | 11 | 13 | 981 | 981 | 981 | 0.023357 | 362 | 0.008619 | 1125 | 0.026786 | 1.44 | A10 | MAXW0.04408311/WF
Horizontal Wall | Maxi | MAXW.04408311/WF/DBE | 44 | 83 | 11 | 13 | 1281 | 1281 | 1281 | 0.0305 | 641 | 0.015262 | 1409 | 0.033548 | 1 | A10 | MAXW0.04408311/WF/DBE
Horizontal Wall | Maxi | MAXW.04408311/WT | 44 | 83 | 11 | 13 | 1091 | 1091 | 1091 | 0.025976 | 403 | 0.0095952 | 1251 | 0.029786 | 1.439 | A10 | MAXW0.04408311/WT
Horizontal Wall | Maxi | MAXW.04408311/WT/DBE | 44 | 83 | 11 | 13 | 1391 | 1391 | 1391 | 0.033119 | 696 | 0.016571 | 1530 | 0.036429 | 1 | A10 | MAXW0.04408311/WT/DBE
Horizontal Wall | Maxi | MAXW.04408315/FF | 44 | 83 | 15 | 18 | 771 | 771 | 771 | 0.018357 | 291 | 0.0069286 | 882 | 0.021 | 1.409 | A10 | MAXW0.04408315/FF
Horizontal Wall | Maxi | MAXW.04408315/FT | 44 | 83 | 15 | 18 | 1041 | 1041 | 1041 | 0.024786 | 396 | 0.0094286 | 1189 | 0.02831 | 1.397 | A10 | MAXW0.04408315/FT
Horizontal Wall | Maxi | MAXW.04408315/WF | 44 | 83 | 15 | 18 | 1098 | 1098 | 1098 | 0.026143 | 418 | 0.0099524 | 1254 | 0.029857 | 1.392 | A10 | MAXW0.04408315/WF
Horizontal Wall | Maxi | MAXW.04408315/WT | 44 | 83 | 15 | 18 | 1362 | 1362 | 1362 | 0.032429 | 523 | 0.012452 | 1554 | 0.037 | 1.38 | A10 | MAXW0.04408315/WT
Horizontal Wall | Maxi | MAXW.04408316/FT | 44 | 83 | 16 | 18 | 1138 | 1138 | 1138 | 0.027095 | 415 | 0.009881 | 1308 | 0.031143 | 1.455 | A10 | MAXW0.04408316/FT
Horizontal Wall | Maxi | MAXW.04408316/FT/DBE | 44 | 83 | 16 | 18 | 1618 | 1618 | 1618 | 0.038524 | 809 | 0.019262 | 1780 | 0.042381 | 1 | A10 | MAXW0.04408316/FT/DBE
Horizontal Wall | Maxi | MAXW.04408316/WF | 44 | 83 | 16 | 18 | 1195 | 1195 | 1195 | 0.028452 | 435 | 0.010357 | 1373 | 0.03269 | 1.457 | A10 | MAXW0.04408316/WF
Horizontal Wall | Maxi | MAXW.04408316/WF/DBE | 44 | 83 | 16 | 18 | 1675 | 1675 | 1675 | 0.039881 | 838 | 0.019952 | 1843 | 0.043881 | 1 | A10 | MAXW0.04408316/WF/DBE
Horizontal Wall | Maxi | MAXW.04408316/WT | 44 | 83 | 16 | 18 | 1477 | 1477 | 1477 | 0.035167 | 536 | 0.012762 | 1699 | 0.040452 | 1.462 | A10 | MAXW0.04408316/WT
Horizontal Wall | Maxi | MAXW.04408316/WT/DBE | 44 | 83 | 16 | 18 | 1957 | 1957 | 1957 | 0.046595 | 979 | 0.02331 | 2153 | 0.051262 | 1 | A10 | MAXW0.04408316/WT/DBE
Horizontal Wall | Maxi | MAXW.04408320/FF | 44 | 83 | 20 | 23 | 986 | 986 | 986 | 0.023476 | 372 | 0.0088571 | 1128 | 0.026857 | 1.409 | A10 | MAXW0.04408320/FF
Horizontal Wall | Maxi | MAXW.04408320/FT | 44 | 83 | 20 | 23 | 1413 | 1413 | 1413 | 0.033643 | 537 | 0.012786 | 1614 | 0.038429 | 1.397 | A10 | MAXW0.04408320/FT
Horizontal Wall | Maxi | MAXW.04408320/WF | 44 | 83 | 20 | 23 | 1464 | 1464 | 1464 | 0.034857 | 558 | 0.013286 | 1672 | 0.03981 | 1.391 | A10 | MAXW0.04408320/WF
Horizontal Wall | Maxi | MAXW.04408320/WT | 44 | 83 | 20 | 23 | 1905 | 1905 | 1905 | 0.045357 | 732 | 0.017429 | 2174 | 0.051762 | 1.38 | A10 | MAXW0.04408320/WT
Horizontal Wall | Maxi | MAXW.04408321/FT | 44 | 83 | 21 | 23 | 1447 | 1447 | 1447 | 0.034452 | 524 | 0.012476 | 1664 | 0.039619 | 1.467 | A10 | MAXW0.04408321/FT
Horizontal Wall | Maxi | MAXW.04408321/FT/DBE | 44 | 83 | 21 | 23 | 1927 | 1927 | 1927 | 0.045881 | 964 | 0.022952 | 2120 | 0.050476 | 1 | A10 | MAXW0.04408321/FT/DBE
Horizontal Wall | Maxi | MAXW.04408321/WF | 44 | 83 | 21 | 23 | 1506 | 1506 | 1506 | 0.035857 | 542 | 0.012905 | 1733 | 0.041262 | 1.472 | A10 | MAXW0.04408321/WF
Horizontal Wall | Maxi | MAXW.04408321/WF/DBE | 44 | 83 | 21 | 23 | 1986 | 1986 | 1986 | 0.047286 | 993 | 0.023643 | 2185 | 0.052024 | 1 | A10 | MAXW0.04408321/WF/DBE
Horizontal Wall | Maxi | MAXW.04408321/WT | 44 | 83 | 21 | 23 | 1990 | 1990 | 1990 | 0.047381 | 712 | 0.016952 | 2290 | 0.054524 | 1.48 | A10 | MAXW0.04408321/WT
Horizontal Wall | Maxi | MAXW.04408321/WT/DBE | 44 | 83 | 21 | 23 | 2470 | 2470 | 2470 | 0.05881 | 1235 | 0.029405 | 2717 | 0.06469 | 1 | A10 | MAXW0.04408321/WT/DBE
Horizontal Wall | Maxi | MAXW.04410310/FF | 44 | 103 | 10 | 13 | 655 | 655 | 655 | 0.015595 | 246 | 0.0058571 | 749 | 0.017833 | 1.414 | A10 | MAXW0.04410310/FF
Horizontal Wall | Maxi | MAXW.04410310/FT | 44 | 103 | 10 | 13 | 835 | 835 | 835 | 0.019881 | 316 | 0.0075238 | 954 | 0.022714 | 1.404 | A10 | MAXW0.04410310/FT
Horizontal Wall | Maxi | MAXW.04410310/WF | 44 | 103 | 10 | 13 | 911 | 911 | 911 | 0.02169 | 345 | 0.0082143 | 1041 | 0.024786 | 1.4 | A10 | MAXW0.04410310/WF
Horizontal Wall | Maxi | MAXW.04410310/WT | 44 | 103 | 10 | 13 | 1042 | 1042 | 1042 | 0.02481 | 397 | 0.0094524 | 1190 | 0.028333 | 1.391 | A10 | MAXW0.04410310/WT
Horizontal Wall | Maxi | MAXW.04410311/FT | 44 | 103 | 11 | 13 | 1138 | 1138 | 1138 | 0.027095 | 420 | 0.01 | 1305 | 0.031071 | 1.44 | A10 | MAXW0.04410311/FT
Horizontal Wall | Maxi | MAXW.04410311/FT/DBE | 44 | 103 | 11 | 13 | 1738 | 1738 | 1738 | 0.041381 | 869 | 0.02069 | 1912 | 0.045524 | 1 | A10 | MAXW0.04410311/FT/DBE
Horizontal Wall | Maxi | MAXW.04410311/WF | 44 | 103 | 11 | 13 | 1217 | 1217 | 1217 | 0.028976 | 449 | 0.01069 | 1396 | 0.033238 | 1.44 | A10 | MAXW0.04410311/WF
Horizontal Wall | Maxi | MAXW.04410311/WF/DBE | 44 | 103 | 11 | 13 | 1817 | 1817 | 1817 | 0.043262 | 909 | 0.021643 | 1999 | 0.047595 | 1 | A10 | MAXW0.04410311/WF/DBE
Horizontal Wall | Maxi | MAXW.04410311/WT | 44 | 103 | 11 | 13 | 1354 | 1354 | 1354 | 0.032238 | 500 | 0.011905 | 1553 | 0.036976 | 1.439 | A10 | MAXW0.04410311/WT
Horizontal Wall | Maxi | MAXW.04410311/WT/DBE | 44 | 103 | 11 | 13 | 1954 | 1954 | 1954 | 0.046524 | 977 | 0.023262 | 2149 | 0.051167 | 1 | A10 | MAXW0.04410311/WT/DBE
Horizontal Wall | Maxi | MAXW.04410315/FF | 44 | 103 | 15 | 18 | 957 | 957 | 957 | 0.022786 | 361 | 0.0085952 | 1095 | 0.026071 | 1.409 | A10 | MAXW0.04410315/FF
Horizontal Wall | Maxi | MAXW.04410315/FT | 44 | 103 | 15 | 18 | 1292 | 1292 | 1292 | 0.030762 | 491 | 0.01169 | 1475 | 0.035119 | 1.397 | A10 | MAXW0.04410315/FT
Horizontal Wall | Maxi | MAXW.04410315/WF | 44 | 103 | 15 | 18 | 1363 | 1363 | 1363 | 0.032452 | 519 | 0.012357 | 1557 | 0.037071 | 1.392 | A10 | MAXW0.04410315/WF
Horizontal Wall | Maxi | MAXW.04410315/WT | 44 | 103 | 15 | 18 | 1690 | 1690 | 1690 | 0.040238 | 649 | 0.015452 | 1928 | 0.045905 | 1.38 | A10 | MAXW0.04410315/WT
Horizontal Wall | Maxi | MAXW.04410316/FT | 44 | 103 | 16 | 18 | 1412 | 1412 | 1412 | 0.033619 | 515 | 0.012262 | 1622 | 0.038619 | 1.455 | A10 | MAXW0.04410316/FT
Horizontal Wall | Maxi | MAXW.04410316/FT/DBE | 44 | 103 | 16 | 18 | 2372 | 2372 | 2372 | 0.056476 | 1186 | 0.028238 | 2609 | 0.062119 | 1 | A10 | MAXW0.04410316/FT/DBE
Horizontal Wall | Maxi | MAXW.04410316/WF | 44 | 103 | 16 | 18 | 1483 | 1483 | 1483 | 0.03531 | 540 | 0.012857 | 1704 | 0.040571 | 1.457 | A10 | MAXW0.04410316/WF
Horizontal Wall | Maxi | MAXW.04410316/WF/DBE | 44 | 103 | 16 | 18 | 2443 | 2443 | 2443 | 0.058167 | 1222 | 0.029095 | 2687 | 0.063976 | 1 | A10 | MAXW0.04410316/WF/DBE
Horizontal Wall | Maxi | MAXW.04410316/WT | 44 | 103 | 16 | 18 | 1833 | 1833 | 1833 | 0.043643 | 665 | 0.015833 | 2108 | 0.05019 | 1.462 | A10 | MAXW0.04410316/WT
Horizontal Wall | Maxi | MAXW.04410316/WT/DBE | 44 | 103 | 16 | 18 | 2793 | 2793 | 2793 | 0.0665 | 1397 | 0.033262 | 3072 | 0.073143 | 1 | A10 | MAXW0.04410316/WT/DBE
Horizontal Wall | Maxi | MAXW.04410320/FF | 44 | 103 | 20 | 23 | 1223 | 1223 | 1223 | 0.029119 | 461 | 0.010976 | 1399 | 0.03331 | 1.409 | A10 | MAXW0.04410320/FF
Horizontal Wall | Maxi | MAXW.04410320/FT | 44 | 103 | 20 | 23 | 1754 | 1754 | 1754 | 0.041762 | 667 | 0.015881 | 2003 | 0.04769 | 1.397 | A10 | MAXW0.04410320/FT
Horizontal Wall | Maxi | MAXW.04410320/WF | 44 | 103 | 20 | 23 | 1817 | 1817 | 1817 | 0.043262 | 692 | 0.016476 | 2075 | 0.049405 | 1.391 | A10 | MAXW0.04410320/WF
Horizontal Wall | Maxi | MAXW.04410320/WT | 44 | 103 | 20 | 23 | 2364 | 2364 | 2364 | 0.056286 | 908 | 0.021619 | 2697 | 0.064214 | 1.38 | A10 | MAXW0.04410320/WT
Horizontal Wall | Maxi | MAXW.04410321/FT | 44 | 103 | 21 | 23 | 1796 | 1796 | 1796 | 0.042762 | 650 | 0.015476 | 2065 | 0.049167 | 1.467 | A10 | MAXW0.04410321/FT
Horizontal Wall | Maxi | MAXW.04410321/FT/DBE | 44 | 103 | 21 | 23 | 2756 | 2756 | 2756 | 0.065619 | 1378 | 0.03281 | 3032 | 0.07219 | 1 | A10 | MAXW0.04410321/FT/DBE
Horizontal Wall | Maxi | MAXW.04410321/WF | 44 | 103 | 21 | 23 | 1869 | 1869 | 1869 | 0.0445 | 673 | 0.016024 | 2151 | 0.051214 | 1.472 | A10 | MAXW0.04410321/WF
Horizontal Wall | Maxi | MAXW.04410321/WF/DBE | 44 | 103 | 21 | 23 | 2829 | 2829 | 2829 | 0.067357 | 1415 | 0.03369 | 3112 | 0.074095 | 1 | A10 | MAXW0.04410321/WF/DBE
Horizontal Wall | Maxi | MAXW.04410321/WT | 44 | 103 | 21 | 23 | 2469 | 2469 | 2469 | 0.058786 | 884 | 0.021048 | 2842 | 0.067667 | 1.48 | A10 | MAXW0.04410321/WT
Horizontal Wall | Maxi | MAXW.04410321/WT/DBE | 44 | 103 | 21 | 23 | 3429 | 3429 | 3429 | 0.081643 | 1715 | 0.040833 | 3772 | 0.08981 | 1 | A10 | MAXW0.04410321/WT/DBE
Horizontal Wall | Maxi | MAXW.04412310/FF | 44 | 123 | 10 | 13 | 782 | 782 | 782 | 0.018619 | 293 | 0.0069762 | 895 | 0.02131 | 1.414 | A10 | MAXW0.04412310/FF
Horizontal Wall | Maxi | MAXW.04412310/FT | 44 | 123 | 10 | 13 | 997 | 997 | 997 | 0.023738 | 377 | 0.0089762 | 1140 | 0.027143 | 1.404 | A10 | MAXW0.04412310/FT
Horizontal Wall | Maxi | MAXW.04412310/WF | 44 | 123 | 10 | 13 | 1088 | 1088 | 1088 | 0.025905 | 412 | 0.0098095 | 1244 | 0.029619 | 1.4 | A10 | MAXW0.04412310/WF
Horizontal Wall | Maxi | MAXW.04412310/WT | 44 | 123 | 10 | 13 | 1244 | 1244 | 1244 | 0.029619 | 474 | 0.011286 | 1421 | 0.033833 | 1.391 | A10 | MAXW0.04412310/WT
Horizontal Wall | Maxi | MAXW.04412311/FT | 44 | 123 | 11 | 13 | 1359 | 1359 | 1359 | 0.032357 | 501 | 0.011929 | 1559 | 0.037119 | 1.44 | A10 | MAXW0.04412311/FT
Horizontal Wall | Maxi | MAXW.04412311/FT/DBE | 44 | 123 | 11 | 13 | 1959 | 1959 | 1959 | 0.046643 | 980 | 0.023333 | 2155 | 0.05131 | 1 | A10 | MAXW0.04412311/FT/DBE
Horizontal Wall | Maxi | MAXW.04412311/WF | 44 | 123 | 11 | 13 | 1453 | 1453 | 1453 | 0.034595 | 536 | 0.012762 | 1667 | 0.03969 | 1.44 | A10 | MAXW0.04412311/WF
Horizontal Wall | Maxi | MAXW.04412311/WF/DBE | 44 | 123 | 11 | 13 | 2053 | 2053 | 2053 | 0.048881 | 1027 | 0.024452 | 2258 | 0.053762 | 1 | A10 | MAXW0.04412311/WF/DBE
Horizontal Wall | Maxi | MAXW.04412311/WT | 44 | 123 | 11 | 13 | 1617 | 1617 | 1617 | 0.0385 | 597 | 0.014214 | 1855 | 0.044167 | 1.439 | A10 | MAXW0.04412311/WT
Horizontal Wall | Maxi | MAXW.04412311/WT/DBE | 44 | 123 | 11 | 13 | 2217 | 2217 | 2217 | 0.052786 | 1109 | 0.026405 | 2439 | 0.058071 | 1 | A10 | MAXW0.04412311/WT/DBE
Horizontal Wall | Maxi | MAXW.04412315/FF | 44 | 123 | 15 | 18 | 1143 | 1143 | 1143 | 0.027214 | 431 | 0.010262 | 1308 | 0.031143 | 1.409 | A10 | MAXW0.04412315/FF
Horizontal Wall | Maxi | MAXW.04412315/FT | 44 | 123 | 15 | 18 | 1543 | 1543 | 1543 | 0.036738 | 586 | 0.013952 | 1762 | 0.041952 | 1.397 | A10 | MAXW0.04412315/FT
Horizontal Wall | Maxi | MAXW.04412315/WF | 44 | 123 | 15 | 18 | 1628 | 1628 | 1628 | 0.038762 | 620 | 0.014762 | 1859 | 0.044262 | 1.392 | A10 | MAXW0.04412315/WF
Horizontal Wall | Maxi | MAXW.04412315/WT | 44 | 123 | 15 | 18 | 2018 | 2018 | 2018 | 0.048048 | 775 | 0.018452 | 2303 | 0.054833 | 1.38 | A10 | MAXW0.04412315/WT
Horizontal Wall | Maxi | MAXW.04412316/FT | 44 | 123 | 16 | 18 | 1686 | 1686 | 1686 | 0.040143 | 615 | 0.014643 | 1937 | 0.046119 | 1.455 | A10 | MAXW0.04412316/FT
Horizontal Wall | Maxi | MAXW.04412316/FT/DBE | 44 | 123 | 16 | 18 | 2646 | 2646 | 2646 | 0.063 | 1323 | 0.0315 | 2911 | 0.06931 | 1 | A10 | MAXW0.04412316/FT/DBE
Horizontal Wall | Maxi | MAXW.04412316/WF | 44 | 123 | 16 | 18 | 1771 | 1771 | 1771 | 0.042167 | 645 | 0.015357 | 2035 | 0.048452 | 1.457 | A10 | MAXW0.04412316/WF
Horizontal Wall | Maxi | MAXW.04412316/WF/DBE | 44 | 123 | 16 | 18 | 2731 | 2731 | 2731 | 0.065024 | 1366 | 0.032524 | 3004 | 0.071524 | 1 | A10 | MAXW0.04412316/WF/DBE
Horizontal Wall | Maxi | MAXW.04412316/WT | 44 | 123 | 16 | 18 | 2189 | 2189 | 2189 | 0.052119 | 795 | 0.018929 | 2517 | 0.059929 | 1.462 | A10 | MAXW0.04412316/WT
Horizontal Wall | Maxi | MAXW.04412316/WT/DBE | 44 | 123 | 16 | 18 | 3149 | 3149 | 3149 | 0.074976 | 1575 | 0.0375 | 3464 | 0.082476 | 1 | A10 | MAXW0.04412316/WT/DBE
Horizontal Wall | Maxi | MAXW.04412320/FF | 44 | 123 | 20 | 23 | 1460 | 1460 | 1460 | 0.034762 | 550 | 0.013095 | 1670 | 0.039762 | 1.409 | A10 | MAXW0.04412320/FF
Horizontal Wall | Maxi | MAXW.04412320/FT | 44 | 123 | 20 | 23 | 2095 | 2095 | 2095 | 0.049881 | 796 | 0.018952 | 2392 | 0.056952 | 1.397 | A10 | MAXW0.04412320/FT
Horizontal Wall | Maxi | MAXW.04412320/WF | 44 | 123 | 20 | 23 | 2170 | 2170 | 2170 | 0.051667 | 827 | 0.01969 | 2478 | 0.059 | 1.391 | A10 | MAXW0.04412320/WF
Horizontal Wall | Maxi | MAXW.04412320/WT | 44 | 123 | 20 | 23 | 2823 | 2823 | 2823 | 0.067214 | 1084 | 0.02581 | 3221 | 0.07669 | 1.38 | A10 | MAXW0.04412320/WT
Horizontal Wall | Maxi | MAXW.04412321/FT | 44 | 123 | 21 | 23 | 2145 | 2145 | 2145 | 0.051071 | 776 | 0.018476 | 2467 | 0.058738 | 1.467 | A10 | MAXW0.04412321/FT
Horizontal Wall | Maxi | MAXW.04412321/FT/DBE | 44 | 123 | 21 | 23 | 3105 | 3105 | 3105 | 0.073929 | 1553 | 0.036976 | 3416 | 0.081333 | 1 | A10 | MAXW0.04412321/FT/DBE
Horizontal Wall | Maxi | MAXW.04412321/WF | 44 | 123 | 21 | 23 | 2232 | 2232 | 2232 | 0.053143 | 804 | 0.019143 | 2569 | 0.061167 | 1.472 | A10 | MAXW0.04412321/WF
Horizontal Wall | Maxi | MAXW.04412321/WF/DBE | 44 | 123 | 21 | 23 | 3192 | 3192 | 3192 | 0.076 | 1596 | 0.038 | 3511 | 0.083595 | 1 | A10 | MAXW0.04412321/WF/DBE
Horizontal Wall | Maxi | MAXW.04412321/WT | 44 | 123 | 21 | 23 | 2948 | 2948 | 2948 | 0.07019 | 1055 | 0.025119 | 3393 | 0.080786 | 1.48 | A10 | MAXW0.04412321/WT
Horizontal Wall | Maxi | MAXW.04412321/WT/DBE | 44 | 123 | 21 | 23 | 3908 | 3908 | 3908 | 0.093048 | 1954 | 0.046524 | 4299 | 0.10236 | 1 | A10 | MAXW0.04412321/WT/DBE
Horizontal Wall | Maxi | MAXW.04414310/FF | 44 | 143 | 10 | 13 | 909 | 909 | 909 | 0.021643 | 341 | 0.008119 | 1040 | 0.024762 | 1.414 | A10 | MAXW0.04414310/FF
Horizontal Wall | Maxi | MAXW.04414310/FT | 44 | 143 | 10 | 13 | 1159 | 1159 | 1159 | 0.027595 | 438 | 0.010429 | 1325 | 0.031548 | 1.404 | A10 | MAXW0.04414310/FT
Horizontal Wall | Maxi | MAXW.04414310/WF | 44 | 143 | 10 | 13 | 1265 | 1265 | 1265 | 0.030119 | 479 | 0.011405 | 1446 | 0.034429 | 1.4 | A10 | MAXW0.04414310/WF
Horizontal Wall | Maxi | MAXW.04414310/WT | 44 | 143 | 10 | 13 | 1447 | 1447 | 1447 | 0.034452 | 551 | 0.013119 | 1652 | 0.039333 | 1.391 | A10 | MAXW0.04414310/WT
Horizontal Wall | Maxi | MAXW.04414311/FT | 44 | 143 | 11 | 13 | 1580 | 1580 | 1580 | 0.037619 | 583 | 0.013881 | 1812 | 0.043143 | 1.44 | A10 | MAXW0.04414311/FT
Horizontal Wall | Maxi | MAXW.04414311/FT/DBE | 44 | 143 | 11 | 13 | 2180 | 2180 | 2180 | 0.051905 | 1090 | 0.025952 | 2398 | 0.057095 | 1 | A10 | MAXW0.04414311/FT/DBE
Horizontal Wall | Maxi | MAXW.04414311/WF | 44 | 143 | 11 | 13 | 1690 | 1690 | 1690 | 0.040238 | 624 | 0.014857 | 1938 | 0.046143 | 1.44 | A10 | MAXW0.04414311/WF
Horizontal Wall | Maxi | MAXW.04414311/WF/DBE | 44 | 143 | 11 | 13 | 2290 | 2290 | 2290 | 0.054524 | 1145 | 0.027262 | 2519 | 0.059976 | 1 | A10 | MAXW0.04414311/WF/DBE
Horizontal Wall | Maxi | MAXW.04414311/WT | 44 | 143 | 11 | 13 | 1880 | 1880 | 1880 | 0.044762 | 694 | 0.016524 | 2156 | 0.051333 | 1.439 | A10 | MAXW0.04414311/WT
Horizontal Wall | Maxi | MAXW.04414311/WT/DBE | 44 | 143 | 11 | 13 | 2480 | 2480 | 2480 | 0.059048 | 1240 | 0.029524 | 2728 | 0.064952 | 1 | A10 | MAXW0.04414311/WT/DBE
Horizontal Wall | Maxi | MAXW.04414315/FF | 44 | 143 | 15 | 18 | 1329 | 1329 | 1329 | 0.031643 | 501 | 0.011929 | 1520 | 0.03619 | 1.409 | A10 | MAXW0.04414315/FF
Horizontal Wall | Maxi | MAXW.04414315/FT | 44 | 143 | 15 | 18 | 1794 | 1794 | 1794 | 0.042714 | 682 | 0.016238 | 2049 | 0.048786 | 1.397 | A10 | MAXW0.04414315/FT
Horizontal Wall | Maxi | MAXW.04414315/WF | 44 | 143 | 15 | 18 | 1892 | 1892 | 1892 | 0.045048 | 721 | 0.017167 | 2161 | 0.051452 | 1.392 | A10 | MAXW0.04414315/WF
Horizontal Wall | Maxi | MAXW.04414315/WT | 44 | 143 | 15 | 18 | 2346 | 2346 | 2346 | 0.055857 | 901 | 0.021452 | 2677 | 0.063738 | 1.38 | A10 | MAXW0.04414315/WT
Horizontal Wall | Maxi | MAXW.04414316/FT | 44 | 143 | 16 | 18 | 1960 | 1960 | 1960 | 0.046667 | 715 | 0.017024 | 2252 | 0.053619 | 1.455 | A10 | MAXW0.04414316/FT
Horizontal Wall | Maxi | MAXW.04414316/FT/DBE | 44 | 143 | 16 | 18 | 2920 | 2920 | 2920 | 0.069524 | 1460 | 0.034762 | 3212 | 0.076476 | 1 | A10 | MAXW0.04414316/FT/DBE
Horizontal Wall | Maxi | MAXW.04414316/WF | 44 | 143 | 16 | 18 | 2059 | 2059 | 2059 | 0.049024 | 749 | 0.017833 | 2366 | 0.056333 | 1.457 | A10 | MAXW0.04414316/WF
Horizontal Wall | Maxi | MAXW.04414316/WF/DBE | 44 | 143 | 16 | 18 | 3019 | 3019 | 3019 | 0.071881 | 1510 | 0.035952 | 3321 | 0.079071 | 1 | A10 | MAXW0.04414316/WF/DBE
Horizontal Wall | Maxi | MAXW.04414316/WT | 44 | 143 | 16 | 18 | 2545 | 2545 | 2545 | 0.060595 | 924 | 0.022 | 2927 | 0.06969 | 1.462 | A10 | MAXW0.04414316/WT
Horizontal Wall | Maxi | MAXW.04414316/WT/DBE | 44 | 143 | 16 | 18 | 3505 | 3505 | 3505 | 0.083452 | 1753 | 0.041738 | 3856 | 0.09181 | 1 | A10 | MAXW0.04414316/WT/DBE
Horizontal Wall | Maxi | MAXW.04414320/FF | 44 | 143 | 20 | 23 | 1698 | 1698 | 1698 | 0.040429 | 640 | 0.015238 | 1943 | 0.046262 | 1.409 | A10 | MAXW0.04414320/FF
Horizontal Wall | Maxi | MAXW.04414320/FT | 44 | 143 | 20 | 23 | 2435 | 2435 | 2435 | 0.057976 | 925 | 0.022024 | 2781 | 0.066214 | 1.397 | A10 | MAXW0.04414320/FT
Horizontal Wall | Maxi | MAXW.04414320/WF | 44 | 143 | 20 | 23 | 2523 | 2523 | 2523 | 0.060071 | 961 | 0.022881 | 2881 | 0.068595 | 1.391 | A10 | MAXW0.04414320/WF
Horizontal Wall | Maxi | MAXW.04414320/WT | 44 | 143 | 20 | 23 | 3282 | 3282 | 3282 | 0.078143 | 1260 | 0.03 | 3745 | 0.089167 | 1.38 | A10 | MAXW0.04414320/WT
Horizontal Wall | Maxi | MAXW.04414321/FT | 44 | 143 | 21 | 23 | 2493 | 2493 | 2493 | 0.059357 | 902 | 0.021476 | 2867 | 0.068262 | 1.467 | A10 | MAXW0.04414321/FT
Horizontal Wall | Maxi | MAXW.04414321/FT/DBE | 44 | 143 | 21 | 23 | 3453 | 3453 | 3453 | 0.082214 | 1727 | 0.041119 | 3798 | 0.090429 | 1 | A10 | MAXW0.04414321/FT/DBE
Horizontal Wall | Maxi | MAXW.04414321/WF | 44 | 143 | 21 | 23 | 2595 | 2595 | 2595 | 0.061786 | 934 | 0.022238 | 2987 | 0.071119 | 1.472 | A10 | MAXW0.04414321/WF
Horizontal Wall | Maxi | MAXW.04414321/WF/DBE | 44 | 143 | 21 | 23 | 3555 | 3555 | 3555 | 0.084643 | 1778 | 0.042333 | 3911 | 0.093119 | 1 | A10 | MAXW0.04414321/WF/DBE
Horizontal Wall | Maxi | MAXW.04414321/WT | 44 | 143 | 21 | 23 | 3428 | 3428 | 3428 | 0.081619 | 1227 | 0.029214 | 3946 | 0.093952 | 1.48 | A10 | MAXW0.04414321/WT
Horizontal Wall | Maxi | MAXW.04414321/WT/DBE | 44 | 143 | 21 | 23 | 4388 | 4388 | 4388 | 0.10448 | 2194 | 0.052238 | 4827 | 0.11493 | 1 | A10 | MAXW0.04414321/WT/DBE
Horizontal Wall | Maxi | MAXW.04416310/FF | 44 | 163 | 10 | 13 | 1037 | 1037 | 1037 | 0.02469 | 389 | 0.0092619 | 1186 | 0.028238 | 1.414 | A10 | MAXW0.04416310/FF
Horizontal Wall | Maxi | MAXW.04416310/FT | 44 | 163 | 10 | 13 | 1321 | 1321 | 1321 | 0.031452 | 499 | 0.011881 | 1510 | 0.035952 | 1.404 | A10 | MAXW0.04416310/FT
Horizontal Wall | Maxi | MAXW.04416310/WF | 44 | 163 | 10 | 13 | 1442 | 1442 | 1442 | 0.034333 | 547 | 0.013024 | 1648 | 0.039238 | 1.4 | A10 | MAXW0.04416310/WF
Horizontal Wall | Maxi | MAXW.04416310/WT | 44 | 163 | 10 | 13 | 1649 | 1649 | 1649 | 0.039262 | 628 | 0.014952 | 1883 | 0.044833 | 1.391 | A10 | MAXW0.04416310/WT
Horizontal Wall | Maxi | MAXW.04416311/FT | 44 | 163 | 11 | 13 | 1801 | 1801 | 1801 | 0.042881 | 665 | 0.015833 | 2066 | 0.04919 | 1.44 | A10 | MAXW0.04416311/FT
Horizontal Wall | Maxi | MAXW.04416311/FT/DBE | 44 | 163 | 11 | 13 | 3001 | 3001 | 3001 | 0.071452 | 1501 | 0.035738 | 3301 | 0.078595 | 1 | A10 | MAXW0.04416311/FT/DBE
Horizontal Wall | Maxi | MAXW.04416311/WF | 44 | 163 | 11 | 13 | 1926 | 1926 | 1926 | 0.045857 | 711 | 0.016929 | 2209 | 0.052595 | 1.44 | A10 | MAXW0.04416311/WF
Horizontal Wall | Maxi | MAXW.04416311/WF/DBE | 44 | 163 | 11 | 13 | 3126 | 3126 | 3126 | 0.074429 | 1563 | 0.037214 | 3439 | 0.081881 | 1 | A10 | MAXW0.04416311/WF/DBE
Horizontal Wall | Maxi | MAXW.04416311/WT | 44 | 163 | 11 | 13 | 2143 | 2143 | 2143 | 0.051024 | 791 | 0.018833 | 2458 | 0.058524 | 1.439 | A10 | MAXW0.04416311/WT
Horizontal Wall | Maxi | MAXW.04416311/WT/DBE | 44 | 163 | 11 | 13 | 3343 | 3343 | 3343 | 0.079595 | 1672 | 0.03981 | 3677 | 0.087548 | 1 | A10 | MAXW0.04416311/WT/DBE
Horizontal Wall | Maxi | MAXW.04416315/FF | 44 | 163 | 15 | 18 | 1514 | 1514 | 1514 | 0.036048 | 571 | 0.013595 | 1732 | 0.041238 | 1.409 | A10 | MAXW0.04416315/FF
Horizontal Wall | Maxi | MAXW.04416315/FT | 44 | 163 | 15 | 18 | 2045 | 2045 | 2045 | 0.04869 | 777 | 0.0185 | 2335 | 0.055595 | 1.397 | A10 | MAXW0.04416315/FT
Horizontal Wall | Maxi | MAXW.04416315/WF | 44 | 163 | 15 | 18 | 2157 | 2157 | 2157 | 0.051357 | 822 | 0.019571 | 2463 | 0.058643 | 1.392 | A10 | MAXW0.04416315/WF
Horizontal Wall | Maxi | MAXW.04416315/WT | 44 | 163 | 15 | 18 | 2674 | 2674 | 2674 | 0.063667 | 1027 | 0.024452 | 3051 | 0.072643 | 1.38 | A10 | MAXW0.04416315/WT
Horizontal Wall | Maxi | MAXW.04416316/FT | 44 | 163 | 16 | 18 | 2235 | 2235 | 2235 | 0.053214 | 816 | 0.019429 | 2568 | 0.061143 | 1.455 | A10 | MAXW0.04416316/FT
Horizontal Wall | Maxi | MAXW.04416316/FT/DBE | 44 | 163 | 16 | 18 | 4155 | 4155 | 4155 | 0.098929 | 2078 | 0.049476 | 4571 | 0.10883 | 1 | A10 | MAXW0.04416316/FT/DBE
Horizontal Wall | Maxi | MAXW.04416316/WF | 44 | 163 | 16 | 18 | 2347 | 2347 | 2347 | 0.055881 | 854 | 0.020333 | 2697 | 0.064214 | 1.457 | A10 | MAXW0.04416316/WF
Horizontal Wall | Maxi | MAXW.04416316/WF/DBE | 44 | 163 | 16 | 18 | 4267 | 4267 | 4267 | 0.1016 | 2134 | 0.05081 | 4694 | 0.11176 | 1 | A10 | MAXW0.04416316/WF/DBE
Horizontal Wall | Maxi | MAXW.04416316/WT | 44 | 163 | 16 | 18 | 2901 | 2901 | 2901 | 0.069071 | 1053 | 0.025071 | 3336 | 0.079429 | 1.462 | A10 | MAXW0.04416316/WT
Horizontal Wall | Maxi | MAXW.04416316/WT/DBE | 44 | 163 | 16 | 18 | 4821 | 4821 | 4821 | 0.11479 | 2411 | 0.057405 | 5303 | 0.12626 | 1 | A10 | MAXW0.04416316/WT/DBE
Horizontal Wall | Maxi | MAXW.04416320/FF | 44 | 163 | 20 | 23 | 1935 | 1935 | 1935 | 0.046071 | 729 | 0.017357 | 2214 | 0.052714 | 1.409 | A10 | MAXW0.04416320/FF
Horizontal Wall | Maxi | MAXW.04416320/FT | 44 | 163 | 20 | 23 | 2776 | 2776 | 2776 | 0.066095 | 1055 | 0.025119 | 3170 | 0.075476 | 1.397 | A10 | MAXW0.04416320/FT
Horizontal Wall | Maxi | MAXW.04416320/WF | 44 | 163 | 20 | 23 | 2875 | 2875 | 2875 | 0.068452 | 1095 | 0.026071 | 3283 | 0.078167 | 1.391 | A10 | MAXW0.04416320/WF
Horizontal Wall | Maxi | MAXW.04416320/WT | 44 | 163 | 20 | 23 | 3741 | 3741 | 3741 | 0.089071 | 1437 | 0.034214 | 4268 | 0.10162 | 1.38 | A10 | MAXW0.04416320/WT
Horizontal Wall | Maxi | MAXW.04416321/FT | 44 | 163 | 21 | 23 | 2842 | 2842 | 2842 | 0.067667 | 1029 | 0.0245 | 3268 | 0.07781 | 1.467 | A10 | MAXW0.04416321/FT
Horizontal Wall | Maxi | MAXW.04416321/FT/DBE | 44 | 163 | 21 | 23 | 4762 | 4762 | 4762 | 0.11338 | 2381 | 0.05669 | 5238 | 0.12471 | 1 | A10 | MAXW0.04416321/FT/DBE
Horizontal Wall | Maxi | MAXW.04416321/WF | 44 | 163 | 21 | 23 | 2958 | 2958 | 2958 | 0.070429 | 1065 | 0.025357 | 3405 | 0.081071 | 1.472 | A10 | MAXW0.04416321/WF
Horizontal Wall | Maxi | MAXW.04416321/WF/DBE | 44 | 163 | 21 | 23 | 4878 | 4878 | 4878 | 0.11614 | 2439 | 0.058071 | 5366 | 0.12776 | 1 | A10 | MAXW0.04416321/WF/DBE
Horizontal Wall | Maxi | MAXW.04416321/WT | 44 | 163 | 21 | 23 | 3907 | 3907 | 3907 | 0.093024 | 1399 | 0.03331 | 4497 | 0.10707 | 1.48 | A10 | MAXW0.04416321/WT
Horizontal Wall | Maxi | MAXW.04416321/WT/DBE | 44 | 163 | 21 | 23 | 5827 | 5827 | 5827 | 0.13874 | 2914 | 0.069381 | 6410 | 0.15262 | 1 | A10 | MAXW0.04416321/WT/DBE
Horizontal Wall | Maxi | MAXW.04418310/FF | 44 | 183 | 10 | 13 | 1164 | 1164 | 1164 | 0.027714 | 437 | 0.010405 | 1332 | 0.031714 | 1.414 | A10 | MAXW0.04418310/FF
Horizontal Wall | Maxi | MAXW.04418310/FT | 44 | 183 | 10 | 13 | 1484 | 1484 | 1484 | 0.035333 | 561 | 0.013357 | 1696 | 0.040381 | 1.404 | A10 | MAXW0.04418310/FT
Horizontal Wall | Maxi | MAXW.04418310/WF | 44 | 183 | 10 | 13 | 1619 | 1619 | 1619 | 0.038548 | 614 | 0.014619 | 1851 | 0.044071 | 1.4 | A10 | MAXW0.04418310/WF
Horizontal Wall | Maxi | MAXW.04418310/WT | 44 | 183 | 10 | 13 | 1851 | 1851 | 1851 | 0.044071 | 705 | 0.016786 | 2114 | 0.050333 | 1.391 | A10 | MAXW0.04418310/WT
Horizontal Wall | Maxi | MAXW.04418311/FT | 44 | 183 | 11 | 13 | 2022 | 2022 | 2022 | 0.048143 | 746 | 0.017762 | 2319 | 0.055214 | 1.44 | A10 | MAXW0.04418311/FT
Horizontal Wall | Maxi | MAXW.04418311/FT/DBE | 44 | 183 | 11 | 13 | 3222 | 3222 | 3222 | 0.076714 | 1611 | 0.038357 | 3544 | 0.084381 | 1 | A10 | MAXW0.04418311/FT/DBE
Horizontal Wall | Maxi | MAXW.04418311/WF | 44 | 183 | 11 | 13 | 2162 | 2162 | 2162 | 0.051476 | 798 | 0.019 | 2480 | 0.059048 | 1.44 | A10 | MAXW0.04418311/WF
Horizontal Wall | Maxi | MAXW.04418311/WF/DBE | 44 | 183 | 11 | 13 | 3362 | 3362 | 3362 | 0.080048 | 1681 | 0.040024 | 3698 | 0.088048 | 1 | A10 | MAXW0.04418311/WF/DBE
Horizontal Wall | Maxi | MAXW.04418311/WT | 44 | 183 | 11 | 13 | 2406 | 2406 | 2406 | 0.057286 | 888 | 0.021143 | 2760 | 0.065714 | 1.439 | A10 | MAXW0.04418311/WT
Horizontal Wall | Maxi | MAXW.04418311/WT/DBE | 44 | 183 | 11 | 13 | 3606 | 3606 | 3606 | 0.085857 | 1803 | 0.042929 | 3967 | 0.094452 | 1 | A10 | MAXW0.04418311/WT/DBE
Horizontal Wall | Maxi | MAXW.04418315/FF | 44 | 183 | 15 | 18 | 1700 | 1700 | 1700 | 0.040476 | 641 | 0.015262 | 1945 | 0.04631 | 1.409 | A10 | MAXW0.04418315/FF
Horizontal Wall | Maxi | MAXW.04418315/FT | 44 | 183 | 15 | 18 | 2295 | 2295 | 2295 | 0.054643 | 872 | 0.020762 | 2621 | 0.062405 | 1.397 | A10 | MAXW0.04418315/FT
Horizontal Wall | Maxi | MAXW.04418315/WF | 44 | 183 | 15 | 18 | 2422 | 2422 | 2422 | 0.057667 | 923 | 0.021976 | 2766 | 0.065857 | 1.392 | A10 | MAXW0.04418315/WF
Horizontal Wall | Maxi | MAXW.04418315/WT | 44 | 183 | 15 | 18 | 3003 | 3003 | 3003 | 0.0715 | 1153 | 0.027452 | 3426 | 0.081571 | 1.38 | A10 | MAXW0.04418315/WT
Horizontal Wall | Maxi | MAXW.04418316/FT | 44 | 183 | 16 | 18 | 2509 | 2509 | 2509 | 0.059738 | 916 | 0.02181 | 2883 | 0.068643 | 1.455 | A10 | MAXW0.04418316/FT
Horizontal Wall | Maxi | MAXW.04418316/FT/DBE | 44 | 183 | 16 | 18 | 4429 | 4429 | 4429 | 0.10545 | 2215 | 0.052738 | 4872 | 0.116 | 1 | A10 | MAXW0.04418316/FT/DBE
Horizontal Wall | Maxi | MAXW.04418316/WF | 44 | 183 | 16 | 18 | 2635 | 2635 | 2635 | 0.062738 | 959 | 0.022833 | 3028 | 0.072095 | 1.457 | A10 | MAXW0.04418316/WF
Horizontal Wall | Maxi | MAXW.04418316/WF/DBE | 44 | 183 | 16 | 18 | 4555 | 4555 | 4555 | 0.10845 | 2278 | 0.054238 | 5011 | 0.11931 | 1 | A10 | MAXW0.04418316/WF/DBE
Horizontal Wall | Maxi | MAXW.04418316/WT | 44 | 183 | 16 | 18 | 3257 | 3257 | 3257 | 0.077548 | 1182 | 0.028143 | 3746 | 0.08919 | 1.462 | A10 | MAXW0.04418316/WT
Horizontal Wall | Maxi | MAXW.04418316/WT/DBE | 44 | 183 | 16 | 18 | 5177 | 5177 | 5177 | 0.12326 | 2589 | 0.061643 | 5695 | 0.1356 | 1 | A10 | MAXW0.04418316/WT/DBE
Horizontal Wall | Maxi | MAXW.04418320/FF | 44 | 183 | 20 | 23 | 2173 | 2173 | 2173 | 0.051738 | 819 | 0.0195 | 2486 | 0.05919 | 1.409 | A10 | MAXW0.04418320/FF
Horizontal Wall | Maxi | MAXW.04418320/FT | 44 | 183 | 20 | 23 | 3116 | 3116 | 3116 | 0.07419 | 1184 | 0.02819 | 3558 | 0.084714 | 1.397 | A10 | MAXW0.04418320/FT
Horizontal Wall | Maxi | MAXW.04418320/WF | 44 | 183 | 20 | 23 | 3228 | 3228 | 3228 | 0.076857 | 1230 | 0.029286 | 3686 | 0.087762 | 1.391 | A10 | MAXW0.04418320/WF
Horizontal Wall | Maxi | MAXW.04418320/WT | 44 | 183 | 20 | 23 | 4200 | 4200 | 4200 | 0.1 | 1613 | 0.038405 | 4792 | 0.1141 | 1.38 | A10 | MAXW0.04418320/WT
Horizontal Wall | Maxi | MAXW.04418321/FT | 44 | 183 | 21 | 23 | 3191 | 3191 | 3191 | 0.075976 | 1155 | 0.0275 | 3670 | 0.087381 | 1.467 | A10 | MAXW0.04418321/FT
Horizontal Wall | Maxi | MAXW.04418321/FT/DBE | 44 | 183 | 21 | 23 | 5111 | 5111 | 5111 | 0.12169 | 2556 | 0.060857 | 5622 | 0.13386 | 1 | A10 | MAXW0.04418321/FT/DBE
Horizontal Wall | Maxi | MAXW.04418321/WF | 44 | 183 | 21 | 23 | 3321 | 3321 | 3321 | 0.079071 | 1196 | 0.028476 | 3822 | 0.091 | 1.472 | A10 | MAXW0.04418321/WF
Horizontal Wall | Maxi | MAXW.04418321/WF/DBE | 44 | 183 | 21 | 23 | 5241 | 5241 | 5241 | 0.12479 | 2621 | 0.062405 | 5765 | 0.13726 | 1 | A10 | MAXW0.04418321/WF/DBE
Horizontal Wall | Maxi | MAXW.04418321/WT | 44 | 183 | 21 | 23 | 4387 | 4387 | 4387 | 0.10445 | 1571 | 0.037405 | 5049 | 0.12021 | 1.48 | A10 | MAXW0.04418321/WT
Horizontal Wall | Maxi | MAXW.04418321/WT/DBE | 44 | 183 | 21 | 23 | 6307 | 6307 | 6307 | 0.15017 | 3154 | 0.075095 | 6938 | 0.16519 | 1 | A10 | MAXW0.04418321/WT/DBE
Horizontal Wall | Maxi | MAXW.04420310/FF | 44 | 203 | 10 | 13 | 1291 | 1291 | 1291 | 0.030738 | 484 | 0.011524 | 1477 | 0.035167 | 1.414 | A10 | MAXW0.04420310/FF
Horizontal Wall | Maxi | MAXW.04420310/FT | 44 | 203 | 10 | 13 | 1646 | 1646 | 1646 | 0.03919 | 622 | 0.01481 | 1881 | 0.044786 | 1.404 | A10 | MAXW0.04420310/FT
Horizontal Wall | Maxi | MAXW.04420310/WF | 44 | 203 | 10 | 13 | 1795 | 1795 | 1795 | 0.042738 | 680 | 0.01619 | 2052 | 0.048857 | 1.4 | A10 | MAXW0.04420310/WF
Horizontal Wall | Maxi | MAXW.04420310/WT | 44 | 203 | 10 | 13 | 2054 | 2054 | 2054 | 0.048905 | 783 | 0.018643 | 2346 | 0.055857 | 1.391 | A10 | MAXW0.04420310/WT
Horizontal Wall | Maxi | MAXW.04420311/FT | 44 | 203 | 11 | 13 | 2243 | 2243 | 2243 | 0.053405 | 828 | 0.019714 | 2573 | 0.061262 | 1.44 | A10 | MAXW0.04420311/FT
Horizontal Wall | Maxi | MAXW.04420311/FT/DBE | 44 | 203 | 11 | 13 | 3443 | 3443 | 3443 | 0.081976 | 1722 | 0.041 | 3787 | 0.090167 | 1 | A10 | MAXW0.04420311/FT/DBE
Horizontal Wall | Maxi | MAXW.04420311/WF | 44 | 203 | 11 | 13 | 2399 | 2399 | 2399 | 0.057119 | 885 | 0.021071 | 2752 | 0.065524 | 1.44 | A10 | MAXW0.04420311/WF
Horizontal Wall | Maxi | MAXW.04420311/WF/DBE | 44 | 203 | 11 | 13 | 3599 | 3599 | 3599 | 0.08569 | 1800 | 0.042857 | 3959 | 0.094262 | 1 | A10 | MAXW0.04420311/WF/DBE
Horizontal Wall | Maxi | MAXW.04420311/WT | 44 | 203 | 11 | 13 | 2669 | 2669 | 2669 | 0.063548 | 985 | 0.023452 | 3061 | 0.072881 | 1.439 | A10 | MAXW0.04420311/WT
Horizontal Wall | Maxi | MAXW.04420311/WT/DBE | 44 | 203 | 11 | 13 | 3869 | 3869 | 3869 | 0.092119 | 1935 | 0.046071 | 4256 | 0.10133 | 1 | A10 | MAXW0.04420311/WT/DBE
Horizontal Wall | Maxi | MAXW.04420315/FF | 44 | 203 | 15 | 18 | 1886 | 1886 | 1886 | 0.044905 | 711 | 0.016929 | 2158 | 0.051381 | 1.409 | A10 | MAXW0.04420315/FF
Horizontal Wall | Maxi | MAXW.04420315/FT | 44 | 203 | 15 | 18 | 2546 | 2546 | 2546 | 0.060619 | 967 | 0.023024 | 2908 | 0.069238 | 1.397 | A10 | MAXW0.04420315/FT
Horizontal Wall | Maxi | MAXW.04420315/WF | 44 | 203 | 15 | 18 | 2686 | 2686 | 2686 | 0.063952 | 1023 | 0.024357 | 3067 | 0.073024 | 1.392 | A10 | MAXW0.04420315/WF
Horizontal Wall | Maxi | MAXW.04420315/WT | 44 | 203 | 15 | 18 | 3331 | 3331 | 3331 | 0.07931 | 1279 | 0.030452 | 3801 | 0.0905 | 1.38 | A10 | MAXW0.04420315/WT
Horizontal Wall | Maxi | MAXW.04420316/FT | 44 | 203 | 16 | 18 | 2783 | 2783 | 2783 | 0.066262 | 1016 | 0.02419 | 3198 | 0.076143 | 1.455 | A10 | MAXW0.04420316/FT
Horizontal Wall | Maxi | MAXW.04420316/FT/DBE | 44 | 203 | 16 | 18 | 4703 | 4703 | 4703 | 0.11198 | 2352 | 0.056 | 5173 | 0.12317 | 1 | A10 | MAXW0.04420316/FT/DBE
Horizontal Wall | Maxi | MAXW.04420316/WF | 44 | 203 | 16 | 18 | 2923 | 2923 | 2923 | 0.069595 | 1064 | 0.025333 | 3359 | 0.079976 | 1.457 | A10 | MAXW0.04420316/WF
Horizontal Wall | Maxi | MAXW.04420316/WF/DBE | 44 | 203 | 16 | 18 | 4843 | 4843 | 4843 | 0.11531 | 2422 | 0.057667 | 5327 | 0.12683 | 1 | A10 | MAXW0.04420316/WF/DBE
Horizontal Wall | Maxi | MAXW.04420316/WT | 44 | 203 | 16 | 18 | 3613 | 3613 | 3613 | 0.086024 | 1312 | 0.031238 | 4155 | 0.098929 | 1.462 | A10 | MAXW0.04420316/WT
Horizontal Wall | Maxi | MAXW.04420316/WT/DBE | 44 | 203 | 16 | 18 | 5533 | 5533 | 5533 | 0.13174 | 2767 | 0.065881 | 6086 | 0.1449 | 1 | A10 | MAXW0.04420316/WT/DBE
Horizontal Wall | Maxi | MAXW.04420320/FF | 44 | 203 | 20 | 23 | 2410 | 2410 | 2410 | 0.057381 | 909 | 0.021643 | 2757 | 0.065643 | 1.409 | A10 | MAXW0.04420320/FF
Horizontal Wall | Maxi | MAXW.04420320/FT | 44 | 203 | 20 | 23 | 3457 | 3457 | 3457 | 0.08231 | 1314 | 0.031286 | 3948 | 0.094 | 1.397 | A10 | MAXW0.04420320/FT
Horizontal Wall | Maxi | MAXW.04420320/WF | 44 | 203 | 20 | 23 | 3581 | 3581 | 3581 | 0.085262 | 1364 | 0.032476 | 4090 | 0.097381 | 1.391 | A10 | MAXW0.04420320/WF
Horizontal Wall | Maxi | MAXW.04420320/WT | 44 | 203 | 20 | 23 | 4659 | 4659 | 4659 | 0.11093 | 1789 | 0.042595 | 5316 | 0.12657 | 1.38 | A10 | MAXW0.04420320/WT
Horizontal Wall | Maxi | MAXW.04420321/FT | 44 | 203 | 21 | 23 | 3540 | 3540 | 3540 | 0.084286 | 1281 | 0.0305 | 4071 | 0.096929 | 1.467 | A10 | MAXW0.04420321/FT
Horizontal Wall | Maxi | MAXW.04420321/FT/DBE | 44 | 203 | 21 | 23 | 5460 | 5460 | 5460 | 0.13 | 2730 | 0.065 | 6006 | 0.143 | 1 | A10 | MAXW0.04420321/FT/DBE
Horizontal Wall | Maxi | MAXW.04420321/WF | 44 | 203 | 21 | 23 | 3684 | 3684 | 3684 | 0.087714 | 1326 | 0.031571 | 4240 | 0.10095 | 1.472 | A10 | MAXW0.04420321/WF
Horizontal Wall | Maxi | MAXW.04420321/WF/DBE | 44 | 203 | 21 | 23 | 5604 | 5604 | 5604 | 0.13343 | 2802 | 0.066714 | 6164 | 0.14676 | 1 | A10 | MAXW0.04420321/WF/DBE
Horizontal Wall | Maxi | MAXW.04420321/WT | 44 | 203 | 21 | 23 | 4866 | 4866 | 4866 | 0.11586 | 1742 | 0.041476 | 5601 | 0.13336 | 1.48 | A10 | MAXW0.04420321/WT
Horizontal Wall | Maxi | MAXW.04420321/WT/DBE | 44 | 203 | 21 | 23 | 6786 | 6786 | 6786 | 0.16157 | 3393 | 0.080786 | 7465 | 0.17774 | 1 | A10 | MAXW0.04420321/WT/DBE
Horizontal Wall | Maxi | MAXW.05906310/FF | 59 | 63 | 10 | 13 | 557 | 557 | 557 | 0.013262 | 211 | 0.0050238 | 637 | 0.015167 | 1.4 | A10 | MAXW0.05906310/FF
Horizontal Wall | Maxi | MAXW.05906310/FT | 59 | 63 | 10 | 13 | 637 | 637 | 637 | 0.015167 | 243 | 0.0057857 | 727 | 0.01731 | 1.391 | A10 | MAXW0.05906310/FT
Horizontal Wall | Maxi | MAXW.05906310/WF | 59 | 63 | 10 | 13 | 672 | 672 | 672 | 0.016 | 257 | 0.006119 | 767 | 0.018262 | 1.386 | A10 | MAXW0.05906310/WF
Horizontal Wall | Maxi | MAXW.05906310/WT | 59 | 63 | 10 | 13 | 732 | 732 | 732 | 0.017429 | 282 | 0.0067143 | 834 | 0.019857 | 1.377 | A10 | MAXW0.05906310/WT
Horizontal Wall | Maxi | MAXW.05906311/FF | 59 | 63 | 11 | 13 | 744 | 744 | 744 | 0.017714 | 275 | 0.0065476 | 853 | 0.02031 | 1.44 | A10 | MAXW0.05906311/FF
Horizontal Wall | Maxi | MAXW.05906311/FF/DBE | 59 | 63 | 11 | 13 | 1044 | 1044 | 1044 | 0.024857 | 522 | 0.012429 | 1148 | 0.027333 | 1 | A10 | MAXW0.05906311/FF/DBE
Horizontal Wall | Maxi | MAXW.05906311/FT | 59 | 63 | 11 | 13 | 828 | 828 | 828 | 0.019714 | 306 | 0.0072857 | 950 | 0.022619 | 1.439 | A10 | MAXW0.05906311/FT
Horizontal Wall | Maxi | MAXW.05906311/FT/DBE | 59 | 63 | 11 | 13 | 1128 | 1128 | 1128 | 0.026857 | 564 | 0.013429 | 1241 | 0.029548 | 1 | A10 | MAXW0.05906311/FT/DBE
Horizontal Wall | Maxi | MAXW.05906311/WF | 59 | 63 | 11 | 13 | 866 | 866 | 866 | 0.020619 | 320 | 0.007619 | 993 | 0.023643 | 1.438 | A10 | MAXW0.05906311/WF
Horizontal Wall | Maxi | MAXW.05906311/WF/DBE | 59 | 63 | 11 | 13 | 1166 | 1166 | 1166 | 0.027762 | 583 | 0.013881 | 1283 | 0.030548 | 1 | A10 | MAXW0.05906311/WF/DBE
Horizontal Wall | Maxi | MAXW.05906311/WT | 59 | 63 | 11 | 13 | 935 | 935 | 935 | 0.022262 | 345 | 0.0082143 | 1072 | 0.025524 | 1.437 | A10 | MAXW0.05906311/WT
Horizontal Wall | Maxi | MAXW.05906311/WT/DBE | 59 | 63 | 11 | 13 | 1235 | 1235 | 1235 | 0.029405 | 618 | 0.014714 | 1359 | 0.032357 | 1 | A10 | MAXW0.05906311/WT/DBE
Horizontal Wall | Maxi | MAXW.05906315/FF | 59 | 63 | 15 | 18 | 801 | 801 | 801 | 0.019071 | 305 | 0.0072619 | 915 | 0.021786 | 1.392 | A10 | MAXW0.05906315/FF
Horizontal Wall | Maxi | MAXW.05906315/FT | 59 | 63 | 15 | 18 | 970 | 970 | 970 | 0.023095 | 372 | 0.0088571 | 1107 | 0.026357 | 1.38 | A10 | MAXW0.05906315/FT
Horizontal Wall | Maxi | MAXW.05906315/WF | 59 | 63 | 15 | 18 | 990 | 990 | 990 | 0.023571 | 382 | 0.0090952 | 1129 | 0.026881 | 1.374 | A10 | MAXW0.05906315/WF
Horizontal Wall | Maxi | MAXW.05906315/WT | 59 | 63 | 15 | 18 | 1169 | 1169 | 1169 | 0.027833 | 455 | 0.010833 | 1331 | 0.03169 | 1.362 | A10 | MAXW0.05906315/WT
Horizontal Wall | Maxi | MAXW.05906316/FF | 59 | 63 | 16 | 18 | 873 | 873 | 873 | 0.020786 | 318 | 0.0075714 | 1003 | 0.023881 | 1.457 | A10 | MAXW0.05906316/FF
Horizontal Wall | Maxi | MAXW.05906316/FF/DBE | 59 | 63 | 16 | 18 | 1353 | 1353 | 1353 | 0.032214 | 677 | 0.016119 | 1488 | 0.035429 | 1 | A10 | MAXW0.05906316/FF/DBE
Horizontal Wall | Maxi | MAXW.05906316/FT | 59 | 63 | 16 | 18 | 1056 | 1056 | 1056 | 0.025143 | 383 | 0.009119 | 1214 | 0.028905 | 1.462 | A10 | MAXW0.05906316/FT
Horizontal Wall | Maxi | MAXW.05906316/FT/DBE | 59 | 63 | 16 | 18 | 1536 | 1536 | 1536 | 0.036571 | 768 | 0.018286 | 1690 | 0.040238 | 1 | A10 | MAXW0.05906316/FT/DBE
Horizontal Wall | Maxi | MAXW.05906316/WF | 59 | 63 | 16 | 18 | 1084 | 1084 | 1084 | 0.02581 | 392 | 0.0093333 | 1247 | 0.02969 | 1.464 | A10 | MAXW0.05906316/WF
Horizontal Wall | Maxi | MAXW.05906316/WF/DBE | 59 | 63 | 16 | 18 | 1564 | 1564 | 1564 | 0.037238 | 782 | 0.018619 | 1720 | 0.040952 | 1 | A10 | MAXW0.05906316/WF/DBE
Horizontal Wall | Maxi | MAXW.05906316/WT | 59 | 63 | 16 | 18 | 1300 | 1300 | 1300 | 0.030952 | 469 | 0.011167 | 1495 | 0.035595 | 1.468 | A10 | MAXW0.05906316/WT
Horizontal Wall | Maxi | MAXW.05906316/WT/DBE | 59 | 63 | 16 | 18 | 1780 | 1780 | 1780 | 0.042381 | 890 | 0.02119 | 1958 | 0.046619 | 1 | A10 | MAXW0.05906316/WT/DBE
Horizontal Wall | Maxi | MAXW.05906320/FF | 59 | 63 | 20 | 23 | 1020 | 1020 | 1020 | 0.024286 | 389 | 0.0092619 | 1165 | 0.027738 | 1.391 | A10 | MAXW0.05906320/FF
Horizontal Wall | Maxi | MAXW.05906320/FT | 59 | 63 | 20 | 23 | 1314 | 1314 | 1314 | 0.031286 | 505 | 0.012024 | 1499 | 0.03569 | 1.38 | A10 | MAXW0.05906320/FT
Horizontal Wall | Maxi | MAXW.05906320/WF | 59 | 63 | 20 | 23 | 1300 | 1300 | 1300 | 0.030952 | 502 | 0.011952 | 1482 | 0.035286 | 1.374 | A10 | MAXW0.05906320/WF
Horizontal Wall | Maxi | MAXW.05906320/WT | 59 | 63 | 20 | 23 | 1633 | 1633 | 1633 | 0.038881 | 635 | 0.015119 | 1860 | 0.044286 | 1.362 | A10 | MAXW0.05906320/WT
Horizontal Wall | Maxi | MAXW.05906321/FF | 59 | 63 | 21 | 23 | 1053 | 1053 | 1053 | 0.025071 | 379 | 0.0090238 | 1212 | 0.028857 | 1.472 | A10 | MAXW0.05906321/FF
Horizontal Wall | Maxi | MAXW.05906321/FF/DBE | 59 | 63 | 21 | 23 | 1533 | 1533 | 1533 | 0.0365 | 767 | 0.018262 | 1686 | 0.040143 | 1 | A10 | MAXW0.05906321/FF/DBE
Horizontal Wall | Maxi | MAXW.05906321/FT | 59 | 63 | 21 | 23 | 1377 | 1377 | 1377 | 0.032786 | 493 | 0.011738 | 1585 | 0.037738 | 1.48 | A10 | MAXW0.05906321/FT
Horizontal Wall | Maxi | MAXW.05906321/FT/DBE | 59 | 63 | 21 | 23 | 1857 | 1857 | 1857 | 0.044214 | 929 | 0.022119 | 2043 | 0.048643 | 1 | A10 | MAXW0.05906321/FT/DBE
Horizontal Wall | Maxi | MAXW.05906321/WF | 59 | 63 | 21 | 23 | 1401 | 1401 | 1401 | 0.033357 | 500 | 0.011905 | 1614 | 0.038429 | 1.484 | A10 | MAXW0.05906321/WF
Horizontal Wall | Maxi | MAXW.05906321/WF/DBE | 59 | 63 | 21 | 23 | 1881 | 1881 | 1881 | 0.044786 | 941 | 0.022405 | 2069 | 0.049262 | 1 | A10 | MAXW0.05906321/WF/DBE
Horizontal Wall | Maxi | MAXW.05906321/WT | 59 | 63 | 21 | 23 | 1796 | 1796 | 1796 | 0.042762 | 639 | 0.015214 | 2071 | 0.04931 | 1.492 | A10 | MAXW0.05906321/WT
Horizontal Wall | Maxi | MAXW.05906321/WT/DBE | 59 | 63 | 21 | 23 | 2276 | 2276 | 2276 | 0.05419 | 1138 | 0.027095 | 2504 | 0.059619 | 1 | A10 | MAXW0.05906321/WT/DBE
Horizontal Wall | Maxi | MAXW.05908310/FF | 59 | 83 | 10 | 13 | 734 | 734 | 734 | 0.017476 | 278 | 0.006619 | 839 | 0.019976 | 1.4 | A10 | MAXW0.05908310/FF
Horizontal Wall | Maxi | MAXW.05908310/FT | 59 | 83 | 10 | 13 | 840 | 840 | 840 | 0.02 | 320 | 0.007619 | 959 | 0.022833 | 1.391 | A10 | MAXW0.05908310/FT
Horizontal Wall | Maxi | MAXW.05908310/WF | 59 | 83 | 10 | 13 | 885 | 885 | 885 | 0.021071 | 339 | 0.0080714 | 1010 | 0.024048 | 1.386 | A10 | MAXW0.05908310/WF
Horizontal Wall | Maxi | MAXW.05908310/WT | 59 | 83 | 10 | 13 | 965 | 965 | 965 | 0.022976 | 372 | 0.0088571 | 1100 | 0.02619 | 1.377 | A10 | MAXW0.05908310/WT
Horizontal Wall | Maxi | MAXW.05908311/FF | 59 | 83 | 11 | 13 | 981 | 981 | 981 | 0.023357 | 362 | 0.008619 | 1125 | 0.026786 | 1.44 | A10 | MAXW0.05908311/FF
Horizontal Wall | Maxi | MAXW.05908311/FF/DBE | 59 | 83 | 11 | 13 | 1281 | 1281 | 1281 | 0.0305 | 641 | 0.015262 | 1409 | 0.033548 | 1 | A10 | MAXW0.05908311/FF/DBE
Horizontal Wall | Maxi | MAXW.05908311/FT | 59 | 83 | 11 | 13 | 1091 | 1091 | 1091 | 0.025976 | 403 | 0.0095952 | 1251 | 0.029786 | 1.439 | A10 | MAXW0.05908311/FT
Horizontal Wall | Maxi | MAXW.05908311/FT/DBE | 59 | 83 | 11 | 13 | 1391 | 1391 | 1391 | 0.033119 | 696 | 0.016571 | 1530 | 0.036429 | 1 | A10 | MAXW0.05908311/FT/DBE
Horizontal Wall | Maxi | MAXW.05908311/WF | 59 | 83 | 11 | 13 | 1141 | 1141 | 1141 | 0.027167 | 421 | 0.010024 | 1309 | 0.031167 | 1.438 | A10 | MAXW0.05908311/WF
Horizontal Wall | Maxi | MAXW.05908311/WF/DBE | 59 | 83 | 11 | 13 | 1441 | 1441 | 1441 | 0.03431 | 721 | 0.017167 | 1585 | 0.037738 | 1 | A10 | MAXW0.05908311/WF/DBE
Horizontal Wall | Maxi | MAXW.05908311/WT | 59 | 83 | 11 | 13 | 1231 | 1231 | 1231 | 0.02931 | 454 | 0.01081 | 1412 | 0.033619 | 1.437 | A10 | MAXW0.05908311/WT
Horizontal Wall | Maxi | MAXW.05908311/WT/DBE | 59 | 83 | 11 | 13 | 1531 | 1531 | 1531 | 0.036452 | 766 | 0.018238 | 1684 | 0.040095 | 1 | A10 | MAXW0.05908311/WT/DBE
Horizontal Wall | Maxi | MAXW.05908315/FF | 59 | 83 | 15 | 18 | 1056 | 1056 | 1056 | 0.025143 | 402 | 0.0095714 | 1206 | 0.028714 | 1.392 | A10 | MAXW0.05908315/FF
Horizontal Wall | Maxi | MAXW.05908315/FT | 59 | 83 | 15 | 18 | 1278 | 1278 | 1278 | 0.030429 | 491 | 0.01169 | 1458 | 0.034714 | 1.38 | A10 | MAXW0.05908315/FT
Horizontal Wall | Maxi | MAXW.05908315/WF | 59 | 83 | 15 | 18 | 1304 | 1304 | 1304 | 0.031048 | 503 | 0.011976 | 1487 | 0.035405 | 1.374 | A10 | MAXW0.05908315/WF
Horizontal Wall | Maxi | MAXW.05908315/WT | 59 | 83 | 15 | 18 | 1541 | 1541 | 1541 | 0.03669 | 599 | 0.014262 | 1755 | 0.041786 | 1.362 | A10 | MAXW0.05908315/WT
Horizontal Wall | Maxi | MAXW.05908316/FF | 59 | 83 | 16 | 18 | 1150 | 1150 | 1150 | 0.027381 | 419 | 0.0099762 | 1321 | 0.031452 | 1.457 | A10 | MAXW0.05908316/FF
Horizontal Wall | Maxi | MAXW.05908316/FF/DBE | 59 | 83 | 16 | 18 | 1630 | 1630 | 1630 | 0.03881 | 815 | 0.019405 | 1793 | 0.04269 | 1 | A10 | MAXW0.05908316/FF/DBE
Horizontal Wall | Maxi | MAXW.05908316/FT | 59 | 83 | 16 | 18 | 1391 | 1391 | 1391 | 0.033119 | 505 | 0.012024 | 1600 | 0.038095 | 1.462 | A10 | MAXW0.05908316/FT
Horizontal Wall | Maxi | MAXW.05908316/FT/DBE | 59 | 83 | 16 | 18 | 1871 | 1871 | 1871 | 0.044548 | 936 | 0.022286 | 2058 | 0.049 | 1 | A10 | MAXW0.05908316/FT/DBE
Horizontal Wall | Maxi | MAXW.05908316/WF | 59 | 83 | 16 | 18 | 1429 | 1429 | 1429 | 0.034024 | 517 | 0.01231 | 1643 | 0.039119 | 1.464 | A10 | MAXW0.05908316/WF
Horizontal Wall | Maxi | MAXW.05908316/WF/DBE | 59 | 83 | 16 | 18 | 1909 | 1909 | 1909 | 0.045452 | 955 | 0.022738 | 2100 | 0.05 | 1 | A10 | MAXW0.05908316/WF/DBE
Horizontal Wall | Maxi | MAXW.05908316/WT | 59 | 83 | 16 | 18 | 1713 | 1713 | 1713 | 0.040786 | 618 | 0.014714 | 1970 | 0.046905 | 1.468 | A10 | MAXW0.05908316/WT
Horizontal Wall | Maxi | MAXW.05908316/WT/DBE | 59 | 83 | 16 | 18 | 2193 | 2193 | 2193 | 0.052214 | 1097 | 0.026119 | 2412 | 0.057429 | 1 | A10 | MAXW0.05908316/WT/DBE
Horizontal Wall | Maxi | MAXW.05908320/FF | 59 | 83 | 20 | 23 | 1344 | 1344 | 1344 | 0.032 | 512 | 0.01219 | 1535 | 0.036548 | 1.391 | A10 | MAXW0.05908320/FF
Horizontal Wall | Maxi | MAXW.05908320/FT | 59 | 83 | 20 | 23 | 1731 | 1731 | 1731 | 0.041214 | 665 | 0.015833 | 1975 | 0.047024 | 1.38 | A10 | MAXW0.05908320/FT
Horizontal Wall | Maxi | MAXW.05908320/WF | 59 | 83 | 20 | 23 | 1713 | 1713 | 1713 | 0.040786 | 661 | 0.015738 | 1953 | 0.0465 | 1.374 | A10 | MAXW0.05908320/WF
Horizontal Wall | Maxi | MAXW.05908320/WT | 59 | 83 | 20 | 23 | 2152 | 2152 | 2152 | 0.051238 | 837 | 0.019929 | 2451 | 0.058357 | 1.362 | A10 | MAXW0.05908320/WT
Horizontal Wall | Maxi | MAXW.05908321/FF | 59 | 83 | 21 | 23 | 1387 | 1387 | 1387 | 0.033024 | 499 | 0.011881 | 1596 | 0.038 | 1.472 | A10 | MAXW0.05908321/FF
Horizontal Wall | Maxi | MAXW.05908321/FF/DBE | 59 | 83 | 21 | 23 | 1867 | 1867 | 1867 | 0.044452 | 934 | 0.022238 | 2054 | 0.048905 | 1 | A10 | MAXW0.05908321/FF/DBE
Horizontal Wall | Maxi | MAXW.05908321/FT | 59 | 83 | 21 | 23 | 1814 | 1814 | 1814 | 0.04319 | 649 | 0.015452 | 2088 | 0.049714 | 1.48 | A10 | MAXW0.05908321/FT
Horizontal Wall | Maxi | MAXW.05908321/FT/DBE | 59 | 83 | 21 | 23 | 2294 | 2294 | 2294 | 0.054619 | 1147 | 0.02731 | 2523 | 0.060071 | 1 | A10 | MAXW0.05908321/FT/DBE
Horizontal Wall | Maxi | MAXW.05908321/WF | 59 | 83 | 21 | 23 | 1846 | 1846 | 1846 | 0.043952 | 659 | 0.01569 | 2127 | 0.050643 | 1.484 | A10 | MAXW0.05908321/WF
Horizontal Wall | Maxi | MAXW.05908321/WF/DBE | 59 | 83 | 21 | 23 | 2326 | 2326 | 2326 | 0.055381 | 1163 | 0.02769 | 2559 | 0.060929 | 1 | A10 | MAXW0.05908321/WF/DBE
Horizontal Wall | Maxi | MAXW.05908321/WT | 59 | 83 | 21 | 23 | 2366 | 2366 | 2366 | 0.056333 | 842 | 0.020048 | 2728 | 0.064952 | 1.492 | A10 | MAXW0.05908321/WT
Horizontal Wall | Maxi | MAXW.05908321/WT/DBE | 59 | 83 | 21 | 23 | 2846 | 2846 | 2846 | 0.067762 | 1423 | 0.033881 | 3131 | 0.074548 | 1 | A10 | MAXW0.05908321/WT/DBE
Horizontal Wall | Maxi | MAXW.05910310/FF | 59 | 103 | 10 | 13 | 911 | 911 | 911 | 0.02169 | 345 | 0.0082143 | 1041 | 0.024786 | 1.4 | A10 | MAXW0.05910310/FF
Horizontal Wall | Maxi | MAXW.05910310/FT | 59 | 103 | 10 | 13 | 1042 | 1042 | 1042 | 0.02481 | 397 | 0.0094524 | 1190 | 0.028333 | 1.391 | A10 | MAXW0.05910310/FT
Horizontal Wall | Maxi | MAXW.05910310/WF | 59 | 103 | 10 | 13 | 1098 | 1098 | 1098 | 0.026143 | 421 | 0.010024 | 1253 | 0.029833 | 1.386 | A10 | MAXW0.05910310/WF
Horizontal Wall | Maxi | MAXW.05910310/WT | 59 | 103 | 10 | 13 | 1197 | 1197 | 1197 | 0.0285 | 461 | 0.010976 | 1365 | 0.0325 | 1.377 | A10 | MAXW0.05910310/WT
Horizontal Wall | Maxi | MAXW.05910311/FF | 59 | 103 | 11 | 13 | 1217 | 1217 | 1217 | 0.028976 | 449 | 0.01069 | 1396 | 0.033238 | 1.44 | A10 | MAXW0.05910311/FF
Horizontal Wall | Maxi | MAXW.05910311/FF/DBE | 59 | 103 | 11 | 13 | 1817 | 1817 | 1817 | 0.043262 | 909 | 0.021643 | 1999 | 0.047595 | 1 | A10 | MAXW0.05910311/FF/DBE
Horizontal Wall | Maxi | MAXW.05910311/FT | 59 | 103 | 11 | 13 | 1354 | 1354 | 1354 | 0.032238 | 500 | 0.011905 | 1553 | 0.036976 | 1.439 | A10 | MAXW0.05910311/FT
Horizontal Wall | Maxi | MAXW.05910311/FT/DBE | 59 | 103 | 11 | 13 | 1954 | 1954 | 1954 | 0.046524 | 977 | 0.023262 | 2149 | 0.051167 | 1 | A10 | MAXW0.05910311/FT/DBE
Horizontal Wall | Maxi | MAXW.05910311/WF | 59 | 103 | 11 | 13 | 1416 | 1416 | 1416 | 0.033714 | 523 | 0.012452 | 1624 | 0.038667 | 1.438 | A10 | MAXW0.05910311/WF
Horizontal Wall | Maxi | MAXW.05910311/WF/DBE | 59 | 103 | 11 | 13 | 2016 | 2016 | 2016 | 0.048 | 1008 | 0.024 | 2218 | 0.05281 | 1 | A10 | MAXW0.05910311/WF/DBE
Horizontal Wall | Maxi | MAXW.05910311/WT | 59 | 103 | 11 | 13 | 1528 | 1528 | 1528 | 0.036381 | 564 | 0.013429 | 1753 | 0.041738 | 1.437 | A10 | MAXW0.05910311/WT
Horizontal Wall | Maxi | MAXW.05910311/WT/DBE | 59 | 103 | 11 | 13 | 2128 | 2128 | 2128 | 0.050667 | 1064 | 0.025333 | 2341 | 0.055738 | 1 | A10 | MAXW0.05910311/WT/DBE
Horizontal Wall | Maxi | MAXW.05910315/FF | 59 | 103 | 15 | 18 | 1310 | 1310 | 1310 | 0.03119 | 499 | 0.011881 | 1496 | 0.035619 | 1.392 | A10 | MAXW0.05910315/FF
Horizontal Wall | Maxi | MAXW.05910315/FT | 59 | 103 | 15 | 18 | 1586 | 1586 | 1586 | 0.037762 | 609 | 0.0145 | 1810 | 0.043095 | 1.38 | A10 | MAXW0.05910315/FT
Horizontal Wall | Maxi | MAXW.05910315/WF | 59 | 103 | 15 | 18 | 1618 | 1618 | 1618 | 0.038524 | 625 | 0.014881 | 1845 | 0.043929 | 1.374 | A10 | MAXW0.05910315/WF
Horizontal Wall | Maxi | MAXW.05910315/WT | 59 | 103 | 15 | 18 | 1912 | 1912 | 1912 | 0.045524 | 744 | 0.017714 | 2178 | 0.051857 | 1.362 | A10 | MAXW0.05910315/WT
Horizontal Wall | Maxi | MAXW.05910316/FF | 59 | 103 | 16 | 18 | 1427 | 1427 | 1427 | 0.033976 | 519 | 0.012357 | 1640 | 0.039048 | 1.457 | A10 | MAXW0.05910316/FF
Horizontal Wall | Maxi | MAXW.05910316/FF/DBE | 59 | 103 | 16 | 18 | 2387 | 2387 | 2387 | 0.056833 | 1194 | 0.028429 | 2626 | 0.062524 | 1 | A10 | MAXW0.05910316/FF/DBE
Horizontal Wall | Maxi | MAXW.05910316/FT | 59 | 103 | 16 | 18 | 1726 | 1726 | 1726 | 0.041095 | 627 | 0.014929 | 1985 | 0.047262 | 1.462 | A10 | MAXW0.05910316/FT
Horizontal Wall | Maxi | MAXW.05910316/FT/DBE | 59 | 103 | 16 | 18 | 2686 | 2686 | 2686 | 0.063952 | 1343 | 0.031976 | 2955 | 0.070357 | 1 | A10 | MAXW0.05910316/FT/DBE
Horizontal Wall | Maxi | MAXW.05910316/WF | 59 | 103 | 16 | 18 | 1773 | 1773 | 1773 | 0.042214 | 642 | 0.015286 | 2039 | 0.048548 | 1.464 | A10 | MAXW0.05910316/WF
Horizontal Wall | Maxi | MAXW.05910316/WF/DBE | 59 | 103 | 16 | 18 | 2733 | 2733 | 2733 | 0.065071 | 1367 | 0.032548 | 3006 | 0.071571 | 1 | A10 | MAXW0.05910316/WF/DBE
Horizontal Wall | Maxi | MAXW.05910316/WT | 59 | 103 | 16 | 18 | 2126 | 2126 | 2126 | 0.050619 | 767 | 0.018262 | 2445 | 0.058214 | 1.468 | A10 | MAXW0.05910316/WT
Horizontal Wall | Maxi | MAXW.05910316/WT/DBE | 59 | 103 | 16 | 18 | 3086 | 3086 | 3086 | 0.073476 | 1543 | 0.036738 | 3395 | 0.080833 | 1 | A10 | MAXW0.05910316/WT/DBE
Horizontal Wall | Maxi | MAXW.05910320/FF | 59 | 103 | 20 | 23 | 1668 | 1668 | 1668 | 0.039714 | 636 | 0.015143 | 1905 | 0.045357 | 1.391 | A10 | MAXW0.05910320/FF
Horizontal Wall | Maxi | MAXW.05910320/FT | 59 | 103 | 20 | 23 | 2148 | 2148 | 2148 | 0.051143 | 825 | 0.019643 | 2451 | 0.058357 | 1.38 | A10 | MAXW0.05910320/FT
Horizontal Wall | Maxi | MAXW.05910320/WF | 59 | 103 | 20 | 23 | 2126 | 2126 | 2126 | 0.050619 | 821 | 0.019548 | 2424 | 0.057714 | 1.374 | A10 | MAXW0.05910320/WF
Horizontal Wall | Maxi | MAXW.05910320/WT | 59 | 103 | 20 | 23 | 2670 | 2670 | 2670 | 0.063571 | 1039 | 0.024738 | 3041 | 0.072405 | 1.362 | A10 | MAXW0.05910320/WT
Horizontal Wall | Maxi | MAXW.05910321/FF | 59 | 103 | 21 | 23 | 1721 | 1721 | 1721 | 0.040976 | 620 | 0.014762 | 1981 | 0.047167 | 1.472 | A10 | MAXW0.05910321/FF
Horizontal Wall | Maxi | MAXW.05910321/FF/DBE | 59 | 103 | 21 | 23 | 2681 | 2681 | 2681 | 0.063833 | 1341 | 0.031929 | 2949 | 0.070214 | 1 | A10 | MAXW0.05910321/FF/DBE
Horizontal Wall | Maxi | MAXW.05910321/FT | 59 | 103 | 21 | 23 | 2251 | 2251 | 2251 | 0.053595 | 806 | 0.01919 | 2591 | 0.06169 | 1.48 | A10 | MAXW0.05910321/FT
Horizontal Wall | Maxi | MAXW.05910321/FT/DBE | 59 | 103 | 21 | 23 | 3211 | 3211 | 3211 | 0.076452 | 1606 | 0.038238 | 3532 | 0.084095 | 1 | A10 | MAXW0.05910321/FT/DBE
Horizontal Wall | Maxi | MAXW.05910321/WF | 59 | 103 | 21 | 23 | 2291 | 2291 | 2291 | 0.054548 | 818 | 0.019476 | 2639 | 0.062833 | 1.484 | A10 | MAXW0.05910321/WF
Horizontal Wall | Maxi | MAXW.05910321/WF/DBE | 59 | 103 | 21 | 23 | 3251 | 3251 | 3251 | 0.077405 | 1626 | 0.038714 | 3576 | 0.085143 | 1 | A10 | MAXW0.05910321/WF/DBE
Horizontal Wall | Maxi | MAXW.05910321/WT | 59 | 103 | 21 | 23 | 2936 | 2936 | 2936 | 0.069905 | 1045 | 0.024881 | 3385 | 0.080595 | 1.492 | A10 | MAXW0.05910321/WT
Horizontal Wall | Maxi | MAXW.05910321/WT/DBE | 59 | 103 | 21 | 23 | 3896 | 3896 | 3896 | 0.092762 | 1948 | 0.046381 | 4286 | 0.10205 | 1 | A10 | MAXW0.05910321/WT/DBE
Horizontal Wall | Maxi | MAXW.05912310/FF | 59 | 123 | 10 | 13 | 1088 | 1088 | 1088 | 0.025905 | 412 | 0.0098095 | 1244 | 0.029619 | 1.4 | A10 | MAXW0.05912310/FF
Horizontal Wall | Maxi | MAXW.05912310/FT | 59 | 123 | 10 | 13 | 1244 | 1244 | 1244 | 0.029619 | 474 | 0.011286 | 1421 | 0.033833 | 1.391 | A10 | MAXW0.05912310/FT
Horizontal Wall | Maxi | MAXW.05912310/WF | 59 | 123 | 10 | 13 | 1311 | 1311 | 1311 | 0.031214 | 502 | 0.011952 | 1496 | 0.035619 | 1.386 | A10 | MAXW0.05912310/WF
Horizontal Wall | Maxi | MAXW.05912310/WT | 59 | 123 | 10 | 13 | 1429 | 1429 | 1429 | 0.034024 | 550 | 0.013095 | 1629 | 0.038786 | 1.377 | A10 | MAXW0.05912310/WT
Horizontal Wall | Maxi | MAXW.05912311/FF | 59 | 123 | 11 | 13 | 1453 | 1453 | 1453 | 0.034595 | 536 | 0.012762 | 1667 | 0.03969 | 1.44 | A10 | MAXW0.05912311/FF
Horizontal Wall | Maxi | MAXW.05912311/FF/DBE | 59 | 123 | 11 | 13 | 2053 | 2053 | 2053 | 0.048881 | 1027 | 0.024452 | 2258 | 0.053762 | 1 | A10 | MAXW0.05912311/FF/DBE
Horizontal Wall | Maxi | MAXW.05912311/FT | 59 | 123 | 11 | 13 | 1617 | 1617 | 1617 | 0.0385 | 597 | 0.014214 | 1855 | 0.044167 | 1.439 | A10 | MAXW0.05912311/FT
Horizontal Wall | Maxi | MAXW.05912311/FT/DBE | 59 | 123 | 11 | 13 | 2217 | 2217 | 2217 | 0.052786 | 1109 | 0.026405 | 2439 | 0.058071 | 1 | A10 | MAXW0.05912311/FT/DBE
Horizontal Wall | Maxi | MAXW.05912311/WF | 59 | 123 | 11 | 13 | 1691 | 1691 | 1691 | 0.040262 | 624 | 0.014857 | 1940 | 0.04619 | 1.438 | A10 | MAXW0.05912311/WF
Horizontal Wall | Maxi | MAXW.05912311/WF/DBE | 59 | 123 | 11 | 13 | 2291 | 2291 | 2291 | 0.054548 | 1146 | 0.027286 | 2520 | 0.06 | 1 | A10 | MAXW0.05912311/WF/DBE
Horizontal Wall | Maxi | MAXW.05912311/WT | 59 | 123 | 11 | 13 | 1825 | 1825 | 1825 | 0.043452 | 673 | 0.016024 | 2093 | 0.049833 | 1.437 | A10 | MAXW0.05912311/WT
Horizontal Wall | Maxi | MAXW.05912311/WT/DBE | 59 | 123 | 11 | 13 | 2425 | 2425 | 2425 | 0.057738 | 1213 | 0.028881 | 2668 | 0.063524 | 1 | A10 | MAXW0.05912311/WT/DBE
Horizontal Wall | Maxi | MAXW.05912315/FF | 59 | 123 | 15 | 18 | 1564 | 1564 | 1564 | 0.037238 | 596 | 0.01419 | 1786 | 0.042524 | 1.392 | A10 | MAXW0.05912315/FF
Horizontal Wall | Maxi | MAXW.05912315/FT | 59 | 123 | 15 | 18 | 1894 | 1894 | 1894 | 0.045095 | 727 | 0.01731 | 2161 | 0.051452 | 1.38 | A10 | MAXW0.05912315/FT
Horizontal Wall | Maxi | MAXW.05912315/WF | 59 | 123 | 15 | 18 | 1932 | 1932 | 1932 | 0.046 | 746 | 0.017762 | 2202 | 0.052429 | 1.374 | A10 | MAXW0.05912315/WF
Horizontal Wall | Maxi | MAXW.05912315/WT | 59 | 123 | 15 | 18 | 2283 | 2283 | 2283 | 0.054357 | 888 | 0.021143 | 2600 | 0.061905 | 1.362 | A10 | MAXW0.05912315/WT
Horizontal Wall | Maxi | MAXW.05912316/FF | 59 | 123 | 16 | 18 | 1704 | 1704 | 1704 | 0.040571 | 620 | 0.014762 | 1958 | 0.046619 | 1.457 | A10 | MAXW0.05912316/FF
Horizontal Wall | Maxi | MAXW.05912316/FF/DBE | 59 | 123 | 16 | 18 | 2664 | 2664 | 2664 | 0.063429 | 1332 | 0.031714 | 2930 | 0.069762 | 1 | A10 | MAXW0.05912316/FF/DBE
Horizontal Wall | Maxi | MAXW.05912316/FT | 59 | 123 | 16 | 18 | 2061 | 2061 | 2061 | 0.049071 | 748 | 0.01781 | 2370 | 0.056429 | 1.462 | A10 | MAXW0.05912316/FT
Horizontal Wall | Maxi | MAXW.05912316/FT/DBE | 59 | 123 | 16 | 18 | 3021 | 3021 | 3021 | 0.071929 | 1511 | 0.035976 | 3323 | 0.079119 | 1 | A10 | MAXW0.05912316/FT/DBE
Horizontal Wall | Maxi | MAXW.05912316/WF | 59 | 123 | 16 | 18 | 2117 | 2117 | 2117 | 0.050405 | 766 | 0.018238 | 2435 | 0.057976 | 1.464 | A10 | MAXW0.05912316/WF
Horizontal Wall | Maxi | MAXW.05912316/WF/DBE | 59 | 123 | 16 | 18 | 3077 | 3077 | 3077 | 0.073262 | 1539 | 0.036643 | 3385 | 0.080595 | 1 | A10 | MAXW0.05912316/WF/DBE
Horizontal Wall | Maxi | MAXW.05912316/WT | 59 | 123 | 16 | 18 | 2539 | 2539 | 2539 | 0.060452 | 917 | 0.021833 | 2920 | 0.069524 | 1.468 | A10 | MAXW0.05912316/WT
Horizontal Wall | Maxi | MAXW.05912316/WT/DBE | 59 | 123 | 16 | 18 | 3499 | 3499 | 3499 | 0.08331 | 1750 | 0.041667 | 3849 | 0.091643 | 1 | A10 | MAXW0.05912316/WT/DBE
Horizontal Wall | Maxi | MAXW.05912320/FF | 59 | 123 | 20 | 23 | 1992 | 1992 | 1992 | 0.047429 | 759 | 0.018071 | 2275 | 0.054167 | 1.391 | A10 | MAXW0.05912320/FF
Horizontal Wall | Maxi | MAXW.05912320/FT | 59 | 123 | 20 | 23 | 2565 | 2565 | 2565 | 0.061071 | 985 | 0.023452 | 2927 | 0.06969 | 1.38 | A10 | MAXW0.05912320/FT
Horizontal Wall | Maxi | MAXW.05912320/WF | 59 | 123 | 20 | 23 | 2539 | 2539 | 2539 | 0.060452 | 980 | 0.023333 | 2894 | 0.068905 | 1.374 | A10 | MAXW0.05912320/WF
Horizontal Wall | Maxi | MAXW.05912320/WT | 59 | 123 | 20 | 23 | 3188 | 3188 | 3188 | 0.075905 | 1240 | 0.029524 | 3631 | 0.086452 | 1.362 | A10 | MAXW0.05912320/WT
Horizontal Wall | Maxi | MAXW.05912321/FF | 59 | 123 | 21 | 23 | 2055 | 2055 | 2055 | 0.048929 | 740 | 0.017619 | 2365 | 0.05631 | 1.472 | A10 | MAXW0.05912321/FF
Horizontal Wall | Maxi | MAXW.05912321/FF/DBE | 59 | 123 | 21 | 23 | 3015 | 3015 | 3015 | 0.071786 | 1508 | 0.035905 | 3317 | 0.078976 | 1 | A10 | MAXW0.05912321/FF/DBE
Horizontal Wall | Maxi | MAXW.05912321/FT | 59 | 123 | 21 | 23 | 2688 | 2688 | 2688 | 0.064 | 962 | 0.022905 | 3094 | 0.073667 | 1.48 | A10 | MAXW0.05912321/FT
Horizontal Wall | Maxi | MAXW.05912321/FT/DBE | 59 | 123 | 21 | 23 | 3648 | 3648 | 3648 | 0.086857 | 1824 | 0.043429 | 4013 | 0.095548 | 1 | A10 | MAXW0.05912321/FT/DBE
Horizontal Wall | Maxi | MAXW.05912321/WF | 59 | 123 | 21 | 23 | 2736 | 2736 | 2736 | 0.065143 | 977 | 0.023262 | 3152 | 0.075048 | 1.484 | A10 | MAXW0.05912321/WF
Horizontal Wall | Maxi | MAXW.05912321/WF/DBE | 59 | 123 | 21 | 23 | 3696 | 3696 | 3696 | 0.088 | 1848 | 0.044 | 4066 | 0.09681 | 1 | A10 | MAXW0.05912321/WF/DBE
Horizontal Wall | Maxi | MAXW.05912321/WT | 59 | 123 | 21 | 23 | 3506 | 3506 | 3506 | 0.083476 | 1248 | 0.029714 | 4042 | 0.096238 | 1.492 | A10 | MAXW0.05912321/WT
Horizontal Wall | Maxi | MAXW.05912321/WT/DBE | 59 | 123 | 21 | 23 | 4466 | 4466 | 4466 | 0.10633 | 2233 | 0.053167 | 4913 | 0.11698 | 1 | A10 | MAXW0.05912321/WT/DBE
Horizontal Wall | Maxi | MAXW.05914310/FF | 59 | 143 | 10 | 13 | 1265 | 1265 | 1265 | 0.030119 | 479 | 0.011405 | 1446 | 0.034429 | 1.4 | A10 | MAXW0.05914310/FF
Horizontal Wall | Maxi | MAXW.05914310/FT | 59 | 143 | 10 | 13 | 1447 | 1447 | 1447 | 0.034452 | 551 | 0.013119 | 1652 | 0.039333 | 1.391 | A10 | MAXW0.05914310/FT
Horizontal Wall | Maxi | MAXW.05914310/WF | 59 | 143 | 10 | 13 | 1524 | 1524 | 1524 | 0.036286 | 584 | 0.013905 | 1739 | 0.041405 | 1.386 | A10 | MAXW0.05914310/WF
Horizontal Wall | Maxi | MAXW.05914310/WT | 59 | 143 | 10 | 13 | 1662 | 1662 | 1662 | 0.039571 | 640 | 0.015238 | 1895 | 0.045119 | 1.377 | A10 | MAXW0.05914310/WT
Horizontal Wall | Maxi | MAXW.05914311/FF | 59 | 143 | 11 | 13 | 1690 | 1690 | 1690 | 0.040238 | 624 | 0.014857 | 1938 | 0.046143 | 1.44 | A10 | MAXW0.05914311/FF
Horizontal Wall | Maxi | MAXW.05914311/FF/DBE | 59 | 143 | 11 | 13 | 2290 | 2290 | 2290 | 0.054524 | 1145 | 0.027262 | 2519 | 0.059976 | 1 | A10 | MAXW0.05914311/FF/DBE
Horizontal Wall | Maxi | MAXW.05914311/FT | 59 | 143 | 11 | 13 | 1880 | 1880 | 1880 | 0.044762 | 694 | 0.016524 | 2156 | 0.051333 | 1.439 | A10 | MAXW0.05914311/FT
Horizontal Wall | Maxi | MAXW.05914311/FT/DBE | 59 | 143 | 11 | 13 | 2480 | 2480 | 2480 | 0.059048 | 1240 | 0.029524 | 2728 | 0.064952 | 1 | A10 | MAXW0.05914311/FT/DBE
Horizontal Wall | Maxi | MAXW.05914311/WF | 59 | 143 | 11 | 13 | 1966 | 1966 | 1966 | 0.04681 | 725 | 0.017262 | 2255 | 0.05369 | 1.438 | A10 | MAXW0.05914311/WF
Horizontal Wall | Maxi | MAXW.05914311/WF/DBE | 59 | 143 | 11 | 13 | 2566 | 2566 | 2566 | 0.061095 | 1283 | 0.030548 | 2823 | 0.067214 | 1 | A10 | MAXW0.05914311/WF/DBE
Horizontal Wall | Maxi | MAXW.05914311/WT | 59 | 143 | 11 | 13 | 2121 | 2121 | 2121 | 0.0505 | 783 | 0.018643 | 2433 | 0.057929 | 1.437 | A10 | MAXW0.05914311/WT
Horizontal Wall | Maxi | MAXW.05914311/WT/DBE | 59 | 143 | 11 | 13 | 2721 | 2721 | 2721 | 0.064786 | 1361 | 0.032405 | 2993 | 0.071262 | 1 | A10 | MAXW0.05914311/WT/DBE
Horizontal Wall | Maxi | MAXW.05914315/FF | 59 | 143 | 15 | 18 | 1819 | 1819 | 1819 | 0.04331 | 693 | 0.0165 | 2077 | 0.049452 | 1.392 | A10 | MAXW0.05914315/FF
Horizontal Wall | Maxi | MAXW.05914315/FT | 59 | 143 | 15 | 18 | 2202 | 2202 | 2202 | 0.052429 | 846 | 0.020143 | 2512 | 0.05981 | 1.38 | A10 | MAXW0.05914315/FT
Horizontal Wall | Maxi | MAXW.05914315/WF | 59 | 143 | 15 | 18 | 2246 | 2246 | 2246 | 0.053476 | 867 | 0.020643 | 2560 | 0.060952 | 1.374 | A10 | MAXW0.05914315/WF
Horizontal Wall | Maxi | MAXW.05914315/WT | 59 | 143 | 15 | 18 | 2655 | 2655 | 2655 | 0.063214 | 1033 | 0.024595 | 3024 | 0.072 | 1.362 | A10 | MAXW0.05914315/WT
Horizontal Wall | Maxi | MAXW.05914316/FF | 59 | 143 | 16 | 18 | 1981 | 1981 | 1981 | 0.047167 | 721 | 0.017167 | 2276 | 0.05419 | 1.457 | A10 | MAXW0.05914316/FF
Horizontal Wall | Maxi | MAXW.05914316/FF/DBE | 59 | 143 | 16 | 18 | 2941 | 2941 | 2941 | 0.070024 | 1471 | 0.035024 | 3235 | 0.077024 | 1 | A10 | MAXW0.05914316/FF/DBE
Horizontal Wall | Maxi | MAXW.05914316/FT | 59 | 143 | 16 | 18 | 2396 | 2396 | 2396 | 0.057048 | 870 | 0.020714 | 2755 | 0.065595 | 1.462 | A10 | MAXW0.05914316/FT
Horizontal Wall | Maxi | MAXW.05914316/FT/DBE | 59 | 143 | 16 | 18 | 3356 | 3356 | 3356 | 0.079905 | 1678 | 0.039952 | 3692 | 0.087905 | 1 | A10 | MAXW0.05914316/FT/DBE
Horizontal Wall | Maxi | MAXW.05914316/WF | 59 | 143 | 16 | 18 | 2462 | 2462 | 2462 | 0.058619 | 891 | 0.021214 | 2831 | 0.067405 | 1.464 | A10 | MAXW0.05914316/WF
Horizontal Wall | Maxi | MAXW.05914316/WF/DBE | 59 | 143 | 16 | 18 | 3422 | 3422 | 3422 | 0.081476 | 1711 | 0.040738 | 3764 | 0.089619 | 1 | A10 | MAXW0.05914316/WF/DBE
Horizontal Wall | Maxi | MAXW.05914316/WT | 59 | 143 | 16 | 18 | 2952 | 2952 | 2952 | 0.070286 | 1066 | 0.025381 | 3395 | 0.080833 | 1.468 | A10 | MAXW0.05914316/WT
Horizontal Wall | Maxi | MAXW.05914316/WT/DBE | 59 | 143 | 16 | 18 | 3912 | 3912 | 3912 | 0.093143 | 1956 | 0.046571 | 4303 | 0.10245 | 1 | A10 | MAXW0.05914316/WT/DBE
Horizontal Wall | Maxi | MAXW.05914320/FF | 59 | 143 | 20 | 23 | 2316 | 2316 | 2316 | 0.055143 | 882 | 0.021 | 2645 | 0.062976 | 1.391 | A10 | MAXW0.05914320/FF
Horizontal Wall | Maxi | MAXW.05914320/FT | 59 | 143 | 20 | 23 | 2982 | 2982 | 2982 | 0.071 | 1145 | 0.027262 | 3402 | 0.081 | 1.38 | A10 | MAXW0.05914320/FT
Horizontal Wall | Maxi | MAXW.05914320/WF | 59 | 143 | 20 | 23 | 2952 | 2952 | 2952 | 0.070286 | 1139 | 0.027119 | 3365 | 0.080119 | 1.374 | A10 | MAXW0.05914320/WF
Horizontal Wall | Maxi | MAXW.05914320/WT | 59 | 143 | 20 | 23 | 3707 | 3707 | 3707 | 0.088262 | 1442 | 0.034333 | 4222 | 0.10052 | 1.362 | A10 | MAXW0.05914320/WT
Horizontal Wall | Maxi | MAXW.05914321/FF | 59 | 143 | 21 | 23 | 2389 | 2389 | 2389 | 0.056881 | 860 | 0.020476 | 2750 | 0.065476 | 1.472 | A10 | MAXW0.05914321/FF
Horizontal Wall | Maxi | MAXW.05914321/FF/DBE | 59 | 143 | 21 | 23 | 3349 | 3349 | 3349 | 0.079738 | 1675 | 0.039881 | 3684 | 0.087714 | 1 | A10 | MAXW0.05914321/FF/DBE
Horizontal Wall | Maxi | MAXW.05914321/FT | 59 | 143 | 21 | 23 | 3125 | 3125 | 3125 | 0.074405 | 1119 | 0.026643 | 3597 | 0.085643 | 1.48 | A10 | MAXW0.05914321/FT
Horizontal Wall | Maxi | MAXW.05914321/FT/DBE | 59 | 143 | 21 | 23 | 4085 | 4085 | 4085 | 0.097262 | 2043 | 0.048643 | 4494 | 0.107 | 1 | A10 | MAXW0.05914321/FT/DBE
Horizontal Wall | Maxi | MAXW.05914321/WF | 59 | 143 | 21 | 23 | 3181 | 3181 | 3181 | 0.075738 | 1136 | 0.027048 | 3665 | 0.087262 | 1.484 | A10 | MAXW0.05914321/WF
Horizontal Wall | Maxi | MAXW.05914321/WF/DBE | 59 | 143 | 21 | 23 | 4141 | 4141 | 4141 | 0.098595 | 2071 | 0.04931 | 4555 | 0.10845 | 1 | A10 | MAXW0.05914321/WF/DBE
Horizontal Wall | Maxi | MAXW.05914321/WT | 59 | 143 | 21 | 23 | 4076 | 4076 | 4076 | 0.097048 | 1451 | 0.034548 | 4700 | 0.1119 | 1.492 | A10 | MAXW0.05914321/WT
Horizontal Wall | Maxi | MAXW.05914321/WT/DBE | 59 | 143 | 21 | 23 | 5036 | 5036 | 5036 | 0.1199 | 2518 | 0.059952 | 5540 | 0.1319 | 1 | A10 | MAXW0.05914321/WT/DBE
Horizontal Wall | Maxi | MAXW.05916310/FF | 59 | 163 | 10 | 13 | 1442 | 1442 | 1442 | 0.034333 | 547 | 0.013024 | 1648 | 0.039238 | 1.4 | A10 | MAXW0.05916310/FF
Horizontal Wall | Maxi | MAXW.05916310/FT | 59 | 163 | 10 | 13 | 1649 | 1649 | 1649 | 0.039262 | 628 | 0.014952 | 1883 | 0.044833 | 1.391 | A10 | MAXW0.05916310/FT
Horizontal Wall | Maxi | MAXW.05916310/WF | 59 | 163 | 10 | 13 | 1738 | 1738 | 1738 | 0.041381 | 666 | 0.015857 | 1983 | 0.047214 | 1.386 | A10 | MAXW0.05916310/WF
Horizontal Wall | Maxi | MAXW.05916310/WT | 59 | 163 | 10 | 13 | 1894 | 1894 | 1894 | 0.045095 | 729 | 0.017357 | 2159 | 0.051405 | 1.377 | A10 | MAXW0.05916310/WT
Horizontal Wall | Maxi | MAXW.05916311/FF | 59 | 163 | 11 | 13 | 1926 | 1926 | 1926 | 0.045857 | 711 | 0.016929 | 2209 | 0.052595 | 1.44 | A10 | MAXW0.05916311/FF
Horizontal Wall | Maxi | MAXW.05916311/FF/DBE | 59 | 163 | 11 | 13 | 3126 | 3126 | 3126 | 0.074429 | 1563 | 0.037214 | 3439 | 0.081881 | 1 | A10 | MAXW0.05916311/FF/DBE
Horizontal Wall | Maxi | MAXW.05916311/FT | 59 | 163 | 11 | 13 | 2143 | 2143 | 2143 | 0.051024 | 791 | 0.018833 | 2458 | 0.058524 | 1.439 | A10 | MAXW0.05916311/FT
Horizontal Wall | Maxi | MAXW.05916311/FT/DBE | 59 | 163 | 11 | 13 | 3343 | 3343 | 3343 | 0.079595 | 1672 | 0.03981 | 3677 | 0.087548 | 1 | A10 | MAXW0.05916311/FT/DBE
Horizontal Wall | Maxi | MAXW.05916311/WF | 59 | 163 | 11 | 13 | 2241 | 2241 | 2241 | 0.053357 | 827 | 0.01969 | 2570 | 0.06119 | 1.438 | A10 | MAXW0.05916311/WF
Horizontal Wall | Maxi | MAXW.05916311/WF/DBE | 59 | 163 | 11 | 13 | 3441 | 3441 | 3441 | 0.081929 | 1721 | 0.040976 | 3785 | 0.090119 | 1 | A10 | MAXW0.05916311/WF/DBE
Horizontal Wall | Maxi | MAXW.05916311/WT | 59 | 163 | 11 | 13 | 2418 | 2418 | 2418 | 0.057571 | 892 | 0.021238 | 2773 | 0.066024 | 1.437 | A10 | MAXW0.05916311/WT
Horizontal Wall | Maxi | MAXW.05916311/WT/DBE | 59 | 163 | 11 | 13 | 3618 | 3618 | 3618 | 0.086143 | 1809 | 0.043071 | 3980 | 0.094762 | 1 | A10 | MAXW0.05916311/WT/DBE
Horizontal Wall | Maxi | MAXW.05916315/FF | 59 | 163 | 15 | 18 | 2073 | 2073 | 2073 | 0.049357 | 790 | 0.01881 | 2367 | 0.056357 | 1.392 | A10 | MAXW0.05916315/FF
Horizontal Wall | Maxi | MAXW.05916315/FT | 59 | 163 | 15 | 18 | 2510 | 2510 | 2510 | 0.059762 | 964 | 0.022952 | 2864 | 0.06819 | 1.38 | A10 | MAXW0.05916315/FT
Horizontal Wall | Maxi | MAXW.05916315/WF | 59 | 163 | 15 | 18 | 2561 | 2561 | 2561 | 0.060976 | 989 | 0.023548 | 2920 | 0.069524 | 1.374 | A10 | MAXW0.05916315/WF
Horizontal Wall | Maxi | MAXW.05916315/WT | 59 | 163 | 15 | 18 | 3026 | 3026 | 3026 | 0.072048 | 1177 | 0.028024 | 3447 | 0.082071 | 1.362 | A10 | MAXW0.05916315/WT
Horizontal Wall | Maxi | MAXW.05916316/FF | 59 | 163 | 16 | 18 | 2258 | 2258 | 2258 | 0.053762 | 822 | 0.019571 | 2594 | 0.061762 | 1.457 | A10 | MAXW0.05916316/FF
Horizontal Wall | Maxi | MAXW.05916316/FF/DBE | 59 | 163 | 16 | 18 | 4178 | 4178 | 4178 | 0.099476 | 2089 | 0.049738 | 4596 | 0.10943 | 1 | A10 | MAXW0.05916316/FF/DBE
Horizontal Wall | Maxi | MAXW.05916316/FT | 59 | 163 | 16 | 18 | 2731 | 2731 | 2731 | 0.065024 | 991 | 0.023595 | 3141 | 0.074786 | 1.462 | A10 | MAXW0.05916316/FT
Horizontal Wall | Maxi | MAXW.05916316/FT/DBE | 59 | 163 | 16 | 18 | 4651 | 4651 | 4651 | 0.11074 | 2326 | 0.055381 | 5116 | 0.12181 | 1 | A10 | MAXW0.05916316/FT/DBE
Horizontal Wall | Maxi | MAXW.05916316/WF | 59 | 163 | 16 | 18 | 2806 | 2806 | 2806 | 0.06681 | 1016 | 0.02419 | 3227 | 0.076833 | 1.464 | A10 | MAXW0.05916316/WF
Horizontal Wall | Maxi | MAXW.05916316/WF/DBE | 59 | 163 | 16 | 18 | 4726 | 4726 | 4726 | 0.11252 | 2363 | 0.056262 | 5199 | 0.12379 | 1 | A10 | MAXW0.05916316/WF/DBE
Horizontal Wall | Maxi | MAXW.05916316/WT | 59 | 163 | 16 | 18 | 3364 | 3364 | 3364 | 0.080095 | 1214 | 0.028905 | 3869 | 0.092119 | 1.468 | A10 | MAXW0.05916316/WT
Horizontal Wall | Maxi | MAXW.05916316/WT/DBE | 59 | 163 | 16 | 18 | 5284 | 5284 | 5284 | 0.12581 | 2642 | 0.062905 | 5812 | 0.13838 | 1 | A10 | MAXW0.05916316/WT/DBE
Horizontal Wall | Maxi | MAXW.05916320/FF | 59 | 163 | 20 | 23 | 2640 | 2640 | 2640 | 0.062857 | 1006 | 0.023952 | 3015 | 0.071786 | 1.391 | A10 | MAXW0.05916320/FF
Horizontal Wall | Maxi | MAXW.05916320/FT | 59 | 163 | 20 | 23 | 3399 | 3399 | 3399 | 0.080929 | 1305 | 0.031071 | 3878 | 0.092333 | 1.38 | A10 | MAXW0.05916320/FT
Horizontal Wall | Maxi | MAXW.05916320/WF | 59 | 163 | 20 | 23 | 3364 | 3364 | 3364 | 0.080095 | 1299 | 0.030929 | 3835 | 0.09131 | 1.374 | A10 | MAXW0.05916320/WF
Horizontal Wall | Maxi | MAXW.05916320/WT | 59 | 163 | 20 | 23 | 4225 | 4225 | 4225 | 0.1006 | 1644 | 0.039143 | 4812 | 0.11457 | 1.362 | A10 | MAXW0.05916320/WT
Horizontal Wall | Maxi | MAXW.05916321/FF | 59 | 163 | 21 | 23 | 2724 | 2724 | 2724 | 0.064857 | 981 | 0.023357 | 3135 | 0.074643 | 1.472 | A10 | MAXW0.05916321/FF
Horizontal Wall | Maxi | MAXW.05916321/FF/DBE | 59 | 163 | 21 | 23 | 4644 | 4644 | 4644 | 0.11057 | 2322 | 0.055286 | 5108 | 0.12162 | 1 | A10 | MAXW0.05916321/FF/DBE
Horizontal Wall | Maxi | MAXW.05916321/FT | 59 | 163 | 21 | 23 | 3562 | 3562 | 3562 | 0.08481 | 1275 | 0.030357 | 4100 | 0.097619 | 1.48 | A10 | MAXW0.05916321/FT
Horizontal Wall | Maxi | MAXW.05916321/FT/DBE | 59 | 163 | 21 | 23 | 5482 | 5482 | 5482 | 0.13052 | 2741 | 0.065262 | 6030 | 0.14357 | 1 | A10 | MAXW0.05916321/FT/DBE
Horizontal Wall | Maxi | MAXW.05916321/WF | 59 | 163 | 21 | 23 | 3626 | 3626 | 3626 | 0.086333 | 1294 | 0.03081 | 4177 | 0.099452 | 1.484 | A10 | MAXW0.05916321/WF
Horizontal Wall | Maxi | MAXW.05916321/WF/DBE | 59 | 163 | 21 | 23 | 5546 | 5546 | 5546 | 0.13205 | 2773 | 0.066024 | 6101 | 0.14526 | 1 | A10 | MAXW0.05916321/WF/DBE
Horizontal Wall | Maxi | MAXW.05916321/WT | 59 | 163 | 21 | 23 | 4646 | 4646 | 4646 | 0.11062 | 1654 | 0.039381 | 5357 | 0.12755 | 1.492 | A10 | MAXW0.05916321/WT
Horizontal Wall | Maxi | MAXW.05916321/WT/DBE | 59 | 163 | 21 | 23 | 6566 | 6566 | 6566 | 0.15633 | 3283 | 0.078167 | 7223 | 0.17198 | 1 | A10 | MAXW0.05916321/WT/DBE
Horizontal Wall | Maxi | MAXW.05918310/FF | 59 | 183 | 10 | 13 | 1619 | 1619 | 1619 | 0.038548 | 614 | 0.014619 | 1851 | 0.044071 | 1.4 | A10 | MAXW0.05918310/FF
Horizontal Wall | Maxi | MAXW.05918310/FT | 59 | 183 | 10 | 13 | 1851 | 1851 | 1851 | 0.044071 | 705 | 0.016786 | 2114 | 0.050333 | 1.391 | A10 | MAXW0.05918310/FT
Horizontal Wall | Maxi | MAXW.05918310/WF | 59 | 183 | 10 | 13 | 1951 | 1951 | 1951 | 0.046452 | 747 | 0.017786 | 2226 | 0.053 | 1.386 | A10 | MAXW0.05918310/WF
Horizontal Wall | Maxi | MAXW.05918310/WT | 59 | 183 | 10 | 13 | 2127 | 2127 | 2127 | 0.050643 | 819 | 0.0195 | 2425 | 0.057738 | 1.377 | A10 | MAXW0.05918310/WT
Horizontal Wall | Maxi | MAXW.05918311/FF | 59 | 183 | 11 | 13 | 2162 | 2162 | 2162 | 0.051476 | 798 | 0.019 | 2480 | 0.059048 | 1.44 | A10 | MAXW0.05918311/FF
Horizontal Wall | Maxi | MAXW.05918311/FF/DBE | 59 | 183 | 11 | 13 | 3362 | 3362 | 3362 | 0.080048 | 1681 | 0.040024 | 3698 | 0.088048 | 1 | A10 | MAXW0.05918311/FF/DBE
Horizontal Wall | Maxi | MAXW.05918311/FT | 59 | 183 | 11 | 13 | 2406 | 2406 | 2406 | 0.057286 | 888 | 0.021143 | 2760 | 0.065714 | 1.439 | A10 | MAXW0.05918311/FT
Horizontal Wall | Maxi | MAXW.05918311/FT/DBE | 59 | 183 | 11 | 13 | 3606 | 3606 | 3606 | 0.085857 | 1803 | 0.042929 | 3967 | 0.094452 | 1 | A10 | MAXW0.05918311/FT/DBE
Horizontal Wall | Maxi | MAXW.05918311/WF | 59 | 183 | 11 | 13 | 2516 | 2516 | 2516 | 0.059905 | 928 | 0.022095 | 2886 | 0.068714 | 1.438 | A10 | MAXW0.05918311/WF
Horizontal Wall | Maxi | MAXW.05918311/WF/DBE | 59 | 183 | 11 | 13 | 3716 | 3716 | 3716 | 0.088476 | 1858 | 0.044238 | 4088 | 0.097333 | 1 | A10 | MAXW0.05918311/WF/DBE
Horizontal Wall | Maxi | MAXW.05918311/WT | 59 | 183 | 11 | 13 | 2715 | 2715 | 2715 | 0.064643 | 1002 | 0.023857 | 3114 | 0.074143 | 1.437 | A10 | MAXW0.05918311/WT
Horizontal Wall | Maxi | MAXW.05918311/WT/DBE | 59 | 183 | 11 | 13 | 3915 | 3915 | 3915 | 0.093214 | 1958 | 0.046619 | 4307 | 0.10255 | 1 | A10 | MAXW0.05918311/WT/DBE
Horizontal Wall | Maxi | MAXW.05918315/FF | 59 | 183 | 15 | 18 | 2327 | 2327 | 2327 | 0.055405 | 887 | 0.021119 | 2657 | 0.063262 | 1.392 | A10 | MAXW0.05918315/FF
Horizontal Wall | Maxi | MAXW.05918315/FT | 59 | 183 | 15 | 18 | 2818 | 2818 | 2818 | 0.067095 | 1082 | 0.025762 | 3215 | 0.076548 | 1.38 | A10 | MAXW0.05918315/FT
Horizontal Wall | Maxi | MAXW.05918315/WF | 59 | 183 | 15 | 18 | 2875 | 2875 | 2875 | 0.068452 | 1110 | 0.026429 | 3278 | 0.078048 | 1.374 | A10 | MAXW0.05918315/WF
Horizontal Wall | Maxi | MAXW.05918315/WT | 59 | 183 | 15 | 18 | 3397 | 3397 | 3397 | 0.080881 | 1321 | 0.031452 | 3869 | 0.092119 | 1.362 | A10 | MAXW0.05918315/WT
Horizontal Wall | Maxi | MAXW.05918316/FF | 59 | 183 | 16 | 18 | 2535 | 2535 | 2535 | 0.060357 | 923 | 0.021976 | 2913 | 0.069357 | 1.457 | A10 | MAXW0.05918316/FF
Horizontal Wall | Maxi | MAXW.05918316/FF/DBE | 59 | 183 | 16 | 18 | 4455 | 4455 | 4455 | 0.10607 | 2228 | 0.053048 | 4901 | 0.11669 | 1 | A10 | MAXW0.05918316/FF/DBE
Horizontal Wall | Maxi | MAXW.05918316/FT | 59 | 183 | 16 | 18 | 3067 | 3067 | 3067 | 0.073024 | 1113 | 0.0265 | 3527 | 0.083976 | 1.462 | A10 | MAXW0.05918316/FT
Horizontal Wall | Maxi | MAXW.05918316/FT/DBE | 59 | 183 | 16 | 18 | 4987 | 4987 | 4987 | 0.11874 | 2494 | 0.059381 | 5486 | 0.13062 | 1 | A10 | MAXW0.05918316/FT/DBE
Horizontal Wall | Maxi | MAXW.05918316/WF | 59 | 183 | 16 | 18 | 3150 | 3150 | 3150 | 0.075 | 1140 | 0.027143 | 3623 | 0.086262 | 1.464 | A10 | MAXW0.05918316/WF
Horizontal Wall | Maxi | MAXW.05918316/WF/DBE | 59 | 183 | 16 | 18 | 5070 | 5070 | 5070 | 0.12071 | 2535 | 0.060357 | 5577 | 0.13279 | 1 | A10 | MAXW0.05918316/WF/DBE
Horizontal Wall | Maxi | MAXW.05918316/WT | 59 | 183 | 16 | 18 | 3777 | 3777 | 3777 | 0.089929 | 1363 | 0.032452 | 4344 | 0.10343 | 1.468 | A10 | MAXW0.05918316/WT
Horizontal Wall | Maxi | MAXW.05918316/WT/DBE | 59 | 183 | 16 | 18 | 5697 | 5697 | 5697 | 0.13564 | 2849 | 0.067833 | 6267 | 0.14921 | 1 | A10 | MAXW0.05918316/WT/DBE
Horizontal Wall | Maxi | MAXW.05918320/FF | 59 | 183 | 20 | 23 | 2964 | 2964 | 2964 | 0.070571 | 1129 | 0.026881 | 3385 | 0.080595 | 1.391 | A10 | MAXW0.05918320/FF
Horizontal Wall | Maxi | MAXW.05918320/FT | 59 | 183 | 20 | 23 | 3816 | 3816 | 3816 | 0.090857 | 1465 | 0.034881 | 4354 | 0.10367 | 1.38 | A10 | MAXW0.05918320/FT
Horizontal Wall | Maxi | MAXW.05918320/WF | 59 | 183 | 20 | 23 | 3777 | 3777 | 3777 | 0.089929 | 1458 | 0.034714 | 4306 | 0.10252 | 1.374 | A10 | MAXW0.05918320/WF
Horizontal Wall | Maxi | MAXW.05918320/WT | 59 | 183 | 20 | 23 | 4744 | 4744 | 4744 | 0.11295 | 1845 | 0.043929 | 5403 | 0.12864 | 1.362 | A10 | MAXW0.05918320/WT
Horizontal Wall | Maxi | MAXW.05918321/FF | 59 | 183 | 21 | 23 | 3058 | 3058 | 3058 | 0.07281 | 1101 | 0.026214 | 3520 | 0.08381 | 1.472 | A10 | MAXW0.05918321/FF
Horizontal Wall | Maxi | MAXW.05918321/FF/DBE | 59 | 183 | 21 | 23 | 4978 | 4978 | 4978 | 0.11852 | 2489 | 0.059262 | 5476 | 0.13038 | 1 | A10 | MAXW0.05918321/FF/DBE
Horizontal Wall | Maxi | MAXW.05918321/FT | 59 | 183 | 21 | 23 | 3999 | 3999 | 3999 | 0.095214 | 1432 | 0.034095 | 4603 | 0.1096 | 1.48 | A10 | MAXW0.05918321/FT
Horizontal Wall | Maxi | MAXW.05918321/FT/DBE | 59 | 183 | 21 | 23 | 5919 | 5919 | 5919 | 0.14093 | 2960 | 0.070476 | 6511 | 0.15502 | 1 | A10 | MAXW0.05918321/FT/DBE
Horizontal Wall | Maxi | MAXW.05918321/WF | 59 | 183 | 21 | 23 | 4070 | 4070 | 4070 | 0.096905 | 1453 | 0.034595 | 4689 | 0.11164 | 1.484 | A10 | MAXW0.05918321/WF
Horizontal Wall | Maxi | MAXW.05918321/WF/DBE | 59 | 183 | 21 | 23 | 5990 | 5990 | 5990 | 0.14262 | 2995 | 0.07131 | 6589 | 0.15688 | 1 | A10 | MAXW0.05918321/WF/DBE
Horizontal Wall | Maxi | MAXW.05918321/WT | 59 | 183 | 21 | 23 | 5216 | 5216 | 5216 | 0.12419 | 1857 | 0.044214 | 6014 | 0.14319 | 1.492 | A10 | MAXW0.05918321/WT
Horizontal Wall | Maxi | MAXW.05918321/WT/DBE | 59 | 183 | 21 | 23 | 7136 | 7136 | 7136 | 0.1699 | 3568 | 0.084952 | 7850 | 0.1869 | 1 | A10 | MAXW0.05918321/WT/DBE
Horizontal Wall | Maxi | MAXW.05920310/FF | 59 | 203 | 10 | 13 | 1795 | 1795 | 1795 | 0.042738 | 680 | 0.01619 | 2052 | 0.048857 | 1.4 | A10 | MAXW0.05920310/FF
Horizontal Wall | Maxi | MAXW.05920310/FT | 59 | 203 | 10 | 13 | 2054 | 2054 | 2054 | 0.048905 | 783 | 0.018643 | 2346 | 0.055857 | 1.391 | A10 | MAXW0.05920310/FT
Horizontal Wall | Maxi | MAXW.05920310/WF | 59 | 203 | 10 | 13 | 2164 | 2164 | 2164 | 0.051524 | 829 | 0.019738 | 2469 | 0.058786 | 1.386 | A10 | MAXW0.05920310/WF
Horizontal Wall | Maxi | MAXW.05920310/WT | 59 | 203 | 10 | 13 | 2359 | 2359 | 2359 | 0.056167 | 908 | 0.021619 | 2689 | 0.064024 | 1.377 | A10 | MAXW0.05920310/WT
Horizontal Wall | Maxi | MAXW.05920311/FF | 59 | 203 | 11 | 13 | 2399 | 2399 | 2399 | 0.057119 | 885 | 0.021071 | 2752 | 0.065524 | 1.44 | A10 | MAXW0.05920311/FF
Horizontal Wall | Maxi | MAXW.05920311/FF/DBE | 59 | 203 | 11 | 13 | 3599 | 3599 | 3599 | 0.08569 | 1800 | 0.042857 | 3959 | 0.094262 | 1 | A10 | MAXW0.05920311/FF/DBE
Horizontal Wall | Maxi | MAXW.05920311/FT | 59 | 203 | 11 | 13 | 2669 | 2669 | 2669 | 0.063548 | 985 | 0.023452 | 3061 | 0.072881 | 1.439 | A10 | MAXW0.05920311/FT
Horizontal Wall | Maxi | MAXW.05920311/FT/DBE | 59 | 203 | 11 | 13 | 3869 | 3869 | 3869 | 0.092119 | 1935 | 0.046071 | 4256 | 0.10133 | 1 | A10 | MAXW0.05920311/FT/DBE
Horizontal Wall | Maxi | MAXW.05920311/WF | 59 | 203 | 11 | 13 | 2791 | 2791 | 2791 | 0.066452 | 1030 | 0.024524 | 3201 | 0.076214 | 1.438 | A10 | MAXW0.05920311/WF
Horizontal Wall | Maxi | MAXW.05920311/WF/DBE | 59 | 203 | 11 | 13 | 3991 | 3991 | 3991 | 0.095024 | 1996 | 0.047524 | 4390 | 0.10452 | 1 | A10 | MAXW0.05920311/WF/DBE
Horizontal Wall | Maxi | MAXW.05920311/WT | 59 | 203 | 11 | 13 | 3011 | 3011 | 3011 | 0.07169 | 1111 | 0.026452 | 3454 | 0.082238 | 1.437 | A10 | MAXW0.05920311/WT
Horizontal Wall | Maxi | MAXW.05920311/WT/DBE | 59 | 203 | 11 | 13 | 4211 | 4211 | 4211 | 0.10026 | 2106 | 0.050143 | 4632 | 0.11029 | 1 | A10 | MAXW0.05920311/WT/DBE
Horizontal Wall | Maxi | MAXW.05920315/FF | 59 | 203 | 15 | 18 | 2582 | 2582 | 2582 | 0.061476 | 984 | 0.023429 | 2949 | 0.070214 | 1.392 | A10 | MAXW0.05920315/FF
Horizontal Wall | Maxi | MAXW.05920315/FT | 59 | 203 | 15 | 18 | 3126 | 3126 | 3126 | 0.074429 | 1200 | 0.028571 | 3567 | 0.084929 | 1.38 | A10 | MAXW0.05920315/FT
Horizontal Wall | Maxi | MAXW.05920315/WF | 59 | 203 | 15 | 18 | 3189 | 3189 | 3189 | 0.075929 | 1231 | 0.02931 | 3635 | 0.086548 | 1.374 | A10 | MAXW0.05920315/WF
Horizontal Wall | Maxi | MAXW.05920315/WT | 59 | 203 | 15 | 18 | 3768 | 3768 | 3768 | 0.089714 | 1466 | 0.034905 | 4292 | 0.10219 | 1.362 | A10 | MAXW0.05920315/WT
Horizontal Wall | Maxi | MAXW.05920316/FF | 59 | 203 | 16 | 18 | 2812 | 2812 | 2812 | 0.066952 | 1024 | 0.024381 | 3231 | 0.076929 | 1.457 | A10 | MAXW0.05920316/FF
Horizontal Wall | Maxi | MAXW.05920316/FF/DBE | 59 | 203 | 16 | 18 | 4732 | 4732 | 4732 | 0.11267 | 2366 | 0.056333 | 5205 | 0.12393 | 1 | A10 | MAXW0.05920316/FF/DBE
Horizontal Wall | Maxi | MAXW.05920316/FT | 59 | 203 | 16 | 18 | 3402 | 3402 | 3402 | 0.081 | 1235 | 0.029405 | 3912 | 0.093143 | 1.462 | A10 | MAXW0.05920316/FT
Horizontal Wall | Maxi | MAXW.05920316/FT/DBE | 59 | 203 | 16 | 18 | 5322 | 5322 | 5322 | 0.12671 | 2661 | 0.063357 | 5854 | 0.13938 | 1 | A10 | MAXW0.05920316/FT/DBE
Horizontal Wall | Maxi | MAXW.05920316/WF | 59 | 203 | 16 | 18 | 3494 | 3494 | 3494 | 0.08319 | 1265 | 0.030119 | 4018 | 0.095667 | 1.464 | A10 | MAXW0.05920316/WF
Horizontal Wall | Maxi | MAXW.05920316/WF/DBE | 59 | 203 | 16 | 18 | 5414 | 5414 | 5414 | 0.1289 | 2707 | 0.064452 | 5955 | 0.14179 | 1 | A10 | MAXW0.05920316/WF/DBE
Horizontal Wall | Maxi | MAXW.05920316/WT | 59 | 203 | 16 | 18 | 4190 | 4190 | 4190 | 0.099762 | 1513 | 0.036024 | 4819 | 0.11474 | 1.468 | A10 | MAXW0.05920316/WT
Horizontal Wall | Maxi | MAXW.05920316/WT/DBE | 59 | 203 | 16 | 18 | 6110 | 6110 | 6110 | 0.14548 | 3055 | 0.072738 | 6721 | 0.16002 | 1 | A10 | MAXW0.05920316/WT/DBE
Horizontal Wall | Maxi | MAXW.05920320/FF | 59 | 203 | 20 | 23 | 3287 | 3287 | 3287 | 0.078262 | 1252 | 0.02981 | 3754 | 0.089381 | 1.391 | A10 | MAXW0.05920320/FF
Horizontal Wall | Maxi | MAXW.05920320/FT | 59 | 203 | 20 | 23 | 4233 | 4233 | 4233 | 0.10079 | 1625 | 0.03869 | 4830 | 0.115 | 1.38 | A10 | MAXW0.05920320/FT
Horizontal Wall | Maxi | MAXW.05920320/WF | 59 | 203 | 20 | 23 | 4190 | 4190 | 4190 | 0.099762 | 1617 | 0.0385 | 4777 | 0.11374 | 1.374 | A10 | MAXW0.05920320/WF
Horizontal Wall | Maxi | MAXW.05920320/WT | 59 | 203 | 20 | 23 | 5262 | 5262 | 5262 | 0.12529 | 2047 | 0.048738 | 5993 | 0.14269 | 1.362 | A10 | MAXW0.05920320/WT
Horizontal Wall | Maxi | MAXW.05920321/FF | 59 | 203 | 21 | 23 | 3392 | 3392 | 3392 | 0.080762 | 1221 | 0.029071 | 3904 | 0.092952 | 1.472 | A10 | MAXW0.05920321/FF
Horizontal Wall | Maxi | MAXW.05920321/FF/DBE | 59 | 203 | 21 | 23 | 5312 | 5312 | 5312 | 0.12648 | 2656 | 0.063238 | 5843 | 0.13912 | 1 | A10 | MAXW0.05920321/FF/DBE
Horizontal Wall | Maxi | MAXW.05920321/FT | 59 | 203 | 21 | 23 | 4436 | 4436 | 4436 | 0.10562 | 1588 | 0.03781 | 5106 | 0.12157 | 1.48 | A10 | MAXW0.05920321/FT
Horizontal Wall | Maxi | MAXW.05920321/FT/DBE | 59 | 203 | 21 | 23 | 6356 | 6356 | 6356 | 0.15133 | 3178 | 0.075667 | 6992 | 0.16648 | 1 | A10 | MAXW0.05920321/FT/DBE
Horizontal Wall | Maxi | MAXW.05920321/WF | 59 | 203 | 21 | 23 | 4515 | 4515 | 4515 | 0.1075 | 1612 | 0.038381 | 5201 | 0.12383 | 1.484 | A10 | MAXW0.05920321/WF
Horizontal Wall | Maxi | MAXW.05920321/WF/DBE | 59 | 203 | 21 | 23 | 6435 | 6435 | 6435 | 0.15321 | 3218 | 0.076619 | 7079 | 0.16855 | 1 | A10 | MAXW0.05920321/WF/DBE
Horizontal Wall | Maxi | MAXW.05920321/WT | 59 | 203 | 21 | 23 | 5786 | 5786 | 5786 | 0.13776 | 2060 | 0.049048 | 6671 | 0.15883 | 1.492 | A10 | MAXW0.05920321/WT
Horizontal Wall | Maxi | MAXW.05920321/WT/DBE | 59 | 203 | 21 | 23 | 7706 | 7706 | 7706 | 0.18348 | 3853 | 0.091738 | 8477 | 0.20183 | 1 | A10 | MAXW0.05920321/WT/DBE
Horizontal Wall | Maxi | MAXW.07406310/FF | 74 | 63 | 10 | 13 | 672 | 672 | 672 | 0.016 | 257 | 0.006119 | 767 | 0.018262 | 1.386 | A10 | MAXW0.07406310/FF
Horizontal Wall | Maxi | MAXW.07406310/FT | 74 | 63 | 10 | 13 | 732 | 732 | 732 | 0.017429 | 282 | 0.0067143 | 834 | 0.019857 | 1.377 | A10 | MAXW0.07406310/FT
Horizontal Wall | Maxi | MAXW.07406310/WF | 74 | 63 | 10 | 13 | 758 | 758 | 758 | 0.018048 | 293 | 0.0069762 | 864 | 0.020571 | 1.372 | A10 | MAXW0.07406310/WF
Horizontal Wall | Maxi | MAXW.07406310/WT | 74 | 63 | 10 | 13 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.363 | A10 | MAXW0.07406310/WT
Horizontal Wall | Maxi | MAXW.07406311/FF | 74 | 63 | 11 | 13 | 866 | 866 | 866 | 0.020619 | 320 | 0.007619 | 993 | 0.023643 | 1.438 | A10 | MAXW0.07406311/FF
Horizontal Wall | Maxi | MAXW.07406311/FF/DBE | 74 | 63 | 11 | 13 | 1166 | 1166 | 1166 | 0.027762 | 583 | 0.013881 | 1283 | 0.030548 | 1 | A10 | MAXW0.07406311/FF/DBE
Horizontal Wall | Maxi | MAXW.07406311/FT | 74 | 63 | 11 | 13 | 935 | 935 | 935 | 0.022262 | 345 | 0.0082143 | 1072 | 0.025524 | 1.437 | A10 | MAXW0.07406311/FT
Horizontal Wall | Maxi | MAXW.07406311/FT/DBE | 74 | 63 | 11 | 13 | 1235 | 1235 | 1235 | 0.029405 | 618 | 0.014714 | 1359 | 0.032357 | 1 | A10 | MAXW0.07406311/FT/DBE
Horizontal Wall | Maxi | MAXW.07406311/WF | 74 | 63 | 11 | 13 | 966 | 966 | 966 | 0.023 | 356 | 0.0084762 | 1108 | 0.026381 | 1.437 | A10 | MAXW0.07406311/WF
Horizontal Wall | Maxi | MAXW.07406311/WF/DBE | 74 | 63 | 11 | 13 | 1266 | 1266 | 1266 | 0.030143 | 633 | 0.015071 | 1393 | 0.033167 | 1 | A10 | MAXW0.07406311/WF/DBE
Horizontal Wall | Maxi | MAXW.07406311/WT | 74 | 63 | 11 | 13 | 1025 | 1025 | 1025 | 0.024405 | 379 | 0.0090238 | 1176 | 0.028 | 1.436 | A10 | MAXW0.07406311/WT
Horizontal Wall | Maxi | MAXW.07406311/WT/DBE | 74 | 63 | 11 | 13 | 1325 | 1325 | 1325 | 0.031548 | 663 | 0.015786 | 1458 | 0.034714 | 1 | A10 | MAXW0.07406311/WT/DBE
Horizontal Wall | Maxi | MAXW.07406315/FF | 74 | 63 | 15 | 18 | 951 | 951 | 951 | 0.022643 | 367 | 0.0087381 | 1084 | 0.02581 | 1.374 | A10 | MAXW0.07406315/FF
Horizontal Wall | Maxi | MAXW.07406315/FT | 74 | 63 | 15 | 18 | 1097 | 1097 | 1097 | 0.026119 | 427 | 0.010167 | 1249 | 0.029738 | 1.362 | A10 | MAXW0.07406315/FT
Horizontal Wall | Maxi | MAXW.07406315/WF | 74 | 63 | 15 | 18 | 1100 | 1100 | 1100 | 0.02619 | 429 | 0.010214 | 1252 | 0.02981 | 1.357 | A10 | MAXW0.07406315/WF
Horizontal Wall | Maxi | MAXW.07406315/WT | 74 | 63 | 15 | 18 | 1266 | 1266 | 1266 | 0.030143 | 499 | 0.011881 | 1439 | 0.034262 | 1.345 | A10 | MAXW0.07406315/WT
Horizontal Wall | Maxi | MAXW.07406316/FF | 74 | 63 | 16 | 18 | 1044 | 1044 | 1044 | 0.024857 | 378 | 0.009 | 1201 | 0.028595 | 1.464 | A10 | MAXW0.07406316/FF
Horizontal Wall | Maxi | MAXW.07406316/FF/DBE | 74 | 63 | 16 | 18 | 1524 | 1524 | 1524 | 0.036286 | 762 | 0.018143 | 1676 | 0.039905 | 1 | A10 | MAXW0.07406316/FF/DBE
Horizontal Wall | Maxi | MAXW.07406316/FT | 74 | 63 | 16 | 18 | 1225 | 1225 | 1225 | 0.029167 | 442 | 0.010524 | 1409 | 0.033548 | 1.468 | A10 | MAXW0.07406316/FT
Horizontal Wall | Maxi | MAXW.07406316/FT/DBE | 74 | 63 | 16 | 18 | 1705 | 1705 | 1705 | 0.040595 | 853 | 0.02031 | 1876 | 0.044667 | 1 | A10 | MAXW0.07406316/FT/DBE
Horizontal Wall | Maxi | MAXW.07406316/WF | 74 | 63 | 16 | 18 | 1244 | 1244 | 1244 | 0.029619 | 449 | 0.01069 | 1431 | 0.034071 | 1.47 | A10 | MAXW0.07406316/WF
Horizontal Wall | Maxi | MAXW.07406316/WF/DBE | 74 | 63 | 16 | 18 | 1724 | 1724 | 1724 | 0.041048 | 862 | 0.020524 | 1896 | 0.045143 | 1 | A10 | MAXW0.07406316/WF/DBE
Horizontal Wall | Maxi | MAXW.07406316/WT | 74 | 63 | 16 | 18 | 1466 | 1466 | 1466 | 0.034905 | 528 | 0.012571 | 1687 | 0.040167 | 1.474 | A10 | MAXW0.07406316/WT
Horizontal Wall | Maxi | MAXW.07406316/WT/DBE | 74 | 63 | 16 | 18 | 1946 | 1946 | 1946 | 0.046333 | 973 | 0.023167 | 2141 | 0.050976 | 1 | A10 | MAXW0.07406316/WT/DBE
Horizontal Wall | Maxi | MAXW.07406320/FF | 74 | 63 | 20 | 23 | 1209 | 1209 | 1209 | 0.028786 | 467 | 0.011119 | 1378 | 0.03281 | 1.374 | A10 | MAXW0.07406320/FF
Horizontal Wall | Maxi | MAXW.07406320/FT | 74 | 63 | 20 | 23 | 1484 | 1484 | 1484 | 0.035333 | 577 | 0.013738 | 1690 | 0.040238 | 1.362 | A10 | MAXW0.07406320/FT
Horizontal Wall | Maxi | MAXW.07406320/WF | 74 | 63 | 20 | 23 | 1461 | 1461 | 1461 | 0.034786 | 571 | 0.013595 | 1663 | 0.039595 | 1.356 | A10 | MAXW0.07406320/WF
Horizontal Wall | Maxi | MAXW.07406320/WT | 74 | 63 | 20 | 23 | 1766 | 1766 | 1766 | 0.042048 | 696 | 0.016571 | 2008 | 0.04781 | 1.345 | A10 | MAXW0.07406320/WT
Horizontal Wall | Maxi | MAXW.07406321/FF | 74 | 63 | 21 | 23 | 1291 | 1291 | 1291 | 0.030738 | 461 | 0.010976 | 1487 | 0.035405 | 1.484 | A10 | MAXW0.07406321/FF
Horizontal Wall | Maxi | MAXW.07406321/FF/DBE | 74 | 63 | 21 | 23 | 1771 | 1771 | 1771 | 0.042167 | 886 | 0.021095 | 1948 | 0.046381 | 1 | A10 | MAXW0.07406321/FF/DBE
Horizontal Wall | Maxi | MAXW.07406321/FT | 74 | 63 | 21 | 23 | 1637 | 1637 | 1637 | 0.038976 | 583 | 0.013881 | 1887 | 0.044929 | 1.492 | A10 | MAXW0.07406321/FT
Horizontal Wall | Maxi | MAXW.07406321/FT/DBE | 74 | 63 | 21 | 23 | 2117 | 2117 | 2117 | 0.050405 | 1059 | 0.025214 | 2329 | 0.055452 | 1 | A10 | MAXW0.07406321/FT/DBE
Horizontal Wall | Maxi | MAXW.07406321/WF | 74 | 63 | 21 | 23 | 1648 | 1648 | 1648 | 0.039238 | 585 | 0.013929 | 1900 | 0.045238 | 1.496 | A10 | MAXW0.07406321/WF
Horizontal Wall | Maxi | MAXW.07406321/WF/DBE | 74 | 63 | 21 | 23 | 2128 | 2128 | 2128 | 0.050667 | 1064 | 0.025333 | 2341 | 0.055738 | 1 | A10 | MAXW0.07406321/WF/DBE
Horizontal Wall | Maxi | MAXW.07406321/WT | 74 | 63 | 21 | 23 | 2075 | 2075 | 2075 | 0.049405 | 730 | 0.017381 | 2395 | 0.057024 | 1.505 | A10 | MAXW0.07406321/WT
Horizontal Wall | Maxi | MAXW.07406321/WT/DBE | 74 | 63 | 21 | 23 | 2555 | 2555 | 2555 | 0.060833 | 1278 | 0.030429 | 2811 | 0.066929 | 1 | A10 | MAXW0.07406321/WT/DBE
Horizontal Wall | Maxi | MAXW.07408310/FF | 74 | 83 | 10 | 13 | 885 | 885 | 885 | 0.021071 | 339 | 0.0080714 | 1010 | 0.024048 | 1.386 | A10 | MAXW0.07408310/FF
Horizontal Wall | Maxi | MAXW.07408310/FT | 74 | 83 | 10 | 13 | 965 | 965 | 965 | 0.022976 | 372 | 0.0088571 | 1100 | 0.02619 | 1.377 | A10 | MAXW0.07408310/FT
Horizontal Wall | Maxi | MAXW.07408310/WF | 74 | 83 | 10 | 13 | 999 | 999 | 999 | 0.023786 | 386 | 0.0091905 | 1139 | 0.027119 | 1.372 | A10 | MAXW0.07408310/WF
Horizontal Wall | Maxi | MAXW.07408310/WT | 74 | 83 | 10 | 13 | 1060 | 1060 | 1060 | 0.025238 | 412 | 0.0098095 | 1207 | 0.028738 | 1.363 | A10 | MAXW0.07408310/WT
Horizontal Wall | Maxi | MAXW.07408311/FF | 74 | 83 | 11 | 13 | 1141 | 1141 | 1141 | 0.027167 | 421 | 0.010024 | 1309 | 0.031167 | 1.438 | A10 | MAXW0.07408311/FF
Horizontal Wall | Maxi | MAXW.07408311/FF/DBE | 74 | 83 | 11 | 13 | 1441 | 1441 | 1441 | 0.03431 | 721 | 0.017167 | 1585 | 0.037738 | 1 | A10 | MAXW0.07408311/FF/DBE
Horizontal Wall | Maxi | MAXW.07408311/FT | 74 | 83 | 11 | 13 | 1231 | 1231 | 1231 | 0.02931 | 454 | 0.01081 | 1412 | 0.033619 | 1.437 | A10 | MAXW0.07408311/FT
Horizontal Wall | Maxi | MAXW.07408311/FT/DBE | 74 | 83 | 11 | 13 | 1531 | 1531 | 1531 | 0.036452 | 766 | 0.018238 | 1684 | 0.040095 | 1 | A10 | MAXW0.07408311/FT/DBE
Horizontal Wall | Maxi | MAXW.07408311/WF | 74 | 83 | 11 | 13 | 1272 | 1272 | 1272 | 0.030286 | 469 | 0.011167 | 1459 | 0.034738 | 1.437 | A10 | MAXW0.07408311/WF
Horizontal Wall | Maxi | MAXW.07408311/WF/DBE | 74 | 83 | 11 | 13 | 1572 | 1572 | 1572 | 0.037429 | 786 | 0.018714 | 1729 | 0.041167 | 1 | A10 | MAXW0.07408311/WF/DBE
Horizontal Wall | Maxi | MAXW.07408311/WT | 74 | 83 | 11 | 13 | 1350 | 1350 | 1350 | 0.032143 | 500 | 0.011905 | 1548 | 0.036857 | 1.436 | A10 | MAXW0.07408311/WT
Horizontal Wall | Maxi | MAXW.07408311/WT/DBE | 74 | 83 | 11 | 13 | 1650 | 1650 | 1650 | 0.039286 | 825 | 0.019643 | 1815 | 0.043214 | 1 | A10 | MAXW0.07408311/WT/DBE
Horizontal Wall | Maxi | MAXW.07408315/FF | 74 | 83 | 15 | 18 | 1252 | 1252 | 1252 | 0.02981 | 483 | 0.0115 | 1427 | 0.033976 | 1.374 | A10 | MAXW0.07408315/FF
Horizontal Wall | Maxi | MAXW.07408315/FT | 74 | 83 | 15 | 18 | 1446 | 1446 | 1446 | 0.034429 | 562 | 0.013381 | 1647 | 0.039214 | 1.362 | A10 | MAXW0.07408315/FT
Horizontal Wall | Maxi | MAXW.07408315/WF | 74 | 83 | 15 | 18 | 1450 | 1450 | 1450 | 0.034524 | 566 | 0.013476 | 1650 | 0.039286 | 1.357 | A10 | MAXW0.07408315/WF
Horizontal Wall | Maxi | MAXW.07408315/WT | 74 | 83 | 15 | 18 | 1668 | 1668 | 1668 | 0.039714 | 657 | 0.015643 | 1897 | 0.045167 | 1.345 | A10 | MAXW0.07408315/WT
Horizontal Wall | Maxi | MAXW.07408316/FF | 74 | 83 | 16 | 18 | 1376 | 1376 | 1376 | 0.032762 | 498 | 0.011857 | 1582 | 0.037667 | 1.464 | A10 | MAXW0.07408316/FF
Horizontal Wall | Maxi | MAXW.07408316/FF/DBE | 74 | 83 | 16 | 18 | 1856 | 1856 | 1856 | 0.04419 | 928 | 0.022095 | 2042 | 0.048619 | 1 | A10 | MAXW0.07408316/FF/DBE
Horizontal Wall | Maxi | MAXW.07408316/FT | 74 | 83 | 16 | 18 | 1613 | 1613 | 1613 | 0.038405 | 582 | 0.013857 | 1855 | 0.044167 | 1.468 | A10 | MAXW0.07408316/FT
Horizontal Wall | Maxi | MAXW.07408316/FT/DBE | 74 | 83 | 16 | 18 | 2093 | 2093 | 2093 | 0.049833 | 1047 | 0.024929 | 2302 | 0.05481 | 1 | A10 | MAXW0.07408316/FT/DBE
Horizontal Wall | Maxi | MAXW.07408316/WF | 74 | 83 | 16 | 18 | 1639 | 1639 | 1639 | 0.039024 | 592 | 0.014095 | 1885 | 0.044881 | 1.47 | A10 | MAXW0.07408316/WF
Horizontal Wall | Maxi | MAXW.07408316/WF/DBE | 74 | 83 | 16 | 18 | 2119 | 2119 | 2119 | 0.050452 | 1060 | 0.025238 | 2331 | 0.0555 | 1 | A10 | MAXW0.07408316/WF/DBE
Horizontal Wall | Maxi | MAXW.07408316/WT | 74 | 83 | 16 | 18 | 1932 | 1932 | 1932 | 0.046 | 696 | 0.016571 | 2224 | 0.052952 | 1.474 | A10 | MAXW0.07408316/WT
Horizontal Wall | Maxi | MAXW.07408316/WT/DBE | 74 | 83 | 16 | 18 | 2412 | 2412 | 2412 | 0.057429 | 1206 | 0.028714 | 2653 | 0.063167 | 1 | A10 | MAXW0.07408316/WT/DBE
Horizontal Wall | Maxi | MAXW.07408320/FF | 74 | 83 | 20 | 23 | 1592 | 1592 | 1592 | 0.037905 | 615 | 0.014643 | 1815 | 0.043214 | 1.374 | A10 | MAXW0.07408320/FF
Horizontal Wall | Maxi | MAXW.07408320/FT | 74 | 83 | 20 | 23 | 1956 | 1956 | 1956 | 0.046571 | 761 | 0.018119 | 2228 | 0.053048 | 1.362 | A10 | MAXW0.07408320/FT
Horizontal Wall | Maxi | MAXW.07408320/WF | 74 | 83 | 20 | 23 | 1925 | 1925 | 1925 | 0.045833 | 753 | 0.017929 | 2191 | 0.052167 | 1.356 | A10 | MAXW0.07408320/WF
Horizontal Wall | Maxi | MAXW.07408320/WT | 74 | 83 | 20 | 23 | 2327 | 2327 | 2327 | 0.055405 | 917 | 0.021833 | 2646 | 0.063 | 1.345 | A10 | MAXW0.07408320/WT
Horizontal Wall | Maxi | MAXW.07408321/FF | 74 | 83 | 21 | 23 | 1700 | 1700 | 1700 | 0.040476 | 607 | 0.014452 | 1958 | 0.046619 | 1.484 | A10 | MAXW0.07408321/FF
Horizontal Wall | Maxi | MAXW.07408321/FF/DBE | 74 | 83 | 21 | 23 | 2180 | 2180 | 2180 | 0.051905 | 1090 | 0.025952 | 2398 | 0.057095 | 1 | A10 | MAXW0.07408321/FF/DBE
Horizontal Wall | Maxi | MAXW.07408321/FT | 74 | 83 | 21 | 23 | 2156 | 2156 | 2156 | 0.051333 | 768 | 0.018286 | 2486 | 0.05919 | 1.492 | A10 | MAXW0.07408321/FT
Horizontal Wall | Maxi | MAXW.07408321/FT/DBE | 74 | 83 | 21 | 23 | 2636 | 2636 | 2636 | 0.062762 | 1318 | 0.031381 | 2900 | 0.069048 | 1 | A10 | MAXW0.07408321/FT/DBE
Horizontal Wall | Maxi | MAXW.07408321/WF | 74 | 83 | 21 | 23 | 2171 | 2171 | 2171 | 0.05169 | 771 | 0.018357 | 2503 | 0.059595 | 1.496 | A10 | MAXW0.07408321/WF
Horizontal Wall | Maxi | MAXW.07408321/WF/DBE | 74 | 83 | 21 | 23 | 2651 | 2651 | 2651 | 0.063119 | 1326 | 0.031571 | 2916 | 0.069429 | 1 | A10 | MAXW0.07408321/WF/DBE
Horizontal Wall | Maxi | MAXW.07408321/WT | 74 | 83 | 21 | 23 | 2733 | 2733 | 2733 | 0.065071 | 962 | 0.022905 | 3154 | 0.075095 | 1.505 | A10 | MAXW0.07408321/WT
Horizontal Wall | Maxi | MAXW.07408321/WT/DBE | 74 | 83 | 21 | 23 | 3213 | 3213 | 3213 | 0.0765 | 1607 | 0.038262 | 3534 | 0.084143 | 1 | A10 | MAXW0.07408321/WT/DBE
Horizontal Wall | Maxi | MAXW.07410310/FF | 74 | 103 | 10 | 13 | 1098 | 1098 | 1098 | 0.026143 | 421 | 0.010024 | 1253 | 0.029833 | 1.386 | A10 | MAXW0.07410310/FF
Horizontal Wall | Maxi | MAXW.07410310/FT | 74 | 103 | 10 | 13 | 1197 | 1197 | 1197 | 0.0285 | 461 | 0.010976 | 1365 | 0.0325 | 1.377 | A10 | MAXW0.07410310/FT
Horizontal Wall | Maxi | MAXW.07410310/WF | 74 | 103 | 10 | 13 | 1240 | 1240 | 1240 | 0.029524 | 479 | 0.011405 | 1414 | 0.033667 | 1.372 | A10 | MAXW0.07410310/WF
Horizontal Wall | Maxi | MAXW.07410310/WT | 74 | 103 | 10 | 13 | 1316 | 1316 | 1316 | 0.031333 | 512 | 0.01219 | 1499 | 0.03569 | 1.363 | A10 | MAXW0.07410310/WT
Horizontal Wall | Maxi | MAXW.07410311/FF | 74 | 103 | 11 | 13 | 1416 | 1416 | 1416 | 0.033714 | 523 | 0.012452 | 1624 | 0.038667 | 1.438 | A10 | MAXW0.07410311/FF
Horizontal Wall | Maxi | MAXW.07410311/FF/DBE | 74 | 103 | 11 | 13 | 2016 | 2016 | 2016 | 0.048 | 1008 | 0.024 | 2218 | 0.05281 | 1 | A10 | MAXW0.07410311/FF/DBE
Horizontal Wall | Maxi | MAXW.07410311/FT | 74 | 103 | 11 | 13 | 1528 | 1528 | 1528 | 0.036381 | 564 | 0.013429 | 1753 | 0.041738 | 1.437 | A10 | MAXW0.07410311/FT
Horizontal Wall | Maxi | MAXW.07410311/FT/DBE | 74 | 103 | 11 | 13 | 2128 | 2128 | 2128 | 0.050667 | 1064 | 0.025333 | 2341 | 0.055738 | 1 | A10 | MAXW0.07410311/FT/DBE
Horizontal Wall | Maxi | MAXW.07410311/WF | 74 | 103 | 11 | 13 | 1579 | 1579 | 1579 | 0.037595 | 583 | 0.013881 | 1811 | 0.043119 | 1.437 | A10 | MAXW0.07410311/WF
Horizontal Wall | Maxi | MAXW.07410311/WF/DBE | 74 | 103 | 11 | 13 | 2179 | 2179 | 2179 | 0.051881 | 1090 | 0.025952 | 2397 | 0.057071 | 1 | A10 | MAXW0.07410311/WF/DBE
Horizontal Wall | Maxi | MAXW.07410311/WT | 74 | 103 | 11 | 13 | 1675 | 1675 | 1675 | 0.039881 | 620 | 0.014762 | 1921 | 0.045738 | 1.436 | A10 | MAXW0.07410311/WT
Horizontal Wall | Maxi | MAXW.07410311/WT/DBE | 74 | 103 | 11 | 13 | 2275 | 2275 | 2275 | 0.054167 | 1138 | 0.027095 | 2503 | 0.059595 | 1 | A10 | MAXW0.07410311/WT/DBE
Horizontal Wall | Maxi | MAXW.07410315/FF | 74 | 103 | 15 | 18 | 1554 | 1554 | 1554 | 0.037 | 600 | 0.014286 | 1772 | 0.04219 | 1.374 | A10 | MAXW0.07410315/FF
Horizontal Wall | Maxi | MAXW.07410315/FT | 74 | 103 | 15 | 18 | 1794 | 1794 | 1794 | 0.042714 | 698 | 0.016619 | 2043 | 0.048643 | 1.362 | A10 | MAXW0.07410315/FT
Horizontal Wall | Maxi | MAXW.07410315/WF | 74 | 103 | 15 | 18 | 1799 | 1799 | 1799 | 0.042833 | 702 | 0.016714 | 2047 | 0.048738 | 1.357 | A10 | MAXW0.07410315/WF
Horizontal Wall | Maxi | MAXW.07410315/WT | 74 | 103 | 15 | 18 | 2070 | 2070 | 2070 | 0.049286 | 816 | 0.019429 | 2354 | 0.056048 | 1.345 | A10 | MAXW0.07410315/WT
Horizontal Wall | Maxi | MAXW.07410316/FF | 74 | 103 | 16 | 18 | 1707 | 1707 | 1707 | 0.040643 | 618 | 0.014714 | 1963 | 0.046738 | 1.464 | A10 | MAXW0.07410316/FF
Horizontal Wall | Maxi | MAXW.07410316/FF/DBE | 74 | 103 | 16 | 18 | 2667 | 2667 | 2667 | 0.0635 | 1334 | 0.031762 | 2934 | 0.069857 | 1 | A10 | MAXW0.07410316/FF/DBE
Horizontal Wall | Maxi | MAXW.07410316/FT | 74 | 103 | 16 | 18 | 2002 | 2002 | 2002 | 0.047667 | 723 | 0.017214 | 2302 | 0.05481 | 1.468 | A10 | MAXW0.07410316/FT
Horizontal Wall | Maxi | MAXW.07410316/FT/DBE | 74 | 103 | 16 | 18 | 2962 | 2962 | 2962 | 0.070524 | 1481 | 0.035262 | 3258 | 0.077571 | 1 | A10 | MAXW0.07410316/FT/DBE
Horizontal Wall | Maxi | MAXW.07410316/WF | 74 | 103 | 16 | 18 | 2034 | 2034 | 2034 | 0.048429 | 734 | 0.017476 | 2339 | 0.05569 | 1.47 | A10 | MAXW0.07410316/WF
Horizontal Wall | Maxi | MAXW.07410316/WF/DBE | 74 | 103 | 16 | 18 | 2994 | 2994 | 2994 | 0.071286 | 1497 | 0.035643 | 3293 | 0.078405 | 1 | A10 | MAXW0.07410316/WF/DBE
Horizontal Wall | Maxi | MAXW.07410316/WT | 74 | 103 | 16 | 18 | 2397 | 2397 | 2397 | 0.057071 | 863 | 0.020548 | 2759 | 0.06569 | 1.474 | A10 | MAXW0.07410316/WT
Horizontal Wall | Maxi | MAXW.07410316/WT/DBE | 74 | 103 | 16 | 18 | 3357 | 3357 | 3357 | 0.079929 | 1679 | 0.039976 | 3693 | 0.087929 | 1 | A10 | MAXW0.07410316/WT/DBE
Horizontal Wall | Maxi | MAXW.07410320/FF | 74 | 103 | 20 | 23 | 1976 | 1976 | 1976 | 0.047048 | 763 | 0.018167 | 2253 | 0.053643 | 1.374 | A10 | MAXW0.07410320/FF
Horizontal Wall | Maxi | MAXW.07410320/FT | 74 | 103 | 20 | 23 | 2427 | 2427 | 2427 | 0.057786 | 944 | 0.022476 | 2764 | 0.06581 | 1.362 | A10 | MAXW0.07410320/FT
Horizontal Wall | Maxi | MAXW.07410320/WF | 74 | 103 | 20 | 23 | 2389 | 2389 | 2389 | 0.056881 | 934 | 0.022238 | 2719 | 0.064738 | 1.356 | A10 | MAXW0.07410320/WF
Horizontal Wall | Maxi | MAXW.07410320/WT | 74 | 103 | 20 | 23 | 2888 | 2888 | 2888 | 0.068762 | 1138 | 0.027095 | 3284 | 0.07819 | 1.345 | A10 | MAXW0.07410320/WT
Horizontal Wall | Maxi | MAXW.07410321/FF | 74 | 103 | 21 | 23 | 2110 | 2110 | 2110 | 0.050238 | 753 | 0.017929 | 2431 | 0.057881 | 1.484 | A10 | MAXW0.07410321/FF
Horizontal Wall | Maxi | MAXW.07410321/FF/DBE | 74 | 103 | 21 | 23 | 3070 | 3070 | 3070 | 0.073095 | 1535 | 0.036548 | 3377 | 0.080405 | 1 | A10 | MAXW0.07410321/FF/DBE
Horizontal Wall | Maxi | MAXW.07410321/FT | 74 | 103 | 21 | 23 | 2676 | 2676 | 2676 | 0.063714 | 953 | 0.02269 | 3085 | 0.073452 | 1.492 | A10 | MAXW0.07410321/FT
Horizontal Wall | Maxi | MAXW.07410321/FT/DBE | 74 | 103 | 21 | 23 | 3636 | 3636 | 3636 | 0.086571 | 1818 | 0.043286 | 4000 | 0.095238 | 1 | A10 | MAXW0.07410321/FT/DBE
Horizontal Wall | Maxi | MAXW.07410321/WF | 74 | 103 | 21 | 23 | 2694 | 2694 | 2694 | 0.064143 | 956 | 0.022762 | 3106 | 0.073952 | 1.496 | A10 | MAXW0.07410321/WF
Horizontal Wall | Maxi | MAXW.07410321/WF/DBE | 74 | 103 | 21 | 23 | 3654 | 3654 | 3654 | 0.087 | 1827 | 0.0435 | 4019 | 0.09569 | 1 | A10 | MAXW0.07410321/WF/DBE
Horizontal Wall | Maxi | MAXW.07410321/WT | 74 | 103 | 21 | 23 | 3392 | 3392 | 3392 | 0.080762 | 1194 | 0.028429 | 3914 | 0.09319 | 1.505 | A10 | MAXW0.07410321/WT
Horizontal Wall | Maxi | MAXW.07410321/WT/DBE | 74 | 103 | 21 | 23 | 4352 | 4352 | 4352 | 0.10362 | 2176 | 0.05181 | 4787 | 0.11398 | 1 | A10 | MAXW0.07410321/WT/DBE
Horizontal Wall | Maxi | MAXW.07412310/FF | 74 | 123 | 10 | 13 | 1311 | 1311 | 1311 | 0.031214 | 502 | 0.011952 | 1496 | 0.035619 | 1.386 | A10 | MAXW0.07412310/FF
Horizontal Wall | Maxi | MAXW.07412310/FT | 74 | 123 | 10 | 13 | 1429 | 1429 | 1429 | 0.034024 | 550 | 0.013095 | 1629 | 0.038786 | 1.377 | A10 | MAXW0.07412310/FT
Horizontal Wall | Maxi | MAXW.07412310/WF | 74 | 123 | 10 | 13 | 1481 | 1481 | 1481 | 0.035262 | 572 | 0.013619 | 1688 | 0.04019 | 1.372 | A10 | MAXW0.07412310/WF
Horizontal Wall | Maxi | MAXW.07412310/WT | 74 | 123 | 10 | 13 | 1572 | 1572 | 1572 | 0.037429 | 612 | 0.014571 | 1791 | 0.042643 | 1.363 | A10 | MAXW0.07412310/WT
Horizontal Wall | Maxi | MAXW.07412311/FF | 74 | 123 | 11 | 13 | 1691 | 1691 | 1691 | 0.040262 | 624 | 0.014857 | 1940 | 0.04619 | 1.438 | A10 | MAXW0.07412311/FF
Horizontal Wall | Maxi | MAXW.07412311/FF/DBE | 74 | 123 | 11 | 13 | 2291 | 2291 | 2291 | 0.054548 | 1146 | 0.027286 | 2520 | 0.06 | 1 | A10 | MAXW0.07412311/FF/DBE
Horizontal Wall | Maxi | MAXW.07412311/FT | 74 | 123 | 11 | 13 | 1825 | 1825 | 1825 | 0.043452 | 673 | 0.016024 | 2093 | 0.049833 | 1.437 | A10 | MAXW0.07412311/FT
Horizontal Wall | Maxi | MAXW.07412311/FT/DBE | 74 | 123 | 11 | 13 | 2425 | 2425 | 2425 | 0.057738 | 1213 | 0.028881 | 2668 | 0.063524 | 1 | A10 | MAXW0.07412311/FT/DBE
Horizontal Wall | Maxi | MAXW.07412311/WF | 74 | 123 | 11 | 13 | 1886 | 1886 | 1886 | 0.044905 | 696 | 0.016571 | 2163 | 0.0515 | 1.437 | A10 | MAXW0.07412311/WF
Horizontal Wall | Maxi | MAXW.07412311/WF/DBE | 74 | 123 | 11 | 13 | 2486 | 2486 | 2486 | 0.05919 | 1243 | 0.029595 | 2735 | 0.065119 | 1 | A10 | MAXW0.07412311/WF/DBE
Horizontal Wall | Maxi | MAXW.07412311/WT | 74 | 123 | 11 | 13 | 2000 | 2000 | 2000 | 0.047619 | 740 | 0.017619 | 2294 | 0.054619 | 1.436 | A10 | MAXW0.07412311/WT
Horizontal Wall | Maxi | MAXW.07412311/WT/DBE | 74 | 123 | 11 | 13 | 2600 | 2600 | 2600 | 0.061905 | 1300 | 0.030952 | 2860 | 0.068095 | 1 | A10 | MAXW0.07412311/WT/DBE
Horizontal Wall | Maxi | MAXW.07412315/FF | 74 | 123 | 15 | 18 | 1856 | 1856 | 1856 | 0.04419 | 716 | 0.017048 | 2116 | 0.050381 | 1.374 | A10 | MAXW0.07412315/FF
Horizontal Wall | Maxi | MAXW.07412315/FT | 74 | 123 | 15 | 18 | 2142 | 2142 | 2142 | 0.051 | 833 | 0.019833 | 2440 | 0.058095 | 1.362 | A10 | MAXW0.07412315/FT
Horizontal Wall | Maxi | MAXW.07412315/WF | 74 | 123 | 15 | 18 | 2148 | 2148 | 2148 | 0.051143 | 838 | 0.019952 | 2444 | 0.05819 | 1.357 | A10 | MAXW0.07412315/WF
Horizontal Wall | Maxi | MAXW.07412315/WT | 74 | 123 | 15 | 18 | 2472 | 2472 | 2472 | 0.058857 | 974 | 0.02319 | 2811 | 0.066929 | 1.345 | A10 | MAXW0.07412315/WT
Horizontal Wall | Maxi | MAXW.07412316/FF | 74 | 123 | 16 | 18 | 2038 | 2038 | 2038 | 0.048524 | 738 | 0.017571 | 2344 | 0.05581 | 1.464 | A10 | MAXW0.07412316/FF
Horizontal Wall | Maxi | MAXW.07412316/FF/DBE | 74 | 123 | 16 | 18 | 2998 | 2998 | 2998 | 0.071381 | 1499 | 0.03569 | 3298 | 0.078524 | 1 | A10 | MAXW0.07412316/FF/DBE
Horizontal Wall | Maxi | MAXW.07412316/FT | 74 | 123 | 16 | 18 | 2391 | 2391 | 2391 | 0.056929 | 863 | 0.020548 | 2750 | 0.065476 | 1.468 | A10 | MAXW0.07412316/FT
Horizontal Wall | Maxi | MAXW.07412316/FT/DBE | 74 | 123 | 16 | 18 | 3351 | 3351 | 3351 | 0.079786 | 1676 | 0.039905 | 3686 | 0.087762 | 1 | A10 | MAXW0.07412316/FT/DBE
Horizontal Wall | Maxi | MAXW.07412316/WF | 74 | 123 | 16 | 18 | 2429 | 2429 | 2429 | 0.057833 | 877 | 0.020881 | 2793 | 0.0665 | 1.47 | A10 | MAXW0.07412316/WF
Horizontal Wall | Maxi | MAXW.07412316/WF/DBE | 74 | 123 | 16 | 18 | 3389 | 3389 | 3389 | 0.08069 | 1695 | 0.040357 | 3728 | 0.088762 | 1 | A10 | MAXW0.07412316/WF/DBE
Horizontal Wall | Maxi | MAXW.07412316/WT | 74 | 123 | 16 | 18 | 2862 | 2862 | 2862 | 0.068143 | 1030 | 0.024524 | 3294 | 0.078429 | 1.474 | A10 | MAXW0.07412316/WT
Horizontal Wall | Maxi | MAXW.07412316/WT/DBE | 74 | 123 | 16 | 18 | 3822 | 3822 | 3822 | 0.091 | 1911 | 0.0455 | 4204 | 0.1001 | 1 | A10 | MAXW0.07412316/WT/DBE
Horizontal Wall | Maxi | MAXW.07412320/FF | 74 | 123 | 20 | 23 | 2360 | 2360 | 2360 | 0.05619 | 911 | 0.02169 | 2690 | 0.064048 | 1.374 | A10 | MAXW0.07412320/FF
Horizontal Wall | Maxi | MAXW.07412320/FT | 74 | 123 | 20 | 23 | 2898 | 2898 | 2898 | 0.069 | 1127 | 0.026833 | 3301 | 0.078595 | 1.362 | A10 | MAXW0.07412320/FT
Horizontal Wall | Maxi | MAXW.07412320/WF | 74 | 123 | 20 | 23 | 2853 | 2853 | 2853 | 0.067929 | 1116 | 0.026571 | 3247 | 0.07731 | 1.356 | A10 | MAXW0.07412320/WF
Horizontal Wall | Maxi | MAXW.07412320/WT | 74 | 123 | 20 | 23 | 3449 | 3449 | 3449 | 0.082119 | 1359 | 0.032357 | 3922 | 0.093381 | 1.345 | A10 | MAXW0.07412320/WT
Horizontal Wall | Maxi | MAXW.07412321/FF | 74 | 123 | 21 | 23 | 2520 | 2520 | 2520 | 0.06 | 900 | 0.021429 | 2903 | 0.069119 | 1.484 | A10 | MAXW0.07412321/FF
Horizontal Wall | Maxi | MAXW.07412321/FF/DBE | 74 | 123 | 21 | 23 | 3480 | 3480 | 3480 | 0.082857 | 1740 | 0.041429 | 3828 | 0.091143 | 1 | A10 | MAXW0.07412321/FF/DBE
Horizontal Wall | Maxi | MAXW.07412321/FT | 74 | 123 | 21 | 23 | 3196 | 3196 | 3196 | 0.076095 | 1138 | 0.027095 | 3685 | 0.087738 | 1.492 | A10 | MAXW0.07412321/FT
Horizontal Wall | Maxi | MAXW.07412321/FT/DBE | 74 | 123 | 21 | 23 | 4156 | 4156 | 4156 | 0.098952 | 2078 | 0.049476 | 4572 | 0.10886 | 1 | A10 | MAXW0.07412321/FT/DBE
Horizontal Wall | Maxi | MAXW.07412321/WF | 74 | 123 | 21 | 23 | 3217 | 3217 | 3217 | 0.076595 | 1142 | 0.02719 | 3709 | 0.08831 | 1.496 | A10 | MAXW0.07412321/WF
Horizontal Wall | Maxi | MAXW.07412321/WF/DBE | 74 | 123 | 21 | 23 | 4177 | 4177 | 4177 | 0.099452 | 2089 | 0.049738 | 4595 | 0.1094 | 1 | A10 | MAXW0.07412321/WF/DBE
Horizontal Wall | Maxi | MAXW.07412321/WT | 74 | 123 | 21 | 23 | 4051 | 4051 | 4051 | 0.096452 | 1426 | 0.033952 | 4675 | 0.11131 | 1.505 | A10 | MAXW0.07412321/WT
Horizontal Wall | Maxi | MAXW.07412321/WT/DBE | 74 | 123 | 21 | 23 | 5011 | 5011 | 5011 | 0.11931 | 2506 | 0.059667 | 5512 | 0.13124 | 1 | A10 | MAXW0.07412321/WT/DBE
Horizontal Wall | Maxi | MAXW.07414310/FF | 74 | 143 | 10 | 13 | 1524 | 1524 | 1524 | 0.036286 | 584 | 0.013905 | 1739 | 0.041405 | 1.386 | A10 | MAXW0.07414310/FF
Horizontal Wall | Maxi | MAXW.07414310/FT | 74 | 143 | 10 | 13 | 1662 | 1662 | 1662 | 0.039571 | 640 | 0.015238 | 1895 | 0.045119 | 1.377 | A10 | MAXW0.07414310/FT
Horizontal Wall | Maxi | MAXW.07414310/WF | 74 | 143 | 10 | 13 | 1722 | 1722 | 1722 | 0.041 | 665 | 0.015833 | 1963 | 0.046738 | 1.372 | A10 | MAXW0.07414310/WF
Horizontal Wall | Maxi | MAXW.07414310/WT | 74 | 143 | 10 | 13 | 1827 | 1827 | 1827 | 0.0435 | 711 | 0.016929 | 2081 | 0.049548 | 1.363 | A10 | MAXW0.07414310/WT
Horizontal Wall | Maxi | MAXW.07414311/FF | 74 | 143 | 11 | 13 | 1966 | 1966 | 1966 | 0.04681 | 725 | 0.017262 | 2255 | 0.05369 | 1.438 | A10 | MAXW0.07414311/FF
Horizontal Wall | Maxi | MAXW.07414311/FF/DBE | 74 | 143 | 11 | 13 | 2566 | 2566 | 2566 | 0.061095 | 1283 | 0.030548 | 2823 | 0.067214 | 1 | A10 | MAXW0.07414311/FF/DBE
Horizontal Wall | Maxi | MAXW.07414311/FT | 74 | 143 | 11 | 13 | 2121 | 2121 | 2121 | 0.0505 | 783 | 0.018643 | 2433 | 0.057929 | 1.437 | A10 | MAXW0.07414311/FT
Horizontal Wall | Maxi | MAXW.07414311/FT/DBE | 74 | 143 | 11 | 13 | 2721 | 2721 | 2721 | 0.064786 | 1361 | 0.032405 | 2993 | 0.071262 | 1 | A10 | MAXW0.07414311/FT/DBE
Horizontal Wall | Maxi | MAXW.07414311/WF | 74 | 143 | 11 | 13 | 2192 | 2192 | 2192 | 0.05219 | 809 | 0.019262 | 2514 | 0.059857 | 1.437 | A10 | MAXW0.07414311/WF
Horizontal Wall | Maxi | MAXW.07414311/WF/DBE | 74 | 143 | 11 | 13 | 2792 | 2792 | 2792 | 0.066476 | 1396 | 0.033238 | 3071 | 0.073119 | 1 | A10 | MAXW0.07414311/WF/DBE
Horizontal Wall | Maxi | MAXW.07414311/WT | 74 | 143 | 11 | 13 | 2325 | 2325 | 2325 | 0.055357 | 860 | 0.020476 | 2667 | 0.0635 | 1.436 | A10 | MAXW0.07414311/WT
Horizontal Wall | Maxi | MAXW.07414311/WT/DBE | 74 | 143 | 11 | 13 | 2925 | 2925 | 2925 | 0.069643 | 1463 | 0.034833 | 3218 | 0.076619 | 1 | A10 | MAXW0.07414311/WT/DBE
Horizontal Wall | Maxi | MAXW.07414315/FF | 74 | 143 | 15 | 18 | 2157 | 2157 | 2157 | 0.051357 | 833 | 0.019833 | 2459 | 0.058548 | 1.374 | A10 | MAXW0.07414315/FF
Horizontal Wall | Maxi | MAXW.07414315/FT | 74 | 143 | 15 | 18 | 2491 | 2491 | 2491 | 0.05931 | 969 | 0.023071 | 2837 | 0.067548 | 1.362 | A10 | MAXW0.07414315/FT
Horizontal Wall | Maxi | MAXW.07414315/WF | 74 | 143 | 15 | 18 | 2498 | 2498 | 2498 | 0.059476 | 974 | 0.02319 | 2843 | 0.06769 | 1.357 | A10 | MAXW0.07414315/WF
Horizontal Wall | Maxi | MAXW.07414315/WT | 74 | 143 | 15 | 18 | 2874 | 2874 | 2874 | 0.068429 | 1132 | 0.026952 | 3268 | 0.07781 | 1.345 | A10 | MAXW0.07414315/WT
Horizontal Wall | Maxi | MAXW.07414316/FF | 74 | 143 | 16 | 18 | 2370 | 2370 | 2370 | 0.056429 | 858 | 0.020429 | 2726 | 0.064905 | 1.464 | A10 | MAXW0.07414316/FF
Horizontal Wall | Maxi | MAXW.07414316/FF/DBE | 74 | 143 | 16 | 18 | 3330 | 3330 | 3330 | 0.079286 | 1665 | 0.039643 | 3663 | 0.087214 | 1 | A10 | MAXW0.07414316/FF/DBE
Horizontal Wall | Maxi | MAXW.07414316/FT | 74 | 143 | 16 | 18 | 2779 | 2779 | 2779 | 0.066167 | 1003 | 0.023881 | 3196 | 0.076095 | 1.468 | A10 | MAXW0.07414316/FT
Horizontal Wall | Maxi | MAXW.07414316/FT/DBE | 74 | 143 | 16 | 18 | 3739 | 3739 | 3739 | 0.089024 | 1870 | 0.044524 | 4113 | 0.097929 | 1 | A10 | MAXW0.07414316/FT/DBE
Horizontal Wall | Maxi | MAXW.07414316/WF | 74 | 143 | 16 | 18 | 2824 | 2824 | 2824 | 0.067238 | 1019 | 0.024262 | 3248 | 0.077333 | 1.47 | A10 | MAXW0.07414316/WF
Horizontal Wall | Maxi | MAXW.07414316/WF/DBE | 74 | 143 | 16 | 18 | 3784 | 3784 | 3784 | 0.090095 | 1892 | 0.045048 | 4162 | 0.099095 | 1 | A10 | MAXW0.07414316/WF/DBE
Horizontal Wall | Maxi | MAXW.07414316/WT | 74 | 143 | 16 | 18 | 3328 | 3328 | 3328 | 0.079238 | 1198 | 0.028524 | 3831 | 0.091214 | 1.474 | A10 | MAXW0.07414316/WT
Horizontal Wall | Maxi | MAXW.07414316/WT/DBE | 74 | 143 | 16 | 18 | 4288 | 4288 | 4288 | 0.1021 | 2144 | 0.051048 | 4717 | 0.11231 | 1 | A10 | MAXW0.07414316/WT/DBE
Horizontal Wall | Maxi | MAXW.07414320/FF | 74 | 143 | 20 | 23 | 2743 | 2743 | 2743 | 0.06531 | 1059 | 0.025214 | 3127 | 0.074452 | 1.374 | A10 | MAXW0.07414320/FF
Horizontal Wall | Maxi | MAXW.07414320/FT | 74 | 143 | 20 | 23 | 3370 | 3370 | 3370 | 0.080238 | 1311 | 0.031214 | 3838 | 0.091381 | 1.362 | A10 | MAXW0.07414320/FT
Horizontal Wall | Maxi | MAXW.07414320/WF | 74 | 143 | 20 | 23 | 3317 | 3317 | 3317 | 0.078976 | 1297 | 0.030881 | 3775 | 0.089881 | 1.356 | A10 | MAXW0.07414320/WF
Horizontal Wall | Maxi | MAXW.07414320/WT | 74 | 143 | 20 | 23 | 4010 | 4010 | 4010 | 0.095476 | 1580 | 0.037619 | 4559 | 0.10855 | 1.345 | A10 | MAXW0.07414320/WT
Horizontal Wall | Maxi | MAXW.07414321/FF | 74 | 143 | 21 | 23 | 2929 | 2929 | 2929 | 0.069738 | 1046 | 0.024905 | 3374 | 0.080333 | 1.484 | A10 | MAXW0.07414321/FF
Horizontal Wall | Maxi | MAXW.07414321/FF/DBE | 74 | 143 | 21 | 23 | 3889 | 3889 | 3889 | 0.092595 | 1945 | 0.04631 | 4278 | 0.10186 | 1 | A10 | MAXW0.07414321/FF/DBE
Horizontal Wall | Maxi | MAXW.07414321/FT | 74 | 143 | 21 | 23 | 3715 | 3715 | 3715 | 0.088452 | 1323 | 0.0315 | 4283 | 0.10198 | 1.492 | A10 | MAXW0.07414321/FT
Horizontal Wall | Maxi | MAXW.07414321/FT/DBE | 74 | 143 | 21 | 23 | 4675 | 4675 | 4675 | 0.11131 | 2338 | 0.055667 | 5143 | 0.12245 | 1 | A10 | MAXW0.07414321/FT/DBE
Horizontal Wall | Maxi | MAXW.07414321/WF | 74 | 143 | 21 | 23 | 3740 | 3740 | 3740 | 0.089048 | 1328 | 0.031619 | 4312 | 0.10267 | 1.496 | A10 | MAXW0.07414321/WF
Horizontal Wall | Maxi | MAXW.07414321/WF/DBE | 74 | 143 | 21 | 23 | 4700 | 4700 | 4700 | 0.1119 | 2350 | 0.055952 | 5170 | 0.1231 | 1 | A10 | MAXW0.07414321/WF/DBE
Horizontal Wall | Maxi | MAXW.07414321/WT | 74 | 143 | 21 | 23 | 4709 | 4709 | 4709 | 0.11212 | 1658 | 0.039476 | 5434 | 0.12938 | 1.505 | A10 | MAXW0.07414321/WT
Horizontal Wall | Maxi | MAXW.07414321/WT/DBE | 74 | 143 | 21 | 23 | 5669 | 5669 | 5669 | 0.13498 | 2835 | 0.0675 | 6236 | 0.14848 | 1 | A10 | MAXW0.07414321/WT/DBE
Horizontal Wall | Maxi | MAXW.07416310/FF | 74 | 163 | 10 | 13 | 1738 | 1738 | 1738 | 0.041381 | 666 | 0.015857 | 1983 | 0.047214 | 1.386 | A10 | MAXW0.07416310/FF
Horizontal Wall | Maxi | MAXW.07416310/FT | 74 | 163 | 10 | 13 | 1894 | 1894 | 1894 | 0.045095 | 729 | 0.017357 | 2159 | 0.051405 | 1.377 | A10 | MAXW0.07416310/FT
Horizontal Wall | Maxi | MAXW.07416310/WF | 74 | 163 | 10 | 13 | 1962 | 1962 | 1962 | 0.046714 | 757 | 0.018024 | 2237 | 0.053262 | 1.372 | A10 | MAXW0.07416310/WF
Horizontal Wall | Maxi | MAXW.07416310/WT | 74 | 163 | 10 | 13 | 2083 | 2083 | 2083 | 0.049595 | 810 | 0.019286 | 2373 | 0.0565 | 1.363 | A10 | MAXW0.07416310/WT
Horizontal Wall | Maxi | MAXW.07416311/FF | 74 | 163 | 11 | 13 | 2241 | 2241 | 2241 | 0.053357 | 827 | 0.01969 | 2570 | 0.06119 | 1.438 | A10 | MAXW0.07416311/FF
Horizontal Wall | Maxi | MAXW.07416311/FF/DBE | 74 | 163 | 11 | 13 | 3441 | 3441 | 3441 | 0.081929 | 1721 | 0.040976 | 3785 | 0.090119 | 1 | A10 | MAXW0.07416311/FF/DBE
Horizontal Wall | Maxi | MAXW.07416311/FT | 74 | 163 | 11 | 13 | 2418 | 2418 | 2418 | 0.057571 | 892 | 0.021238 | 2773 | 0.066024 | 1.437 | A10 | MAXW0.07416311/FT
Horizontal Wall | Maxi | MAXW.07416311/FT/DBE | 74 | 163 | 11 | 13 | 3618 | 3618 | 3618 | 0.086143 | 1809 | 0.043071 | 3980 | 0.094762 | 1 | A10 | MAXW0.07416311/FT/DBE
Horizontal Wall | Maxi | MAXW.07416311/WF | 74 | 163 | 11 | 13 | 2499 | 2499 | 2499 | 0.0595 | 922 | 0.021952 | 2866 | 0.068238 | 1.437 | A10 | MAXW0.07416311/WF
Horizontal Wall | Maxi | MAXW.07416311/WF/DBE | 74 | 163 | 11 | 13 | 3699 | 3699 | 3699 | 0.088071 | 1850 | 0.044048 | 4069 | 0.096881 | 1 | A10 | MAXW0.07416311/WF/DBE
Horizontal Wall | Maxi | MAXW.07416311/WT | 74 | 163 | 11 | 13 | 2651 | 2651 | 2651 | 0.063119 | 981 | 0.023357 | 3041 | 0.072405 | 1.436 | A10 | MAXW0.07416311/WT
Horizontal Wall | Maxi | MAXW.07416311/WT/DBE | 74 | 163 | 11 | 13 | 3851 | 3851 | 3851 | 0.09169 | 1926 | 0.045857 | 4236 | 0.10086 | 1 | A10 | MAXW0.07416311/WT/DBE
Horizontal Wall | Maxi | MAXW.07416315/FF | 74 | 163 | 15 | 18 | 2459 | 2459 | 2459 | 0.058548 | 949 | 0.022595 | 2803 | 0.066738 | 1.374 | A10 | MAXW0.07416315/FF
Horizontal Wall | Maxi | MAXW.07416315/FT | 74 | 163 | 15 | 18 | 2839 | 2839 | 2839 | 0.067595 | 1104 | 0.026286 | 3234 | 0.077 | 1.362 | A10 | MAXW0.07416315/FT
Horizontal Wall | Maxi | MAXW.07416315/WF | 74 | 163 | 15 | 18 | 2847 | 2847 | 2847 | 0.067786 | 1110 | 0.026429 | 3240 | 0.077143 | 1.357 | A10 | MAXW0.07416315/WF
Horizontal Wall | Maxi | MAXW.07416315/WT | 74 | 163 | 15 | 18 | 3276 | 3276 | 3276 | 0.078 | 1291 | 0.030738 | 3725 | 0.08869 | 1.345 | A10 | MAXW0.07416315/WT
Horizontal Wall | Maxi | MAXW.07416316/FF | 74 | 163 | 16 | 18 | 2701 | 2701 | 2701 | 0.06431 | 978 | 0.023286 | 3106 | 0.073952 | 1.464 | A10 | MAXW0.07416316/FF
Horizontal Wall | Maxi | MAXW.07416316/FF/DBE | 74 | 163 | 16 | 18 | 4621 | 4621 | 4621 | 0.11002 | 2311 | 0.055024 | 5083 | 0.12102 | 1 | A10 | MAXW0.07416316/FF/DBE
Horizontal Wall | Maxi | MAXW.07416316/FT | 74 | 163 | 16 | 18 | 3168 | 3168 | 3168 | 0.075429 | 1144 | 0.027238 | 3643 | 0.086738 | 1.468 | A10 | MAXW0.07416316/FT
Horizontal Wall | Maxi | MAXW.07416316/FT/DBE | 74 | 163 | 16 | 18 | 5088 | 5088 | 5088 | 0.12114 | 2544 | 0.060571 | 5597 | 0.13326 | 1 | A10 | MAXW0.07416316/FT/DBE
Horizontal Wall | Maxi | MAXW.07416316/WF | 74 | 163 | 16 | 18 | 3219 | 3219 | 3219 | 0.076643 | 1162 | 0.027667 | 3702 | 0.088143 | 1.47 | A10 | MAXW0.07416316/WF
Horizontal Wall | Maxi | MAXW.07416316/WF/DBE | 74 | 163 | 16 | 18 | 5139 | 5139 | 5139 | 0.12236 | 2570 | 0.06119 | 5653 | 0.1346 | 1 | A10 | MAXW0.07416316/WF/DBE
Horizontal Wall | Maxi | MAXW.07416316/WT | 74 | 163 | 16 | 18 | 3793 | 3793 | 3793 | 0.09031 | 1365 | 0.0325 | 4366 | 0.10395 | 1.474 | A10 | MAXW0.07416316/WT
Horizontal Wall | Maxi | MAXW.07416316/WT/DBE | 74 | 163 | 16 | 18 | 5713 | 5713 | 5713 | 0.13602 | 2857 | 0.068024 | 6284 | 0.14962 | 1 | A10 | MAXW0.07416316/WT/DBE
Horizontal Wall | Maxi | MAXW.07416320/FF | 74 | 163 | 20 | 23 | 3127 | 3127 | 3127 | 0.074452 | 1207 | 0.028738 | 3565 | 0.084881 | 1.374 | A10 | MAXW0.07416320/FF
Horizontal Wall | Maxi | MAXW.07416320/FT | 74 | 163 | 20 | 23 | 3841 | 3841 | 3841 | 0.091452 | 1494 | 0.035571 | 4375 | 0.10417 | 1.362 | A10 | MAXW0.07416320/FT
Horizontal Wall | Maxi | MAXW.07416320/WF | 74 | 163 | 20 | 23 | 3781 | 3781 | 3781 | 0.090024 | 1478 | 0.03519 | 4303 | 0.10245 | 1.356 | A10 | MAXW0.07416320/WF
Horizontal Wall | Maxi | MAXW.07416320/WT | 74 | 163 | 20 | 23 | 4570 | 4570 | 4570 | 0.10881 | 1801 | 0.042881 | 5196 | 0.12371 | 1.345 | A10 | MAXW0.07416320/WT
Horizontal Wall | Maxi | MAXW.07416321/FF | 74 | 163 | 21 | 23 | 3339 | 3339 | 3339 | 0.0795 | 1192 | 0.028381 | 3847 | 0.091595 | 1.484 | A10 | MAXW0.07416321/FF
Horizontal Wall | Maxi | MAXW.07416321/FF/DBE | 74 | 163 | 21 | 23 | 5259 | 5259 | 5259 | 0.12521 | 2630 | 0.062619 | 5785 | 0.13774 | 1 | A10 | MAXW0.07416321/FF/DBE
Horizontal Wall | Maxi | MAXW.07416321/FT | 74 | 163 | 21 | 23 | 4235 | 4235 | 4235 | 0.10083 | 1508 | 0.035905 | 4883 | 0.11626 | 1.492 | A10 | MAXW0.07416321/FT
Horizontal Wall | Maxi | MAXW.07416321/FT/DBE | 74 | 163 | 21 | 23 | 6155 | 6155 | 6155 | 0.14655 | 3078 | 0.073286 | 6771 | 0.16121 | 1 | A10 | MAXW0.07416321/FT/DBE
Horizontal Wall | Maxi | MAXW.07416321/WF | 74 | 163 | 21 | 23 | 4263 | 4263 | 4263 | 0.1015 | 1513 | 0.036024 | 4915 | 0.11702 | 1.496 | A10 | MAXW0.07416321/WF
Horizontal Wall | Maxi | MAXW.07416321/WF/DBE | 74 | 163 | 21 | 23 | 6183 | 6183 | 6183 | 0.14721 | 3092 | 0.073619 | 6801 | 0.16193 | 1 | A10 | MAXW0.07416321/WF/DBE
Horizontal Wall | Maxi | MAXW.07416321/WT | 74 | 163 | 21 | 23 | 5368 | 5368 | 5368 | 0.12781 | 1890 | 0.045 | 6195 | 0.1475 | 1.505 | A10 | MAXW0.07416321/WT
Horizontal Wall | Maxi | MAXW.07416321/WT/DBE | 74 | 163 | 21 | 23 | 7288 | 7288 | 7288 | 0.17352 | 3644 | 0.086762 | 8017 | 0.19088 | 1 | A10 | MAXW0.07416321/WT/DBE
Horizontal Wall | Maxi | MAXW.07418310/FF | 74 | 183 | 10 | 13 | 1951 | 1951 | 1951 | 0.046452 | 747 | 0.017786 | 2226 | 0.053 | 1.386 | A10 | MAXW0.07418310/FF
Horizontal Wall | Maxi | MAXW.07418310/FT | 74 | 183 | 10 | 13 | 2127 | 2127 | 2127 | 0.050643 | 819 | 0.0195 | 2425 | 0.057738 | 1.377 | A10 | MAXW0.07418310/FT
Horizontal Wall | Maxi | MAXW.07418310/WF | 74 | 183 | 10 | 13 | 2203 | 2203 | 2203 | 0.052452 | 850 | 0.020238 | 2511 | 0.059786 | 1.372 | A10 | MAXW0.07418310/WF
Horizontal Wall | Maxi | MAXW.07418310/WT | 74 | 183 | 10 | 13 | 2338 | 2338 | 2338 | 0.055667 | 909 | 0.021643 | 2663 | 0.063405 | 1.363 | A10 | MAXW0.07418310/WT
Horizontal Wall | Maxi | MAXW.07418311/FF | 74 | 183 | 11 | 13 | 2516 | 2516 | 2516 | 0.059905 | 928 | 0.022095 | 2886 | 0.068714 | 1.438 | A10 | MAXW0.07418311/FF
Horizontal Wall | Maxi | MAXW.07418311/FF/DBE | 74 | 183 | 11 | 13 | 3716 | 3716 | 3716 | 0.088476 | 1858 | 0.044238 | 4088 | 0.097333 | 1 | A10 | MAXW0.07418311/FF/DBE
Horizontal Wall | Maxi | MAXW.07418311/FT | 74 | 183 | 11 | 13 | 2715 | 2715 | 2715 | 0.064643 | 1002 | 0.023857 | 3114 | 0.074143 | 1.437 | A10 | MAXW0.07418311/FT
Horizontal Wall | Maxi | MAXW.07418311/FT/DBE | 74 | 183 | 11 | 13 | 3915 | 3915 | 3915 | 0.093214 | 1958 | 0.046619 | 4307 | 0.10255 | 1 | A10 | MAXW0.07418311/FT/DBE
Horizontal Wall | Maxi | MAXW.07418311/WF | 74 | 183 | 11 | 13 | 2805 | 2805 | 2805 | 0.066786 | 1035 | 0.024643 | 3217 | 0.076595 | 1.437 | A10 | MAXW0.07418311/WF
Horizontal Wall | Maxi | MAXW.07418311/WF/DBE | 74 | 183 | 11 | 13 | 4005 | 4005 | 4005 | 0.095357 | 2003 | 0.04769 | 4406 | 0.1049 | 1 | A10 | MAXW0.07418311/WF/DBE
Horizontal Wall | Maxi | MAXW.07418311/WT | 74 | 183 | 11 | 13 | 2976 | 2976 | 2976 | 0.070857 | 1101 | 0.026214 | 3413 | 0.081262 | 1.436 | A10 | MAXW0.07418311/WT
Horizontal Wall | Maxi | MAXW.07418311/WT/DBE | 74 | 183 | 11 | 13 | 4176 | 4176 | 4176 | 0.099429 | 2088 | 0.049714 | 4594 | 0.10938 | 1 | A10 | MAXW0.07418311/WT/DBE
Horizontal Wall | Maxi | MAXW.07418315/FF | 74 | 183 | 15 | 18 | 2761 | 2761 | 2761 | 0.065738 | 1066 | 0.025381 | 3148 | 0.074952 | 1.374 | A10 | MAXW0.07418315/FF
Horizontal Wall | Maxi | MAXW.07418315/FT | 74 | 183 | 15 | 18 | 3187 | 3187 | 3187 | 0.075881 | 1240 | 0.029524 | 3630 | 0.086429 | 1.362 | A10 | MAXW0.07418315/FT
Horizontal Wall | Maxi | MAXW.07418315/WF | 74 | 183 | 15 | 18 | 3196 | 3196 | 3196 | 0.076095 | 1246 | 0.029667 | 3637 | 0.086595 | 1.357 | A10 | MAXW0.07418315/WF
Horizontal Wall | Maxi | MAXW.07418315/WT | 74 | 183 | 15 | 18 | 3678 | 3678 | 3678 | 0.087571 | 1449 | 0.0345 | 4182 | 0.099571 | 1.345 | A10 | MAXW0.07418315/WT
Horizontal Wall | Maxi | MAXW.07418316/FF | 74 | 183 | 16 | 18 | 3033 | 3033 | 3033 | 0.072214 | 1098 | 0.026143 | 3488 | 0.083048 | 1.464 | A10 | MAXW0.07418316/FF
Horizontal Wall | Maxi | MAXW.07418316/FF/DBE | 74 | 183 | 16 | 18 | 4953 | 4953 | 4953 | 0.11793 | 2477 | 0.058976 | 5448 | 0.12971 | 1 | A10 | MAXW0.07418316/FF/DBE
Horizontal Wall | Maxi | MAXW.07418316/FT | 74 | 183 | 16 | 18 | 3557 | 3557 | 3557 | 0.08469 | 1284 | 0.030571 | 4091 | 0.097405 | 1.468 | A10 | MAXW0.07418316/FT
Horizontal Wall | Maxi | MAXW.07418316/FT/DBE | 74 | 183 | 16 | 18 | 5477 | 5477 | 5477 | 0.1304 | 2739 | 0.065214 | 6025 | 0.14345 | 1 | A10 | MAXW0.07418316/FT/DBE
Horizontal Wall | Maxi | MAXW.07418316/WF | 74 | 183 | 16 | 18 | 3614 | 3614 | 3614 | 0.086048 | 1305 | 0.031071 | 4156 | 0.098952 | 1.47 | A10 | MAXW0.07418316/WF
Horizontal Wall | Maxi | MAXW.07418316/WF/DBE | 74 | 183 | 16 | 18 | 5534 | 5534 | 5534 | 0.13176 | 2767 | 0.065881 | 6087 | 0.14493 | 1 | A10 | MAXW0.07418316/WF/DBE
Horizontal Wall | Maxi | MAXW.07418316/WT | 74 | 183 | 16 | 18 | 4259 | 4259 | 4259 | 0.1014 | 1533 | 0.0365 | 4902 | 0.11671 | 1.474 | A10 | MAXW0.07418316/WT
Horizontal Wall | Maxi | MAXW.07418316/WT/DBE | 74 | 183 | 16 | 18 | 6179 | 6179 | 6179 | 0.14712 | 3090 | 0.073571 | 6797 | 0.16183 | 1 | A10 | MAXW0.07418316/WT/DBE
Horizontal Wall | Maxi | MAXW.07418320/FF | 74 | 183 | 20 | 23 | 3511 | 3511 | 3511 | 0.083595 | 1355 | 0.032262 | 4003 | 0.09531 | 1.374 | A10 | MAXW0.07418320/FF
Horizontal Wall | Maxi | MAXW.07418320/FT | 74 | 183 | 20 | 23 | 4312 | 4312 | 4312 | 0.10267 | 1677 | 0.039929 | 4911 | 0.11693 | 1.362 | A10 | MAXW0.07418320/FT
Horizontal Wall | Maxi | MAXW.07418320/WF | 74 | 183 | 20 | 23 | 4245 | 4245 | 4245 | 0.10107 | 1660 | 0.039524 | 4831 | 0.11502 | 1.356 | A10 | MAXW0.07418320/WF
Horizontal Wall | Maxi | MAXW.07418320/WT | 74 | 183 | 20 | 23 | 5131 | 5131 | 5131 | 0.12217 | 2022 | 0.048143 | 5834 | 0.1389 | 1.345 | A10 | MAXW0.07418320/WT
Horizontal Wall | Maxi | MAXW.07418321/FF | 74 | 183 | 21 | 23 | 3749 | 3749 | 3749 | 0.089262 | 1338 | 0.031857 | 4319 | 0.10283 | 1.484 | A10 | MAXW0.07418321/FF
Horizontal Wall | Maxi | MAXW.07418321/FF/DBE | 74 | 183 | 21 | 23 | 5669 | 5669 | 5669 | 0.13498 | 2835 | 0.0675 | 6236 | 0.14848 | 1 | A10 | MAXW0.07418321/FF/DBE
Horizontal Wall | Maxi | MAXW.07418321/FT | 74 | 183 | 21 | 23 | 4754 | 4754 | 4754 | 0.11319 | 1692 | 0.040286 | 5481 | 0.1305 | 1.492 | A10 | MAXW0.07418321/FT
Horizontal Wall | Maxi | MAXW.07418321/FT/DBE | 74 | 183 | 21 | 23 | 6674 | 6674 | 6674 | 0.1589 | 3337 | 0.079452 | 7341 | 0.17479 | 1 | A10 | MAXW0.07418321/FT/DBE
Horizontal Wall | Maxi | MAXW.07418321/WF | 74 | 183 | 21 | 23 | 4786 | 4786 | 4786 | 0.11395 | 1699 | 0.040452 | 5518 | 0.13138 | 1.496 | A10 | MAXW0.07418321/WF
Horizontal Wall | Maxi | MAXW.07418321/WF/DBE | 74 | 183 | 21 | 23 | 6706 | 6706 | 6706 | 0.15967 | 3353 | 0.079833 | 7377 | 0.17564 | 1 | A10 | MAXW0.07418321/WF/DBE
Horizontal Wall | Maxi | MAXW.07418321/WT | 74 | 183 | 21 | 23 | 6027 | 6027 | 6027 | 0.1435 | 2122 | 0.050524 | 6955 | 0.1656 | 1.505 | A10 | MAXW0.07418321/WT
Horizontal Wall | Maxi | MAXW.07418321/WT/DBE | 74 | 183 | 21 | 23 | 7947 | 7947 | 7947 | 0.18921 | 3974 | 0.094619 | 8742 | 0.20814 | 1 | A10 | MAXW0.07418321/WT/DBE
Horizontal Wall | Maxi | MAXW.07420310/FF | 74 | 203 | 10 | 13 | 2164 | 2164 | 2164 | 0.051524 | 829 | 0.019738 | 2469 | 0.058786 | 1.386 | A10 | MAXW0.07420310/FF
Horizontal Wall | Maxi | MAXW.07420310/FT | 74 | 203 | 10 | 13 | 2359 | 2359 | 2359 | 0.056167 | 908 | 0.021619 | 2689 | 0.064024 | 1.377 | A10 | MAXW0.07420310/FT
Horizontal Wall | Maxi | MAXW.07420310/WF | 74 | 203 | 10 | 13 | 2444 | 2444 | 2444 | 0.05819 | 943 | 0.022452 | 2786 | 0.066333 | 1.372 | A10 | MAXW0.07420310/WF
Horizontal Wall | Maxi | MAXW.07420310/WT | 74 | 203 | 10 | 13 | 2594 | 2594 | 2594 | 0.061762 | 1009 | 0.024024 | 2955 | 0.070357 | 1.363 | A10 | MAXW0.07420310/WT
Horizontal Wall | Maxi | MAXW.07420311/FF | 74 | 203 | 11 | 13 | 2791 | 2791 | 2791 | 0.066452 | 1030 | 0.024524 | 3201 | 0.076214 | 1.438 | A10 | MAXW0.07420311/FF
Horizontal Wall | Maxi | MAXW.07420311/FF/DBE | 74 | 203 | 11 | 13 | 3991 | 3991 | 3991 | 0.095024 | 1996 | 0.047524 | 4390 | 0.10452 | 1 | A10 | MAXW0.07420311/FF/DBE
Horizontal Wall | Maxi | MAXW.07420311/FT | 74 | 203 | 11 | 13 | 3011 | 3011 | 3011 | 0.07169 | 1111 | 0.026452 | 3454 | 0.082238 | 1.437 | A10 | MAXW0.07420311/FT
Horizontal Wall | Maxi | MAXW.07420311/FT/DBE | 74 | 203 | 11 | 13 | 4211 | 4211 | 4211 | 0.10026 | 2106 | 0.050143 | 4632 | 0.11029 | 1 | A10 | MAXW0.07420311/FT/DBE
Horizontal Wall | Maxi | MAXW.07420311/WF | 74 | 203 | 11 | 13 | 3112 | 3112 | 3112 | 0.074095 | 1148 | 0.027333 | 3569 | 0.084976 | 1.437 | A10 | MAXW0.07420311/WF
Horizontal Wall | Maxi | MAXW.07420311/WF/DBE | 74 | 203 | 11 | 13 | 4312 | 4312 | 4312 | 0.10267 | 2156 | 0.051333 | 4743 | 0.11293 | 1 | A10 | MAXW0.07420311/WF/DBE
Horizontal Wall | Maxi | MAXW.07420311/WT | 74 | 203 | 11 | 13 | 3301 | 3301 | 3301 | 0.078595 | 1221 | 0.029071 | 3786 | 0.090143 | 1.436 | A10 | MAXW0.07420311/WT
Horizontal Wall | Maxi | MAXW.07420311/WT/DBE | 74 | 203 | 11 | 13 | 4501 | 4501 | 4501 | 0.10717 | 2251 | 0.053595 | 4951 | 0.11788 | 1 | A10 | MAXW0.07420311/WT/DBE
Horizontal Wall | Maxi | MAXW.07420315/FF | 74 | 203 | 15 | 18 | 3063 | 3063 | 3063 | 0.072929 | 1182 | 0.028143 | 3492 | 0.083143 | 1.374 | A10 | MAXW0.07420315/FF
Horizontal Wall | Maxi | MAXW.07420315/FT | 74 | 203 | 15 | 18 | 3536 | 3536 | 3536 | 0.08419 | 1376 | 0.032762 | 4028 | 0.095905 | 1.362 | A10 | MAXW0.07420315/FT
Horizontal Wall | Maxi | MAXW.07420315/WF | 74 | 203 | 15 | 18 | 3546 | 3546 | 3546 | 0.084429 | 1383 | 0.032929 | 4035 | 0.096071 | 1.357 | A10 | MAXW0.07420315/WF
Horizontal Wall | Maxi | MAXW.07420315/WT | 74 | 203 | 15 | 18 | 4080 | 4080 | 4080 | 0.097143 | 1608 | 0.038286 | 4639 | 0.11045 | 1.345 | A10 | MAXW0.07420315/WT
Horizontal Wall | Maxi | MAXW.07420316/FF | 74 | 203 | 16 | 18 | 3364 | 3364 | 3364 | 0.080095 | 1218 | 0.029 | 3869 | 0.092119 | 1.464 | A10 | MAXW0.07420316/FF
Horizontal Wall | Maxi | MAXW.07420316/FF/DBE | 74 | 203 | 16 | 18 | 5284 | 5284 | 5284 | 0.12581 | 2642 | 0.062905 | 5812 | 0.13838 | 1 | A10 | MAXW0.07420316/FF/DBE
Horizontal Wall | Maxi | MAXW.07420316/FT | 74 | 203 | 16 | 18 | 3946 | 3946 | 3946 | 0.093952 | 1425 | 0.033929 | 4538 | 0.10805 | 1.468 | A10 | MAXW0.07420316/FT
Horizontal Wall | Maxi | MAXW.07420316/FT/DBE | 74 | 203 | 16 | 18 | 5866 | 5866 | 5866 | 0.13967 | 2933 | 0.069833 | 6453 | 0.15364 | 1 | A10 | MAXW0.07420316/FT/DBE
Horizontal Wall | Maxi | MAXW.07420316/WF | 74 | 203 | 16 | 18 | 4009 | 4009 | 4009 | 0.095452 | 1447 | 0.034452 | 4610 | 0.10976 | 1.47 | A10 | MAXW0.07420316/WF
Horizontal Wall | Maxi | MAXW.07420316/WF/DBE | 74 | 203 | 16 | 18 | 5929 | 5929 | 5929 | 0.14117 | 2965 | 0.070595 | 6522 | 0.15529 | 1 | A10 | MAXW0.07420316/WF/DBE
Horizontal Wall | Maxi | MAXW.07420316/WT | 74 | 203 | 16 | 18 | 4724 | 4724 | 4724 | 0.11248 | 1701 | 0.0405 | 5437 | 0.12945 | 1.474 | A10 | MAXW0.07420316/WT
Horizontal Wall | Maxi | MAXW.07420316/WT/DBE | 74 | 203 | 16 | 18 | 6644 | 6644 | 6644 | 0.15819 | 3322 | 0.079095 | 7308 | 0.174 | 1 | A10 | MAXW0.07420316/WT/DBE
Horizontal Wall | Maxi | MAXW.07420320/FF | 74 | 203 | 20 | 23 | 3894 | 3894 | 3894 | 0.092714 | 1503 | 0.035786 | 4439 | 0.10569 | 1.374 | A10 | MAXW0.07420320/FF
Horizontal Wall | Maxi | MAXW.07420320/FT | 74 | 203 | 20 | 23 | 4783 | 4783 | 4783 | 0.11388 | 1861 | 0.04431 | 5448 | 0.12971 | 1.362 | A10 | MAXW0.07420320/FT
Horizontal Wall | Maxi | MAXW.07420320/WF | 74 | 203 | 20 | 23 | 4708 | 4708 | 4708 | 0.1121 | 1841 | 0.043833 | 5358 | 0.12757 | 1.356 | A10 | MAXW0.07420320/WF
Horizontal Wall | Maxi | MAXW.07420320/WT | 74 | 203 | 20 | 23 | 5692 | 5692 | 5692 | 0.13552 | 2243 | 0.053405 | 6472 | 0.1541 | 1.345 | A10 | MAXW0.07420320/WT
Horizontal Wall | Maxi | MAXW.07420321/FF | 74 | 203 | 21 | 23 | 4159 | 4159 | 4159 | 0.099024 | 1485 | 0.035357 | 4791 | 0.11407 | 1.484 | A10 | MAXW0.07420321/FF
Horizontal Wall | Maxi | MAXW.07420321/FF/DBE | 74 | 203 | 21 | 23 | 6079 | 6079 | 6079 | 0.14474 | 3040 | 0.072381 | 6687 | 0.15921 | 1 | A10 | MAXW0.07420321/FF/DBE
Horizontal Wall | Maxi | MAXW.07420321/FT | 74 | 203 | 21 | 23 | 5274 | 5274 | 5274 | 0.12557 | 1878 | 0.044714 | 6081 | 0.14479 | 1.492 | A10 | MAXW0.07420321/FT
Horizontal Wall | Maxi | MAXW.07420321/FT/DBE | 74 | 203 | 21 | 23 | 7194 | 7194 | 7194 | 0.17129 | 3597 | 0.085643 | 7913 | 0.1884 | 1 | A10 | MAXW0.07420321/FT/DBE
Horizontal Wall | Maxi | MAXW.07420321/WF | 74 | 203 | 21 | 23 | 5310 | 5310 | 5310 | 0.12643 | 1885 | 0.044881 | 6122 | 0.14576 | 1.496 | A10 | MAXW0.07420321/WF
Horizontal Wall | Maxi | MAXW.07420321/WF/DBE | 74 | 203 | 21 | 23 | 7230 | 7230 | 7230 | 0.17214 | 3615 | 0.086071 | 7953 | 0.18936 | 1 | A10 | MAXW0.07420321/WF/DBE
Horizontal Wall | Maxi | MAXW.07420321/WT | 74 | 203 | 21 | 23 | 6685 | 6685 | 6685 | 0.15917 | 2353 | 0.056024 | 7714 | 0.18367 | 1.505 | A10 | MAXW0.07420321/WT
Horizontal Wall | Maxi | MAXW.07420321/WT/DBE | 74 | 203 | 21 | 23 | 8605 | 8605 | 8605 | 0.20488 | 4303 | 0.10245 | 9466 | 0.22538 | 1 | A10 | MAXW0.07420321/WT/DBE
Build-In Floor | Mini Canal DBE | MDCL.01407026/ANA | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01407026/DBL | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01407026/DBN | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01407026/DBR | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01407026/DBV | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01407026/DDB | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01407026/DMN | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01407026/DMV | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01407026/DNA | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01407026/DNC | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01407026/DON | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/DON
Build-In Floor | Mini Canal DBE | MDCL.01407026/DOV | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01407026/PNC | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01407026/RBL | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01407026/RBN | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01407026/RBR | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01407026/RBV | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01407026/RDB | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01407026/RMN | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01407026/RMV | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01407026/RNA | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01407026/RON | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/RON
Build-In Floor | Mini Canal DBE | MDCL.01407026/ROV | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01407026/RSS | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01407026/SBL | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01407026/SBR | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01407026/SDB | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01407026/SNA | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01407026/SNC | 14 | 70 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 248 | 0.0059048 | 604 | 0.014381 | 1.13 | D06 | MDCL0.01407026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01407034/ANA | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01407034/DBL | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01407034/DBN | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01407034/DBR | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01407034/DBV | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01407034/DDB | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01407034/DMN | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01407034/DMV | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01407034/DNA | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01407034/DNC | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01407034/DON | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/DON
Build-In Floor | Mini Canal DBE | MDCL.01407034/DOV | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01407034/PNC | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01407034/RBL | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01407034/RBN | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01407034/RBR | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01407034/RBV | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01407034/RDB | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01407034/RMN | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01407034/RMV | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01407034/RNA | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01407034/RON | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/RON
Build-In Floor | Mini Canal DBE | MDCL.01407034/ROV | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01407034/RSS | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01407034/SBL | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01407034/SBR | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01407034/SDB | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01407034/SNA | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01407034/SNC | 14 | 70 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 322 | 0.0076667 | 785 | 0.01869 | 1.13 | D06 | MDCL0.01407034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01407042/ANA | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01407042/DBL | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01407042/DBN | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01407042/DBR | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01407042/DBV | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01407042/DDB | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01407042/DMN | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01407042/DMV | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01407042/DNA | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01407042/DNC | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01407042/DON | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/DON
Build-In Floor | Mini Canal DBE | MDCL.01407042/DOV | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01407042/PNC | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01407042/RBL | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01407042/RBN | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01407042/RBR | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01407042/RBV | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01407042/RDB | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01407042/RMN | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01407042/RMV | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01407042/RNA | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01407042/RON | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/RON
Build-In Floor | Mini Canal DBE | MDCL.01407042/ROV | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01407042/RSS | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01407042/SBL | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01407042/SBR | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01407042/SDB | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01407042/SNA | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01407042/SNC | 14 | 70 | 42 | 42 | 897 | 897 | 897 | 0.021357 | 410 | 0.0097619 | 999 | 0.023786 | 1.13 | D06 | MDCL0.01407042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01408026/ANA | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01408026/DBL | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01408026/DBN | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01408026/DBR | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01408026/DBV | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01408026/DDB | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01408026/DMN | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01408026/DMV | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01408026/DNA | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01408026/DNC | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01408026/DON | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/DON
Build-In Floor | Mini Canal DBE | MDCL.01408026/DOV | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01408026/PNC | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01408026/RBL | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01408026/RBN | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01408026/RBR | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01408026/RBV | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01408026/RDB | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01408026/RMN | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01408026/RMV | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01408026/RNA | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01408026/RON | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/RON
Build-In Floor | Mini Canal DBE | MDCL.01408026/ROV | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01408026/RSS | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01408026/SBL | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01408026/SBR | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01408026/SDB | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01408026/SNA | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01408026/SNC | 14 | 80 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 267 | 0.0063571 | 652 | 0.015524 | 1.13 | D06 | MDCL0.01408026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01408034/ANA | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01408034/DBL | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01408034/DBN | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01408034/DBR | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01408034/DBV | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01408034/DDB | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01408034/DMN | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01408034/DMV | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01408034/DNA | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01408034/DNC | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01408034/DON | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/DON
Build-In Floor | Mini Canal DBE | MDCL.01408034/DOV | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01408034/PNC | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01408034/RBL | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01408034/RBN | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01408034/RBR | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01408034/RBV | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01408034/RDB | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01408034/RMN | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01408034/RMV | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01408034/RNA | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01408034/RON | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/RON
Build-In Floor | Mini Canal DBE | MDCL.01408034/ROV | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01408034/RSS | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01408034/SBL | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01408034/SBR | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01408034/SDB | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01408034/SNA | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01408034/SNC | 14 | 80 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 349 | 0.0083095 | 851 | 0.020262 | 1.13 | D06 | MDCL0.01408034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01408042/ANA | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01408042/DBL | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01408042/DBN | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01408042/DBR | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01408042/DBV | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01408042/DDB | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01408042/DMN | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01408042/DMV | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01408042/DNA | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01408042/DNC | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01408042/DON | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/DON
Build-In Floor | Mini Canal DBE | MDCL.01408042/DOV | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01408042/PNC | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01408042/RBL | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01408042/RBN | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01408042/RBR | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01408042/RBV | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01408042/RDB | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01408042/RMN | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01408042/RMV | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01408042/RNA | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01408042/RON | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/RON
Build-In Floor | Mini Canal DBE | MDCL.01408042/ROV | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01408042/RSS | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01408042/SBL | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01408042/SBR | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01408042/SDB | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01408042/SNA | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01408042/SNC | 14 | 80 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 446 | 0.010619 | 1087 | 0.025881 | 1.13 | D06 | MDCL0.01408042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01409026/ANA | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01409026/DBL | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01409026/DBN | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01409026/DBR | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01409026/DBV | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01409026/DDB | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01409026/DMN | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01409026/DMV | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01409026/DNA | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01409026/DNC | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01409026/DON | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/DON
Build-In Floor | Mini Canal DBE | MDCL.01409026/DOV | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01409026/PNC | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01409026/RBL | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01409026/RBN | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01409026/RBR | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01409026/RBV | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01409026/RDB | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01409026/RMN | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01409026/RMV | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01409026/RNA | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01409026/RON | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/RON
Build-In Floor | Mini Canal DBE | MDCL.01409026/ROV | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01409026/RSS | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01409026/SBL | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01409026/SBR | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01409026/SDB | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01409026/SNA | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01409026/SNC | 14 | 90 | 26 | 26 | 628 | 628 | 628 | 0.014952 | 287 | 0.0068333 | 700 | 0.016667 | 1.13 | D06 | MDCL0.01409026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01409034/ANA | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01409034/DBL | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01409034/DBN | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01409034/DBR | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01409034/DBV | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01409034/DDB | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01409034/DMN | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01409034/DMV | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01409034/DNA | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01409034/DNC | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01409034/DON | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/DON
Build-In Floor | Mini Canal DBE | MDCL.01409034/DOV | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01409034/PNC | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01409034/RBL | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01409034/RBN | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01409034/RBR | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01409034/RBV | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01409034/RDB | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01409034/RMN | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01409034/RMV | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01409034/RNA | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01409034/RON | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/RON
Build-In Floor | Mini Canal DBE | MDCL.01409034/ROV | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01409034/RSS | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01409034/SBL | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01409034/SBR | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01409034/SDB | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01409034/SNA | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01409034/SNC | 14 | 90 | 34 | 34 | 823 | 823 | 823 | 0.019595 | 376 | 0.0089524 | 917 | 0.021833 | 1.13 | D06 | MDCL0.01409034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01409042/ANA | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01409042/DBL | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01409042/DBN | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01409042/DBR | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01409042/DBV | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01409042/DDB | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01409042/DMN | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01409042/DMV | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01409042/DNA | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01409042/DNC | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01409042/DON | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/DON
Build-In Floor | Mini Canal DBE | MDCL.01409042/DOV | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01409042/PNC | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01409042/RBL | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01409042/RBN | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01409042/RBR | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01409042/RBV | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01409042/RDB | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01409042/RMN | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01409042/RMV | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01409042/RNA | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01409042/RON | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/RON
Build-In Floor | Mini Canal DBE | MDCL.01409042/ROV | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01409042/RSS | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01409042/SBL | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01409042/SBR | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01409042/SDB | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01409042/SNA | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01409042/SNC | 14 | 90 | 42 | 42 | 1055 | 1055 | 1055 | 0.025119 | 482 | 0.011476 | 1175 | 0.027976 | 1.13 | D06 | MDCL0.01409042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01410026/ANA | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01410026/DBL | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01410026/DBN | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01410026/DBR | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01410026/DBV | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01410026/DDB | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01410026/DMN | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01410026/DMV | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01410026/DNA | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01410026/DNC | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01410026/DON | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/DON
Build-In Floor | Mini Canal DBE | MDCL.01410026/DOV | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01410026/PNC | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01410026/RBL | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01410026/RBN | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01410026/RBR | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01410026/RBV | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01410026/RDB | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01410026/RMN | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01410026/RMV | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01410026/RNA | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01410026/RON | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/RON
Build-In Floor | Mini Canal DBE | MDCL.01410026/ROV | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01410026/RSS | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01410026/SBL | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01410026/SBR | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01410026/SDB | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01410026/SNA | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01410026/SNC | 14 | 100 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 476 | 0.011333 | 1160 | 0.027619 | 1.13 | D06 | MDCL0.01410026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01410034/ANA | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01410034/DBL | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01410034/DBN | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01410034/DBR | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01410034/DBV | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01410034/DDB | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01410034/DMN | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01410034/DMV | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01410034/DNA | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01410034/DNC | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01410034/DON | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/DON
Build-In Floor | Mini Canal DBE | MDCL.01410034/DOV | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01410034/PNC | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01410034/RBL | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01410034/RBN | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01410034/RBR | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01410034/RBV | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01410034/RDB | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01410034/RMN | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01410034/RMV | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01410034/RNA | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01410034/RON | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/RON
Build-In Floor | Mini Canal DBE | MDCL.01410034/ROV | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01410034/RSS | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01410034/SBL | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01410034/SBR | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01410034/SDB | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01410034/SNA | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01410034/SNC | 14 | 100 | 34 | 34 | 1351 | 1351 | 1351 | 0.032167 | 617 | 0.01469 | 1505 | 0.035833 | 1.13 | D06 | MDCL0.01410034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01410042/ANA | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01410042/DBL | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01410042/DBN | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01410042/DBR | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01410042/DBV | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01410042/DDB | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01410042/DMN | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01410042/DMV | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01410042/DNA | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01410042/DNC | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01410042/DON | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/DON
Build-In Floor | Mini Canal DBE | MDCL.01410042/DOV | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01410042/PNC | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01410042/RBL | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01410042/RBN | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01410042/RBR | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01410042/RBV | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01410042/RDB | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01410042/RMN | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01410042/RMV | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01410042/RNA | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01410042/RON | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/RON
Build-In Floor | Mini Canal DBE | MDCL.01410042/ROV | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01410042/RSS | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01410042/SBL | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01410042/SBR | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01410042/SDB | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01410042/SNA | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01410042/SNC | 14 | 100 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 784 | 0.018667 | 1911 | 0.0455 | 1.13 | D06 | MDCL0.01410042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01411026/ANA | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01411026/DBL | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01411026/DBN | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01411026/DBR | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01411026/DBV | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01411026/DDB | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01411026/DMN | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01411026/DMV | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01411026/DNA | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01411026/DNC | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01411026/DON | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/DON
Build-In Floor | Mini Canal DBE | MDCL.01411026/DOV | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01411026/PNC | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01411026/RBL | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01411026/RBN | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01411026/RBR | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01411026/RBV | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01411026/RDB | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01411026/RMN | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01411026/RMV | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01411026/RNA | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01411026/RON | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/RON
Build-In Floor | Mini Canal DBE | MDCL.01411026/ROV | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01411026/RSS | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01411026/SBL | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01411026/SBR | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01411026/SDB | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01411026/SNA | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01411026/SNC | 14 | 110 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 496 | 0.01181 | 1209 | 0.028786 | 1.13 | D06 | MDCL0.01411026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01411034/ANA | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01411034/DBL | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01411034/DBN | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01411034/DBR | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01411034/DBV | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01411034/DDB | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01411034/DMN | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01411034/DMV | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01411034/DNA | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01411034/DNC | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01411034/DON | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/DON
Build-In Floor | Mini Canal DBE | MDCL.01411034/DOV | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01411034/PNC | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01411034/RBL | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01411034/RBN | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01411034/RBR | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01411034/RBV | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01411034/RDB | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01411034/RMN | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01411034/RMV | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01411034/RNA | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01411034/RON | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/RON
Build-In Floor | Mini Canal DBE | MDCL.01411034/ROV | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01411034/RSS | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01411034/SBL | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01411034/SBR | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01411034/SDB | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01411034/SNA | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01411034/SNC | 14 | 110 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 644 | 0.015333 | 1571 | 0.037405 | 1.13 | D06 | MDCL0.01411034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01411042/ANA | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01411042/DBL | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01411042/DBN | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01411042/DBR | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01411042/DBV | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01411042/DDB | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01411042/DMN | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01411042/DMV | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01411042/DNA | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01411042/DNC | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01411042/DON | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/DON
Build-In Floor | Mini Canal DBE | MDCL.01411042/DOV | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01411042/PNC | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01411042/RBL | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01411042/RBN | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01411042/RBR | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01411042/RBV | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01411042/RDB | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01411042/RMN | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01411042/RMV | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01411042/RNA | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01411042/RON | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/RON
Build-In Floor | Mini Canal DBE | MDCL.01411042/ROV | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01411042/RSS | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01411042/SBL | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01411042/SBR | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01411042/SDB | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01411042/SNA | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01411042/SNC | 14 | 110 | 42 | 42 | 1793 | 1793 | 1793 | 0.04269 | 819 | 0.0195 | 1997 | 0.047548 | 1.13 | D06 | MDCL0.01411042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01412026/ANA | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01412026/DBL | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01412026/DBN | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01412026/DBR | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01412026/DBV | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01412026/DDB | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01412026/DMN | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01412026/DMV | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01412026/DNA | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01412026/DNC | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01412026/DON | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/DON
Build-In Floor | Mini Canal DBE | MDCL.01412026/DOV | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01412026/PNC | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01412026/RBL | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01412026/RBN | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01412026/RBR | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01412026/RBV | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01412026/RDB | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01412026/RMN | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01412026/RMV | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01412026/RNA | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01412026/RON | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/RON
Build-In Floor | Mini Canal DBE | MDCL.01412026/ROV | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01412026/RSS | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01412026/SBL | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01412026/SBR | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01412026/SDB | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01412026/SNA | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01412026/SNC | 14 | 120 | 26 | 26 | 1128 | 1128 | 1128 | 0.026857 | 515 | 0.012262 | 1257 | 0.029929 | 1.13 | D06 | MDCL0.01412026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01412034/ANA | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01412034/DBL | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01412034/DBN | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01412034/DBR | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01412034/DBV | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01412034/DDB | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01412034/DMN | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01412034/DMV | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01412034/DNA | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01412034/DNC | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01412034/DON | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/DON
Build-In Floor | Mini Canal DBE | MDCL.01412034/DOV | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01412034/PNC | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01412034/RBL | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01412034/RBN | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01412034/RBR | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01412034/RBV | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01412034/RDB | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01412034/RMN | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01412034/RMV | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01412034/RNA | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01412034/RON | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/RON
Build-In Floor | Mini Canal DBE | MDCL.01412034/ROV | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01412034/RSS | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01412034/SBL | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01412034/SBR | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01412034/SDB | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01412034/SNA | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01412034/SNC | 14 | 120 | 34 | 34 | 1469 | 1469 | 1469 | 0.034976 | 671 | 0.015976 | 1636 | 0.038952 | 1.13 | D06 | MDCL0.01412034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01412042/ANA | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01412042/DBL | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01412042/DBN | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01412042/DBR | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01412042/DBV | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01412042/DDB | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01412042/DMN | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01412042/DMV | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01412042/DNA | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01412042/DNC | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01412042/DON | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/DON
Build-In Floor | Mini Canal DBE | MDCL.01412042/DOV | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01412042/PNC | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01412042/RBL | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01412042/RBN | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01412042/RBR | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01412042/RBV | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01412042/RDB | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01412042/RMN | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01412042/RMV | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01412042/RNA | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01412042/RON | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/RON
Build-In Floor | Mini Canal DBE | MDCL.01412042/ROV | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01412042/RSS | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01412042/SBL | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01412042/SBR | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01412042/SDB | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01412042/SNA | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01412042/SNC | 14 | 120 | 42 | 42 | 1873 | 1873 | 1873 | 0.044595 | 856 | 0.020381 | 2087 | 0.04969 | 1.13 | D06 | MDCL0.01412042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01413026/ANA | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01413026/DBL | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01413026/DBN | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01413026/DBR | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01413026/DBV | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01413026/DDB | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01413026/DMN | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01413026/DMV | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01413026/DNA | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01413026/DNC | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01413026/DON | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/DON
Build-In Floor | Mini Canal DBE | MDCL.01413026/DOV | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01413026/PNC | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01413026/RBL | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01413026/RBN | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01413026/RBR | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01413026/RBV | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01413026/RDB | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01413026/RMN | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01413026/RMV | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01413026/RNA | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01413026/RON | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/RON
Build-In Floor | Mini Canal DBE | MDCL.01413026/ROV | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01413026/RSS | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01413026/SBL | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01413026/SBR | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01413026/SDB | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01413026/SNA | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01413026/SNC | 14 | 130 | 26 | 26 | 1171 | 1171 | 1171 | 0.027881 | 535 | 0.012738 | 1304 | 0.031048 | 1.13 | D06 | MDCL0.01413026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01413034/ANA | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01413034/DBL | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01413034/DBN | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01413034/DBR | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01413034/DBV | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01413034/DDB | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01413034/DMN | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01413034/DMV | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01413034/DNA | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01413034/DNC | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01413034/DON | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/DON
Build-In Floor | Mini Canal DBE | MDCL.01413034/DOV | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01413034/PNC | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01413034/RBL | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01413034/RBN | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01413034/RBR | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01413034/RBV | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01413034/RDB | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01413034/RMN | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01413034/RMV | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01413034/RNA | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01413034/RON | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/RON
Build-In Floor | Mini Canal DBE | MDCL.01413034/ROV | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01413034/RSS | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01413034/SBL | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01413034/SBR | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01413034/SDB | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01413034/SNA | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01413034/SNC | 14 | 130 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 698 | 0.016619 | 1701 | 0.0405 | 1.13 | D06 | MDCL0.01413034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01413042/ANA | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01413042/DBL | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01413042/DBN | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01413042/DBR | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01413042/DBV | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01413042/DDB | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01413042/DMN | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01413042/DMV | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01413042/DNA | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01413042/DNC | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01413042/DON | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/DON
Build-In Floor | Mini Canal DBE | MDCL.01413042/DOV | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01413042/PNC | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01413042/RBL | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01413042/RBN | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01413042/RBR | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01413042/RBV | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01413042/RDB | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01413042/RMN | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01413042/RMV | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01413042/RNA | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01413042/RON | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/RON
Build-In Floor | Mini Canal DBE | MDCL.01413042/ROV | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01413042/RSS | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01413042/SBL | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01413042/SBR | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01413042/SDB | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01413042/SNA | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01413042/SNC | 14 | 130 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 892 | 0.021238 | 2175 | 0.051786 | 1.13 | D06 | MDCL0.01413042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01415026/ANA | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01415026/DBL | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01415026/DBN | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01415026/DBR | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01415026/DBV | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01415026/DDB | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01415026/DMN | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01415026/DMV | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01415026/DNA | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01415026/DNC | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01415026/DON | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/DON
Build-In Floor | Mini Canal DBE | MDCL.01415026/DOV | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01415026/PNC | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01415026/RBL | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01415026/RBN | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01415026/RBR | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01415026/RBV | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01415026/RDB | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01415026/RMN | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01415026/RMV | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01415026/RNA | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01415026/RON | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/RON
Build-In Floor | Mini Canal DBE | MDCL.01415026/ROV | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01415026/RSS | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01415026/SBL | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01415026/SBR | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01415026/SDB | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01415026/SNA | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01415026/SNC | 14 | 150 | 26 | 26 | 1626 | 1626 | 1626 | 0.038714 | 743 | 0.01769 | 1811 | 0.043119 | 1.13 | D06 | MDCL0.01415026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01415034/ANA | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01415034/DBL | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01415034/DBN | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01415034/DBR | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01415034/DBV | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01415034/DDB | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01415034/DMN | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01415034/DMV | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01415034/DNA | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01415034/DNC | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01415034/DON | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/DON
Build-In Floor | Mini Canal DBE | MDCL.01415034/DOV | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01415034/PNC | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01415034/RBL | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01415034/RBN | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01415034/RBR | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01415034/RBV | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01415034/RDB | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01415034/RMN | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01415034/RMV | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01415034/RNA | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01415034/RON | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/RON
Build-In Floor | Mini Canal DBE | MDCL.01415034/ROV | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01415034/RSS | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01415034/SBL | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01415034/SBR | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01415034/SDB | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01415034/SNA | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01415034/SNC | 14 | 150 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 967 | 0.023024 | 2356 | 0.056095 | 1.13 | D06 | MDCL0.01415034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01415042/ANA | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01415042/DBL | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01415042/DBN | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01415042/DBR | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01415042/DBV | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01415042/DDB | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01415042/DMN | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01415042/DMV | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01415042/DNA | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01415042/DNC | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01415042/DON | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/DON
Build-In Floor | Mini Canal DBE | MDCL.01415042/DOV | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01415042/PNC | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01415042/RBL | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01415042/RBN | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01415042/RBR | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01415042/RBV | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01415042/RDB | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01415042/RMN | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01415042/RMV | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01415042/RNA | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01415042/RON | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/RON
Build-In Floor | Mini Canal DBE | MDCL.01415042/ROV | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01415042/RSS | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01415042/SBL | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01415042/SBR | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01415042/SDB | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01415042/SNA | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01415042/SNC | 14 | 150 | 42 | 42 | 2690 | 2690 | 2690 | 0.064048 | 1229 | 0.029262 | 2997 | 0.071357 | 1.13 | D06 | MDCL0.01415042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01417026/ANA | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01417026/DBL | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01417026/DBN | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01417026/DBR | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01417026/DBV | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01417026/DDB | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01417026/DMN | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01417026/DMV | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01417026/DNA | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01417026/DNC | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01417026/DON | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/DON
Build-In Floor | Mini Canal DBE | MDCL.01417026/DOV | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01417026/PNC | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01417026/RBL | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01417026/RBN | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01417026/RBR | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01417026/RBV | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01417026/RDB | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01417026/RMN | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01417026/RMV | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01417026/RNA | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01417026/RON | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/RON
Build-In Floor | Mini Canal DBE | MDCL.01417026/ROV | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01417026/RSS | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01417026/SBL | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01417026/SBR | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01417026/SDB | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01417026/SNA | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01417026/SNC | 14 | 170 | 26 | 26 | 2083 | 2083 | 2083 | 0.049595 | 952 | 0.022667 | 2320 | 0.055238 | 1.13 | D06 | MDCL0.01417026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01417034/ANA | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01417034/DBL | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01417034/DBN | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01417034/DBR | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01417034/DBV | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01417034/DDB | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01417034/DMN | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01417034/DMV | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01417034/DNA | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01417034/DNC | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01417034/DON | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/DON
Build-In Floor | Mini Canal DBE | MDCL.01417034/DOV | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01417034/PNC | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01417034/RBL | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01417034/RBN | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01417034/RBR | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01417034/RBV | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01417034/RDB | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01417034/RMN | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01417034/RMV | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01417034/RNA | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01417034/RON | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/RON
Build-In Floor | Mini Canal DBE | MDCL.01417034/ROV | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01417034/RSS | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01417034/SBL | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01417034/SBR | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01417034/SDB | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01417034/SNA | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01417034/SNC | 14 | 170 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1235 | 0.029405 | 3010 | 0.071667 | 1.13 | D06 | MDCL0.01417034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01417042/ANA | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01417042/DBL | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01417042/DBN | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01417042/DBR | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01417042/DBV | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01417042/DDB | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01417042/DMN | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01417042/DMV | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01417042/DNA | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01417042/DNC | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01417042/DON | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/DON
Build-In Floor | Mini Canal DBE | MDCL.01417042/DOV | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01417042/PNC | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01417042/RBL | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01417042/RBN | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01417042/RBR | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01417042/RBV | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01417042/RDB | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01417042/RMN | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01417042/RMV | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01417042/RNA | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01417042/RON | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/RON
Build-In Floor | Mini Canal DBE | MDCL.01417042/ROV | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01417042/RSS | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01417042/SBL | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01417042/SBR | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01417042/SDB | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01417042/SNA | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01417042/SNC | 14 | 170 | 42 | 42 | 3428 | 3428 | 3428 | 0.081619 | 1567 | 0.03731 | 3819 | 0.090929 | 1.13 | D06 | MDCL0.01417042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01419026/ANA | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01419026/DBL | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01419026/DBN | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01419026/DBR | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01419026/DBV | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01419026/DDB | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01419026/DMN | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01419026/DMV | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01419026/DNA | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01419026/DNC | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01419026/DON | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/DON
Build-In Floor | Mini Canal DBE | MDCL.01419026/DOV | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01419026/PNC | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01419026/RBL | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01419026/RBN | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01419026/RBR | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01419026/RBV | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01419026/RDB | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01419026/RMN | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01419026/RMV | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01419026/RNA | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01419026/RON | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/RON
Build-In Floor | Mini Canal DBE | MDCL.01419026/ROV | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01419026/RSS | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01419026/SBL | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01419026/SBR | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01419026/SDB | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01419026/SNA | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01419026/SNC | 14 | 190 | 26 | 26 | 2169 | 2169 | 2169 | 0.051643 | 991 | 0.023595 | 2416 | 0.057524 | 1.13 | D06 | MDCL0.01419026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01419034/ANA | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01419034/DBL | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01419034/DBN | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01419034/DBR | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01419034/DBV | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01419034/DDB | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01419034/DMN | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01419034/DMV | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01419034/DNA | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01419034/DNC | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01419034/DON | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/DON
Build-In Floor | Mini Canal DBE | MDCL.01419034/DOV | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01419034/PNC | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01419034/RBL | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01419034/RBN | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01419034/RBR | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01419034/RBV | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01419034/RDB | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01419034/RMN | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01419034/RMV | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01419034/RNA | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01419034/RON | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/RON
Build-In Floor | Mini Canal DBE | MDCL.01419034/ROV | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01419034/RSS | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01419034/SBL | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01419034/SBR | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01419034/SDB | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01419034/SNA | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01419034/SNC | 14 | 190 | 34 | 34 | 2820 | 2820 | 2820 | 0.067143 | 1289 | 0.03069 | 3141 | 0.074786 | 1.13 | D06 | MDCL0.01419034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01419042/ANA | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01419042/DBL | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01419042/DBN | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01419042/DBR | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01419042/DBV | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01419042/DDB | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01419042/DMN | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01419042/DMV | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01419042/DNA | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01419042/DNC | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01419042/DON | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/DON
Build-In Floor | Mini Canal DBE | MDCL.01419042/DOV | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01419042/PNC | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01419042/RBL | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01419042/RBN | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01419042/RBR | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01419042/RBV | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01419042/RDB | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01419042/RMN | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01419042/RMV | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01419042/RNA | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01419042/RON | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/RON
Build-In Floor | Mini Canal DBE | MDCL.01419042/ROV | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01419042/RSS | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01419042/SBL | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01419042/SBR | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01419042/SDB | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01419042/SNA | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01419042/SNC | 14 | 190 | 42 | 42 | 3587 | 3587 | 3587 | 0.085405 | 1639 | 0.039024 | 3996 | 0.095143 | 1.13 | D06 | MDCL0.01419042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01421026/ANA | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01421026/DBL | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01421026/DBN | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01421026/DBR | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01421026/DBV | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01421026/DDB | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01421026/DMN | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01421026/DMV | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01421026/DNA | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01421026/DNC | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01421026/DON | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/DON
Build-In Floor | Mini Canal DBE | MDCL.01421026/DOV | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01421026/PNC | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01421026/RBL | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01421026/RBN | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01421026/RBR | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01421026/RBV | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01421026/RDB | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01421026/RMN | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01421026/RMV | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01421026/RNA | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01421026/RON | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/RON
Build-In Floor | Mini Canal DBE | MDCL.01421026/ROV | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01421026/RSS | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01421026/SBL | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01421026/SBR | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01421026/SDB | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01421026/SNA | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01421026/SNC | 14 | 210 | 26 | 26 | 2625 | 2625 | 2625 | 0.0625 | 1200 | 0.028571 | 2924 | 0.069619 | 1.13 | D06 | MDCL0.01421026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01421034/ANA | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01421034/DBL | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01421034/DBN | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01421034/DBR | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01421034/DBV | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01421034/DDB | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01421034/DMN | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01421034/DMV | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01421034/DNA | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01421034/DNC | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01421034/DON | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/DON
Build-In Floor | Mini Canal DBE | MDCL.01421034/DOV | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01421034/PNC | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01421034/RBL | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01421034/RBN | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01421034/RBR | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01421034/RBV | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01421034/RDB | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01421034/RMN | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01421034/RMV | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01421034/RNA | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01421034/RON | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/RON
Build-In Floor | Mini Canal DBE | MDCL.01421034/ROV | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01421034/RSS | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01421034/SBL | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01421034/SBR | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01421034/SDB | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01421034/SNA | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01421034/SNC | 14 | 210 | 34 | 34 | 3407 | 3407 | 3407 | 0.081119 | 1557 | 0.037071 | 3795 | 0.090357 | 1.13 | D06 | MDCL0.01421034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01421042/ANA | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01421042/DBL | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01421042/DBN | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01421042/DBR | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01421042/DBV | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01421042/DDB | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01421042/DMN | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01421042/DMV | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01421042/DNA | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01421042/DNC | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01421042/DON | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/DON
Build-In Floor | Mini Canal DBE | MDCL.01421042/DOV | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01421042/PNC | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01421042/RBL | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01421042/RBN | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01421042/RBR | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01421042/RBV | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01421042/RDB | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01421042/RMN | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01421042/RMV | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01421042/RNA | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01421042/RON | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/RON
Build-In Floor | Mini Canal DBE | MDCL.01421042/ROV | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01421042/RSS | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01421042/SBL | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01421042/SBR | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01421042/SDB | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01421042/SNA | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01421042/SNC | 14 | 210 | 42 | 42 | 4325 | 4325 | 4325 | 0.10298 | 1977 | 0.047071 | 4818 | 0.11471 | 1.13 | D06 | MDCL0.01421042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01423026/ANA | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01423026/DBL | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01423026/DBN | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01423026/DBR | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01423026/DBV | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01423026/DDB | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01423026/DMN | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01423026/DMV | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01423026/DNA | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01423026/DNC | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01423026/DON | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/DON
Build-In Floor | Mini Canal DBE | MDCL.01423026/DOV | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01423026/PNC | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01423026/RBL | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01423026/RBN | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01423026/RBR | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01423026/RBV | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01423026/RDB | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01423026/RMN | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01423026/RMV | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01423026/RNA | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01423026/RON | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/RON
Build-In Floor | Mini Canal DBE | MDCL.01423026/ROV | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01423026/RSS | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01423026/SBL | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01423026/SBR | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01423026/SDB | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01423026/SNA | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01423026/SNC | 14 | 230 | 26 | 26 | 2711 | 2711 | 2711 | 0.064548 | 1239 | 0.0295 | 3020 | 0.071905 | 1.13 | D06 | MDCL0.01423026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01423034/ANA | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01423034/DBL | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01423034/DBN | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01423034/DBR | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01423034/DBV | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01423034/DDB | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01423034/DMN | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01423034/DMV | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01423034/DNA | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01423034/DNC | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01423034/DON | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/DON
Build-In Floor | Mini Canal DBE | MDCL.01423034/DOV | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01423034/PNC | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01423034/RBL | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01423034/RBN | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01423034/RBR | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01423034/RBV | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01423034/RDB | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01423034/RMN | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01423034/RMV | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01423034/RNA | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01423034/RON | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/RON
Build-In Floor | Mini Canal DBE | MDCL.01423034/ROV | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01423034/RSS | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01423034/SBL | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01423034/SBR | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01423034/SDB | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01423034/SNA | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01423034/SNC | 14 | 230 | 34 | 34 | 3525 | 3525 | 3525 | 0.083929 | 1611 | 0.038357 | 3927 | 0.0935 | 1.13 | D06 | MDCL0.01423034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01423042/ANA | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01423042/DBL | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01423042/DBN | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01423042/DBR | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01423042/DBV | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01423042/DDB | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01423042/DMN | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01423042/DMV | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01423042/DNA | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01423042/DNC | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01423042/DON | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/DON
Build-In Floor | Mini Canal DBE | MDCL.01423042/DOV | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01423042/PNC | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01423042/RBL | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01423042/RBN | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01423042/RBR | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01423042/RBV | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01423042/RDB | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01423042/RMN | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01423042/RMV | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01423042/RNA | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01423042/RON | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/RON
Build-In Floor | Mini Canal DBE | MDCL.01423042/ROV | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01423042/RSS | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01423042/SBL | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01423042/SBR | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01423042/SDB | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01423042/SNA | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01423042/SNC | 14 | 230 | 42 | 42 | 4483 | 4483 | 4483 | 0.10674 | 2049 | 0.048786 | 4994 | 0.1189 | 1.13 | D06 | MDCL0.01423042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01425026/ANA | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01425026/DBL | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01425026/DBN | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01425026/DBR | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01425026/DBV | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01425026/DDB | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01425026/DMN | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01425026/DMV | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01425026/DNA | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01425026/DNC | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01425026/DON | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/DON
Build-In Floor | Mini Canal DBE | MDCL.01425026/DOV | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01425026/PNC | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01425026/RBL | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01425026/RBN | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01425026/RBR | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01425026/RBV | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01425026/RDB | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01425026/RMN | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01425026/RMV | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01425026/RNA | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01425026/RON | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/RON
Build-In Floor | Mini Canal DBE | MDCL.01425026/ROV | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01425026/RSS | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01425026/SBL | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01425026/SBR | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01425026/SDB | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01425026/SNA | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01425026/SNC | 14 | 250 | 26 | 26 | 3167 | 3167 | 3167 | 0.075405 | 1447 | 0.034452 | 3528 | 0.084 | 1.13 | D06 | MDCL0.01425026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01425034/ANA | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01425034/DBL | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01425034/DBN | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01425034/DBR | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01425034/DBV | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01425034/DDB | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01425034/DMN | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01425034/DMV | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01425034/DNA | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01425034/DNC | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01425034/DON | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/DON
Build-In Floor | Mini Canal DBE | MDCL.01425034/DOV | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01425034/PNC | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01425034/RBL | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01425034/RBN | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01425034/RBR | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01425034/RBV | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01425034/RDB | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01425034/RMN | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01425034/RMV | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01425034/RNA | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01425034/RON | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/RON
Build-In Floor | Mini Canal DBE | MDCL.01425034/ROV | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01425034/RSS | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01425034/SBL | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01425034/SBR | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01425034/SDB | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01425034/SNA | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01425034/SNC | 14 | 250 | 34 | 34 | 4112 | 4112 | 4112 | 0.097905 | 1879 | 0.044738 | 4581 | 0.10907 | 1.13 | D06 | MDCL0.01425034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01425042/ANA | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01425042/DBL | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01425042/DBN | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01425042/DBR | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01425042/DBV | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01425042/DDB | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01425042/DMN | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01425042/DMV | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01425042/DNA | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01425042/DNC | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01425042/DON | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/DON
Build-In Floor | Mini Canal DBE | MDCL.01425042/DOV | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01425042/PNC | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01425042/RBL | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01425042/RBN | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01425042/RBR | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01425042/RBV | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01425042/RDB | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01425042/RMN | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01425042/RMV | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01425042/RNA | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01425042/RON | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/RON
Build-In Floor | Mini Canal DBE | MDCL.01425042/ROV | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01425042/RSS | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01425042/SBL | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01425042/SBR | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01425042/SDB | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01425042/SNA | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01425042/SNC | 14 | 250 | 42 | 42 | 5222 | 5222 | 5222 | 0.12433 | 2386 | 0.05681 | 5817 | 0.1385 | 1.13 | D06 | MDCL0.01425042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01427026/ANA | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01427026/DBL | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01427026/DBN | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01427026/DBR | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01427026/DBV | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01427026/DDB | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01427026/DMN | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01427026/DMV | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01427026/DNA | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01427026/DNC | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01427026/DON | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/DON
Build-In Floor | Mini Canal DBE | MDCL.01427026/DOV | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01427026/PNC | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01427026/RBL | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01427026/RBN | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01427026/RBR | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01427026/RBV | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01427026/RDB | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01427026/RMN | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01427026/RMV | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01427026/RNA | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01427026/RON | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/RON
Build-In Floor | Mini Canal DBE | MDCL.01427026/ROV | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01427026/RSS | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01427026/SBL | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01427026/SBR | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01427026/SDB | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01427026/SNA | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01427026/SNC | 14 | 270 | 26 | 26 | 3254 | 3254 | 3254 | 0.077476 | 1487 | 0.035405 | 3625 | 0.08631 | 1.13 | D06 | MDCL0.01427026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01427034/ANA | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01427034/DBL | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01427034/DBN | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01427034/DBR | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01427034/DBV | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01427034/DDB | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01427034/DMN | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01427034/DMV | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01427034/DNA | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01427034/DNC | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01427034/DON | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/DON
Build-In Floor | Mini Canal DBE | MDCL.01427034/DOV | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01427034/PNC | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01427034/RBL | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01427034/RBN | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01427034/RBR | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01427034/RBV | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01427034/RDB | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01427034/RMN | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01427034/RMV | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01427034/RNA | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01427034/RON | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/RON
Build-In Floor | Mini Canal DBE | MDCL.01427034/ROV | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01427034/RSS | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01427034/SBL | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01427034/SBR | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01427034/SDB | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01427034/SNA | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01427034/SNC | 14 | 270 | 34 | 34 | 4229 | 4229 | 4229 | 0.10069 | 1933 | 0.046024 | 4711 | 0.11217 | 1.13 | D06 | MDCL0.01427034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01427042/ANA | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01427042/DBL | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01427042/DBN | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01427042/DBR | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01427042/DBV | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01427042/DDB | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01427042/DMN | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01427042/DMV | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01427042/DNA | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01427042/DNC | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01427042/DON | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/DON
Build-In Floor | Mini Canal DBE | MDCL.01427042/DOV | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01427042/PNC | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01427042/RBL | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01427042/RBN | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01427042/RBR | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01427042/RBV | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01427042/RDB | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01427042/RMN | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01427042/RMV | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01427042/RNA | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01427042/RON | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/RON
Build-In Floor | Mini Canal DBE | MDCL.01427042/ROV | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01427042/RSS | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01427042/SBL | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01427042/SBR | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01427042/SDB | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01427042/SNA | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01427042/SNC | 14 | 270 | 42 | 42 | 5380 | 5380 | 5380 | 0.1281 | 2459 | 0.058548 | 5993 | 0.14269 | 1.13 | D06 | MDCL0.01427042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01429026/ANA | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01429026/DBL | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01429026/DBN | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01429026/DBR | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01429026/DBV | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01429026/DDB | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01429026/DMN | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01429026/DMV | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01429026/DNA | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01429026/DNC | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01429026/DON | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/DON
Build-In Floor | Mini Canal DBE | MDCL.01429026/DOV | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01429026/PNC | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01429026/RBL | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01429026/RBN | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01429026/RBR | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01429026/RBV | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01429026/RDB | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01429026/RMN | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01429026/RMV | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01429026/RNA | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01429026/RON | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/RON
Build-In Floor | Mini Canal DBE | MDCL.01429026/ROV | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01429026/RSS | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01429026/SBL | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01429026/SBR | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01429026/SDB | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01429026/SNA | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01429026/SNC | 14 | 290 | 26 | 26 | 3709 | 3709 | 3709 | 0.08831 | 1695 | 0.040357 | 4132 | 0.098381 | 1.13 | D06 | MDCL0.01429026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01429034/ANA | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01429034/DBL | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01429034/DBN | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01429034/DBR | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01429034/DBV | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01429034/DDB | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01429034/DMN | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01429034/DMV | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01429034/DNA | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01429034/DNC | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01429034/DON | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/DON
Build-In Floor | Mini Canal DBE | MDCL.01429034/DOV | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01429034/PNC | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01429034/RBL | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01429034/RBN | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01429034/RBR | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01429034/RBV | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01429034/RDB | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01429034/RMN | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01429034/RMV | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01429034/RNA | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01429034/RON | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/RON
Build-In Floor | Mini Canal DBE | MDCL.01429034/ROV | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01429034/RSS | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01429034/SBL | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01429034/SBR | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01429034/SDB | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01429034/SNA | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01429034/SNC | 14 | 290 | 34 | 34 | 4817 | 4817 | 4817 | 0.11469 | 2201 | 0.052405 | 5366 | 0.12776 | 1.13 | D06 | MDCL0.01429034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01429042/ANA | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01429042/DBL | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01429042/DBN | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01429042/DBR | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01429042/DBV | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01429042/DDB | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01429042/DMN | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01429042/DMV | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01429042/DNA | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01429042/DNC | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01429042/DON | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/DON
Build-In Floor | Mini Canal DBE | MDCL.01429042/DOV | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01429042/PNC | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01429042/RBL | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01429042/RBN | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01429042/RBR | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01429042/RBV | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01429042/RDB | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01429042/RMN | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01429042/RMV | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01429042/RNA | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01429042/RON | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/RON
Build-In Floor | Mini Canal DBE | MDCL.01429042/ROV | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01429042/RSS | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01429042/SBL | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01429042/SBR | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01429042/SDB | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01429042/SNA | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01429042/SNC | 14 | 290 | 42 | 42 | 6118 | 6118 | 6118 | 0.14567 | 2796 | 0.066571 | 6815 | 0.16226 | 1.13 | D06 | MDCL0.01429042/SNC
Build-In Floor | Mini Canal DBE | MDCL.01431026/ANA | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/ANA
Build-In Floor | Mini Canal DBE | MDCL.01431026/DBL | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/DBL
Build-In Floor | Mini Canal DBE | MDCL.01431026/DBN | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/DBN
Build-In Floor | Mini Canal DBE | MDCL.01431026/DBR | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/DBR
Build-In Floor | Mini Canal DBE | MDCL.01431026/DBV | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/DBV
Build-In Floor | Mini Canal DBE | MDCL.01431026/DDB | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/DDB
Build-In Floor | Mini Canal DBE | MDCL.01431026/DMN | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/DMN
Build-In Floor | Mini Canal DBE | MDCL.01431026/DMV | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/DMV
Build-In Floor | Mini Canal DBE | MDCL.01431026/DNA | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/DNA
Build-In Floor | Mini Canal DBE | MDCL.01431026/DNC | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/DNC
Build-In Floor | Mini Canal DBE | MDCL.01431026/DON | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/DON
Build-In Floor | Mini Canal DBE | MDCL.01431026/DOV | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/DOV
Build-In Floor | Mini Canal DBE | MDCL.01431026/PNC | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/PNC
Build-In Floor | Mini Canal DBE | MDCL.01431026/RBL | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/RBL
Build-In Floor | Mini Canal DBE | MDCL.01431026/RBN | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/RBN
Build-In Floor | Mini Canal DBE | MDCL.01431026/RBR | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/RBR
Build-In Floor | Mini Canal DBE | MDCL.01431026/RBV | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/RBV
Build-In Floor | Mini Canal DBE | MDCL.01431026/RDB | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/RDB
Build-In Floor | Mini Canal DBE | MDCL.01431026/RMN | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/RMN
Build-In Floor | Mini Canal DBE | MDCL.01431026/RMV | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/RMV
Build-In Floor | Mini Canal DBE | MDCL.01431026/RNA | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/RNA
Build-In Floor | Mini Canal DBE | MDCL.01431026/RON | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/RON
Build-In Floor | Mini Canal DBE | MDCL.01431026/ROV | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/ROV
Build-In Floor | Mini Canal DBE | MDCL.01431026/RSS | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/RSS
Build-In Floor | Mini Canal DBE | MDCL.01431026/SBL | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/SBL
Build-In Floor | Mini Canal DBE | MDCL.01431026/SBR | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/SBR
Build-In Floor | Mini Canal DBE | MDCL.01431026/SDB | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/SDB
Build-In Floor | Mini Canal DBE | MDCL.01431026/SNA | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/SNA
Build-In Floor | Mini Canal DBE | MDCL.01431026/SNC | 14 | 310 | 26 | 26 | 4166 | 4166 | 4166 | 0.09919 | 1904 | 0.045333 | 4641 | 0.1105 | 1.13 | D06 | MDCL0.01431026/SNC
Build-In Floor | Mini Canal DBE | MDCL.01431034/ANA | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/ANA
Build-In Floor | Mini Canal DBE | MDCL.01431034/DBL | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/DBL
Build-In Floor | Mini Canal DBE | MDCL.01431034/DBN | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/DBN
Build-In Floor | Mini Canal DBE | MDCL.01431034/DBR | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/DBR
Build-In Floor | Mini Canal DBE | MDCL.01431034/DBV | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/DBV
Build-In Floor | Mini Canal DBE | MDCL.01431034/DDB | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/DDB
Build-In Floor | Mini Canal DBE | MDCL.01431034/DMN | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/DMN
Build-In Floor | Mini Canal DBE | MDCL.01431034/DMV | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/DMV
Build-In Floor | Mini Canal DBE | MDCL.01431034/DNA | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/DNA
Build-In Floor | Mini Canal DBE | MDCL.01431034/DNC | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/DNC
Build-In Floor | Mini Canal DBE | MDCL.01431034/DON | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/DON
Build-In Floor | Mini Canal DBE | MDCL.01431034/DOV | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/DOV
Build-In Floor | Mini Canal DBE | MDCL.01431034/PNC | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/PNC
Build-In Floor | Mini Canal DBE | MDCL.01431034/RBL | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/RBL
Build-In Floor | Mini Canal DBE | MDCL.01431034/RBN | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/RBN
Build-In Floor | Mini Canal DBE | MDCL.01431034/RBR | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/RBR
Build-In Floor | Mini Canal DBE | MDCL.01431034/RBV | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/RBV
Build-In Floor | Mini Canal DBE | MDCL.01431034/RDB | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/RDB
Build-In Floor | Mini Canal DBE | MDCL.01431034/RMN | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/RMN
Build-In Floor | Mini Canal DBE | MDCL.01431034/RMV | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/RMV
Build-In Floor | Mini Canal DBE | MDCL.01431034/RNA | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/RNA
Build-In Floor | Mini Canal DBE | MDCL.01431034/RON | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/RON
Build-In Floor | Mini Canal DBE | MDCL.01431034/ROV | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/ROV
Build-In Floor | Mini Canal DBE | MDCL.01431034/RSS | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/RSS
Build-In Floor | Mini Canal DBE | MDCL.01431034/SBL | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/SBL
Build-In Floor | Mini Canal DBE | MDCL.01431034/SBR | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/SBR
Build-In Floor | Mini Canal DBE | MDCL.01431034/SDB | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/SDB
Build-In Floor | Mini Canal DBE | MDCL.01431034/SNA | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/SNA
Build-In Floor | Mini Canal DBE | MDCL.01431034/SNC | 14 | 310 | 34 | 34 | 5404 | 5404 | 5404 | 0.12867 | 2470 | 0.05881 | 6020 | 0.14333 | 1.13 | D06 | MDCL0.01431034/SNC
Build-In Floor | Mini Canal DBE | MDCL.01431042/ANA | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/ANA
Build-In Floor | Mini Canal DBE | MDCL.01431042/DBL | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/DBL
Build-In Floor | Mini Canal DBE | MDCL.01431042/DBN | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/DBN
Build-In Floor | Mini Canal DBE | MDCL.01431042/DBR | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/DBR
Build-In Floor | Mini Canal DBE | MDCL.01431042/DBV | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/DBV
Build-In Floor | Mini Canal DBE | MDCL.01431042/DDB | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/DDB
Build-In Floor | Mini Canal DBE | MDCL.01431042/DMN | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/DMN
Build-In Floor | Mini Canal DBE | MDCL.01431042/DMV | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/DMV
Build-In Floor | Mini Canal DBE | MDCL.01431042/DNA | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/DNA
Build-In Floor | Mini Canal DBE | MDCL.01431042/DNC | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/DNC
Build-In Floor | Mini Canal DBE | MDCL.01431042/DON | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/DON
Build-In Floor | Mini Canal DBE | MDCL.01431042/DOV | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/DOV
Build-In Floor | Mini Canal DBE | MDCL.01431042/PNC | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/PNC
Build-In Floor | Mini Canal DBE | MDCL.01431042/RBL | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/RBL
Build-In Floor | Mini Canal DBE | MDCL.01431042/RBN | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/RBN
Build-In Floor | Mini Canal DBE | MDCL.01431042/RBR | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/RBR
Build-In Floor | Mini Canal DBE | MDCL.01431042/RBV | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/RBV
Build-In Floor | Mini Canal DBE | MDCL.01431042/RDB | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/RDB
Build-In Floor | Mini Canal DBE | MDCL.01431042/RMN | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/RMN
Build-In Floor | Mini Canal DBE | MDCL.01431042/RMV | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/RMV
Build-In Floor | Mini Canal DBE | MDCL.01431042/RNA | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/RNA
Build-In Floor | Mini Canal DBE | MDCL.01431042/RON | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/RON
Build-In Floor | Mini Canal DBE | MDCL.01431042/ROV | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/ROV
Build-In Floor | Mini Canal DBE | MDCL.01431042/RSS | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/RSS
Build-In Floor | Mini Canal DBE | MDCL.01431042/SBL | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/SBL
Build-In Floor | Mini Canal DBE | MDCL.01431042/SBR | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/SBR
Build-In Floor | Mini Canal DBE | MDCL.01431042/SDB | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/SDB
Build-In Floor | Mini Canal DBE | MDCL.01431042/SNA | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/SNA
Build-In Floor | Mini Canal DBE | MDCL.01431042/SNC | 14 | 310 | 42 | 42 | 6857 | 6857 | 6857 | 0.16326 | 3134 | 0.074619 | 7639 | 0.18188 | 1.13 | D06 | MDCL0.01431042/SNC
Build-In Floor | Mini Canal | MICL.00907014/ANA | 9 | 70 | 14 | 14 | 57 | 57 | 57 | 0.0013571 | 22 | 0.00052381 | 65 | 0.0015476 | 1.362 | A04 | MICL0.00907014/ANA
Build-In Floor | Mini Canal | MICL.00907014/DBL | 9 | 70 | 14 | 14 | 74 | 74 | 74 | 0.0017619 | 29 | 0.00069048 | 84 | 0.002 | 1.362 | A04 | MICL0.00907014/DBL
Build-In Floor | Mini Canal | MICL.00907014/DBN | 9 | 70 | 14 | 14 | 71 | 71 | 71 | 0.0016905 | 28 | 0.00066667 | 81 | 0.0019286 | 1.362 | A04 | MICL0.00907014/DBN
Build-In Floor | Mini Canal | MICL.00907014/DBR | 9 | 70 | 14 | 14 | 74 | 74 | 74 | 0.0017619 | 29 | 0.00069048 | 84 | 0.002 | 1.362 | A04 | MICL0.00907014/DBR
Build-In Floor | Mini Canal | MICL.00907014/DBV | 9 | 70 | 14 | 14 | 71 | 71 | 71 | 0.0016905 | 28 | 0.00066667 | 81 | 0.0019286 | 1.362 | A04 | MICL0.00907014/DBV
Build-In Floor | Mini Canal | MICL.00907014/DDB | 9 | 70 | 14 | 14 | 74 | 74 | 74 | 0.0017619 | 29 | 0.00069048 | 84 | 0.002 | 1.362 | A04 | MICL0.00907014/DDB
Build-In Floor | Mini Canal | MICL.00907014/DMN | 9 | 70 | 14 | 14 | 71 | 71 | 71 | 0.0016905 | 28 | 0.00066667 | 81 | 0.0019286 | 1.362 | A04 | MICL0.00907014/DMN
Build-In Floor | Mini Canal | MICL.00907014/DMV | 9 | 70 | 14 | 14 | 71 | 71 | 71 | 0.0016905 | 28 | 0.00066667 | 81 | 0.0019286 | 1.362 | A04 | MICL0.00907014/DMV
Build-In Floor | Mini Canal | MICL.00907014/DNA | 9 | 70 | 14 | 14 | 74 | 74 | 74 | 0.0017619 | 29 | 0.00069048 | 84 | 0.002 | 1.362 | A04 | MICL0.00907014/DNA
Build-In Floor | Mini Canal | MICL.00907014/DNC | 9 | 70 | 14 | 14 | 74 | 74 | 74 | 0.0017619 | 29 | 0.00069048 | 84 | 0.002 | 1.362 | A04 | MICL0.00907014/DNC
Build-In Floor | Mini Canal | MICL.00907014/DON | 9 | 70 | 14 | 14 | 71 | 71 | 71 | 0.0016905 | 28 | 0.00066667 | 81 | 0.0019286 | 1.362 | A04 | MICL0.00907014/DON
Build-In Floor | Mini Canal | MICL.00907014/DOV | 9 | 70 | 14 | 14 | 71 | 71 | 71 | 0.0016905 | 28 | 0.00066667 | 81 | 0.0019286 | 1.362 | A04 | MICL0.00907014/DOV
Build-In Floor | Mini Canal | MICL.00907014/RBL | 9 | 70 | 14 | 14 | 76 | 76 | 76 | 0.0018095 | 30 | 0.00071429 | 87 | 0.0020714 | 1.362 | A04 | MICL0.00907014/RBL
Build-In Floor | Mini Canal | MICL.00907014/RBN | 9 | 70 | 14 | 14 | 74 | 74 | 74 | 0.0017619 | 29 | 0.00069048 | 84 | 0.002 | 1.362 | A04 | MICL0.00907014/RBN
Build-In Floor | Mini Canal | MICL.00907014/RBR | 9 | 70 | 14 | 14 | 76 | 76 | 76 | 0.0018095 | 30 | 0.00071429 | 87 | 0.0020714 | 1.362 | A04 | MICL0.00907014/RBR
Build-In Floor | Mini Canal | MICL.00907014/RBV | 9 | 70 | 14 | 14 | 74 | 74 | 74 | 0.0017619 | 29 | 0.00069048 | 84 | 0.002 | 1.362 | A04 | MICL0.00907014/RBV
Build-In Floor | Mini Canal | MICL.00907014/RDB | 9 | 70 | 14 | 14 | 76 | 76 | 76 | 0.0018095 | 30 | 0.00071429 | 87 | 0.0020714 | 1.362 | A04 | MICL0.00907014/RDB
Build-In Floor | Mini Canal | MICL.00907014/RMN | 9 | 70 | 14 | 14 | 74 | 74 | 74 | 0.0017619 | 29 | 0.00069048 | 84 | 0.002 | 1.362 | A04 | MICL0.00907014/RMN
Build-In Floor | Mini Canal | MICL.00907014/RMV | 9 | 70 | 14 | 14 | 74 | 74 | 74 | 0.0017619 | 29 | 0.00069048 | 84 | 0.002 | 1.362 | A04 | MICL0.00907014/RMV
Build-In Floor | Mini Canal | MICL.00907014/RNA | 9 | 70 | 14 | 14 | 76 | 76 | 76 | 0.0018095 | 30 | 0.00071429 | 87 | 0.0020714 | 1.362 | A04 | MICL0.00907014/RNA
Build-In Floor | Mini Canal | MICL.00907014/RON | 9 | 70 | 14 | 14 | 74 | 74 | 74 | 0.0017619 | 29 | 0.00069048 | 84 | 0.002 | 1.362 | A04 | MICL0.00907014/RON
Build-In Floor | Mini Canal | MICL.00907014/ROV | 9 | 70 | 14 | 14 | 74 | 74 | 74 | 0.0017619 | 29 | 0.00069048 | 84 | 0.002 | 1.362 | A04 | MICL0.00907014/ROV
Build-In Floor | Mini Canal | MICL.00907014/RSS | 9 | 70 | 14 | 14 | 73 | 73 | 73 | 0.0017381 | 28 | 0.00066667 | 83 | 0.0019762 | 1.362 | A04 | MICL0.00907014/RSS
Build-In Floor | Mini Canal | MICL.00907014/SBL | 9 | 70 | 14 | 14 | 76 | 76 | 76 | 0.0018095 | 30 | 0.00071429 | 87 | 0.0020714 | 1.362 | A04 | MICL0.00907014/SBL
Build-In Floor | Mini Canal | MICL.00907014/SBR | 9 | 70 | 14 | 14 | 76 | 76 | 76 | 0.0018095 | 30 | 0.00071429 | 87 | 0.0020714 | 1.362 | A04 | MICL0.00907014/SBR
Build-In Floor | Mini Canal | MICL.00907014/SDB | 9 | 70 | 14 | 14 | 76 | 76 | 76 | 0.0018095 | 30 | 0.00071429 | 87 | 0.0020714 | 1.362 | A04 | MICL0.00907014/SDB
Build-In Floor | Mini Canal | MICL.00907014/SNA | 9 | 70 | 14 | 14 | 76 | 76 | 76 | 0.0018095 | 30 | 0.00071429 | 87 | 0.0020714 | 1.362 | A04 | MICL0.00907014/SNA
Build-In Floor | Mini Canal | MICL.00907014/SNC | 9 | 70 | 14 | 14 | 76 | 76 | 76 | 0.0018095 | 30 | 0.00071429 | 87 | 0.0020714 | 1.362 | A04 | MICL0.00907014/SNC
Build-In Floor | Mini Canal | MICL.00907018/ANA | 9 | 70 | 18 | 18 | 68 | 68 | 68 | 0.001619 | 26 | 0.00061905 | 77 | 0.0018333 | 1.362 | A04 | MICL0.00907018/ANA
Build-In Floor | Mini Canal | MICL.00907018/DBL | 9 | 70 | 18 | 18 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.00907018/DBL
Build-In Floor | Mini Canal | MICL.00907018/DBN | 9 | 70 | 18 | 18 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.00907018/DBN
Build-In Floor | Mini Canal | MICL.00907018/DBR | 9 | 70 | 18 | 18 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.00907018/DBR
Build-In Floor | Mini Canal | MICL.00907018/DBV | 9 | 70 | 18 | 18 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.00907018/DBV
Build-In Floor | Mini Canal | MICL.00907018/DDB | 9 | 70 | 18 | 18 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.00907018/DDB
Build-In Floor | Mini Canal | MICL.00907018/DMN | 9 | 70 | 18 | 18 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.00907018/DMN
Build-In Floor | Mini Canal | MICL.00907018/DMV | 9 | 70 | 18 | 18 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.00907018/DMV
Build-In Floor | Mini Canal | MICL.00907018/DNA | 9 | 70 | 18 | 18 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.00907018/DNA
Build-In Floor | Mini Canal | MICL.00907018/DNC | 9 | 70 | 18 | 18 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.00907018/DNC
Build-In Floor | Mini Canal | MICL.00907018/DON | 9 | 70 | 18 | 18 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.00907018/DON
Build-In Floor | Mini Canal | MICL.00907018/DOV | 9 | 70 | 18 | 18 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.00907018/DOV
Build-In Floor | Mini Canal | MICL.00907018/RBL | 9 | 70 | 18 | 18 | 90 | 90 | 90 | 0.0021429 | 35 | 0.00083333 | 103 | 0.0024524 | 1.362 | A04 | MICL0.00907018/RBL
Build-In Floor | Mini Canal | MICL.00907018/RBN | 9 | 70 | 18 | 18 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.00907018/RBN
Build-In Floor | Mini Canal | MICL.00907018/RBR | 9 | 70 | 18 | 18 | 90 | 90 | 90 | 0.0021429 | 35 | 0.00083333 | 103 | 0.0024524 | 1.362 | A04 | MICL0.00907018/RBR
Build-In Floor | Mini Canal | MICL.00907018/RBV | 9 | 70 | 18 | 18 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.00907018/RBV
Build-In Floor | Mini Canal | MICL.00907018/RDB | 9 | 70 | 18 | 18 | 90 | 90 | 90 | 0.0021429 | 35 | 0.00083333 | 103 | 0.0024524 | 1.362 | A04 | MICL0.00907018/RDB
Build-In Floor | Mini Canal | MICL.00907018/RMN | 9 | 70 | 18 | 18 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.00907018/RMN
Build-In Floor | Mini Canal | MICL.00907018/RMV | 9 | 70 | 18 | 18 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.00907018/RMV
Build-In Floor | Mini Canal | MICL.00907018/RNA | 9 | 70 | 18 | 18 | 90 | 90 | 90 | 0.0021429 | 35 | 0.00083333 | 103 | 0.0024524 | 1.362 | A04 | MICL0.00907018/RNA
Build-In Floor | Mini Canal | MICL.00907018/RON | 9 | 70 | 18 | 18 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.00907018/RON
Build-In Floor | Mini Canal | MICL.00907018/ROV | 9 | 70 | 18 | 18 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.00907018/ROV
Build-In Floor | Mini Canal | MICL.00907018/RSS | 9 | 70 | 18 | 18 | 86 | 86 | 86 | 0.0020476 | 33 | 0.00078571 | 98 | 0.0023333 | 1.362 | A04 | MICL0.00907018/RSS
Build-In Floor | Mini Canal | MICL.00907018/SBL | 9 | 70 | 18 | 18 | 90 | 90 | 90 | 0.0021429 | 35 | 0.00083333 | 103 | 0.0024524 | 1.362 | A04 | MICL0.00907018/SBL
Build-In Floor | Mini Canal | MICL.00907018/SBR | 9 | 70 | 18 | 18 | 90 | 90 | 90 | 0.0021429 | 35 | 0.00083333 | 103 | 0.0024524 | 1.362 | A04 | MICL0.00907018/SBR
Build-In Floor | Mini Canal | MICL.00907018/SDB | 9 | 70 | 18 | 18 | 90 | 90 | 90 | 0.0021429 | 35 | 0.00083333 | 103 | 0.0024524 | 1.362 | A04 | MICL0.00907018/SDB
Build-In Floor | Mini Canal | MICL.00907018/SNA | 9 | 70 | 18 | 18 | 90 | 90 | 90 | 0.0021429 | 35 | 0.00083333 | 103 | 0.0024524 | 1.362 | A04 | MICL0.00907018/SNA
Build-In Floor | Mini Canal | MICL.00907018/SNC | 9 | 70 | 18 | 18 | 90 | 90 | 90 | 0.0021429 | 35 | 0.00083333 | 103 | 0.0024524 | 1.362 | A04 | MICL0.00907018/SNC
Build-In Floor | Mini Canal | MICL.00907026/ANA | 9 | 70 | 26 | 26 | 89 | 89 | 89 | 0.002119 | 35 | 0.00083333 | 101 | 0.0024048 | 1.362 | A04 | MICL0.00907026/ANA
Build-In Floor | Mini Canal | MICL.00907026/DBL | 9 | 70 | 26 | 26 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.00907026/DBL
Build-In Floor | Mini Canal | MICL.00907026/DBN | 9 | 70 | 26 | 26 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00907026/DBN
Build-In Floor | Mini Canal | MICL.00907026/DBR | 9 | 70 | 26 | 26 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.00907026/DBR
Build-In Floor | Mini Canal | MICL.00907026/DBV | 9 | 70 | 26 | 26 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00907026/DBV
Build-In Floor | Mini Canal | MICL.00907026/DDB | 9 | 70 | 26 | 26 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.00907026/DDB
Build-In Floor | Mini Canal | MICL.00907026/DMN | 9 | 70 | 26 | 26 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00907026/DMN
Build-In Floor | Mini Canal | MICL.00907026/DMV | 9 | 70 | 26 | 26 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00907026/DMV
Build-In Floor | Mini Canal | MICL.00907026/DNA | 9 | 70 | 26 | 26 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.00907026/DNA
Build-In Floor | Mini Canal | MICL.00907026/DNC | 9 | 70 | 26 | 26 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.00907026/DNC
Build-In Floor | Mini Canal | MICL.00907026/DON | 9 | 70 | 26 | 26 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00907026/DON
Build-In Floor | Mini Canal | MICL.00907026/DOV | 9 | 70 | 26 | 26 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00907026/DOV
Build-In Floor | Mini Canal | MICL.00907026/PNC | 9 | 70 | 26 | 26 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.00907026/PNC
Build-In Floor | Mini Canal | MICL.00907026/RBL | 9 | 70 | 26 | 26 | 119 | 119 | 119 | 0.0028333 | 46 | 0.0010952 | 136 | 0.0032381 | 1.362 | A04 | MICL0.00907026/RBL
Build-In Floor | Mini Canal | MICL.00907026/RBN | 9 | 70 | 26 | 26 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.00907026/RBN
Build-In Floor | Mini Canal | MICL.00907026/RBR | 9 | 70 | 26 | 26 | 119 | 119 | 119 | 0.0028333 | 46 | 0.0010952 | 136 | 0.0032381 | 1.362 | A04 | MICL0.00907026/RBR
Build-In Floor | Mini Canal | MICL.00907026/RBV | 9 | 70 | 26 | 26 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.00907026/RBV
Build-In Floor | Mini Canal | MICL.00907026/RDB | 9 | 70 | 26 | 26 | 119 | 119 | 119 | 0.0028333 | 46 | 0.0010952 | 136 | 0.0032381 | 1.362 | A04 | MICL0.00907026/RDB
Build-In Floor | Mini Canal | MICL.00907026/RMN | 9 | 70 | 26 | 26 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.00907026/RMN
Build-In Floor | Mini Canal | MICL.00907026/RMV | 9 | 70 | 26 | 26 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.00907026/RMV
Build-In Floor | Mini Canal | MICL.00907026/RNA | 9 | 70 | 26 | 26 | 119 | 119 | 119 | 0.0028333 | 46 | 0.0010952 | 136 | 0.0032381 | 1.362 | A04 | MICL0.00907026/RNA
Build-In Floor | Mini Canal | MICL.00907026/RON | 9 | 70 | 26 | 26 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.00907026/RON
Build-In Floor | Mini Canal | MICL.00907026/ROV | 9 | 70 | 26 | 26 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.00907026/ROV
Build-In Floor | Mini Canal | MICL.00907026/RSS | 9 | 70 | 26 | 26 | 114 | 114 | 114 | 0.0027143 | 44 | 0.0010476 | 130 | 0.0030952 | 1.362 | A04 | MICL0.00907026/RSS
Build-In Floor | Mini Canal | MICL.00907026/SBL | 9 | 70 | 26 | 26 | 119 | 119 | 119 | 0.0028333 | 46 | 0.0010952 | 136 | 0.0032381 | 1.362 | A04 | MICL0.00907026/SBL
Build-In Floor | Mini Canal | MICL.00907026/SBR | 9 | 70 | 26 | 26 | 119 | 119 | 119 | 0.0028333 | 46 | 0.0010952 | 136 | 0.0032381 | 1.362 | A04 | MICL0.00907026/SBR
Build-In Floor | Mini Canal | MICL.00907026/SDB | 9 | 70 | 26 | 26 | 119 | 119 | 119 | 0.0028333 | 46 | 0.0010952 | 136 | 0.0032381 | 1.362 | A04 | MICL0.00907026/SDB
Build-In Floor | Mini Canal | MICL.00907026/SNA | 9 | 70 | 26 | 26 | 119 | 119 | 119 | 0.0028333 | 46 | 0.0010952 | 136 | 0.0032381 | 1.362 | A04 | MICL0.00907026/SNA
Build-In Floor | Mini Canal | MICL.00907026/SNC | 9 | 70 | 26 | 26 | 119 | 119 | 119 | 0.0028333 | 46 | 0.0010952 | 136 | 0.0032381 | 1.362 | A04 | MICL0.00907026/SNC
Build-In Floor | Mini Canal | MICL.00907034/ANA | 9 | 70 | 34 | 34 | 116 | 116 | 116 | 0.0027619 | 45 | 0.0010714 | 132 | 0.0031429 | 1.362 | A04 | MICL0.00907034/ANA
Build-In Floor | Mini Canal | MICL.00907034/DBL | 9 | 70 | 34 | 34 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.00907034/DBL
Build-In Floor | Mini Canal | MICL.00907034/DBN | 9 | 70 | 34 | 34 | 143 | 143 | 143 | 0.0034048 | 56 | 0.0013333 | 163 | 0.003881 | 1.362 | A04 | MICL0.00907034/DBN
Build-In Floor | Mini Canal | MICL.00907034/DBR | 9 | 70 | 34 | 34 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.00907034/DBR
Build-In Floor | Mini Canal | MICL.00907034/DBV | 9 | 70 | 34 | 34 | 143 | 143 | 143 | 0.0034048 | 56 | 0.0013333 | 163 | 0.003881 | 1.362 | A04 | MICL0.00907034/DBV
Build-In Floor | Mini Canal | MICL.00907034/DDB | 9 | 70 | 34 | 34 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.00907034/DDB
Build-In Floor | Mini Canal | MICL.00907034/DMN | 9 | 70 | 34 | 34 | 143 | 143 | 143 | 0.0034048 | 56 | 0.0013333 | 163 | 0.003881 | 1.362 | A04 | MICL0.00907034/DMN
Build-In Floor | Mini Canal | MICL.00907034/DMV | 9 | 70 | 34 | 34 | 143 | 143 | 143 | 0.0034048 | 56 | 0.0013333 | 163 | 0.003881 | 1.362 | A04 | MICL0.00907034/DMV
Build-In Floor | Mini Canal | MICL.00907034/DNA | 9 | 70 | 34 | 34 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.00907034/DNA
Build-In Floor | Mini Canal | MICL.00907034/DNC | 9 | 70 | 34 | 34 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.00907034/DNC
Build-In Floor | Mini Canal | MICL.00907034/DON | 9 | 70 | 34 | 34 | 143 | 143 | 143 | 0.0034048 | 56 | 0.0013333 | 163 | 0.003881 | 1.362 | A04 | MICL0.00907034/DON
Build-In Floor | Mini Canal | MICL.00907034/DOV | 9 | 70 | 34 | 34 | 143 | 143 | 143 | 0.0034048 | 56 | 0.0013333 | 163 | 0.003881 | 1.362 | A04 | MICL0.00907034/DOV
Build-In Floor | Mini Canal | MICL.00907034/PNC | 9 | 70 | 34 | 34 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.00907034/PNC
Build-In Floor | Mini Canal | MICL.00907034/RBL | 9 | 70 | 34 | 34 | 154 | 154 | 154 | 0.0036667 | 60 | 0.0014286 | 175 | 0.0041667 | 1.362 | A04 | MICL0.00907034/RBL
Build-In Floor | Mini Canal | MICL.00907034/RBN | 9 | 70 | 34 | 34 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.00907034/RBN
Build-In Floor | Mini Canal | MICL.00907034/RBR | 9 | 70 | 34 | 34 | 154 | 154 | 154 | 0.0036667 | 60 | 0.0014286 | 175 | 0.0041667 | 1.362 | A04 | MICL0.00907034/RBR
Build-In Floor | Mini Canal | MICL.00907034/RBV | 9 | 70 | 34 | 34 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.00907034/RBV
Build-In Floor | Mini Canal | MICL.00907034/RDB | 9 | 70 | 34 | 34 | 154 | 154 | 154 | 0.0036667 | 60 | 0.0014286 | 175 | 0.0041667 | 1.362 | A04 | MICL0.00907034/RDB
Build-In Floor | Mini Canal | MICL.00907034/RMN | 9 | 70 | 34 | 34 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.00907034/RMN
Build-In Floor | Mini Canal | MICL.00907034/RMV | 9 | 70 | 34 | 34 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.00907034/RMV
Build-In Floor | Mini Canal | MICL.00907034/RNA | 9 | 70 | 34 | 34 | 154 | 154 | 154 | 0.0036667 | 60 | 0.0014286 | 175 | 0.0041667 | 1.362 | A04 | MICL0.00907034/RNA
Build-In Floor | Mini Canal | MICL.00907034/RON | 9 | 70 | 34 | 34 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.00907034/RON
Build-In Floor | Mini Canal | MICL.00907034/ROV | 9 | 70 | 34 | 34 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.00907034/ROV
Build-In Floor | Mini Canal | MICL.00907034/RSS | 9 | 70 | 34 | 34 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.00907034/RSS
Build-In Floor | Mini Canal | MICL.00907034/SBL | 9 | 70 | 34 | 34 | 154 | 154 | 154 | 0.0036667 | 60 | 0.0014286 | 175 | 0.0041667 | 1.362 | A04 | MICL0.00907034/SBL
Build-In Floor | Mini Canal | MICL.00907034/SBR | 9 | 70 | 34 | 34 | 154 | 154 | 154 | 0.0036667 | 60 | 0.0014286 | 175 | 0.0041667 | 1.362 | A04 | MICL0.00907034/SBR
Build-In Floor | Mini Canal | MICL.00907034/SDB | 9 | 70 | 34 | 34 | 154 | 154 | 154 | 0.0036667 | 60 | 0.0014286 | 175 | 0.0041667 | 1.362 | A04 | MICL0.00907034/SDB
Build-In Floor | Mini Canal | MICL.00907034/SNA | 9 | 70 | 34 | 34 | 154 | 154 | 154 | 0.0036667 | 60 | 0.0014286 | 175 | 0.0041667 | 1.362 | A04 | MICL0.00907034/SNA
Build-In Floor | Mini Canal | MICL.00907034/SNC | 9 | 70 | 34 | 34 | 154 | 154 | 154 | 0.0036667 | 60 | 0.0014286 | 175 | 0.0041667 | 1.362 | A04 | MICL0.00907034/SNC
Build-In Floor | Mini Canal | MICL.00907042/ANA | 9 | 70 | 42 | 42 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00907042/ANA
Build-In Floor | Mini Canal | MICL.00907042/DBL | 9 | 70 | 42 | 42 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00907042/DBL
Build-In Floor | Mini Canal | MICL.00907042/DBN | 9 | 70 | 42 | 42 | 206 | 206 | 206 | 0.0049048 | 80 | 0.0019048 | 235 | 0.0055952 | 1.362 | A04 | MICL0.00907042/DBN
Build-In Floor | Mini Canal | MICL.00907042/DBR | 9 | 70 | 42 | 42 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00907042/DBR
Build-In Floor | Mini Canal | MICL.00907042/DBV | 9 | 70 | 42 | 42 | 206 | 206 | 206 | 0.0049048 | 80 | 0.0019048 | 235 | 0.0055952 | 1.362 | A04 | MICL0.00907042/DBV
Build-In Floor | Mini Canal | MICL.00907042/DDB | 9 | 70 | 42 | 42 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00907042/DDB
Build-In Floor | Mini Canal | MICL.00907042/DMN | 9 | 70 | 42 | 42 | 206 | 206 | 206 | 0.0049048 | 80 | 0.0019048 | 235 | 0.0055952 | 1.362 | A04 | MICL0.00907042/DMN
Build-In Floor | Mini Canal | MICL.00907042/DMV | 9 | 70 | 42 | 42 | 206 | 206 | 206 | 0.0049048 | 80 | 0.0019048 | 235 | 0.0055952 | 1.362 | A04 | MICL0.00907042/DMV
Build-In Floor | Mini Canal | MICL.00907042/DNA | 9 | 70 | 42 | 42 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00907042/DNA
Build-In Floor | Mini Canal | MICL.00907042/DNC | 9 | 70 | 42 | 42 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00907042/DNC
Build-In Floor | Mini Canal | MICL.00907042/DON | 9 | 70 | 42 | 42 | 206 | 206 | 206 | 0.0049048 | 80 | 0.0019048 | 235 | 0.0055952 | 1.362 | A04 | MICL0.00907042/DON
Build-In Floor | Mini Canal | MICL.00907042/DOV | 9 | 70 | 42 | 42 | 206 | 206 | 206 | 0.0049048 | 80 | 0.0019048 | 235 | 0.0055952 | 1.362 | A04 | MICL0.00907042/DOV
Build-In Floor | Mini Canal | MICL.00907042/PNC | 9 | 70 | 42 | 42 | 189 | 189 | 189 | 0.0045 | 74 | 0.0017619 | 215 | 0.005119 | 1.362 | A04 | MICL0.00907042/PNC
Build-In Floor | Mini Canal | MICL.00907042/RBL | 9 | 70 | 42 | 42 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00907042/RBL
Build-In Floor | Mini Canal | MICL.00907042/RBN | 9 | 70 | 42 | 42 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00907042/RBN
Build-In Floor | Mini Canal | MICL.00907042/RBR | 9 | 70 | 42 | 42 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00907042/RBR
Build-In Floor | Mini Canal | MICL.00907042/RBV | 9 | 70 | 42 | 42 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00907042/RBV
Build-In Floor | Mini Canal | MICL.00907042/RDB | 9 | 70 | 42 | 42 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00907042/RDB
Build-In Floor | Mini Canal | MICL.00907042/RMN | 9 | 70 | 42 | 42 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00907042/RMN
Build-In Floor | Mini Canal | MICL.00907042/RMV | 9 | 70 | 42 | 42 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00907042/RMV
Build-In Floor | Mini Canal | MICL.00907042/RNA | 9 | 70 | 42 | 42 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00907042/RNA
Build-In Floor | Mini Canal | MICL.00907042/RON | 9 | 70 | 42 | 42 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00907042/RON
Build-In Floor | Mini Canal | MICL.00907042/ROV | 9 | 70 | 42 | 42 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00907042/ROV
Build-In Floor | Mini Canal | MICL.00907042/RSS | 9 | 70 | 42 | 42 | 213 | 213 | 213 | 0.0050714 | 83 | 0.0019762 | 243 | 0.0057857 | 1.362 | A04 | MICL0.00907042/RSS
Build-In Floor | Mini Canal | MICL.00907042/SBL | 9 | 70 | 42 | 42 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00907042/SBL
Build-In Floor | Mini Canal | MICL.00907042/SBR | 9 | 70 | 42 | 42 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00907042/SBR
Build-In Floor | Mini Canal | MICL.00907042/SDB | 9 | 70 | 42 | 42 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00907042/SDB
Build-In Floor | Mini Canal | MICL.00907042/SNA | 9 | 70 | 42 | 42 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00907042/SNA
Build-In Floor | Mini Canal | MICL.00907042/SNC | 9 | 70 | 42 | 42 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00907042/SNC
Build-In Floor | Mini Canal | MICL.00908014/ANA | 9 | 80 | 14 | 14 | 71 | 71 | 71 | 0.0016905 | 28 | 0.00066667 | 81 | 0.0019286 | 1.362 | A04 | MICL0.00908014/ANA
Build-In Floor | Mini Canal | MICL.00908014/DBL | 9 | 80 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.00908014/DBL
Build-In Floor | Mini Canal | MICL.00908014/DBN | 9 | 80 | 14 | 14 | 88 | 88 | 88 | 0.0020952 | 34 | 0.00080952 | 100 | 0.002381 | 1.362 | A04 | MICL0.00908014/DBN
Build-In Floor | Mini Canal | MICL.00908014/DBR | 9 | 80 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.00908014/DBR
Build-In Floor | Mini Canal | MICL.00908014/DBV | 9 | 80 | 14 | 14 | 88 | 88 | 88 | 0.0020952 | 34 | 0.00080952 | 100 | 0.002381 | 1.362 | A04 | MICL0.00908014/DBV
Build-In Floor | Mini Canal | MICL.00908014/DDB | 9 | 80 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.00908014/DDB
Build-In Floor | Mini Canal | MICL.00908014/DMN | 9 | 80 | 14 | 14 | 88 | 88 | 88 | 0.0020952 | 34 | 0.00080952 | 100 | 0.002381 | 1.362 | A04 | MICL0.00908014/DMN
Build-In Floor | Mini Canal | MICL.00908014/DMV | 9 | 80 | 14 | 14 | 88 | 88 | 88 | 0.0020952 | 34 | 0.00080952 | 100 | 0.002381 | 1.362 | A04 | MICL0.00908014/DMV
Build-In Floor | Mini Canal | MICL.00908014/DNA | 9 | 80 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.00908014/DNA
Build-In Floor | Mini Canal | MICL.00908014/DNC | 9 | 80 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.00908014/DNC
Build-In Floor | Mini Canal | MICL.00908014/DON | 9 | 80 | 14 | 14 | 88 | 88 | 88 | 0.0020952 | 34 | 0.00080952 | 100 | 0.002381 | 1.362 | A04 | MICL0.00908014/DON
Build-In Floor | Mini Canal | MICL.00908014/DOV | 9 | 80 | 14 | 14 | 88 | 88 | 88 | 0.0020952 | 34 | 0.00080952 | 100 | 0.002381 | 1.362 | A04 | MICL0.00908014/DOV
Build-In Floor | Mini Canal | MICL.00908014/RBL | 9 | 80 | 14 | 14 | 95 | 95 | 95 | 0.0022619 | 37 | 0.00088095 | 108 | 0.0025714 | 1.362 | A04 | MICL0.00908014/RBL
Build-In Floor | Mini Canal | MICL.00908014/RBN | 9 | 80 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.00908014/RBN
Build-In Floor | Mini Canal | MICL.00908014/RBR | 9 | 80 | 14 | 14 | 95 | 95 | 95 | 0.0022619 | 37 | 0.00088095 | 108 | 0.0025714 | 1.362 | A04 | MICL0.00908014/RBR
Build-In Floor | Mini Canal | MICL.00908014/RBV | 9 | 80 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.00908014/RBV
Build-In Floor | Mini Canal | MICL.00908014/RDB | 9 | 80 | 14 | 14 | 95 | 95 | 95 | 0.0022619 | 37 | 0.00088095 | 108 | 0.0025714 | 1.362 | A04 | MICL0.00908014/RDB
Build-In Floor | Mini Canal | MICL.00908014/RMN | 9 | 80 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.00908014/RMN
Build-In Floor | Mini Canal | MICL.00908014/RMV | 9 | 80 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.00908014/RMV
Build-In Floor | Mini Canal | MICL.00908014/RNA | 9 | 80 | 14 | 14 | 95 | 95 | 95 | 0.0022619 | 37 | 0.00088095 | 108 | 0.0025714 | 1.362 | A04 | MICL0.00908014/RNA
Build-In Floor | Mini Canal | MICL.00908014/RON | 9 | 80 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.00908014/RON
Build-In Floor | Mini Canal | MICL.00908014/ROV | 9 | 80 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.00908014/ROV
Build-In Floor | Mini Canal | MICL.00908014/RSS | 9 | 80 | 14 | 14 | 91 | 91 | 91 | 0.0021667 | 35 | 0.00083333 | 104 | 0.0024762 | 1.362 | A04 | MICL0.00908014/RSS
Build-In Floor | Mini Canal | MICL.00908014/SBL | 9 | 80 | 14 | 14 | 95 | 95 | 95 | 0.0022619 | 37 | 0.00088095 | 108 | 0.0025714 | 1.362 | A04 | MICL0.00908014/SBL
Build-In Floor | Mini Canal | MICL.00908014/SBR | 9 | 80 | 14 | 14 | 95 | 95 | 95 | 0.0022619 | 37 | 0.00088095 | 108 | 0.0025714 | 1.362 | A04 | MICL0.00908014/SBR
Build-In Floor | Mini Canal | MICL.00908014/SDB | 9 | 80 | 14 | 14 | 95 | 95 | 95 | 0.0022619 | 37 | 0.00088095 | 108 | 0.0025714 | 1.362 | A04 | MICL0.00908014/SDB
Build-In Floor | Mini Canal | MICL.00908014/SNA | 9 | 80 | 14 | 14 | 95 | 95 | 95 | 0.0022619 | 37 | 0.00088095 | 108 | 0.0025714 | 1.362 | A04 | MICL0.00908014/SNA
Build-In Floor | Mini Canal | MICL.00908014/SNC | 9 | 80 | 14 | 14 | 95 | 95 | 95 | 0.0022619 | 37 | 0.00088095 | 108 | 0.0025714 | 1.362 | A04 | MICL0.00908014/SNC
Build-In Floor | Mini Canal | MICL.00908018/ANA | 9 | 80 | 18 | 18 | 85 | 85 | 85 | 0.0020238 | 33 | 0.00078571 | 97 | 0.0023095 | 1.362 | A04 | MICL0.00908018/ANA
Build-In Floor | Mini Canal | MICL.00908018/DBL | 9 | 80 | 18 | 18 | 110 | 110 | 110 | 0.002619 | 43 | 0.0010238 | 125 | 0.0029762 | 1.362 | A04 | MICL0.00908018/DBL
Build-In Floor | Mini Canal | MICL.00908018/DBN | 9 | 80 | 18 | 18 | 105 | 105 | 105 | 0.0025 | 41 | 0.00097619 | 120 | 0.0028571 | 1.362 | A04 | MICL0.00908018/DBN
Build-In Floor | Mini Canal | MICL.00908018/DBR | 9 | 80 | 18 | 18 | 110 | 110 | 110 | 0.002619 | 43 | 0.0010238 | 125 | 0.0029762 | 1.362 | A04 | MICL0.00908018/DBR
Build-In Floor | Mini Canal | MICL.00908018/DBV | 9 | 80 | 18 | 18 | 105 | 105 | 105 | 0.0025 | 41 | 0.00097619 | 120 | 0.0028571 | 1.362 | A04 | MICL0.00908018/DBV
Build-In Floor | Mini Canal | MICL.00908018/DDB | 9 | 80 | 18 | 18 | 110 | 110 | 110 | 0.002619 | 43 | 0.0010238 | 125 | 0.0029762 | 1.362 | A04 | MICL0.00908018/DDB
Build-In Floor | Mini Canal | MICL.00908018/DMN | 9 | 80 | 18 | 18 | 105 | 105 | 105 | 0.0025 | 41 | 0.00097619 | 120 | 0.0028571 | 1.362 | A04 | MICL0.00908018/DMN
Build-In Floor | Mini Canal | MICL.00908018/DMV | 9 | 80 | 18 | 18 | 105 | 105 | 105 | 0.0025 | 41 | 0.00097619 | 120 | 0.0028571 | 1.362 | A04 | MICL0.00908018/DMV
Build-In Floor | Mini Canal | MICL.00908018/DNA | 9 | 80 | 18 | 18 | 110 | 110 | 110 | 0.002619 | 43 | 0.0010238 | 125 | 0.0029762 | 1.362 | A04 | MICL0.00908018/DNA
Build-In Floor | Mini Canal | MICL.00908018/DNC | 9 | 80 | 18 | 18 | 110 | 110 | 110 | 0.002619 | 43 | 0.0010238 | 125 | 0.0029762 | 1.362 | A04 | MICL0.00908018/DNC
Build-In Floor | Mini Canal | MICL.00908018/DON | 9 | 80 | 18 | 18 | 105 | 105 | 105 | 0.0025 | 41 | 0.00097619 | 120 | 0.0028571 | 1.362 | A04 | MICL0.00908018/DON
Build-In Floor | Mini Canal | MICL.00908018/DOV | 9 | 80 | 18 | 18 | 105 | 105 | 105 | 0.0025 | 41 | 0.00097619 | 120 | 0.0028571 | 1.362 | A04 | MICL0.00908018/DOV
Build-In Floor | Mini Canal | MICL.00908018/RBL | 9 | 80 | 18 | 18 | 113 | 113 | 113 | 0.0026905 | 44 | 0.0010476 | 129 | 0.0030714 | 1.362 | A04 | MICL0.00908018/RBL
Build-In Floor | Mini Canal | MICL.00908018/RBN | 9 | 80 | 18 | 18 | 110 | 110 | 110 | 0.002619 | 43 | 0.0010238 | 125 | 0.0029762 | 1.362 | A04 | MICL0.00908018/RBN
Build-In Floor | Mini Canal | MICL.00908018/RBR | 9 | 80 | 18 | 18 | 113 | 113 | 113 | 0.0026905 | 44 | 0.0010476 | 129 | 0.0030714 | 1.362 | A04 | MICL0.00908018/RBR
Build-In Floor | Mini Canal | MICL.00908018/RBV | 9 | 80 | 18 | 18 | 110 | 110 | 110 | 0.002619 | 43 | 0.0010238 | 125 | 0.0029762 | 1.362 | A04 | MICL0.00908018/RBV
Build-In Floor | Mini Canal | MICL.00908018/RDB | 9 | 80 | 18 | 18 | 113 | 113 | 113 | 0.0026905 | 44 | 0.0010476 | 129 | 0.0030714 | 1.362 | A04 | MICL0.00908018/RDB
Build-In Floor | Mini Canal | MICL.00908018/RMN | 9 | 80 | 18 | 18 | 110 | 110 | 110 | 0.002619 | 43 | 0.0010238 | 125 | 0.0029762 | 1.362 | A04 | MICL0.00908018/RMN
Build-In Floor | Mini Canal | MICL.00908018/RMV | 9 | 80 | 18 | 18 | 110 | 110 | 110 | 0.002619 | 43 | 0.0010238 | 125 | 0.0029762 | 1.362 | A04 | MICL0.00908018/RMV
Build-In Floor | Mini Canal | MICL.00908018/RNA | 9 | 80 | 18 | 18 | 113 | 113 | 113 | 0.0026905 | 44 | 0.0010476 | 129 | 0.0030714 | 1.362 | A04 | MICL0.00908018/RNA
Build-In Floor | Mini Canal | MICL.00908018/RON | 9 | 80 | 18 | 18 | 110 | 110 | 110 | 0.002619 | 43 | 0.0010238 | 125 | 0.0029762 | 1.362 | A04 | MICL0.00908018/RON
Build-In Floor | Mini Canal | MICL.00908018/ROV | 9 | 80 | 18 | 18 | 110 | 110 | 110 | 0.002619 | 43 | 0.0010238 | 125 | 0.0029762 | 1.362 | A04 | MICL0.00908018/ROV
Build-In Floor | Mini Canal | MICL.00908018/RSS | 9 | 80 | 18 | 18 | 108 | 108 | 108 | 0.0025714 | 42 | 0.001 | 123 | 0.0029286 | 1.362 | A04 | MICL0.00908018/RSS
Build-In Floor | Mini Canal | MICL.00908018/SBL | 9 | 80 | 18 | 18 | 113 | 113 | 113 | 0.0026905 | 44 | 0.0010476 | 129 | 0.0030714 | 1.362 | A04 | MICL0.00908018/SBL
Build-In Floor | Mini Canal | MICL.00908018/SBR | 9 | 80 | 18 | 18 | 113 | 113 | 113 | 0.0026905 | 44 | 0.0010476 | 129 | 0.0030714 | 1.362 | A04 | MICL0.00908018/SBR
Build-In Floor | Mini Canal | MICL.00908018/SDB | 9 | 80 | 18 | 18 | 113 | 113 | 113 | 0.0026905 | 44 | 0.0010476 | 129 | 0.0030714 | 1.362 | A04 | MICL0.00908018/SDB
Build-In Floor | Mini Canal | MICL.00908018/SNA | 9 | 80 | 18 | 18 | 113 | 113 | 113 | 0.0026905 | 44 | 0.0010476 | 129 | 0.0030714 | 1.362 | A04 | MICL0.00908018/SNA
Build-In Floor | Mini Canal | MICL.00908018/SNC | 9 | 80 | 18 | 18 | 113 | 113 | 113 | 0.0026905 | 44 | 0.0010476 | 129 | 0.0030714 | 1.362 | A04 | MICL0.00908018/SNC
Build-In Floor | Mini Canal | MICL.00908026/ANA | 9 | 80 | 26 | 26 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00908026/ANA
Build-In Floor | Mini Canal | MICL.00908026/DBL | 9 | 80 | 26 | 26 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.00908026/DBL
Build-In Floor | Mini Canal | MICL.00908026/DBN | 9 | 80 | 26 | 26 | 138 | 138 | 138 | 0.0032857 | 54 | 0.0012857 | 157 | 0.0037381 | 1.362 | A04 | MICL0.00908026/DBN
Build-In Floor | Mini Canal | MICL.00908026/DBR | 9 | 80 | 26 | 26 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.00908026/DBR
Build-In Floor | Mini Canal | MICL.00908026/DBV | 9 | 80 | 26 | 26 | 138 | 138 | 138 | 0.0032857 | 54 | 0.0012857 | 157 | 0.0037381 | 1.362 | A04 | MICL0.00908026/DBV
Build-In Floor | Mini Canal | MICL.00908026/DDB | 9 | 80 | 26 | 26 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.00908026/DDB
Build-In Floor | Mini Canal | MICL.00908026/DMN | 9 | 80 | 26 | 26 | 138 | 138 | 138 | 0.0032857 | 54 | 0.0012857 | 157 | 0.0037381 | 1.362 | A04 | MICL0.00908026/DMN
Build-In Floor | Mini Canal | MICL.00908026/DMV | 9 | 80 | 26 | 26 | 138 | 138 | 138 | 0.0032857 | 54 | 0.0012857 | 157 | 0.0037381 | 1.362 | A04 | MICL0.00908026/DMV
Build-In Floor | Mini Canal | MICL.00908026/DNA | 9 | 80 | 26 | 26 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.00908026/DNA
Build-In Floor | Mini Canal | MICL.00908026/DNC | 9 | 80 | 26 | 26 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.00908026/DNC
Build-In Floor | Mini Canal | MICL.00908026/DON | 9 | 80 | 26 | 26 | 138 | 138 | 138 | 0.0032857 | 54 | 0.0012857 | 157 | 0.0037381 | 1.362 | A04 | MICL0.00908026/DON
Build-In Floor | Mini Canal | MICL.00908026/DOV | 9 | 80 | 26 | 26 | 138 | 138 | 138 | 0.0032857 | 54 | 0.0012857 | 157 | 0.0037381 | 1.362 | A04 | MICL0.00908026/DOV
Build-In Floor | Mini Canal | MICL.00908026/PNC | 9 | 80 | 26 | 26 | 126 | 126 | 126 | 0.003 | 49 | 0.0011667 | 144 | 0.0034286 | 1.362 | A04 | MICL0.00908026/PNC
Build-In Floor | Mini Canal | MICL.00908026/RBL | 9 | 80 | 26 | 26 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.00908026/RBL
Build-In Floor | Mini Canal | MICL.00908026/RBN | 9 | 80 | 26 | 26 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.00908026/RBN
Build-In Floor | Mini Canal | MICL.00908026/RBR | 9 | 80 | 26 | 26 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.00908026/RBR
Build-In Floor | Mini Canal | MICL.00908026/RBV | 9 | 80 | 26 | 26 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.00908026/RBV
Build-In Floor | Mini Canal | MICL.00908026/RDB | 9 | 80 | 26 | 26 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.00908026/RDB
Build-In Floor | Mini Canal | MICL.00908026/RMN | 9 | 80 | 26 | 26 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.00908026/RMN
Build-In Floor | Mini Canal | MICL.00908026/RMV | 9 | 80 | 26 | 26 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.00908026/RMV
Build-In Floor | Mini Canal | MICL.00908026/RNA | 9 | 80 | 26 | 26 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.00908026/RNA
Build-In Floor | Mini Canal | MICL.00908026/RON | 9 | 80 | 26 | 26 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.00908026/RON
Build-In Floor | Mini Canal | MICL.00908026/ROV | 9 | 80 | 26 | 26 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.00908026/ROV
Build-In Floor | Mini Canal | MICL.00908026/RSS | 9 | 80 | 26 | 26 | 142 | 142 | 142 | 0.003381 | 55 | 0.0013095 | 162 | 0.0038571 | 1.362 | A04 | MICL0.00908026/RSS
Build-In Floor | Mini Canal | MICL.00908026/SBL | 9 | 80 | 26 | 26 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.00908026/SBL
Build-In Floor | Mini Canal | MICL.00908026/SBR | 9 | 80 | 26 | 26 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.00908026/SBR
Build-In Floor | Mini Canal | MICL.00908026/SDB | 9 | 80 | 26 | 26 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.00908026/SDB
Build-In Floor | Mini Canal | MICL.00908026/SNA | 9 | 80 | 26 | 26 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.00908026/SNA
Build-In Floor | Mini Canal | MICL.00908026/SNC | 9 | 80 | 26 | 26 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.00908026/SNC
Build-In Floor | Mini Canal | MICL.00908034/ANA | 9 | 80 | 34 | 34 | 145 | 145 | 145 | 0.0034524 | 56 | 0.0013333 | 165 | 0.0039286 | 1.362 | A04 | MICL0.00908034/ANA
Build-In Floor | Mini Canal | MICL.00908034/DBL | 9 | 80 | 34 | 34 | 187 | 187 | 187 | 0.0044524 | 73 | 0.0017381 | 213 | 0.0050714 | 1.362 | A04 | MICL0.00908034/DBL
Build-In Floor | Mini Canal | MICL.00908034/DBN | 9 | 80 | 34 | 34 | 179 | 179 | 179 | 0.0042619 | 70 | 0.0016667 | 204 | 0.0048571 | 1.362 | A04 | MICL0.00908034/DBN
Build-In Floor | Mini Canal | MICL.00908034/DBR | 9 | 80 | 34 | 34 | 187 | 187 | 187 | 0.0044524 | 73 | 0.0017381 | 213 | 0.0050714 | 1.362 | A04 | MICL0.00908034/DBR
Build-In Floor | Mini Canal | MICL.00908034/DBV | 9 | 80 | 34 | 34 | 179 | 179 | 179 | 0.0042619 | 70 | 0.0016667 | 204 | 0.0048571 | 1.362 | A04 | MICL0.00908034/DBV
Build-In Floor | Mini Canal | MICL.00908034/DDB | 9 | 80 | 34 | 34 | 187 | 187 | 187 | 0.0044524 | 73 | 0.0017381 | 213 | 0.0050714 | 1.362 | A04 | MICL0.00908034/DDB
Build-In Floor | Mini Canal | MICL.00908034/DMN | 9 | 80 | 34 | 34 | 179 | 179 | 179 | 0.0042619 | 70 | 0.0016667 | 204 | 0.0048571 | 1.362 | A04 | MICL0.00908034/DMN
Build-In Floor | Mini Canal | MICL.00908034/DMV | 9 | 80 | 34 | 34 | 179 | 179 | 179 | 0.0042619 | 70 | 0.0016667 | 204 | 0.0048571 | 1.362 | A04 | MICL0.00908034/DMV
Build-In Floor | Mini Canal | MICL.00908034/DNA | 9 | 80 | 34 | 34 | 187 | 187 | 187 | 0.0044524 | 73 | 0.0017381 | 213 | 0.0050714 | 1.362 | A04 | MICL0.00908034/DNA
Build-In Floor | Mini Canal | MICL.00908034/DNC | 9 | 80 | 34 | 34 | 187 | 187 | 187 | 0.0044524 | 73 | 0.0017381 | 213 | 0.0050714 | 1.362 | A04 | MICL0.00908034/DNC
Build-In Floor | Mini Canal | MICL.00908034/DON | 9 | 80 | 34 | 34 | 179 | 179 | 179 | 0.0042619 | 70 | 0.0016667 | 204 | 0.0048571 | 1.362 | A04 | MICL0.00908034/DON
Build-In Floor | Mini Canal | MICL.00908034/DOV | 9 | 80 | 34 | 34 | 179 | 179 | 179 | 0.0042619 | 70 | 0.0016667 | 204 | 0.0048571 | 1.362 | A04 | MICL0.00908034/DOV
Build-In Floor | Mini Canal | MICL.00908034/PNC | 9 | 80 | 34 | 34 | 164 | 164 | 164 | 0.0039048 | 64 | 0.0015238 | 187 | 0.0044524 | 1.362 | A04 | MICL0.00908034/PNC
Build-In Floor | Mini Canal | MICL.00908034/RBL | 9 | 80 | 34 | 34 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00908034/RBL
Build-In Floor | Mini Canal | MICL.00908034/RBN | 9 | 80 | 34 | 34 | 187 | 187 | 187 | 0.0044524 | 73 | 0.0017381 | 213 | 0.0050714 | 1.362 | A04 | MICL0.00908034/RBN
Build-In Floor | Mini Canal | MICL.00908034/RBR | 9 | 80 | 34 | 34 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00908034/RBR
Build-In Floor | Mini Canal | MICL.00908034/RBV | 9 | 80 | 34 | 34 | 187 | 187 | 187 | 0.0044524 | 73 | 0.0017381 | 213 | 0.0050714 | 1.362 | A04 | MICL0.00908034/RBV
Build-In Floor | Mini Canal | MICL.00908034/RDB | 9 | 80 | 34 | 34 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00908034/RDB
Build-In Floor | Mini Canal | MICL.00908034/RMN | 9 | 80 | 34 | 34 | 187 | 187 | 187 | 0.0044524 | 73 | 0.0017381 | 213 | 0.0050714 | 1.362 | A04 | MICL0.00908034/RMN
Build-In Floor | Mini Canal | MICL.00908034/RMV | 9 | 80 | 34 | 34 | 187 | 187 | 187 | 0.0044524 | 73 | 0.0017381 | 213 | 0.0050714 | 1.362 | A04 | MICL0.00908034/RMV
Build-In Floor | Mini Canal | MICL.00908034/RNA | 9 | 80 | 34 | 34 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00908034/RNA
Build-In Floor | Mini Canal | MICL.00908034/RON | 9 | 80 | 34 | 34 | 187 | 187 | 187 | 0.0044524 | 73 | 0.0017381 | 213 | 0.0050714 | 1.362 | A04 | MICL0.00908034/RON
Build-In Floor | Mini Canal | MICL.00908034/ROV | 9 | 80 | 34 | 34 | 187 | 187 | 187 | 0.0044524 | 73 | 0.0017381 | 213 | 0.0050714 | 1.362 | A04 | MICL0.00908034/ROV
Build-In Floor | Mini Canal | MICL.00908034/RSS | 9 | 80 | 34 | 34 | 185 | 185 | 185 | 0.0044048 | 72 | 0.0017143 | 211 | 0.0050238 | 1.362 | A04 | MICL0.00908034/RSS
Build-In Floor | Mini Canal | MICL.00908034/SBL | 9 | 80 | 34 | 34 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00908034/SBL
Build-In Floor | Mini Canal | MICL.00908034/SBR | 9 | 80 | 34 | 34 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00908034/SBR
Build-In Floor | Mini Canal | MICL.00908034/SDB | 9 | 80 | 34 | 34 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00908034/SDB
Build-In Floor | Mini Canal | MICL.00908034/SNA | 9 | 80 | 34 | 34 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00908034/SNA
Build-In Floor | Mini Canal | MICL.00908034/SNC | 9 | 80 | 34 | 34 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00908034/SNC
Build-In Floor | Mini Canal | MICL.00908042/ANA | 9 | 80 | 42 | 42 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.00908042/ANA
Build-In Floor | Mini Canal | MICL.00908042/DBL | 9 | 80 | 42 | 42 | 270 | 270 | 270 | 0.0064286 | 105 | 0.0025 | 308 | 0.0073333 | 1.362 | A04 | MICL0.00908042/DBL
Build-In Floor | Mini Canal | MICL.00908042/DBN | 9 | 80 | 42 | 42 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00908042/DBN
Build-In Floor | Mini Canal | MICL.00908042/DBR | 9 | 80 | 42 | 42 | 270 | 270 | 270 | 0.0064286 | 105 | 0.0025 | 308 | 0.0073333 | 1.362 | A04 | MICL0.00908042/DBR
Build-In Floor | Mini Canal | MICL.00908042/DBV | 9 | 80 | 42 | 42 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00908042/DBV
Build-In Floor | Mini Canal | MICL.00908042/DDB | 9 | 80 | 42 | 42 | 270 | 270 | 270 | 0.0064286 | 105 | 0.0025 | 308 | 0.0073333 | 1.362 | A04 | MICL0.00908042/DDB
Build-In Floor | Mini Canal | MICL.00908042/DMN | 9 | 80 | 42 | 42 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00908042/DMN
Build-In Floor | Mini Canal | MICL.00908042/DMV | 9 | 80 | 42 | 42 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00908042/DMV
Build-In Floor | Mini Canal | MICL.00908042/DNA | 9 | 80 | 42 | 42 | 270 | 270 | 270 | 0.0064286 | 105 | 0.0025 | 308 | 0.0073333 | 1.362 | A04 | MICL0.00908042/DNA
Build-In Floor | Mini Canal | MICL.00908042/DNC | 9 | 80 | 42 | 42 | 270 | 270 | 270 | 0.0064286 | 105 | 0.0025 | 308 | 0.0073333 | 1.362 | A04 | MICL0.00908042/DNC
Build-In Floor | Mini Canal | MICL.00908042/DON | 9 | 80 | 42 | 42 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00908042/DON
Build-In Floor | Mini Canal | MICL.00908042/DOV | 9 | 80 | 42 | 42 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00908042/DOV
Build-In Floor | Mini Canal | MICL.00908042/PNC | 9 | 80 | 42 | 42 | 236 | 236 | 236 | 0.005619 | 92 | 0.0021905 | 269 | 0.0064048 | 1.362 | A04 | MICL0.00908042/PNC
Build-In Floor | Mini Canal | MICL.00908042/RBL | 9 | 80 | 42 | 42 | 278 | 278 | 278 | 0.006619 | 108 | 0.0025714 | 317 | 0.0075476 | 1.362 | A04 | MICL0.00908042/RBL
Build-In Floor | Mini Canal | MICL.00908042/RBN | 9 | 80 | 42 | 42 | 270 | 270 | 270 | 0.0064286 | 105 | 0.0025 | 308 | 0.0073333 | 1.362 | A04 | MICL0.00908042/RBN
Build-In Floor | Mini Canal | MICL.00908042/RBR | 9 | 80 | 42 | 42 | 278 | 278 | 278 | 0.006619 | 108 | 0.0025714 | 317 | 0.0075476 | 1.362 | A04 | MICL0.00908042/RBR
Build-In Floor | Mini Canal | MICL.00908042/RBV | 9 | 80 | 42 | 42 | 270 | 270 | 270 | 0.0064286 | 105 | 0.0025 | 308 | 0.0073333 | 1.362 | A04 | MICL0.00908042/RBV
Build-In Floor | Mini Canal | MICL.00908042/RDB | 9 | 80 | 42 | 42 | 278 | 278 | 278 | 0.006619 | 108 | 0.0025714 | 317 | 0.0075476 | 1.362 | A04 | MICL0.00908042/RDB
Build-In Floor | Mini Canal | MICL.00908042/RMN | 9 | 80 | 42 | 42 | 270 | 270 | 270 | 0.0064286 | 105 | 0.0025 | 308 | 0.0073333 | 1.362 | A04 | MICL0.00908042/RMN
Build-In Floor | Mini Canal | MICL.00908042/RMV | 9 | 80 | 42 | 42 | 270 | 270 | 270 | 0.0064286 | 105 | 0.0025 | 308 | 0.0073333 | 1.362 | A04 | MICL0.00908042/RMV
Build-In Floor | Mini Canal | MICL.00908042/RNA | 9 | 80 | 42 | 42 | 278 | 278 | 278 | 0.006619 | 108 | 0.0025714 | 317 | 0.0075476 | 1.362 | A04 | MICL0.00908042/RNA
Build-In Floor | Mini Canal | MICL.00908042/RON | 9 | 80 | 42 | 42 | 270 | 270 | 270 | 0.0064286 | 105 | 0.0025 | 308 | 0.0073333 | 1.362 | A04 | MICL0.00908042/RON
Build-In Floor | Mini Canal | MICL.00908042/ROV | 9 | 80 | 42 | 42 | 270 | 270 | 270 | 0.0064286 | 105 | 0.0025 | 308 | 0.0073333 | 1.362 | A04 | MICL0.00908042/ROV
Build-In Floor | Mini Canal | MICL.00908042/RSS | 9 | 80 | 42 | 42 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00908042/RSS
Build-In Floor | Mini Canal | MICL.00908042/SBL | 9 | 80 | 42 | 42 | 278 | 278 | 278 | 0.006619 | 108 | 0.0025714 | 317 | 0.0075476 | 1.362 | A04 | MICL0.00908042/SBL
Build-In Floor | Mini Canal | MICL.00908042/SBR | 9 | 80 | 42 | 42 | 278 | 278 | 278 | 0.006619 | 108 | 0.0025714 | 317 | 0.0075476 | 1.362 | A04 | MICL0.00908042/SBR
Build-In Floor | Mini Canal | MICL.00908042/SDB | 9 | 80 | 42 | 42 | 278 | 278 | 278 | 0.006619 | 108 | 0.0025714 | 317 | 0.0075476 | 1.362 | A04 | MICL0.00908042/SDB
Build-In Floor | Mini Canal | MICL.00908042/SNA | 9 | 80 | 42 | 42 | 278 | 278 | 278 | 0.006619 | 108 | 0.0025714 | 317 | 0.0075476 | 1.362 | A04 | MICL0.00908042/SNA
Build-In Floor | Mini Canal | MICL.00908042/SNC | 9 | 80 | 42 | 42 | 278 | 278 | 278 | 0.006619 | 108 | 0.0025714 | 317 | 0.0075476 | 1.362 | A04 | MICL0.00908042/SNC
Build-In Floor | Mini Canal | MICL.00909014/ANA | 9 | 90 | 14 | 14 | 86 | 86 | 86 | 0.0020476 | 33 | 0.00078571 | 98 | 0.0023333 | 1.362 | A04 | MICL0.00909014/ANA
Build-In Floor | Mini Canal | MICL.00909014/DBL | 9 | 90 | 14 | 14 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00909014/DBL
Build-In Floor | Mini Canal | MICL.00909014/DBN | 9 | 90 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.00909014/DBN
Build-In Floor | Mini Canal | MICL.00909014/DBR | 9 | 90 | 14 | 14 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00909014/DBR
Build-In Floor | Mini Canal | MICL.00909014/DBV | 9 | 90 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.00909014/DBV
Build-In Floor | Mini Canal | MICL.00909014/DDB | 9 | 90 | 14 | 14 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00909014/DDB
Build-In Floor | Mini Canal | MICL.00909014/DMN | 9 | 90 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.00909014/DMN
Build-In Floor | Mini Canal | MICL.00909014/DMV | 9 | 90 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.00909014/DMV
Build-In Floor | Mini Canal | MICL.00909014/DNA | 9 | 90 | 14 | 14 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00909014/DNA
Build-In Floor | Mini Canal | MICL.00909014/DNC | 9 | 90 | 14 | 14 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00909014/DNC
Build-In Floor | Mini Canal | MICL.00909014/DON | 9 | 90 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.00909014/DON
Build-In Floor | Mini Canal | MICL.00909014/DOV | 9 | 90 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.00909014/DOV
Build-In Floor | Mini Canal | MICL.00909014/RBL | 9 | 90 | 14 | 14 | 114 | 114 | 114 | 0.0027143 | 44 | 0.0010476 | 130 | 0.0030952 | 1.362 | A04 | MICL0.00909014/RBL
Build-In Floor | Mini Canal | MICL.00909014/RBN | 9 | 90 | 14 | 14 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00909014/RBN
Build-In Floor | Mini Canal | MICL.00909014/RBR | 9 | 90 | 14 | 14 | 114 | 114 | 114 | 0.0027143 | 44 | 0.0010476 | 130 | 0.0030952 | 1.362 | A04 | MICL0.00909014/RBR
Build-In Floor | Mini Canal | MICL.00909014/RBV | 9 | 90 | 14 | 14 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00909014/RBV
Build-In Floor | Mini Canal | MICL.00909014/RDB | 9 | 90 | 14 | 14 | 114 | 114 | 114 | 0.0027143 | 44 | 0.0010476 | 130 | 0.0030952 | 1.362 | A04 | MICL0.00909014/RDB
Build-In Floor | Mini Canal | MICL.00909014/RMN | 9 | 90 | 14 | 14 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00909014/RMN
Build-In Floor | Mini Canal | MICL.00909014/RMV | 9 | 90 | 14 | 14 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00909014/RMV
Build-In Floor | Mini Canal | MICL.00909014/RNA | 9 | 90 | 14 | 14 | 114 | 114 | 114 | 0.0027143 | 44 | 0.0010476 | 130 | 0.0030952 | 1.362 | A04 | MICL0.00909014/RNA
Build-In Floor | Mini Canal | MICL.00909014/RON | 9 | 90 | 14 | 14 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00909014/RON
Build-In Floor | Mini Canal | MICL.00909014/ROV | 9 | 90 | 14 | 14 | 111 | 111 | 111 | 0.0026429 | 43 | 0.0010238 | 126 | 0.003 | 1.362 | A04 | MICL0.00909014/ROV
Build-In Floor | Mini Canal | MICL.00909014/RSS | 9 | 90 | 14 | 14 | 109 | 109 | 109 | 0.0025952 | 42 | 0.001 | 124 | 0.0029524 | 1.362 | A04 | MICL0.00909014/RSS
Build-In Floor | Mini Canal | MICL.00909014/SBL | 9 | 90 | 14 | 14 | 114 | 114 | 114 | 0.0027143 | 44 | 0.0010476 | 130 | 0.0030952 | 1.362 | A04 | MICL0.00909014/SBL
Build-In Floor | Mini Canal | MICL.00909014/SBR | 9 | 90 | 14 | 14 | 114 | 114 | 114 | 0.0027143 | 44 | 0.0010476 | 130 | 0.0030952 | 1.362 | A04 | MICL0.00909014/SBR
Build-In Floor | Mini Canal | MICL.00909014/SDB | 9 | 90 | 14 | 14 | 114 | 114 | 114 | 0.0027143 | 44 | 0.0010476 | 130 | 0.0030952 | 1.362 | A04 | MICL0.00909014/SDB
Build-In Floor | Mini Canal | MICL.00909014/SNA | 9 | 90 | 14 | 14 | 114 | 114 | 114 | 0.0027143 | 44 | 0.0010476 | 130 | 0.0030952 | 1.362 | A04 | MICL0.00909014/SNA
Build-In Floor | Mini Canal | MICL.00909014/SNC | 9 | 90 | 14 | 14 | 114 | 114 | 114 | 0.0027143 | 44 | 0.0010476 | 130 | 0.0030952 | 1.362 | A04 | MICL0.00909014/SNC
Build-In Floor | Mini Canal | MICL.00909018/ANA | 9 | 90 | 18 | 18 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.00909018/ANA
Build-In Floor | Mini Canal | MICL.00909018/DBL | 9 | 90 | 18 | 18 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.00909018/DBL
Build-In Floor | Mini Canal | MICL.00909018/DBN | 9 | 90 | 18 | 18 | 126 | 126 | 126 | 0.003 | 49 | 0.0011667 | 144 | 0.0034286 | 1.362 | A04 | MICL0.00909018/DBN
Build-In Floor | Mini Canal | MICL.00909018/DBR | 9 | 90 | 18 | 18 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.00909018/DBR
Build-In Floor | Mini Canal | MICL.00909018/DBV | 9 | 90 | 18 | 18 | 126 | 126 | 126 | 0.003 | 49 | 0.0011667 | 144 | 0.0034286 | 1.362 | A04 | MICL0.00909018/DBV
Build-In Floor | Mini Canal | MICL.00909018/DDB | 9 | 90 | 18 | 18 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.00909018/DDB
Build-In Floor | Mini Canal | MICL.00909018/DMN | 9 | 90 | 18 | 18 | 126 | 126 | 126 | 0.003 | 49 | 0.0011667 | 144 | 0.0034286 | 1.362 | A04 | MICL0.00909018/DMN
Build-In Floor | Mini Canal | MICL.00909018/DMV | 9 | 90 | 18 | 18 | 126 | 126 | 126 | 0.003 | 49 | 0.0011667 | 144 | 0.0034286 | 1.362 | A04 | MICL0.00909018/DMV
Build-In Floor | Mini Canal | MICL.00909018/DNA | 9 | 90 | 18 | 18 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.00909018/DNA
Build-In Floor | Mini Canal | MICL.00909018/DNC | 9 | 90 | 18 | 18 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.00909018/DNC
Build-In Floor | Mini Canal | MICL.00909018/DON | 9 | 90 | 18 | 18 | 126 | 126 | 126 | 0.003 | 49 | 0.0011667 | 144 | 0.0034286 | 1.362 | A04 | MICL0.00909018/DON
Build-In Floor | Mini Canal | MICL.00909018/DOV | 9 | 90 | 18 | 18 | 126 | 126 | 126 | 0.003 | 49 | 0.0011667 | 144 | 0.0034286 | 1.362 | A04 | MICL0.00909018/DOV
Build-In Floor | Mini Canal | MICL.00909018/RBL | 9 | 90 | 18 | 18 | 135 | 135 | 135 | 0.0032143 | 53 | 0.0012619 | 154 | 0.0036667 | 1.362 | A04 | MICL0.00909018/RBL
Build-In Floor | Mini Canal | MICL.00909018/RBN | 9 | 90 | 18 | 18 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.00909018/RBN
Build-In Floor | Mini Canal | MICL.00909018/RBR | 9 | 90 | 18 | 18 | 135 | 135 | 135 | 0.0032143 | 53 | 0.0012619 | 154 | 0.0036667 | 1.362 | A04 | MICL0.00909018/RBR
Build-In Floor | Mini Canal | MICL.00909018/RBV | 9 | 90 | 18 | 18 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.00909018/RBV
Build-In Floor | Mini Canal | MICL.00909018/RDB | 9 | 90 | 18 | 18 | 135 | 135 | 135 | 0.0032143 | 53 | 0.0012619 | 154 | 0.0036667 | 1.362 | A04 | MICL0.00909018/RDB
Build-In Floor | Mini Canal | MICL.00909018/RMN | 9 | 90 | 18 | 18 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.00909018/RMN
Build-In Floor | Mini Canal | MICL.00909018/RMV | 9 | 90 | 18 | 18 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.00909018/RMV
Build-In Floor | Mini Canal | MICL.00909018/RNA | 9 | 90 | 18 | 18 | 135 | 135 | 135 | 0.0032143 | 53 | 0.0012619 | 154 | 0.0036667 | 1.362 | A04 | MICL0.00909018/RNA
Build-In Floor | Mini Canal | MICL.00909018/RON | 9 | 90 | 18 | 18 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.00909018/RON
Build-In Floor | Mini Canal | MICL.00909018/ROV | 9 | 90 | 18 | 18 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.00909018/ROV
Build-In Floor | Mini Canal | MICL.00909018/RSS | 9 | 90 | 18 | 18 | 130 | 130 | 130 | 0.0030952 | 51 | 0.0012143 | 148 | 0.0035238 | 1.362 | A04 | MICL0.00909018/RSS
Build-In Floor | Mini Canal | MICL.00909018/SBL | 9 | 90 | 18 | 18 | 135 | 135 | 135 | 0.0032143 | 53 | 0.0012619 | 154 | 0.0036667 | 1.362 | A04 | MICL0.00909018/SBL
Build-In Floor | Mini Canal | MICL.00909018/SBR | 9 | 90 | 18 | 18 | 135 | 135 | 135 | 0.0032143 | 53 | 0.0012619 | 154 | 0.0036667 | 1.362 | A04 | MICL0.00909018/SBR
Build-In Floor | Mini Canal | MICL.00909018/SDB | 9 | 90 | 18 | 18 | 135 | 135 | 135 | 0.0032143 | 53 | 0.0012619 | 154 | 0.0036667 | 1.362 | A04 | MICL0.00909018/SDB
Build-In Floor | Mini Canal | MICL.00909018/SNA | 9 | 90 | 18 | 18 | 135 | 135 | 135 | 0.0032143 | 53 | 0.0012619 | 154 | 0.0036667 | 1.362 | A04 | MICL0.00909018/SNA
Build-In Floor | Mini Canal | MICL.00909018/SNC | 9 | 90 | 18 | 18 | 135 | 135 | 135 | 0.0032143 | 53 | 0.0012619 | 154 | 0.0036667 | 1.362 | A04 | MICL0.00909018/SNC
Build-In Floor | Mini Canal | MICL.00909026/ANA | 9 | 90 | 26 | 26 | 134 | 134 | 134 | 0.0031905 | 52 | 0.0012381 | 153 | 0.0036429 | 1.362 | A04 | MICL0.00909026/ANA
Build-In Floor | Mini Canal | MICL.00909026/DBL | 9 | 90 | 26 | 26 | 173 | 173 | 173 | 0.004119 | 67 | 0.0015952 | 197 | 0.0046905 | 1.362 | A04 | MICL0.00909026/DBL
Build-In Floor | Mini Canal | MICL.00909026/DBN | 9 | 90 | 26 | 26 | 166 | 166 | 166 | 0.0039524 | 65 | 0.0015476 | 189 | 0.0045 | 1.362 | A04 | MICL0.00909026/DBN
Build-In Floor | Mini Canal | MICL.00909026/DBR | 9 | 90 | 26 | 26 | 173 | 173 | 173 | 0.004119 | 67 | 0.0015952 | 197 | 0.0046905 | 1.362 | A04 | MICL0.00909026/DBR
Build-In Floor | Mini Canal | MICL.00909026/DBV | 9 | 90 | 26 | 26 | 166 | 166 | 166 | 0.0039524 | 65 | 0.0015476 | 189 | 0.0045 | 1.362 | A04 | MICL0.00909026/DBV
Build-In Floor | Mini Canal | MICL.00909026/DDB | 9 | 90 | 26 | 26 | 173 | 173 | 173 | 0.004119 | 67 | 0.0015952 | 197 | 0.0046905 | 1.362 | A04 | MICL0.00909026/DDB
Build-In Floor | Mini Canal | MICL.00909026/DMN | 9 | 90 | 26 | 26 | 166 | 166 | 166 | 0.0039524 | 65 | 0.0015476 | 189 | 0.0045 | 1.362 | A04 | MICL0.00909026/DMN
Build-In Floor | Mini Canal | MICL.00909026/DMV | 9 | 90 | 26 | 26 | 166 | 166 | 166 | 0.0039524 | 65 | 0.0015476 | 189 | 0.0045 | 1.362 | A04 | MICL0.00909026/DMV
Build-In Floor | Mini Canal | MICL.00909026/DNA | 9 | 90 | 26 | 26 | 173 | 173 | 173 | 0.004119 | 67 | 0.0015952 | 197 | 0.0046905 | 1.362 | A04 | MICL0.00909026/DNA
Build-In Floor | Mini Canal | MICL.00909026/DNC | 9 | 90 | 26 | 26 | 173 | 173 | 173 | 0.004119 | 67 | 0.0015952 | 197 | 0.0046905 | 1.362 | A04 | MICL0.00909026/DNC
Build-In Floor | Mini Canal | MICL.00909026/DON | 9 | 90 | 26 | 26 | 166 | 166 | 166 | 0.0039524 | 65 | 0.0015476 | 189 | 0.0045 | 1.362 | A04 | MICL0.00909026/DON
Build-In Floor | Mini Canal | MICL.00909026/DOV | 9 | 90 | 26 | 26 | 166 | 166 | 166 | 0.0039524 | 65 | 0.0015476 | 189 | 0.0045 | 1.362 | A04 | MICL0.00909026/DOV
Build-In Floor | Mini Canal | MICL.00909026/PNC | 9 | 90 | 26 | 26 | 151 | 151 | 151 | 0.0035952 | 59 | 0.0014048 | 172 | 0.0040952 | 1.362 | A04 | MICL0.00909026/PNC
Build-In Floor | Mini Canal | MICL.00909026/RBL | 9 | 90 | 26 | 26 | 178 | 178 | 178 | 0.0042381 | 69 | 0.0016429 | 203 | 0.0048333 | 1.362 | A04 | MICL0.00909026/RBL
Build-In Floor | Mini Canal | MICL.00909026/RBN | 9 | 90 | 26 | 26 | 173 | 173 | 173 | 0.004119 | 67 | 0.0015952 | 197 | 0.0046905 | 1.362 | A04 | MICL0.00909026/RBN
Build-In Floor | Mini Canal | MICL.00909026/RBR | 9 | 90 | 26 | 26 | 178 | 178 | 178 | 0.0042381 | 69 | 0.0016429 | 203 | 0.0048333 | 1.362 | A04 | MICL0.00909026/RBR
Build-In Floor | Mini Canal | MICL.00909026/RBV | 9 | 90 | 26 | 26 | 173 | 173 | 173 | 0.004119 | 67 | 0.0015952 | 197 | 0.0046905 | 1.362 | A04 | MICL0.00909026/RBV
Build-In Floor | Mini Canal | MICL.00909026/RDB | 9 | 90 | 26 | 26 | 178 | 178 | 178 | 0.0042381 | 69 | 0.0016429 | 203 | 0.0048333 | 1.362 | A04 | MICL0.00909026/RDB
Build-In Floor | Mini Canal | MICL.00909026/RMN | 9 | 90 | 26 | 26 | 173 | 173 | 173 | 0.004119 | 67 | 0.0015952 | 197 | 0.0046905 | 1.362 | A04 | MICL0.00909026/RMN
Build-In Floor | Mini Canal | MICL.00909026/RMV | 9 | 90 | 26 | 26 | 173 | 173 | 173 | 0.004119 | 67 | 0.0015952 | 197 | 0.0046905 | 1.362 | A04 | MICL0.00909026/RMV
Build-In Floor | Mini Canal | MICL.00909026/RNA | 9 | 90 | 26 | 26 | 178 | 178 | 178 | 0.0042381 | 69 | 0.0016429 | 203 | 0.0048333 | 1.362 | A04 | MICL0.00909026/RNA
Build-In Floor | Mini Canal | MICL.00909026/RON | 9 | 90 | 26 | 26 | 173 | 173 | 173 | 0.004119 | 67 | 0.0015952 | 197 | 0.0046905 | 1.362 | A04 | MICL0.00909026/RON
Build-In Floor | Mini Canal | MICL.00909026/ROV | 9 | 90 | 26 | 26 | 173 | 173 | 173 | 0.004119 | 67 | 0.0015952 | 197 | 0.0046905 | 1.362 | A04 | MICL0.00909026/ROV
Build-In Floor | Mini Canal | MICL.00909026/RSS | 9 | 90 | 26 | 26 | 171 | 171 | 171 | 0.0040714 | 67 | 0.0015952 | 195 | 0.0046429 | 1.362 | A04 | MICL0.00909026/RSS
Build-In Floor | Mini Canal | MICL.00909026/SBL | 9 | 90 | 26 | 26 | 178 | 178 | 178 | 0.0042381 | 69 | 0.0016429 | 203 | 0.0048333 | 1.362 | A04 | MICL0.00909026/SBL
Build-In Floor | Mini Canal | MICL.00909026/SBR | 9 | 90 | 26 | 26 | 178 | 178 | 178 | 0.0042381 | 69 | 0.0016429 | 203 | 0.0048333 | 1.362 | A04 | MICL0.00909026/SBR
Build-In Floor | Mini Canal | MICL.00909026/SDB | 9 | 90 | 26 | 26 | 178 | 178 | 178 | 0.0042381 | 69 | 0.0016429 | 203 | 0.0048333 | 1.362 | A04 | MICL0.00909026/SDB
Build-In Floor | Mini Canal | MICL.00909026/SNA | 9 | 90 | 26 | 26 | 178 | 178 | 178 | 0.0042381 | 69 | 0.0016429 | 203 | 0.0048333 | 1.362 | A04 | MICL0.00909026/SNA
Build-In Floor | Mini Canal | MICL.00909026/SNC | 9 | 90 | 26 | 26 | 178 | 178 | 178 | 0.0042381 | 69 | 0.0016429 | 203 | 0.0048333 | 1.362 | A04 | MICL0.00909026/SNC
Build-In Floor | Mini Canal | MICL.00909034/ANA | 9 | 90 | 34 | 34 | 173 | 173 | 173 | 0.004119 | 67 | 0.0015952 | 197 | 0.0046905 | 1.362 | A04 | MICL0.00909034/ANA
Build-In Floor | Mini Canal | MICL.00909034/DBL | 9 | 90 | 34 | 34 | 224 | 224 | 224 | 0.0053333 | 87 | 0.0020714 | 255 | 0.0060714 | 1.362 | A04 | MICL0.00909034/DBL
Build-In Floor | Mini Canal | MICL.00909034/DBN | 9 | 90 | 34 | 34 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00909034/DBN
Build-In Floor | Mini Canal | MICL.00909034/DBR | 9 | 90 | 34 | 34 | 224 | 224 | 224 | 0.0053333 | 87 | 0.0020714 | 255 | 0.0060714 | 1.362 | A04 | MICL0.00909034/DBR
Build-In Floor | Mini Canal | MICL.00909034/DBV | 9 | 90 | 34 | 34 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00909034/DBV
Build-In Floor | Mini Canal | MICL.00909034/DDB | 9 | 90 | 34 | 34 | 224 | 224 | 224 | 0.0053333 | 87 | 0.0020714 | 255 | 0.0060714 | 1.362 | A04 | MICL0.00909034/DDB
Build-In Floor | Mini Canal | MICL.00909034/DMN | 9 | 90 | 34 | 34 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00909034/DMN
Build-In Floor | Mini Canal | MICL.00909034/DMV | 9 | 90 | 34 | 34 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00909034/DMV
Build-In Floor | Mini Canal | MICL.00909034/DNA | 9 | 90 | 34 | 34 | 224 | 224 | 224 | 0.0053333 | 87 | 0.0020714 | 255 | 0.0060714 | 1.362 | A04 | MICL0.00909034/DNA
Build-In Floor | Mini Canal | MICL.00909034/DNC | 9 | 90 | 34 | 34 | 224 | 224 | 224 | 0.0053333 | 87 | 0.0020714 | 255 | 0.0060714 | 1.362 | A04 | MICL0.00909034/DNC
Build-In Floor | Mini Canal | MICL.00909034/DON | 9 | 90 | 34 | 34 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00909034/DON
Build-In Floor | Mini Canal | MICL.00909034/DOV | 9 | 90 | 34 | 34 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.00909034/DOV
Build-In Floor | Mini Canal | MICL.00909034/PNC | 9 | 90 | 34 | 34 | 196 | 196 | 196 | 0.0046667 | 76 | 0.0018095 | 223 | 0.0053095 | 1.362 | A04 | MICL0.00909034/PNC
Build-In Floor | Mini Canal | MICL.00909034/RBL | 9 | 90 | 34 | 34 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.00909034/RBL
Build-In Floor | Mini Canal | MICL.00909034/RBN | 9 | 90 | 34 | 34 | 224 | 224 | 224 | 0.0053333 | 87 | 0.0020714 | 255 | 0.0060714 | 1.362 | A04 | MICL0.00909034/RBN
Build-In Floor | Mini Canal | MICL.00909034/RBR | 9 | 90 | 34 | 34 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.00909034/RBR
Build-In Floor | Mini Canal | MICL.00909034/RBV | 9 | 90 | 34 | 34 | 224 | 224 | 224 | 0.0053333 | 87 | 0.0020714 | 255 | 0.0060714 | 1.362 | A04 | MICL0.00909034/RBV
Build-In Floor | Mini Canal | MICL.00909034/RDB | 9 | 90 | 34 | 34 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.00909034/RDB
Build-In Floor | Mini Canal | MICL.00909034/RMN | 9 | 90 | 34 | 34 | 224 | 224 | 224 | 0.0053333 | 87 | 0.0020714 | 255 | 0.0060714 | 1.362 | A04 | MICL0.00909034/RMN
Build-In Floor | Mini Canal | MICL.00909034/RMV | 9 | 90 | 34 | 34 | 224 | 224 | 224 | 0.0053333 | 87 | 0.0020714 | 255 | 0.0060714 | 1.362 | A04 | MICL0.00909034/RMV
Build-In Floor | Mini Canal | MICL.00909034/RNA | 9 | 90 | 34 | 34 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.00909034/RNA
Build-In Floor | Mini Canal | MICL.00909034/RON | 9 | 90 | 34 | 34 | 224 | 224 | 224 | 0.0053333 | 87 | 0.0020714 | 255 | 0.0060714 | 1.362 | A04 | MICL0.00909034/RON
Build-In Floor | Mini Canal | MICL.00909034/ROV | 9 | 90 | 34 | 34 | 224 | 224 | 224 | 0.0053333 | 87 | 0.0020714 | 255 | 0.0060714 | 1.362 | A04 | MICL0.00909034/ROV
Build-In Floor | Mini Canal | MICL.00909034/RSS | 9 | 90 | 34 | 34 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00909034/RSS
Build-In Floor | Mini Canal | MICL.00909034/SBL | 9 | 90 | 34 | 34 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.00909034/SBL
Build-In Floor | Mini Canal | MICL.00909034/SBR | 9 | 90 | 34 | 34 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.00909034/SBR
Build-In Floor | Mini Canal | MICL.00909034/SDB | 9 | 90 | 34 | 34 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.00909034/SDB
Build-In Floor | Mini Canal | MICL.00909034/SNA | 9 | 90 | 34 | 34 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.00909034/SNA
Build-In Floor | Mini Canal | MICL.00909034/SNC | 9 | 90 | 34 | 34 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.00909034/SNC
Build-In Floor | Mini Canal | MICL.00909042/ANA | 9 | 90 | 42 | 42 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.00909042/ANA
Build-In Floor | Mini Canal | MICL.00909042/DBL | 9 | 90 | 42 | 42 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.00909042/DBL
Build-In Floor | Mini Canal | MICL.00909042/DBN | 9 | 90 | 42 | 42 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.00909042/DBN
Build-In Floor | Mini Canal | MICL.00909042/DBR | 9 | 90 | 42 | 42 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.00909042/DBR
Build-In Floor | Mini Canal | MICL.00909042/DBV | 9 | 90 | 42 | 42 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.00909042/DBV
Build-In Floor | Mini Canal | MICL.00909042/DDB | 9 | 90 | 42 | 42 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.00909042/DDB
Build-In Floor | Mini Canal | MICL.00909042/DMN | 9 | 90 | 42 | 42 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.00909042/DMN
Build-In Floor | Mini Canal | MICL.00909042/DMV | 9 | 90 | 42 | 42 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.00909042/DMV
Build-In Floor | Mini Canal | MICL.00909042/DNA | 9 | 90 | 42 | 42 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.00909042/DNA
Build-In Floor | Mini Canal | MICL.00909042/DNC | 9 | 90 | 42 | 42 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.00909042/DNC
Build-In Floor | Mini Canal | MICL.00909042/DON | 9 | 90 | 42 | 42 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.00909042/DON
Build-In Floor | Mini Canal | MICL.00909042/DOV | 9 | 90 | 42 | 42 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.00909042/DOV
Build-In Floor | Mini Canal | MICL.00909042/PNC | 9 | 90 | 42 | 42 | 283 | 283 | 283 | 0.0067381 | 110 | 0.002619 | 322 | 0.0076667 | 1.362 | A04 | MICL0.00909042/PNC
Build-In Floor | Mini Canal | MICL.00909042/RBL | 9 | 90 | 42 | 42 | 333 | 333 | 333 | 0.0079286 | 130 | 0.0030952 | 379 | 0.0090238 | 1.362 | A04 | MICL0.00909042/RBL
Build-In Floor | Mini Canal | MICL.00909042/RBN | 9 | 90 | 42 | 42 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.00909042/RBN
Build-In Floor | Mini Canal | MICL.00909042/RBR | 9 | 90 | 42 | 42 | 333 | 333 | 333 | 0.0079286 | 130 | 0.0030952 | 379 | 0.0090238 | 1.362 | A04 | MICL0.00909042/RBR
Build-In Floor | Mini Canal | MICL.00909042/RBV | 9 | 90 | 42 | 42 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.00909042/RBV
Build-In Floor | Mini Canal | MICL.00909042/RDB | 9 | 90 | 42 | 42 | 333 | 333 | 333 | 0.0079286 | 130 | 0.0030952 | 379 | 0.0090238 | 1.362 | A04 | MICL0.00909042/RDB
Build-In Floor | Mini Canal | MICL.00909042/RMN | 9 | 90 | 42 | 42 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.00909042/RMN
Build-In Floor | Mini Canal | MICL.00909042/RMV | 9 | 90 | 42 | 42 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.00909042/RMV
Build-In Floor | Mini Canal | MICL.00909042/RNA | 9 | 90 | 42 | 42 | 333 | 333 | 333 | 0.0079286 | 130 | 0.0030952 | 379 | 0.0090238 | 1.362 | A04 | MICL0.00909042/RNA
Build-In Floor | Mini Canal | MICL.00909042/RON | 9 | 90 | 42 | 42 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.00909042/RON
Build-In Floor | Mini Canal | MICL.00909042/ROV | 9 | 90 | 42 | 42 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.00909042/ROV
Build-In Floor | Mini Canal | MICL.00909042/RSS | 9 | 90 | 42 | 42 | 320 | 320 | 320 | 0.007619 | 124 | 0.0029524 | 364 | 0.0086667 | 1.362 | A04 | MICL0.00909042/RSS
Build-In Floor | Mini Canal | MICL.00909042/SBL | 9 | 90 | 42 | 42 | 333 | 333 | 333 | 0.0079286 | 130 | 0.0030952 | 379 | 0.0090238 | 1.362 | A04 | MICL0.00909042/SBL
Build-In Floor | Mini Canal | MICL.00909042/SBR | 9 | 90 | 42 | 42 | 333 | 333 | 333 | 0.0079286 | 130 | 0.0030952 | 379 | 0.0090238 | 1.362 | A04 | MICL0.00909042/SBR
Build-In Floor | Mini Canal | MICL.00909042/SDB | 9 | 90 | 42 | 42 | 333 | 333 | 333 | 0.0079286 | 130 | 0.0030952 | 379 | 0.0090238 | 1.362 | A04 | MICL0.00909042/SDB
Build-In Floor | Mini Canal | MICL.00909042/SNA | 9 | 90 | 42 | 42 | 333 | 333 | 333 | 0.0079286 | 130 | 0.0030952 | 379 | 0.0090238 | 1.362 | A04 | MICL0.00909042/SNA
Build-In Floor | Mini Canal | MICL.00909042/SNC | 9 | 90 | 42 | 42 | 333 | 333 | 333 | 0.0079286 | 130 | 0.0030952 | 379 | 0.0090238 | 1.362 | A04 | MICL0.00909042/SNC
Build-In Floor | Mini Canal | MICL.00910014/ANA | 9 | 100 | 14 | 14 | 100 | 100 | 100 | 0.002381 | 39 | 0.00092857 | 114 | 0.0027143 | 1.362 | A04 | MICL0.00910014/ANA
Build-In Floor | Mini Canal | MICL.00910014/DBL | 9 | 100 | 14 | 14 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.00910014/DBL
Build-In Floor | Mini Canal | MICL.00910014/DBN | 9 | 100 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.00910014/DBN
Build-In Floor | Mini Canal | MICL.00910014/DBR | 9 | 100 | 14 | 14 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.00910014/DBR
Build-In Floor | Mini Canal | MICL.00910014/DBV | 9 | 100 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.00910014/DBV
Build-In Floor | Mini Canal | MICL.00910014/DDB | 9 | 100 | 14 | 14 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.00910014/DDB
Build-In Floor | Mini Canal | MICL.00910014/DMN | 9 | 100 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.00910014/DMN
Build-In Floor | Mini Canal | MICL.00910014/DMV | 9 | 100 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.00910014/DMV
Build-In Floor | Mini Canal | MICL.00910014/DNA | 9 | 100 | 14 | 14 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.00910014/DNA
Build-In Floor | Mini Canal | MICL.00910014/DNC | 9 | 100 | 14 | 14 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.00910014/DNC
Build-In Floor | Mini Canal | MICL.00910014/DON | 9 | 100 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.00910014/DON
Build-In Floor | Mini Canal | MICL.00910014/DOV | 9 | 100 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.00910014/DOV
Build-In Floor | Mini Canal | MICL.00910014/RBL | 9 | 100 | 14 | 14 | 133 | 133 | 133 | 0.0031667 | 52 | 0.0012381 | 151 | 0.0035952 | 1.362 | A04 | MICL0.00910014/RBL
Build-In Floor | Mini Canal | MICL.00910014/RBN | 9 | 100 | 14 | 14 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.00910014/RBN
Build-In Floor | Mini Canal | MICL.00910014/RBR | 9 | 100 | 14 | 14 | 133 | 133 | 133 | 0.0031667 | 52 | 0.0012381 | 151 | 0.0035952 | 1.362 | A04 | MICL0.00910014/RBR
Build-In Floor | Mini Canal | MICL.00910014/RBV | 9 | 100 | 14 | 14 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.00910014/RBV
Build-In Floor | Mini Canal | MICL.00910014/RDB | 9 | 100 | 14 | 14 | 133 | 133 | 133 | 0.0031667 | 52 | 0.0012381 | 151 | 0.0035952 | 1.362 | A04 | MICL0.00910014/RDB
Build-In Floor | Mini Canal | MICL.00910014/RMN | 9 | 100 | 14 | 14 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.00910014/RMN
Build-In Floor | Mini Canal | MICL.00910014/RMV | 9 | 100 | 14 | 14 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.00910014/RMV
Build-In Floor | Mini Canal | MICL.00910014/RNA | 9 | 100 | 14 | 14 | 133 | 133 | 133 | 0.0031667 | 52 | 0.0012381 | 151 | 0.0035952 | 1.362 | A04 | MICL0.00910014/RNA
Build-In Floor | Mini Canal | MICL.00910014/RON | 9 | 100 | 14 | 14 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.00910014/RON
Build-In Floor | Mini Canal | MICL.00910014/ROV | 9 | 100 | 14 | 14 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.00910014/ROV
Build-In Floor | Mini Canal | MICL.00910014/RSS | 9 | 100 | 14 | 14 | 128 | 128 | 128 | 0.0030476 | 50 | 0.0011905 | 146 | 0.0034762 | 1.362 | A04 | MICL0.00910014/RSS
Build-In Floor | Mini Canal | MICL.00910014/SBL | 9 | 100 | 14 | 14 | 133 | 133 | 133 | 0.0031667 | 52 | 0.0012381 | 151 | 0.0035952 | 1.362 | A04 | MICL0.00910014/SBL
Build-In Floor | Mini Canal | MICL.00910014/SBR | 9 | 100 | 14 | 14 | 133 | 133 | 133 | 0.0031667 | 52 | 0.0012381 | 151 | 0.0035952 | 1.362 | A04 | MICL0.00910014/SBR
Build-In Floor | Mini Canal | MICL.00910014/SDB | 9 | 100 | 14 | 14 | 133 | 133 | 133 | 0.0031667 | 52 | 0.0012381 | 151 | 0.0035952 | 1.362 | A04 | MICL0.00910014/SDB
Build-In Floor | Mini Canal | MICL.00910014/SNA | 9 | 100 | 14 | 14 | 133 | 133 | 133 | 0.0031667 | 52 | 0.0012381 | 151 | 0.0035952 | 1.362 | A04 | MICL0.00910014/SNA
Build-In Floor | Mini Canal | MICL.00910014/SNC | 9 | 100 | 14 | 14 | 133 | 133 | 133 | 0.0031667 | 52 | 0.0012381 | 151 | 0.0035952 | 1.362 | A04 | MICL0.00910014/SNC
Build-In Floor | Mini Canal | MICL.00910018/ANA | 9 | 100 | 18 | 18 | 119 | 119 | 119 | 0.0028333 | 46 | 0.0010952 | 136 | 0.0032381 | 1.362 | A04 | MICL0.00910018/ANA
Build-In Floor | Mini Canal | MICL.00910018/DBL | 9 | 100 | 18 | 18 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.00910018/DBL
Build-In Floor | Mini Canal | MICL.00910018/DBN | 9 | 100 | 18 | 18 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00910018/DBN
Build-In Floor | Mini Canal | MICL.00910018/DBR | 9 | 100 | 18 | 18 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.00910018/DBR
Build-In Floor | Mini Canal | MICL.00910018/DBV | 9 | 100 | 18 | 18 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00910018/DBV
Build-In Floor | Mini Canal | MICL.00910018/DDB | 9 | 100 | 18 | 18 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.00910018/DDB
Build-In Floor | Mini Canal | MICL.00910018/DMN | 9 | 100 | 18 | 18 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00910018/DMN
Build-In Floor | Mini Canal | MICL.00910018/DMV | 9 | 100 | 18 | 18 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00910018/DMV
Build-In Floor | Mini Canal | MICL.00910018/DNA | 9 | 100 | 18 | 18 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.00910018/DNA
Build-In Floor | Mini Canal | MICL.00910018/DNC | 9 | 100 | 18 | 18 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.00910018/DNC
Build-In Floor | Mini Canal | MICL.00910018/DON | 9 | 100 | 18 | 18 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00910018/DON
Build-In Floor | Mini Canal | MICL.00910018/DOV | 9 | 100 | 18 | 18 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00910018/DOV
Build-In Floor | Mini Canal | MICL.00910018/RBL | 9 | 100 | 18 | 18 | 158 | 158 | 158 | 0.0037619 | 61 | 0.0014524 | 180 | 0.0042857 | 1.362 | A04 | MICL0.00910018/RBL
Build-In Floor | Mini Canal | MICL.00910018/RBN | 9 | 100 | 18 | 18 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.00910018/RBN
Build-In Floor | Mini Canal | MICL.00910018/RBR | 9 | 100 | 18 | 18 | 158 | 158 | 158 | 0.0037619 | 61 | 0.0014524 | 180 | 0.0042857 | 1.362 | A04 | MICL0.00910018/RBR
Build-In Floor | Mini Canal | MICL.00910018/RBV | 9 | 100 | 18 | 18 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.00910018/RBV
Build-In Floor | Mini Canal | MICL.00910018/RDB | 9 | 100 | 18 | 18 | 158 | 158 | 158 | 0.0037619 | 61 | 0.0014524 | 180 | 0.0042857 | 1.362 | A04 | MICL0.00910018/RDB
Build-In Floor | Mini Canal | MICL.00910018/RMN | 9 | 100 | 18 | 18 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.00910018/RMN
Build-In Floor | Mini Canal | MICL.00910018/RMV | 9 | 100 | 18 | 18 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.00910018/RMV
Build-In Floor | Mini Canal | MICL.00910018/RNA | 9 | 100 | 18 | 18 | 158 | 158 | 158 | 0.0037619 | 61 | 0.0014524 | 180 | 0.0042857 | 1.362 | A04 | MICL0.00910018/RNA
Build-In Floor | Mini Canal | MICL.00910018/RON | 9 | 100 | 18 | 18 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.00910018/RON
Build-In Floor | Mini Canal | MICL.00910018/ROV | 9 | 100 | 18 | 18 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.00910018/ROV
Build-In Floor | Mini Canal | MICL.00910018/RSS | 9 | 100 | 18 | 18 | 152 | 152 | 152 | 0.003619 | 59 | 0.0014048 | 173 | 0.004119 | 1.362 | A04 | MICL0.00910018/RSS
Build-In Floor | Mini Canal | MICL.00910018/SBL | 9 | 100 | 18 | 18 | 158 | 158 | 158 | 0.0037619 | 61 | 0.0014524 | 180 | 0.0042857 | 1.362 | A04 | MICL0.00910018/SBL
Build-In Floor | Mini Canal | MICL.00910018/SBR | 9 | 100 | 18 | 18 | 158 | 158 | 158 | 0.0037619 | 61 | 0.0014524 | 180 | 0.0042857 | 1.362 | A04 | MICL0.00910018/SBR
Build-In Floor | Mini Canal | MICL.00910018/SDB | 9 | 100 | 18 | 18 | 158 | 158 | 158 | 0.0037619 | 61 | 0.0014524 | 180 | 0.0042857 | 1.362 | A04 | MICL0.00910018/SDB
Build-In Floor | Mini Canal | MICL.00910018/SNA | 9 | 100 | 18 | 18 | 158 | 158 | 158 | 0.0037619 | 61 | 0.0014524 | 180 | 0.0042857 | 1.362 | A04 | MICL0.00910018/SNA
Build-In Floor | Mini Canal | MICL.00910018/SNC | 9 | 100 | 18 | 18 | 158 | 158 | 158 | 0.0037619 | 61 | 0.0014524 | 180 | 0.0042857 | 1.362 | A04 | MICL0.00910018/SNC
Build-In Floor | Mini Canal | MICL.00910026/ANA | 9 | 100 | 26 | 26 | 155 | 155 | 155 | 0.0036905 | 60 | 0.0014286 | 177 | 0.0042143 | 1.362 | A04 | MICL0.00910026/ANA
Build-In Floor | Mini Canal | MICL.00910026/DBL | 9 | 100 | 26 | 26 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.00910026/DBL
Build-In Floor | Mini Canal | MICL.00910026/DBN | 9 | 100 | 26 | 26 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00910026/DBN
Build-In Floor | Mini Canal | MICL.00910026/DBR | 9 | 100 | 26 | 26 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.00910026/DBR
Build-In Floor | Mini Canal | MICL.00910026/DBV | 9 | 100 | 26 | 26 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00910026/DBV
Build-In Floor | Mini Canal | MICL.00910026/DDB | 9 | 100 | 26 | 26 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.00910026/DDB
Build-In Floor | Mini Canal | MICL.00910026/DMN | 9 | 100 | 26 | 26 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00910026/DMN
Build-In Floor | Mini Canal | MICL.00910026/DMV | 9 | 100 | 26 | 26 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00910026/DMV
Build-In Floor | Mini Canal | MICL.00910026/DNA | 9 | 100 | 26 | 26 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.00910026/DNA
Build-In Floor | Mini Canal | MICL.00910026/DNC | 9 | 100 | 26 | 26 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.00910026/DNC
Build-In Floor | Mini Canal | MICL.00910026/DON | 9 | 100 | 26 | 26 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00910026/DON
Build-In Floor | Mini Canal | MICL.00910026/DOV | 9 | 100 | 26 | 26 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.00910026/DOV
Build-In Floor | Mini Canal | MICL.00910026/PNC | 9 | 100 | 26 | 26 | 176 | 176 | 176 | 0.0041905 | 68 | 0.001619 | 200 | 0.0047619 | 1.362 | A04 | MICL0.00910026/PNC
Build-In Floor | Mini Canal | MICL.00910026/RBL | 9 | 100 | 26 | 26 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.00910026/RBL
Build-In Floor | Mini Canal | MICL.00910026/RBN | 9 | 100 | 26 | 26 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.00910026/RBN
Build-In Floor | Mini Canal | MICL.00910026/RBR | 9 | 100 | 26 | 26 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.00910026/RBR
Build-In Floor | Mini Canal | MICL.00910026/RBV | 9 | 100 | 26 | 26 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.00910026/RBV
Build-In Floor | Mini Canal | MICL.00910026/RDB | 9 | 100 | 26 | 26 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.00910026/RDB
Build-In Floor | Mini Canal | MICL.00910026/RMN | 9 | 100 | 26 | 26 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.00910026/RMN
Build-In Floor | Mini Canal | MICL.00910026/RMV | 9 | 100 | 26 | 26 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.00910026/RMV
Build-In Floor | Mini Canal | MICL.00910026/RNA | 9 | 100 | 26 | 26 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.00910026/RNA
Build-In Floor | Mini Canal | MICL.00910026/RON | 9 | 100 | 26 | 26 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.00910026/RON
Build-In Floor | Mini Canal | MICL.00910026/ROV | 9 | 100 | 26 | 26 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.00910026/ROV
Build-In Floor | Mini Canal | MICL.00910026/RSS | 9 | 100 | 26 | 26 | 199 | 199 | 199 | 0.0047381 | 77 | 0.0018333 | 227 | 0.0054048 | 1.362 | A04 | MICL0.00910026/RSS
Build-In Floor | Mini Canal | MICL.00910026/SBL | 9 | 100 | 26 | 26 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.00910026/SBL
Build-In Floor | Mini Canal | MICL.00910026/SBR | 9 | 100 | 26 | 26 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.00910026/SBR
Build-In Floor | Mini Canal | MICL.00910026/SDB | 9 | 100 | 26 | 26 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.00910026/SDB
Build-In Floor | Mini Canal | MICL.00910026/SNA | 9 | 100 | 26 | 26 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.00910026/SNA
Build-In Floor | Mini Canal | MICL.00910026/SNC | 9 | 100 | 26 | 26 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.00910026/SNC
Build-In Floor | Mini Canal | MICL.00910034/ANA | 9 | 100 | 34 | 34 | 202 | 202 | 202 | 0.0048095 | 79 | 0.001881 | 230 | 0.0054762 | 1.362 | A04 | MICL0.00910034/ANA
Build-In Floor | Mini Canal | MICL.00910034/DBL | 9 | 100 | 34 | 34 | 261 | 261 | 261 | 0.0062143 | 102 | 0.0024286 | 297 | 0.0070714 | 1.362 | A04 | MICL0.00910034/DBL
Build-In Floor | Mini Canal | MICL.00910034/DBN | 9 | 100 | 34 | 34 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.00910034/DBN
Build-In Floor | Mini Canal | MICL.00910034/DBR | 9 | 100 | 34 | 34 | 261 | 261 | 261 | 0.0062143 | 102 | 0.0024286 | 297 | 0.0070714 | 1.362 | A04 | MICL0.00910034/DBR
Build-In Floor | Mini Canal | MICL.00910034/DBV | 9 | 100 | 34 | 34 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.00910034/DBV
Build-In Floor | Mini Canal | MICL.00910034/DDB | 9 | 100 | 34 | 34 | 261 | 261 | 261 | 0.0062143 | 102 | 0.0024286 | 297 | 0.0070714 | 1.362 | A04 | MICL0.00910034/DDB
Build-In Floor | Mini Canal | MICL.00910034/DMN | 9 | 100 | 34 | 34 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.00910034/DMN
Build-In Floor | Mini Canal | MICL.00910034/DMV | 9 | 100 | 34 | 34 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.00910034/DMV
Build-In Floor | Mini Canal | MICL.00910034/DNA | 9 | 100 | 34 | 34 | 261 | 261 | 261 | 0.0062143 | 102 | 0.0024286 | 297 | 0.0070714 | 1.362 | A04 | MICL0.00910034/DNA
Build-In Floor | Mini Canal | MICL.00910034/DNC | 9 | 100 | 34 | 34 | 261 | 261 | 261 | 0.0062143 | 102 | 0.0024286 | 297 | 0.0070714 | 1.362 | A04 | MICL0.00910034/DNC
Build-In Floor | Mini Canal | MICL.00910034/DON | 9 | 100 | 34 | 34 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.00910034/DON
Build-In Floor | Mini Canal | MICL.00910034/DOV | 9 | 100 | 34 | 34 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.00910034/DOV
Build-In Floor | Mini Canal | MICL.00910034/PNC | 9 | 100 | 34 | 34 | 229 | 229 | 229 | 0.0054524 | 89 | 0.002119 | 261 | 0.0062143 | 1.362 | A04 | MICL0.00910034/PNC
Build-In Floor | Mini Canal | MICL.00910034/RBL | 9 | 100 | 34 | 34 | 269 | 269 | 269 | 0.0064048 | 105 | 0.0025 | 306 | 0.0072857 | 1.362 | A04 | MICL0.00910034/RBL
Build-In Floor | Mini Canal | MICL.00910034/RBN | 9 | 100 | 34 | 34 | 261 | 261 | 261 | 0.0062143 | 102 | 0.0024286 | 297 | 0.0070714 | 1.362 | A04 | MICL0.00910034/RBN
Build-In Floor | Mini Canal | MICL.00910034/RBR | 9 | 100 | 34 | 34 | 269 | 269 | 269 | 0.0064048 | 105 | 0.0025 | 306 | 0.0072857 | 1.362 | A04 | MICL0.00910034/RBR
Build-In Floor | Mini Canal | MICL.00910034/RBV | 9 | 100 | 34 | 34 | 261 | 261 | 261 | 0.0062143 | 102 | 0.0024286 | 297 | 0.0070714 | 1.362 | A04 | MICL0.00910034/RBV
Build-In Floor | Mini Canal | MICL.00910034/RDB | 9 | 100 | 34 | 34 | 269 | 269 | 269 | 0.0064048 | 105 | 0.0025 | 306 | 0.0072857 | 1.362 | A04 | MICL0.00910034/RDB
Build-In Floor | Mini Canal | MICL.00910034/RMN | 9 | 100 | 34 | 34 | 261 | 261 | 261 | 0.0062143 | 102 | 0.0024286 | 297 | 0.0070714 | 1.362 | A04 | MICL0.00910034/RMN
Build-In Floor | Mini Canal | MICL.00910034/RMV | 9 | 100 | 34 | 34 | 261 | 261 | 261 | 0.0062143 | 102 | 0.0024286 | 297 | 0.0070714 | 1.362 | A04 | MICL0.00910034/RMV
Build-In Floor | Mini Canal | MICL.00910034/RNA | 9 | 100 | 34 | 34 | 269 | 269 | 269 | 0.0064048 | 105 | 0.0025 | 306 | 0.0072857 | 1.362 | A04 | MICL0.00910034/RNA
Build-In Floor | Mini Canal | MICL.00910034/RON | 9 | 100 | 34 | 34 | 261 | 261 | 261 | 0.0062143 | 102 | 0.0024286 | 297 | 0.0070714 | 1.362 | A04 | MICL0.00910034/RON
Build-In Floor | Mini Canal | MICL.00910034/ROV | 9 | 100 | 34 | 34 | 261 | 261 | 261 | 0.0062143 | 102 | 0.0024286 | 297 | 0.0070714 | 1.362 | A04 | MICL0.00910034/ROV
Build-In Floor | Mini Canal | MICL.00910034/RSS | 9 | 100 | 34 | 34 | 258 | 258 | 258 | 0.0061429 | 100 | 0.002381 | 294 | 0.007 | 1.362 | A04 | MICL0.00910034/RSS
Build-In Floor | Mini Canal | MICL.00910034/SBL | 9 | 100 | 34 | 34 | 269 | 269 | 269 | 0.0064048 | 105 | 0.0025 | 306 | 0.0072857 | 1.362 | A04 | MICL0.00910034/SBL
Build-In Floor | Mini Canal | MICL.00910034/SBR | 9 | 100 | 34 | 34 | 269 | 269 | 269 | 0.0064048 | 105 | 0.0025 | 306 | 0.0072857 | 1.362 | A04 | MICL0.00910034/SBR
Build-In Floor | Mini Canal | MICL.00910034/SDB | 9 | 100 | 34 | 34 | 269 | 269 | 269 | 0.0064048 | 105 | 0.0025 | 306 | 0.0072857 | 1.362 | A04 | MICL0.00910034/SDB
Build-In Floor | Mini Canal | MICL.00910034/SNA | 9 | 100 | 34 | 34 | 269 | 269 | 269 | 0.0064048 | 105 | 0.0025 | 306 | 0.0072857 | 1.362 | A04 | MICL0.00910034/SNA
Build-In Floor | Mini Canal | MICL.00910034/SNC | 9 | 100 | 34 | 34 | 269 | 269 | 269 | 0.0064048 | 105 | 0.0025 | 306 | 0.0072857 | 1.362 | A04 | MICL0.00910034/SNC
Build-In Floor | Mini Canal | MICL.00910042/ANA | 9 | 100 | 42 | 42 | 291 | 291 | 291 | 0.0069286 | 113 | 0.0026905 | 331 | 0.007881 | 1.362 | A04 | MICL0.00910042/ANA
Build-In Floor | Mini Canal | MICL.00910042/DBL | 9 | 100 | 42 | 42 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.00910042/DBL
Build-In Floor | Mini Canal | MICL.00910042/DBN | 9 | 100 | 42 | 42 | 361 | 361 | 361 | 0.0085952 | 140 | 0.0033333 | 411 | 0.0097857 | 1.362 | A04 | MICL0.00910042/DBN
Build-In Floor | Mini Canal | MICL.00910042/DBR | 9 | 100 | 42 | 42 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.00910042/DBR
Build-In Floor | Mini Canal | MICL.00910042/DBV | 9 | 100 | 42 | 42 | 361 | 361 | 361 | 0.0085952 | 140 | 0.0033333 | 411 | 0.0097857 | 1.362 | A04 | MICL0.00910042/DBV
Build-In Floor | Mini Canal | MICL.00910042/DDB | 9 | 100 | 42 | 42 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.00910042/DDB
Build-In Floor | Mini Canal | MICL.00910042/DMN | 9 | 100 | 42 | 42 | 361 | 361 | 361 | 0.0085952 | 140 | 0.0033333 | 411 | 0.0097857 | 1.362 | A04 | MICL0.00910042/DMN
Build-In Floor | Mini Canal | MICL.00910042/DMV | 9 | 100 | 42 | 42 | 361 | 361 | 361 | 0.0085952 | 140 | 0.0033333 | 411 | 0.0097857 | 1.362 | A04 | MICL0.00910042/DMV
Build-In Floor | Mini Canal | MICL.00910042/DNA | 9 | 100 | 42 | 42 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.00910042/DNA
Build-In Floor | Mini Canal | MICL.00910042/DNC | 9 | 100 | 42 | 42 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.00910042/DNC
Build-In Floor | Mini Canal | MICL.00910042/DON | 9 | 100 | 42 | 42 | 361 | 361 | 361 | 0.0085952 | 140 | 0.0033333 | 411 | 0.0097857 | 1.362 | A04 | MICL0.00910042/DON
Build-In Floor | Mini Canal | MICL.00910042/DOV | 9 | 100 | 42 | 42 | 361 | 361 | 361 | 0.0085952 | 140 | 0.0033333 | 411 | 0.0097857 | 1.362 | A04 | MICL0.00910042/DOV
Build-In Floor | Mini Canal | MICL.00910042/PNC | 9 | 100 | 42 | 42 | 330 | 330 | 330 | 0.0078571 | 128 | 0.0030476 | 376 | 0.0089524 | 1.362 | A04 | MICL0.00910042/PNC
Build-In Floor | Mini Canal | MICL.00910042/RBL | 9 | 100 | 42 | 42 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.00910042/RBL
Build-In Floor | Mini Canal | MICL.00910042/RBN | 9 | 100 | 42 | 42 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.00910042/RBN
Build-In Floor | Mini Canal | MICL.00910042/RBR | 9 | 100 | 42 | 42 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.00910042/RBR
Build-In Floor | Mini Canal | MICL.00910042/RBV | 9 | 100 | 42 | 42 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.00910042/RBV
Build-In Floor | Mini Canal | MICL.00910042/RDB | 9 | 100 | 42 | 42 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.00910042/RDB
Build-In Floor | Mini Canal | MICL.00910042/RMN | 9 | 100 | 42 | 42 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.00910042/RMN
Build-In Floor | Mini Canal | MICL.00910042/RMV | 9 | 100 | 42 | 42 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.00910042/RMV
Build-In Floor | Mini Canal | MICL.00910042/RNA | 9 | 100 | 42 | 42 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.00910042/RNA
Build-In Floor | Mini Canal | MICL.00910042/RON | 9 | 100 | 42 | 42 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.00910042/RON
Build-In Floor | Mini Canal | MICL.00910042/ROV | 9 | 100 | 42 | 42 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.00910042/ROV
Build-In Floor | Mini Canal | MICL.00910042/RSS | 9 | 100 | 42 | 42 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.00910042/RSS
Build-In Floor | Mini Canal | MICL.00910042/SBL | 9 | 100 | 42 | 42 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.00910042/SBL
Build-In Floor | Mini Canal | MICL.00910042/SBR | 9 | 100 | 42 | 42 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.00910042/SBR
Build-In Floor | Mini Canal | MICL.00910042/SDB | 9 | 100 | 42 | 42 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.00910042/SDB
Build-In Floor | Mini Canal | MICL.00910042/SNA | 9 | 100 | 42 | 42 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.00910042/SNA
Build-In Floor | Mini Canal | MICL.00910042/SNC | 9 | 100 | 42 | 42 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.00910042/SNC
Build-In Floor | Mini Canal | MICL.00911014/ANA | 9 | 110 | 14 | 14 | 114 | 114 | 114 | 0.0027143 | 44 | 0.0010476 | 130 | 0.0030952 | 1.362 | A04 | MICL0.00911014/ANA
Build-In Floor | Mini Canal | MICL.00911014/DBL | 9 | 110 | 14 | 14 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00911014/DBL
Build-In Floor | Mini Canal | MICL.00911014/DBN | 9 | 110 | 14 | 14 | 141 | 141 | 141 | 0.0033571 | 55 | 0.0013095 | 161 | 0.0038333 | 1.362 | A04 | MICL0.00911014/DBN
Build-In Floor | Mini Canal | MICL.00911014/DBR | 9 | 110 | 14 | 14 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00911014/DBR
Build-In Floor | Mini Canal | MICL.00911014/DBV | 9 | 110 | 14 | 14 | 141 | 141 | 141 | 0.0033571 | 55 | 0.0013095 | 161 | 0.0038333 | 1.362 | A04 | MICL0.00911014/DBV
Build-In Floor | Mini Canal | MICL.00911014/DDB | 9 | 110 | 14 | 14 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00911014/DDB
Build-In Floor | Mini Canal | MICL.00911014/DMN | 9 | 110 | 14 | 14 | 141 | 141 | 141 | 0.0033571 | 55 | 0.0013095 | 161 | 0.0038333 | 1.362 | A04 | MICL0.00911014/DMN
Build-In Floor | Mini Canal | MICL.00911014/DMV | 9 | 110 | 14 | 14 | 141 | 141 | 141 | 0.0033571 | 55 | 0.0013095 | 161 | 0.0038333 | 1.362 | A04 | MICL0.00911014/DMV
Build-In Floor | Mini Canal | MICL.00911014/DNA | 9 | 110 | 14 | 14 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00911014/DNA
Build-In Floor | Mini Canal | MICL.00911014/DNC | 9 | 110 | 14 | 14 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00911014/DNC
Build-In Floor | Mini Canal | MICL.00911014/DON | 9 | 110 | 14 | 14 | 141 | 141 | 141 | 0.0033571 | 55 | 0.0013095 | 161 | 0.0038333 | 1.362 | A04 | MICL0.00911014/DON
Build-In Floor | Mini Canal | MICL.00911014/DOV | 9 | 110 | 14 | 14 | 141 | 141 | 141 | 0.0033571 | 55 | 0.0013095 | 161 | 0.0038333 | 1.362 | A04 | MICL0.00911014/DOV
Build-In Floor | Mini Canal | MICL.00911014/RBL | 9 | 110 | 14 | 14 | 152 | 152 | 152 | 0.003619 | 59 | 0.0014048 | 173 | 0.004119 | 1.362 | A04 | MICL0.00911014/RBL
Build-In Floor | Mini Canal | MICL.00911014/RBN | 9 | 110 | 14 | 14 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00911014/RBN
Build-In Floor | Mini Canal | MICL.00911014/RBR | 9 | 110 | 14 | 14 | 152 | 152 | 152 | 0.003619 | 59 | 0.0014048 | 173 | 0.004119 | 1.362 | A04 | MICL0.00911014/RBR
Build-In Floor | Mini Canal | MICL.00911014/RBV | 9 | 110 | 14 | 14 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00911014/RBV
Build-In Floor | Mini Canal | MICL.00911014/RDB | 9 | 110 | 14 | 14 | 152 | 152 | 152 | 0.003619 | 59 | 0.0014048 | 173 | 0.004119 | 1.362 | A04 | MICL0.00911014/RDB
Build-In Floor | Mini Canal | MICL.00911014/RMN | 9 | 110 | 14 | 14 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00911014/RMN
Build-In Floor | Mini Canal | MICL.00911014/RMV | 9 | 110 | 14 | 14 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00911014/RMV
Build-In Floor | Mini Canal | MICL.00911014/RNA | 9 | 110 | 14 | 14 | 152 | 152 | 152 | 0.003619 | 59 | 0.0014048 | 173 | 0.004119 | 1.362 | A04 | MICL0.00911014/RNA
Build-In Floor | Mini Canal | MICL.00911014/RON | 9 | 110 | 14 | 14 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00911014/RON
Build-In Floor | Mini Canal | MICL.00911014/ROV | 9 | 110 | 14 | 14 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.00911014/ROV
Build-In Floor | Mini Canal | MICL.00911014/RSS | 9 | 110 | 14 | 14 | 146 | 146 | 146 | 0.0034762 | 57 | 0.0013571 | 166 | 0.0039524 | 1.362 | A04 | MICL0.00911014/RSS
Build-In Floor | Mini Canal | MICL.00911014/SBL | 9 | 110 | 14 | 14 | 152 | 152 | 152 | 0.003619 | 59 | 0.0014048 | 173 | 0.004119 | 1.362 | A04 | MICL0.00911014/SBL
Build-In Floor | Mini Canal | MICL.00911014/SBR | 9 | 110 | 14 | 14 | 152 | 152 | 152 | 0.003619 | 59 | 0.0014048 | 173 | 0.004119 | 1.362 | A04 | MICL0.00911014/SBR
Build-In Floor | Mini Canal | MICL.00911014/SDB | 9 | 110 | 14 | 14 | 152 | 152 | 152 | 0.003619 | 59 | 0.0014048 | 173 | 0.004119 | 1.362 | A04 | MICL0.00911014/SDB
Build-In Floor | Mini Canal | MICL.00911014/SNA | 9 | 110 | 14 | 14 | 152 | 152 | 152 | 0.003619 | 59 | 0.0014048 | 173 | 0.004119 | 1.362 | A04 | MICL0.00911014/SNA
Build-In Floor | Mini Canal | MICL.00911014/SNC | 9 | 110 | 14 | 14 | 152 | 152 | 152 | 0.003619 | 59 | 0.0014048 | 173 | 0.004119 | 1.362 | A04 | MICL0.00911014/SNC
Build-In Floor | Mini Canal | MICL.00911018/ANA | 9 | 110 | 18 | 18 | 135 | 135 | 135 | 0.0032143 | 53 | 0.0012619 | 154 | 0.0036667 | 1.362 | A04 | MICL0.00911018/ANA
Build-In Floor | Mini Canal | MICL.00911018/DBL | 9 | 110 | 18 | 18 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.00911018/DBL
Build-In Floor | Mini Canal | MICL.00911018/DBN | 9 | 110 | 18 | 18 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00911018/DBN
Build-In Floor | Mini Canal | MICL.00911018/DBR | 9 | 110 | 18 | 18 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.00911018/DBR
Build-In Floor | Mini Canal | MICL.00911018/DBV | 9 | 110 | 18 | 18 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00911018/DBV
Build-In Floor | Mini Canal | MICL.00911018/DDB | 9 | 110 | 18 | 18 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.00911018/DDB
Build-In Floor | Mini Canal | MICL.00911018/DMN | 9 | 110 | 18 | 18 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00911018/DMN
Build-In Floor | Mini Canal | MICL.00911018/DMV | 9 | 110 | 18 | 18 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00911018/DMV
Build-In Floor | Mini Canal | MICL.00911018/DNA | 9 | 110 | 18 | 18 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.00911018/DNA
Build-In Floor | Mini Canal | MICL.00911018/DNC | 9 | 110 | 18 | 18 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.00911018/DNC
Build-In Floor | Mini Canal | MICL.00911018/DON | 9 | 110 | 18 | 18 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00911018/DON
Build-In Floor | Mini Canal | MICL.00911018/DOV | 9 | 110 | 18 | 18 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00911018/DOV
Build-In Floor | Mini Canal | MICL.00911018/RBL | 9 | 110 | 18 | 18 | 180 | 180 | 180 | 0.0042857 | 70 | 0.0016667 | 205 | 0.004881 | 1.362 | A04 | MICL0.00911018/RBL
Build-In Floor | Mini Canal | MICL.00911018/RBN | 9 | 110 | 18 | 18 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.00911018/RBN
Build-In Floor | Mini Canal | MICL.00911018/RBR | 9 | 110 | 18 | 18 | 180 | 180 | 180 | 0.0042857 | 70 | 0.0016667 | 205 | 0.004881 | 1.362 | A04 | MICL0.00911018/RBR
Build-In Floor | Mini Canal | MICL.00911018/RBV | 9 | 110 | 18 | 18 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.00911018/RBV
Build-In Floor | Mini Canal | MICL.00911018/RDB | 9 | 110 | 18 | 18 | 180 | 180 | 180 | 0.0042857 | 70 | 0.0016667 | 205 | 0.004881 | 1.362 | A04 | MICL0.00911018/RDB
Build-In Floor | Mini Canal | MICL.00911018/RMN | 9 | 110 | 18 | 18 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.00911018/RMN
Build-In Floor | Mini Canal | MICL.00911018/RMV | 9 | 110 | 18 | 18 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.00911018/RMV
Build-In Floor | Mini Canal | MICL.00911018/RNA | 9 | 110 | 18 | 18 | 180 | 180 | 180 | 0.0042857 | 70 | 0.0016667 | 205 | 0.004881 | 1.362 | A04 | MICL0.00911018/RNA
Build-In Floor | Mini Canal | MICL.00911018/RON | 9 | 110 | 18 | 18 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.00911018/RON
Build-In Floor | Mini Canal | MICL.00911018/ROV | 9 | 110 | 18 | 18 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.00911018/ROV
Build-In Floor | Mini Canal | MICL.00911018/RSS | 9 | 110 | 18 | 18 | 173 | 173 | 173 | 0.004119 | 67 | 0.0015952 | 197 | 0.0046905 | 1.362 | A04 | MICL0.00911018/RSS
Build-In Floor | Mini Canal | MICL.00911018/SBL | 9 | 110 | 18 | 18 | 180 | 180 | 180 | 0.0042857 | 70 | 0.0016667 | 205 | 0.004881 | 1.362 | A04 | MICL0.00911018/SBL
Build-In Floor | Mini Canal | MICL.00911018/SBR | 9 | 110 | 18 | 18 | 180 | 180 | 180 | 0.0042857 | 70 | 0.0016667 | 205 | 0.004881 | 1.362 | A04 | MICL0.00911018/SBR
Build-In Floor | Mini Canal | MICL.00911018/SDB | 9 | 110 | 18 | 18 | 180 | 180 | 180 | 0.0042857 | 70 | 0.0016667 | 205 | 0.004881 | 1.362 | A04 | MICL0.00911018/SDB
Build-In Floor | Mini Canal | MICL.00911018/SNA | 9 | 110 | 18 | 18 | 180 | 180 | 180 | 0.0042857 | 70 | 0.0016667 | 205 | 0.004881 | 1.362 | A04 | MICL0.00911018/SNA
Build-In Floor | Mini Canal | MICL.00911018/SNC | 9 | 110 | 18 | 18 | 180 | 180 | 180 | 0.0042857 | 70 | 0.0016667 | 205 | 0.004881 | 1.362 | A04 | MICL0.00911018/SNC
Build-In Floor | Mini Canal | MICL.00911026/ANA | 9 | 110 | 26 | 26 | 178 | 178 | 178 | 0.0042381 | 69 | 0.0016429 | 203 | 0.0048333 | 1.362 | A04 | MICL0.00911026/ANA
Build-In Floor | Mini Canal | MICL.00911026/DBL | 9 | 110 | 26 | 26 | 230 | 230 | 230 | 0.0054762 | 89 | 0.002119 | 262 | 0.0062381 | 1.362 | A04 | MICL0.00911026/DBL
Build-In Floor | Mini Canal | MICL.00911026/DBN | 9 | 110 | 26 | 26 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.00911026/DBN
Build-In Floor | Mini Canal | MICL.00911026/DBR | 9 | 110 | 26 | 26 | 230 | 230 | 230 | 0.0054762 | 89 | 0.002119 | 262 | 0.0062381 | 1.362 | A04 | MICL0.00911026/DBR
Build-In Floor | Mini Canal | MICL.00911026/DBV | 9 | 110 | 26 | 26 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.00911026/DBV
Build-In Floor | Mini Canal | MICL.00911026/DDB | 9 | 110 | 26 | 26 | 230 | 230 | 230 | 0.0054762 | 89 | 0.002119 | 262 | 0.0062381 | 1.362 | A04 | MICL0.00911026/DDB
Build-In Floor | Mini Canal | MICL.00911026/DMN | 9 | 110 | 26 | 26 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.00911026/DMN
Build-In Floor | Mini Canal | MICL.00911026/DMV | 9 | 110 | 26 | 26 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.00911026/DMV
Build-In Floor | Mini Canal | MICL.00911026/DNA | 9 | 110 | 26 | 26 | 230 | 230 | 230 | 0.0054762 | 89 | 0.002119 | 262 | 0.0062381 | 1.362 | A04 | MICL0.00911026/DNA
Build-In Floor | Mini Canal | MICL.00911026/DNC | 9 | 110 | 26 | 26 | 230 | 230 | 230 | 0.0054762 | 89 | 0.002119 | 262 | 0.0062381 | 1.362 | A04 | MICL0.00911026/DNC
Build-In Floor | Mini Canal | MICL.00911026/DON | 9 | 110 | 26 | 26 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.00911026/DON
Build-In Floor | Mini Canal | MICL.00911026/DOV | 9 | 110 | 26 | 26 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.00911026/DOV
Build-In Floor | Mini Canal | MICL.00911026/PNC | 9 | 110 | 26 | 26 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.00911026/PNC
Build-In Floor | Mini Canal | MICL.00911026/RBL | 9 | 110 | 26 | 26 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.00911026/RBL
Build-In Floor | Mini Canal | MICL.00911026/RBN | 9 | 110 | 26 | 26 | 230 | 230 | 230 | 0.0054762 | 89 | 0.002119 | 262 | 0.0062381 | 1.362 | A04 | MICL0.00911026/RBN
Build-In Floor | Mini Canal | MICL.00911026/RBR | 9 | 110 | 26 | 26 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.00911026/RBR
Build-In Floor | Mini Canal | MICL.00911026/RBV | 9 | 110 | 26 | 26 | 230 | 230 | 230 | 0.0054762 | 89 | 0.002119 | 262 | 0.0062381 | 1.362 | A04 | MICL0.00911026/RBV
Build-In Floor | Mini Canal | MICL.00911026/RDB | 9 | 110 | 26 | 26 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.00911026/RDB
Build-In Floor | Mini Canal | MICL.00911026/RMN | 9 | 110 | 26 | 26 | 230 | 230 | 230 | 0.0054762 | 89 | 0.002119 | 262 | 0.0062381 | 1.362 | A04 | MICL0.00911026/RMN
Build-In Floor | Mini Canal | MICL.00911026/RMV | 9 | 110 | 26 | 26 | 230 | 230 | 230 | 0.0054762 | 89 | 0.002119 | 262 | 0.0062381 | 1.362 | A04 | MICL0.00911026/RMV
Build-In Floor | Mini Canal | MICL.00911026/RNA | 9 | 110 | 26 | 26 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.00911026/RNA
Build-In Floor | Mini Canal | MICL.00911026/RON | 9 | 110 | 26 | 26 | 230 | 230 | 230 | 0.0054762 | 89 | 0.002119 | 262 | 0.0062381 | 1.362 | A04 | MICL0.00911026/RON
Build-In Floor | Mini Canal | MICL.00911026/ROV | 9 | 110 | 26 | 26 | 230 | 230 | 230 | 0.0054762 | 89 | 0.002119 | 262 | 0.0062381 | 1.362 | A04 | MICL0.00911026/ROV
Build-In Floor | Mini Canal | MICL.00911026/RSS | 9 | 110 | 26 | 26 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.00911026/RSS
Build-In Floor | Mini Canal | MICL.00911026/SBL | 9 | 110 | 26 | 26 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.00911026/SBL
Build-In Floor | Mini Canal | MICL.00911026/SBR | 9 | 110 | 26 | 26 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.00911026/SBR
Build-In Floor | Mini Canal | MICL.00911026/SDB | 9 | 110 | 26 | 26 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.00911026/SDB
Build-In Floor | Mini Canal | MICL.00911026/SNA | 9 | 110 | 26 | 26 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.00911026/SNA
Build-In Floor | Mini Canal | MICL.00911026/SNC | 9 | 110 | 26 | 26 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.00911026/SNC
Build-In Floor | Mini Canal | MICL.00911034/ANA | 9 | 110 | 34 | 34 | 230 | 230 | 230 | 0.0054762 | 89 | 0.002119 | 262 | 0.0062381 | 1.362 | A04 | MICL0.00911034/ANA
Build-In Floor | Mini Canal | MICL.00911034/DBL | 9 | 110 | 34 | 34 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.00911034/DBL
Build-In Floor | Mini Canal | MICL.00911034/DBN | 9 | 110 | 34 | 34 | 286 | 286 | 286 | 0.0068095 | 111 | 0.0026429 | 326 | 0.0077619 | 1.362 | A04 | MICL0.00911034/DBN
Build-In Floor | Mini Canal | MICL.00911034/DBR | 9 | 110 | 34 | 34 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.00911034/DBR
Build-In Floor | Mini Canal | MICL.00911034/DBV | 9 | 110 | 34 | 34 | 286 | 286 | 286 | 0.0068095 | 111 | 0.0026429 | 326 | 0.0077619 | 1.362 | A04 | MICL0.00911034/DBV
Build-In Floor | Mini Canal | MICL.00911034/DDB | 9 | 110 | 34 | 34 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.00911034/DDB
Build-In Floor | Mini Canal | MICL.00911034/DMN | 9 | 110 | 34 | 34 | 286 | 286 | 286 | 0.0068095 | 111 | 0.0026429 | 326 | 0.0077619 | 1.362 | A04 | MICL0.00911034/DMN
Build-In Floor | Mini Canal | MICL.00911034/DMV | 9 | 110 | 34 | 34 | 286 | 286 | 286 | 0.0068095 | 111 | 0.0026429 | 326 | 0.0077619 | 1.362 | A04 | MICL0.00911034/DMV
Build-In Floor | Mini Canal | MICL.00911034/DNA | 9 | 110 | 34 | 34 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.00911034/DNA
Build-In Floor | Mini Canal | MICL.00911034/DNC | 9 | 110 | 34 | 34 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.00911034/DNC
Build-In Floor | Mini Canal | MICL.00911034/DON | 9 | 110 | 34 | 34 | 286 | 286 | 286 | 0.0068095 | 111 | 0.0026429 | 326 | 0.0077619 | 1.362 | A04 | MICL0.00911034/DON
Build-In Floor | Mini Canal | MICL.00911034/DOV | 9 | 110 | 34 | 34 | 286 | 286 | 286 | 0.0068095 | 111 | 0.0026429 | 326 | 0.0077619 | 1.362 | A04 | MICL0.00911034/DOV
Build-In Floor | Mini Canal | MICL.00911034/PNC | 9 | 110 | 34 | 34 | 261 | 261 | 261 | 0.0062143 | 102 | 0.0024286 | 297 | 0.0070714 | 1.362 | A04 | MICL0.00911034/PNC
Build-In Floor | Mini Canal | MICL.00911034/RBL | 9 | 110 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00911034/RBL
Build-In Floor | Mini Canal | MICL.00911034/RBN | 9 | 110 | 34 | 34 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.00911034/RBN
Build-In Floor | Mini Canal | MICL.00911034/RBR | 9 | 110 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00911034/RBR
Build-In Floor | Mini Canal | MICL.00911034/RBV | 9 | 110 | 34 | 34 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.00911034/RBV
Build-In Floor | Mini Canal | MICL.00911034/RDB | 9 | 110 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00911034/RDB
Build-In Floor | Mini Canal | MICL.00911034/RMN | 9 | 110 | 34 | 34 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.00911034/RMN
Build-In Floor | Mini Canal | MICL.00911034/RMV | 9 | 110 | 34 | 34 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.00911034/RMV
Build-In Floor | Mini Canal | MICL.00911034/RNA | 9 | 110 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00911034/RNA
Build-In Floor | Mini Canal | MICL.00911034/RON | 9 | 110 | 34 | 34 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.00911034/RON
Build-In Floor | Mini Canal | MICL.00911034/ROV | 9 | 110 | 34 | 34 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.00911034/ROV
Build-In Floor | Mini Canal | MICL.00911034/RSS | 9 | 110 | 34 | 34 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.00911034/RSS
Build-In Floor | Mini Canal | MICL.00911034/SBL | 9 | 110 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00911034/SBL
Build-In Floor | Mini Canal | MICL.00911034/SBR | 9 | 110 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00911034/SBR
Build-In Floor | Mini Canal | MICL.00911034/SDB | 9 | 110 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00911034/SDB
Build-In Floor | Mini Canal | MICL.00911034/SNA | 9 | 110 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00911034/SNA
Build-In Floor | Mini Canal | MICL.00911034/SNC | 9 | 110 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00911034/SNC
Build-In Floor | Mini Canal | MICL.00911042/ANA | 9 | 110 | 42 | 42 | 334 | 334 | 334 | 0.0079524 | 130 | 0.0030952 | 380 | 0.0090476 | 1.362 | A04 | MICL0.00911042/ANA
Build-In Floor | Mini Canal | MICL.00911042/DBL | 9 | 110 | 42 | 42 | 432 | 432 | 432 | 0.010286 | 168 | 0.004 | 492 | 0.011714 | 1.362 | A04 | MICL0.00911042/DBL
Build-In Floor | Mini Canal | MICL.00911042/DBN | 9 | 110 | 42 | 42 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.00911042/DBN
Build-In Floor | Mini Canal | MICL.00911042/DBR | 9 | 110 | 42 | 42 | 432 | 432 | 432 | 0.010286 | 168 | 0.004 | 492 | 0.011714 | 1.362 | A04 | MICL0.00911042/DBR
Build-In Floor | Mini Canal | MICL.00911042/DBV | 9 | 110 | 42 | 42 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.00911042/DBV
Build-In Floor | Mini Canal | MICL.00911042/DDB | 9 | 110 | 42 | 42 | 432 | 432 | 432 | 0.010286 | 168 | 0.004 | 492 | 0.011714 | 1.362 | A04 | MICL0.00911042/DDB
Build-In Floor | Mini Canal | MICL.00911042/DMN | 9 | 110 | 42 | 42 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.00911042/DMN
Build-In Floor | Mini Canal | MICL.00911042/DMV | 9 | 110 | 42 | 42 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.00911042/DMV
Build-In Floor | Mini Canal | MICL.00911042/DNA | 9 | 110 | 42 | 42 | 432 | 432 | 432 | 0.010286 | 168 | 0.004 | 492 | 0.011714 | 1.362 | A04 | MICL0.00911042/DNA
Build-In Floor | Mini Canal | MICL.00911042/DNC | 9 | 110 | 42 | 42 | 432 | 432 | 432 | 0.010286 | 168 | 0.004 | 492 | 0.011714 | 1.362 | A04 | MICL0.00911042/DNC
Build-In Floor | Mini Canal | MICL.00911042/DON | 9 | 110 | 42 | 42 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.00911042/DON
Build-In Floor | Mini Canal | MICL.00911042/DOV | 9 | 110 | 42 | 42 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.00911042/DOV
Build-In Floor | Mini Canal | MICL.00911042/PNC | 9 | 110 | 42 | 42 | 378 | 378 | 378 | 0.009 | 147 | 0.0035 | 431 | 0.010262 | 1.362 | A04 | MICL0.00911042/PNC
Build-In Floor | Mini Canal | MICL.00911042/RBL | 9 | 110 | 42 | 42 | 445 | 445 | 445 | 0.010595 | 173 | 0.004119 | 507 | 0.012071 | 1.362 | A04 | MICL0.00911042/RBL
Build-In Floor | Mini Canal | MICL.00911042/RBN | 9 | 110 | 42 | 42 | 432 | 432 | 432 | 0.010286 | 168 | 0.004 | 492 | 0.011714 | 1.362 | A04 | MICL0.00911042/RBN
Build-In Floor | Mini Canal | MICL.00911042/RBR | 9 | 110 | 42 | 42 | 445 | 445 | 445 | 0.010595 | 173 | 0.004119 | 507 | 0.012071 | 1.362 | A04 | MICL0.00911042/RBR
Build-In Floor | Mini Canal | MICL.00911042/RBV | 9 | 110 | 42 | 42 | 432 | 432 | 432 | 0.010286 | 168 | 0.004 | 492 | 0.011714 | 1.362 | A04 | MICL0.00911042/RBV
Build-In Floor | Mini Canal | MICL.00911042/RDB | 9 | 110 | 42 | 42 | 445 | 445 | 445 | 0.010595 | 173 | 0.004119 | 507 | 0.012071 | 1.362 | A04 | MICL0.00911042/RDB
Build-In Floor | Mini Canal | MICL.00911042/RMN | 9 | 110 | 42 | 42 | 432 | 432 | 432 | 0.010286 | 168 | 0.004 | 492 | 0.011714 | 1.362 | A04 | MICL0.00911042/RMN
Build-In Floor | Mini Canal | MICL.00911042/RMV | 9 | 110 | 42 | 42 | 432 | 432 | 432 | 0.010286 | 168 | 0.004 | 492 | 0.011714 | 1.362 | A04 | MICL0.00911042/RMV
Build-In Floor | Mini Canal | MICL.00911042/RNA | 9 | 110 | 42 | 42 | 445 | 445 | 445 | 0.010595 | 173 | 0.004119 | 507 | 0.012071 | 1.362 | A04 | MICL0.00911042/RNA
Build-In Floor | Mini Canal | MICL.00911042/RON | 9 | 110 | 42 | 42 | 432 | 432 | 432 | 0.010286 | 168 | 0.004 | 492 | 0.011714 | 1.362 | A04 | MICL0.00911042/RON
Build-In Floor | Mini Canal | MICL.00911042/ROV | 9 | 110 | 42 | 42 | 432 | 432 | 432 | 0.010286 | 168 | 0.004 | 492 | 0.011714 | 1.362 | A04 | MICL0.00911042/ROV
Build-In Floor | Mini Canal | MICL.00911042/RSS | 9 | 110 | 42 | 42 | 427 | 427 | 427 | 0.010167 | 166 | 0.0039524 | 486 | 0.011571 | 1.362 | A04 | MICL0.00911042/RSS
Build-In Floor | Mini Canal | MICL.00911042/SBL | 9 | 110 | 42 | 42 | 445 | 445 | 445 | 0.010595 | 173 | 0.004119 | 507 | 0.012071 | 1.362 | A04 | MICL0.00911042/SBL
Build-In Floor | Mini Canal | MICL.00911042/SBR | 9 | 110 | 42 | 42 | 445 | 445 | 445 | 0.010595 | 173 | 0.004119 | 507 | 0.012071 | 1.362 | A04 | MICL0.00911042/SBR
Build-In Floor | Mini Canal | MICL.00911042/SDB | 9 | 110 | 42 | 42 | 445 | 445 | 445 | 0.010595 | 173 | 0.004119 | 507 | 0.012071 | 1.362 | A04 | MICL0.00911042/SDB
Build-In Floor | Mini Canal | MICL.00911042/SNA | 9 | 110 | 42 | 42 | 445 | 445 | 445 | 0.010595 | 173 | 0.004119 | 507 | 0.012071 | 1.362 | A04 | MICL0.00911042/SNA
Build-In Floor | Mini Canal | MICL.00911042/SNC | 9 | 110 | 42 | 42 | 445 | 445 | 445 | 0.010595 | 173 | 0.004119 | 507 | 0.012071 | 1.362 | A04 | MICL0.00911042/SNC
Build-In Floor | Mini Canal | MICL.00912014/ANA | 9 | 120 | 14 | 14 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.00912014/ANA
Build-In Floor | Mini Canal | MICL.00912014/DBL | 9 | 120 | 14 | 14 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00912014/DBL
Build-In Floor | Mini Canal | MICL.00912014/DBN | 9 | 120 | 14 | 14 | 160 | 160 | 160 | 0.0038095 | 62 | 0.0014762 | 182 | 0.0043333 | 1.362 | A04 | MICL0.00912014/DBN
Build-In Floor | Mini Canal | MICL.00912014/DBR | 9 | 120 | 14 | 14 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00912014/DBR
Build-In Floor | Mini Canal | MICL.00912014/DBV | 9 | 120 | 14 | 14 | 160 | 160 | 160 | 0.0038095 | 62 | 0.0014762 | 182 | 0.0043333 | 1.362 | A04 | MICL0.00912014/DBV
Build-In Floor | Mini Canal | MICL.00912014/DDB | 9 | 120 | 14 | 14 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00912014/DDB
Build-In Floor | Mini Canal | MICL.00912014/DMN | 9 | 120 | 14 | 14 | 160 | 160 | 160 | 0.0038095 | 62 | 0.0014762 | 182 | 0.0043333 | 1.362 | A04 | MICL0.00912014/DMN
Build-In Floor | Mini Canal | MICL.00912014/DMV | 9 | 120 | 14 | 14 | 160 | 160 | 160 | 0.0038095 | 62 | 0.0014762 | 182 | 0.0043333 | 1.362 | A04 | MICL0.00912014/DMV
Build-In Floor | Mini Canal | MICL.00912014/DNA | 9 | 120 | 14 | 14 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00912014/DNA
Build-In Floor | Mini Canal | MICL.00912014/DNC | 9 | 120 | 14 | 14 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00912014/DNC
Build-In Floor | Mini Canal | MICL.00912014/DON | 9 | 120 | 14 | 14 | 160 | 160 | 160 | 0.0038095 | 62 | 0.0014762 | 182 | 0.0043333 | 1.362 | A04 | MICL0.00912014/DON
Build-In Floor | Mini Canal | MICL.00912014/DOV | 9 | 120 | 14 | 14 | 160 | 160 | 160 | 0.0038095 | 62 | 0.0014762 | 182 | 0.0043333 | 1.362 | A04 | MICL0.00912014/DOV
Build-In Floor | Mini Canal | MICL.00912014/RBL | 9 | 120 | 14 | 14 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.00912014/RBL
Build-In Floor | Mini Canal | MICL.00912014/RBN | 9 | 120 | 14 | 14 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00912014/RBN
Build-In Floor | Mini Canal | MICL.00912014/RBR | 9 | 120 | 14 | 14 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.00912014/RBR
Build-In Floor | Mini Canal | MICL.00912014/RBV | 9 | 120 | 14 | 14 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00912014/RBV
Build-In Floor | Mini Canal | MICL.00912014/RDB | 9 | 120 | 14 | 14 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.00912014/RDB
Build-In Floor | Mini Canal | MICL.00912014/RMN | 9 | 120 | 14 | 14 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00912014/RMN
Build-In Floor | Mini Canal | MICL.00912014/RMV | 9 | 120 | 14 | 14 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00912014/RMV
Build-In Floor | Mini Canal | MICL.00912014/RNA | 9 | 120 | 14 | 14 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.00912014/RNA
Build-In Floor | Mini Canal | MICL.00912014/RON | 9 | 120 | 14 | 14 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00912014/RON
Build-In Floor | Mini Canal | MICL.00912014/ROV | 9 | 120 | 14 | 14 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.00912014/ROV
Build-In Floor | Mini Canal | MICL.00912014/RSS | 9 | 120 | 14 | 14 | 165 | 165 | 165 | 0.0039286 | 64 | 0.0015238 | 188 | 0.0044762 | 1.362 | A04 | MICL0.00912014/RSS
Build-In Floor | Mini Canal | MICL.00912014/SBL | 9 | 120 | 14 | 14 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.00912014/SBL
Build-In Floor | Mini Canal | MICL.00912014/SBR | 9 | 120 | 14 | 14 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.00912014/SBR
Build-In Floor | Mini Canal | MICL.00912014/SDB | 9 | 120 | 14 | 14 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.00912014/SDB
Build-In Floor | Mini Canal | MICL.00912014/SNA | 9 | 120 | 14 | 14 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.00912014/SNA
Build-In Floor | Mini Canal | MICL.00912014/SNC | 9 | 120 | 14 | 14 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.00912014/SNC
Build-In Floor | Mini Canal | MICL.00912018/ANA | 9 | 120 | 18 | 18 | 152 | 152 | 152 | 0.003619 | 59 | 0.0014048 | 173 | 0.004119 | 1.362 | A04 | MICL0.00912018/ANA
Build-In Floor | Mini Canal | MICL.00912018/DBL | 9 | 120 | 18 | 18 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.00912018/DBL
Build-In Floor | Mini Canal | MICL.00912018/DBN | 9 | 120 | 18 | 18 | 189 | 189 | 189 | 0.0045 | 74 | 0.0017619 | 215 | 0.005119 | 1.362 | A04 | MICL0.00912018/DBN
Build-In Floor | Mini Canal | MICL.00912018/DBR | 9 | 120 | 18 | 18 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.00912018/DBR
Build-In Floor | Mini Canal | MICL.00912018/DBV | 9 | 120 | 18 | 18 | 189 | 189 | 189 | 0.0045 | 74 | 0.0017619 | 215 | 0.005119 | 1.362 | A04 | MICL0.00912018/DBV
Build-In Floor | Mini Canal | MICL.00912018/DDB | 9 | 120 | 18 | 18 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.00912018/DDB
Build-In Floor | Mini Canal | MICL.00912018/DMN | 9 | 120 | 18 | 18 | 189 | 189 | 189 | 0.0045 | 74 | 0.0017619 | 215 | 0.005119 | 1.362 | A04 | MICL0.00912018/DMN
Build-In Floor | Mini Canal | MICL.00912018/DMV | 9 | 120 | 18 | 18 | 189 | 189 | 189 | 0.0045 | 74 | 0.0017619 | 215 | 0.005119 | 1.362 | A04 | MICL0.00912018/DMV
Build-In Floor | Mini Canal | MICL.00912018/DNA | 9 | 120 | 18 | 18 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.00912018/DNA
Build-In Floor | Mini Canal | MICL.00912018/DNC | 9 | 120 | 18 | 18 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.00912018/DNC
Build-In Floor | Mini Canal | MICL.00912018/DON | 9 | 120 | 18 | 18 | 189 | 189 | 189 | 0.0045 | 74 | 0.0017619 | 215 | 0.005119 | 1.362 | A04 | MICL0.00912018/DON
Build-In Floor | Mini Canal | MICL.00912018/DOV | 9 | 120 | 18 | 18 | 189 | 189 | 189 | 0.0045 | 74 | 0.0017619 | 215 | 0.005119 | 1.362 | A04 | MICL0.00912018/DOV
Build-In Floor | Mini Canal | MICL.00912018/RBL | 9 | 120 | 18 | 18 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.00912018/RBL
Build-In Floor | Mini Canal | MICL.00912018/RBN | 9 | 120 | 18 | 18 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.00912018/RBN
Build-In Floor | Mini Canal | MICL.00912018/RBR | 9 | 120 | 18 | 18 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.00912018/RBR
Build-In Floor | Mini Canal | MICL.00912018/RBV | 9 | 120 | 18 | 18 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.00912018/RBV
Build-In Floor | Mini Canal | MICL.00912018/RDB | 9 | 120 | 18 | 18 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.00912018/RDB
Build-In Floor | Mini Canal | MICL.00912018/RMN | 9 | 120 | 18 | 18 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.00912018/RMN
Build-In Floor | Mini Canal | MICL.00912018/RMV | 9 | 120 | 18 | 18 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.00912018/RMV
Build-In Floor | Mini Canal | MICL.00912018/RNA | 9 | 120 | 18 | 18 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.00912018/RNA
Build-In Floor | Mini Canal | MICL.00912018/RON | 9 | 120 | 18 | 18 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.00912018/RON
Build-In Floor | Mini Canal | MICL.00912018/ROV | 9 | 120 | 18 | 18 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.00912018/ROV
Build-In Floor | Mini Canal | MICL.00912018/RSS | 9 | 120 | 18 | 18 | 195 | 195 | 195 | 0.0046429 | 76 | 0.0018095 | 222 | 0.0052857 | 1.362 | A04 | MICL0.00912018/RSS
Build-In Floor | Mini Canal | MICL.00912018/SBL | 9 | 120 | 18 | 18 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.00912018/SBL
Build-In Floor | Mini Canal | MICL.00912018/SBR | 9 | 120 | 18 | 18 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.00912018/SBR
Build-In Floor | Mini Canal | MICL.00912018/SDB | 9 | 120 | 18 | 18 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.00912018/SDB
Build-In Floor | Mini Canal | MICL.00912018/SNA | 9 | 120 | 18 | 18 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.00912018/SNA
Build-In Floor | Mini Canal | MICL.00912018/SNC | 9 | 120 | 18 | 18 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.00912018/SNC
Build-In Floor | Mini Canal | MICL.00912026/ANA | 9 | 120 | 26 | 26 | 200 | 200 | 200 | 0.0047619 | 78 | 0.0018571 | 228 | 0.0054286 | 1.362 | A04 | MICL0.00912026/ANA
Build-In Floor | Mini Canal | MICL.00912026/DBL | 9 | 120 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00912026/DBL
Build-In Floor | Mini Canal | MICL.00912026/DBN | 9 | 120 | 26 | 26 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.00912026/DBN
Build-In Floor | Mini Canal | MICL.00912026/DBR | 9 | 120 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00912026/DBR
Build-In Floor | Mini Canal | MICL.00912026/DBV | 9 | 120 | 26 | 26 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.00912026/DBV
Build-In Floor | Mini Canal | MICL.00912026/DDB | 9 | 120 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00912026/DDB
Build-In Floor | Mini Canal | MICL.00912026/DMN | 9 | 120 | 26 | 26 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.00912026/DMN
Build-In Floor | Mini Canal | MICL.00912026/DMV | 9 | 120 | 26 | 26 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.00912026/DMV
Build-In Floor | Mini Canal | MICL.00912026/DNA | 9 | 120 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00912026/DNA
Build-In Floor | Mini Canal | MICL.00912026/DNC | 9 | 120 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00912026/DNC
Build-In Floor | Mini Canal | MICL.00912026/DON | 9 | 120 | 26 | 26 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.00912026/DON
Build-In Floor | Mini Canal | MICL.00912026/DOV | 9 | 120 | 26 | 26 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.00912026/DOV
Build-In Floor | Mini Canal | MICL.00912026/PNC | 9 | 120 | 26 | 26 | 227 | 227 | 227 | 0.0054048 | 88 | 0.0020952 | 259 | 0.0061667 | 1.362 | A04 | MICL0.00912026/PNC
Build-In Floor | Mini Canal | MICL.00912026/RBL | 9 | 120 | 26 | 26 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00912026/RBL
Build-In Floor | Mini Canal | MICL.00912026/RBN | 9 | 120 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00912026/RBN
Build-In Floor | Mini Canal | MICL.00912026/RBR | 9 | 120 | 26 | 26 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00912026/RBR
Build-In Floor | Mini Canal | MICL.00912026/RBV | 9 | 120 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00912026/RBV
Build-In Floor | Mini Canal | MICL.00912026/RDB | 9 | 120 | 26 | 26 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00912026/RDB
Build-In Floor | Mini Canal | MICL.00912026/RMN | 9 | 120 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00912026/RMN
Build-In Floor | Mini Canal | MICL.00912026/RMV | 9 | 120 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00912026/RMV
Build-In Floor | Mini Canal | MICL.00912026/RNA | 9 | 120 | 26 | 26 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00912026/RNA
Build-In Floor | Mini Canal | MICL.00912026/RON | 9 | 120 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00912026/RON
Build-In Floor | Mini Canal | MICL.00912026/ROV | 9 | 120 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00912026/ROV
Build-In Floor | Mini Canal | MICL.00912026/RSS | 9 | 120 | 26 | 26 | 256 | 256 | 256 | 0.0060952 | 100 | 0.002381 | 292 | 0.0069524 | 1.362 | A04 | MICL0.00912026/RSS
Build-In Floor | Mini Canal | MICL.00912026/SBL | 9 | 120 | 26 | 26 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00912026/SBL
Build-In Floor | Mini Canal | MICL.00912026/SBR | 9 | 120 | 26 | 26 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00912026/SBR
Build-In Floor | Mini Canal | MICL.00912026/SDB | 9 | 120 | 26 | 26 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00912026/SDB
Build-In Floor | Mini Canal | MICL.00912026/SNA | 9 | 120 | 26 | 26 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00912026/SNA
Build-In Floor | Mini Canal | MICL.00912026/SNC | 9 | 120 | 26 | 26 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00912026/SNC
Build-In Floor | Mini Canal | MICL.00912034/ANA | 9 | 120 | 34 | 34 | 260 | 260 | 260 | 0.0061905 | 101 | 0.0024048 | 296 | 0.0070476 | 1.362 | A04 | MICL0.00912034/ANA
Build-In Floor | Mini Canal | MICL.00912034/DBL | 9 | 120 | 34 | 34 | 336 | 336 | 336 | 0.008 | 131 | 0.003119 | 383 | 0.009119 | 1.362 | A04 | MICL0.00912034/DBL
Build-In Floor | Mini Canal | MICL.00912034/DBN | 9 | 120 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.00912034/DBN
Build-In Floor | Mini Canal | MICL.00912034/DBR | 9 | 120 | 34 | 34 | 336 | 336 | 336 | 0.008 | 131 | 0.003119 | 383 | 0.009119 | 1.362 | A04 | MICL0.00912034/DBR
Build-In Floor | Mini Canal | MICL.00912034/DBV | 9 | 120 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.00912034/DBV
Build-In Floor | Mini Canal | MICL.00912034/DDB | 9 | 120 | 34 | 34 | 336 | 336 | 336 | 0.008 | 131 | 0.003119 | 383 | 0.009119 | 1.362 | A04 | MICL0.00912034/DDB
Build-In Floor | Mini Canal | MICL.00912034/DMN | 9 | 120 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.00912034/DMN
Build-In Floor | Mini Canal | MICL.00912034/DMV | 9 | 120 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.00912034/DMV
Build-In Floor | Mini Canal | MICL.00912034/DNA | 9 | 120 | 34 | 34 | 336 | 336 | 336 | 0.008 | 131 | 0.003119 | 383 | 0.009119 | 1.362 | A04 | MICL0.00912034/DNA
Build-In Floor | Mini Canal | MICL.00912034/DNC | 9 | 120 | 34 | 34 | 336 | 336 | 336 | 0.008 | 131 | 0.003119 | 383 | 0.009119 | 1.362 | A04 | MICL0.00912034/DNC
Build-In Floor | Mini Canal | MICL.00912034/DON | 9 | 120 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.00912034/DON
Build-In Floor | Mini Canal | MICL.00912034/DOV | 9 | 120 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.00912034/DOV
Build-In Floor | Mini Canal | MICL.00912034/PNC | 9 | 120 | 34 | 34 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.00912034/PNC
Build-In Floor | Mini Canal | MICL.00912034/RBL | 9 | 120 | 34 | 34 | 346 | 346 | 346 | 0.0082381 | 135 | 0.0032143 | 394 | 0.009381 | 1.362 | A04 | MICL0.00912034/RBL
Build-In Floor | Mini Canal | MICL.00912034/RBN | 9 | 120 | 34 | 34 | 336 | 336 | 336 | 0.008 | 131 | 0.003119 | 383 | 0.009119 | 1.362 | A04 | MICL0.00912034/RBN
Build-In Floor | Mini Canal | MICL.00912034/RBR | 9 | 120 | 34 | 34 | 346 | 346 | 346 | 0.0082381 | 135 | 0.0032143 | 394 | 0.009381 | 1.362 | A04 | MICL0.00912034/RBR
Build-In Floor | Mini Canal | MICL.00912034/RBV | 9 | 120 | 34 | 34 | 336 | 336 | 336 | 0.008 | 131 | 0.003119 | 383 | 0.009119 | 1.362 | A04 | MICL0.00912034/RBV
Build-In Floor | Mini Canal | MICL.00912034/RDB | 9 | 120 | 34 | 34 | 346 | 346 | 346 | 0.0082381 | 135 | 0.0032143 | 394 | 0.009381 | 1.362 | A04 | MICL0.00912034/RDB
Build-In Floor | Mini Canal | MICL.00912034/RMN | 9 | 120 | 34 | 34 | 336 | 336 | 336 | 0.008 | 131 | 0.003119 | 383 | 0.009119 | 1.362 | A04 | MICL0.00912034/RMN
Build-In Floor | Mini Canal | MICL.00912034/RMV | 9 | 120 | 34 | 34 | 336 | 336 | 336 | 0.008 | 131 | 0.003119 | 383 | 0.009119 | 1.362 | A04 | MICL0.00912034/RMV
Build-In Floor | Mini Canal | MICL.00912034/RNA | 9 | 120 | 34 | 34 | 346 | 346 | 346 | 0.0082381 | 135 | 0.0032143 | 394 | 0.009381 | 1.362 | A04 | MICL0.00912034/RNA
Build-In Floor | Mini Canal | MICL.00912034/RON | 9 | 120 | 34 | 34 | 336 | 336 | 336 | 0.008 | 131 | 0.003119 | 383 | 0.009119 | 1.362 | A04 | MICL0.00912034/RON
Build-In Floor | Mini Canal | MICL.00912034/ROV | 9 | 120 | 34 | 34 | 336 | 336 | 336 | 0.008 | 131 | 0.003119 | 383 | 0.009119 | 1.362 | A04 | MICL0.00912034/ROV
Build-In Floor | Mini Canal | MICL.00912034/RSS | 9 | 120 | 34 | 34 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.00912034/RSS
Build-In Floor | Mini Canal | MICL.00912034/SBL | 9 | 120 | 34 | 34 | 346 | 346 | 346 | 0.0082381 | 135 | 0.0032143 | 394 | 0.009381 | 1.362 | A04 | MICL0.00912034/SBL
Build-In Floor | Mini Canal | MICL.00912034/SBR | 9 | 120 | 34 | 34 | 346 | 346 | 346 | 0.0082381 | 135 | 0.0032143 | 394 | 0.009381 | 1.362 | A04 | MICL0.00912034/SBR
Build-In Floor | Mini Canal | MICL.00912034/SDB | 9 | 120 | 34 | 34 | 346 | 346 | 346 | 0.0082381 | 135 | 0.0032143 | 394 | 0.009381 | 1.362 | A04 | MICL0.00912034/SDB
Build-In Floor | Mini Canal | MICL.00912034/SNA | 9 | 120 | 34 | 34 | 346 | 346 | 346 | 0.0082381 | 135 | 0.0032143 | 394 | 0.009381 | 1.362 | A04 | MICL0.00912034/SNA
Build-In Floor | Mini Canal | MICL.00912034/SNC | 9 | 120 | 34 | 34 | 346 | 346 | 346 | 0.0082381 | 135 | 0.0032143 | 394 | 0.009381 | 1.362 | A04 | MICL0.00912034/SNC
Build-In Floor | Mini Canal | MICL.00912042/ANA | 9 | 120 | 42 | 42 | 375 | 375 | 375 | 0.0089286 | 146 | 0.0034762 | 427 | 0.010167 | 1.362 | A04 | MICL0.00912042/ANA
Build-In Floor | Mini Canal | MICL.00912042/DBL | 9 | 120 | 42 | 42 | 485 | 485 | 485 | 0.011548 | 189 | 0.0045 | 552 | 0.013143 | 1.362 | A04 | MICL0.00912042/DBL
Build-In Floor | Mini Canal | MICL.00912042/DBN | 9 | 120 | 42 | 42 | 465 | 465 | 465 | 0.011071 | 181 | 0.0043095 | 530 | 0.012619 | 1.362 | A04 | MICL0.00912042/DBN
Build-In Floor | Mini Canal | MICL.00912042/DBR | 9 | 120 | 42 | 42 | 485 | 485 | 485 | 0.011548 | 189 | 0.0045 | 552 | 0.013143 | 1.362 | A04 | MICL0.00912042/DBR
Build-In Floor | Mini Canal | MICL.00912042/DBV | 9 | 120 | 42 | 42 | 465 | 465 | 465 | 0.011071 | 181 | 0.0043095 | 530 | 0.012619 | 1.362 | A04 | MICL0.00912042/DBV
Build-In Floor | Mini Canal | MICL.00912042/DDB | 9 | 120 | 42 | 42 | 485 | 485 | 485 | 0.011548 | 189 | 0.0045 | 552 | 0.013143 | 1.362 | A04 | MICL0.00912042/DDB
Build-In Floor | Mini Canal | MICL.00912042/DMN | 9 | 120 | 42 | 42 | 465 | 465 | 465 | 0.011071 | 181 | 0.0043095 | 530 | 0.012619 | 1.362 | A04 | MICL0.00912042/DMN
Build-In Floor | Mini Canal | MICL.00912042/DMV | 9 | 120 | 42 | 42 | 465 | 465 | 465 | 0.011071 | 181 | 0.0043095 | 530 | 0.012619 | 1.362 | A04 | MICL0.00912042/DMV
Build-In Floor | Mini Canal | MICL.00912042/DNA | 9 | 120 | 42 | 42 | 485 | 485 | 485 | 0.011548 | 189 | 0.0045 | 552 | 0.013143 | 1.362 | A04 | MICL0.00912042/DNA
Build-In Floor | Mini Canal | MICL.00912042/DNC | 9 | 120 | 42 | 42 | 485 | 485 | 485 | 0.011548 | 189 | 0.0045 | 552 | 0.013143 | 1.362 | A04 | MICL0.00912042/DNC
Build-In Floor | Mini Canal | MICL.00912042/DON | 9 | 120 | 42 | 42 | 465 | 465 | 465 | 0.011071 | 181 | 0.0043095 | 530 | 0.012619 | 1.362 | A04 | MICL0.00912042/DON
Build-In Floor | Mini Canal | MICL.00912042/DOV | 9 | 120 | 42 | 42 | 465 | 465 | 465 | 0.011071 | 181 | 0.0043095 | 530 | 0.012619 | 1.362 | A04 | MICL0.00912042/DOV
Build-In Floor | Mini Canal | MICL.00912042/PNC | 9 | 120 | 42 | 42 | 425 | 425 | 425 | 0.010119 | 165 | 0.0039286 | 484 | 0.011524 | 1.362 | A04 | MICL0.00912042/PNC
Build-In Floor | Mini Canal | MICL.00912042/RBL | 9 | 120 | 42 | 42 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00912042/RBL
Build-In Floor | Mini Canal | MICL.00912042/RBN | 9 | 120 | 42 | 42 | 485 | 485 | 485 | 0.011548 | 189 | 0.0045 | 552 | 0.013143 | 1.362 | A04 | MICL0.00912042/RBN
Build-In Floor | Mini Canal | MICL.00912042/RBR | 9 | 120 | 42 | 42 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00912042/RBR
Build-In Floor | Mini Canal | MICL.00912042/RBV | 9 | 120 | 42 | 42 | 485 | 485 | 485 | 0.011548 | 189 | 0.0045 | 552 | 0.013143 | 1.362 | A04 | MICL0.00912042/RBV
Build-In Floor | Mini Canal | MICL.00912042/RDB | 9 | 120 | 42 | 42 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00912042/RDB
Build-In Floor | Mini Canal | MICL.00912042/RMN | 9 | 120 | 42 | 42 | 485 | 485 | 485 | 0.011548 | 189 | 0.0045 | 552 | 0.013143 | 1.362 | A04 | MICL0.00912042/RMN
Build-In Floor | Mini Canal | MICL.00912042/RMV | 9 | 120 | 42 | 42 | 485 | 485 | 485 | 0.011548 | 189 | 0.0045 | 552 | 0.013143 | 1.362 | A04 | MICL0.00912042/RMV
Build-In Floor | Mini Canal | MICL.00912042/RNA | 9 | 120 | 42 | 42 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00912042/RNA
Build-In Floor | Mini Canal | MICL.00912042/RON | 9 | 120 | 42 | 42 | 485 | 485 | 485 | 0.011548 | 189 | 0.0045 | 552 | 0.013143 | 1.362 | A04 | MICL0.00912042/RON
Build-In Floor | Mini Canal | MICL.00912042/ROV | 9 | 120 | 42 | 42 | 485 | 485 | 485 | 0.011548 | 189 | 0.0045 | 552 | 0.013143 | 1.362 | A04 | MICL0.00912042/ROV
Build-In Floor | Mini Canal | MICL.00912042/RSS | 9 | 120 | 42 | 42 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.00912042/RSS
Build-In Floor | Mini Canal | MICL.00912042/SBL | 9 | 120 | 42 | 42 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00912042/SBL
Build-In Floor | Mini Canal | MICL.00912042/SBR | 9 | 120 | 42 | 42 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00912042/SBR
Build-In Floor | Mini Canal | MICL.00912042/SDB | 9 | 120 | 42 | 42 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00912042/SDB
Build-In Floor | Mini Canal | MICL.00912042/SNA | 9 | 120 | 42 | 42 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00912042/SNA
Build-In Floor | Mini Canal | MICL.00912042/SNC | 9 | 120 | 42 | 42 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00912042/SNC
Build-In Floor | Mini Canal | MICL.00913014/ANA | 9 | 130 | 14 | 14 | 143 | 143 | 143 | 0.0034048 | 56 | 0.0013333 | 163 | 0.003881 | 1.362 | A04 | MICL0.00913014/ANA
Build-In Floor | Mini Canal | MICL.00913014/DBL | 9 | 130 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.00913014/DBL
Build-In Floor | Mini Canal | MICL.00913014/DBN | 9 | 130 | 14 | 14 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.00913014/DBN
Build-In Floor | Mini Canal | MICL.00913014/DBR | 9 | 130 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.00913014/DBR
Build-In Floor | Mini Canal | MICL.00913014/DBV | 9 | 130 | 14 | 14 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.00913014/DBV
Build-In Floor | Mini Canal | MICL.00913014/DDB | 9 | 130 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.00913014/DDB
Build-In Floor | Mini Canal | MICL.00913014/DMN | 9 | 130 | 14 | 14 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.00913014/DMN
Build-In Floor | Mini Canal | MICL.00913014/DMV | 9 | 130 | 14 | 14 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.00913014/DMV
Build-In Floor | Mini Canal | MICL.00913014/DNA | 9 | 130 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.00913014/DNA
Build-In Floor | Mini Canal | MICL.00913014/DNC | 9 | 130 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.00913014/DNC
Build-In Floor | Mini Canal | MICL.00913014/DON | 9 | 130 | 14 | 14 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.00913014/DON
Build-In Floor | Mini Canal | MICL.00913014/DOV | 9 | 130 | 14 | 14 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.00913014/DOV
Build-In Floor | Mini Canal | MICL.00913014/RBL | 9 | 130 | 14 | 14 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.00913014/RBL
Build-In Floor | Mini Canal | MICL.00913014/RBN | 9 | 130 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.00913014/RBN
Build-In Floor | Mini Canal | MICL.00913014/RBR | 9 | 130 | 14 | 14 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.00913014/RBR
Build-In Floor | Mini Canal | MICL.00913014/RBV | 9 | 130 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.00913014/RBV
Build-In Floor | Mini Canal | MICL.00913014/RDB | 9 | 130 | 14 | 14 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.00913014/RDB
Build-In Floor | Mini Canal | MICL.00913014/RMN | 9 | 130 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.00913014/RMN
Build-In Floor | Mini Canal | MICL.00913014/RMV | 9 | 130 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.00913014/RMV
Build-In Floor | Mini Canal | MICL.00913014/RNA | 9 | 130 | 14 | 14 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.00913014/RNA
Build-In Floor | Mini Canal | MICL.00913014/RON | 9 | 130 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.00913014/RON
Build-In Floor | Mini Canal | MICL.00913014/ROV | 9 | 130 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.00913014/ROV
Build-In Floor | Mini Canal | MICL.00913014/RSS | 9 | 130 | 14 | 14 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.00913014/RSS
Build-In Floor | Mini Canal | MICL.00913014/SBL | 9 | 130 | 14 | 14 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.00913014/SBL
Build-In Floor | Mini Canal | MICL.00913014/SBR | 9 | 130 | 14 | 14 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.00913014/SBR
Build-In Floor | Mini Canal | MICL.00913014/SDB | 9 | 130 | 14 | 14 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.00913014/SDB
Build-In Floor | Mini Canal | MICL.00913014/SNA | 9 | 130 | 14 | 14 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.00913014/SNA
Build-In Floor | Mini Canal | MICL.00913014/SNC | 9 | 130 | 14 | 14 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.00913014/SNC
Build-In Floor | Mini Canal | MICL.00913018/ANA | 9 | 130 | 18 | 18 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.00913018/ANA
Build-In Floor | Mini Canal | MICL.00913018/DBL | 9 | 130 | 18 | 18 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.00913018/DBL
Build-In Floor | Mini Canal | MICL.00913018/DBN | 9 | 130 | 18 | 18 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.00913018/DBN
Build-In Floor | Mini Canal | MICL.00913018/DBR | 9 | 130 | 18 | 18 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.00913018/DBR
Build-In Floor | Mini Canal | MICL.00913018/DBV | 9 | 130 | 18 | 18 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.00913018/DBV
Build-In Floor | Mini Canal | MICL.00913018/DDB | 9 | 130 | 18 | 18 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.00913018/DDB
Build-In Floor | Mini Canal | MICL.00913018/DMN | 9 | 130 | 18 | 18 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.00913018/DMN
Build-In Floor | Mini Canal | MICL.00913018/DMV | 9 | 130 | 18 | 18 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.00913018/DMV
Build-In Floor | Mini Canal | MICL.00913018/DNA | 9 | 130 | 18 | 18 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.00913018/DNA
Build-In Floor | Mini Canal | MICL.00913018/DNC | 9 | 130 | 18 | 18 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.00913018/DNC
Build-In Floor | Mini Canal | MICL.00913018/DON | 9 | 130 | 18 | 18 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.00913018/DON
Build-In Floor | Mini Canal | MICL.00913018/DOV | 9 | 130 | 18 | 18 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.00913018/DOV
Build-In Floor | Mini Canal | MICL.00913018/RBL | 9 | 130 | 18 | 18 | 225 | 225 | 225 | 0.0053571 | 88 | 0.0020952 | 256 | 0.0060952 | 1.362 | A04 | MICL0.00913018/RBL
Build-In Floor | Mini Canal | MICL.00913018/RBN | 9 | 130 | 18 | 18 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.00913018/RBN
Build-In Floor | Mini Canal | MICL.00913018/RBR | 9 | 130 | 18 | 18 | 225 | 225 | 225 | 0.0053571 | 88 | 0.0020952 | 256 | 0.0060952 | 1.362 | A04 | MICL0.00913018/RBR
Build-In Floor | Mini Canal | MICL.00913018/RBV | 9 | 130 | 18 | 18 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.00913018/RBV
Build-In Floor | Mini Canal | MICL.00913018/RDB | 9 | 130 | 18 | 18 | 225 | 225 | 225 | 0.0053571 | 88 | 0.0020952 | 256 | 0.0060952 | 1.362 | A04 | MICL0.00913018/RDB
Build-In Floor | Mini Canal | MICL.00913018/RMN | 9 | 130 | 18 | 18 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.00913018/RMN
Build-In Floor | Mini Canal | MICL.00913018/RMV | 9 | 130 | 18 | 18 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.00913018/RMV
Build-In Floor | Mini Canal | MICL.00913018/RNA | 9 | 130 | 18 | 18 | 225 | 225 | 225 | 0.0053571 | 88 | 0.0020952 | 256 | 0.0060952 | 1.362 | A04 | MICL0.00913018/RNA
Build-In Floor | Mini Canal | MICL.00913018/RON | 9 | 130 | 18 | 18 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.00913018/RON
Build-In Floor | Mini Canal | MICL.00913018/ROV | 9 | 130 | 18 | 18 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.00913018/ROV
Build-In Floor | Mini Canal | MICL.00913018/RSS | 9 | 130 | 18 | 18 | 216 | 216 | 216 | 0.0051429 | 84 | 0.002 | 246 | 0.0058571 | 1.362 | A04 | MICL0.00913018/RSS
Build-In Floor | Mini Canal | MICL.00913018/SBL | 9 | 130 | 18 | 18 | 225 | 225 | 225 | 0.0053571 | 88 | 0.0020952 | 256 | 0.0060952 | 1.362 | A04 | MICL0.00913018/SBL
Build-In Floor | Mini Canal | MICL.00913018/SBR | 9 | 130 | 18 | 18 | 225 | 225 | 225 | 0.0053571 | 88 | 0.0020952 | 256 | 0.0060952 | 1.362 | A04 | MICL0.00913018/SBR
Build-In Floor | Mini Canal | MICL.00913018/SDB | 9 | 130 | 18 | 18 | 225 | 225 | 225 | 0.0053571 | 88 | 0.0020952 | 256 | 0.0060952 | 1.362 | A04 | MICL0.00913018/SDB
Build-In Floor | Mini Canal | MICL.00913018/SNA | 9 | 130 | 18 | 18 | 225 | 225 | 225 | 0.0053571 | 88 | 0.0020952 | 256 | 0.0060952 | 1.362 | A04 | MICL0.00913018/SNA
Build-In Floor | Mini Canal | MICL.00913018/SNC | 9 | 130 | 18 | 18 | 225 | 225 | 225 | 0.0053571 | 88 | 0.0020952 | 256 | 0.0060952 | 1.362 | A04 | MICL0.00913018/SNC
Build-In Floor | Mini Canal | MICL.00913026/ANA | 9 | 130 | 26 | 26 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00913026/ANA
Build-In Floor | Mini Canal | MICL.00913026/DBL | 9 | 130 | 26 | 26 | 287 | 287 | 287 | 0.0068333 | 112 | 0.0026667 | 327 | 0.0077857 | 1.362 | A04 | MICL0.00913026/DBL
Build-In Floor | Mini Canal | MICL.00913026/DBN | 9 | 130 | 26 | 26 | 275 | 275 | 275 | 0.0065476 | 107 | 0.0025476 | 313 | 0.0074524 | 1.362 | A04 | MICL0.00913026/DBN
Build-In Floor | Mini Canal | MICL.00913026/DBR | 9 | 130 | 26 | 26 | 287 | 287 | 287 | 0.0068333 | 112 | 0.0026667 | 327 | 0.0077857 | 1.362 | A04 | MICL0.00913026/DBR
Build-In Floor | Mini Canal | MICL.00913026/DBV | 9 | 130 | 26 | 26 | 275 | 275 | 275 | 0.0065476 | 107 | 0.0025476 | 313 | 0.0074524 | 1.362 | A04 | MICL0.00913026/DBV
Build-In Floor | Mini Canal | MICL.00913026/DDB | 9 | 130 | 26 | 26 | 287 | 287 | 287 | 0.0068333 | 112 | 0.0026667 | 327 | 0.0077857 | 1.362 | A04 | MICL0.00913026/DDB
Build-In Floor | Mini Canal | MICL.00913026/DMN | 9 | 130 | 26 | 26 | 275 | 275 | 275 | 0.0065476 | 107 | 0.0025476 | 313 | 0.0074524 | 1.362 | A04 | MICL0.00913026/DMN
Build-In Floor | Mini Canal | MICL.00913026/DMV | 9 | 130 | 26 | 26 | 275 | 275 | 275 | 0.0065476 | 107 | 0.0025476 | 313 | 0.0074524 | 1.362 | A04 | MICL0.00913026/DMV
Build-In Floor | Mini Canal | MICL.00913026/DNA | 9 | 130 | 26 | 26 | 287 | 287 | 287 | 0.0068333 | 112 | 0.0026667 | 327 | 0.0077857 | 1.362 | A04 | MICL0.00913026/DNA
Build-In Floor | Mini Canal | MICL.00913026/DNC | 9 | 130 | 26 | 26 | 287 | 287 | 287 | 0.0068333 | 112 | 0.0026667 | 327 | 0.0077857 | 1.362 | A04 | MICL0.00913026/DNC
Build-In Floor | Mini Canal | MICL.00913026/DON | 9 | 130 | 26 | 26 | 275 | 275 | 275 | 0.0065476 | 107 | 0.0025476 | 313 | 0.0074524 | 1.362 | A04 | MICL0.00913026/DON
Build-In Floor | Mini Canal | MICL.00913026/DOV | 9 | 130 | 26 | 26 | 275 | 275 | 275 | 0.0065476 | 107 | 0.0025476 | 313 | 0.0074524 | 1.362 | A04 | MICL0.00913026/DOV
Build-In Floor | Mini Canal | MICL.00913026/PNC | 9 | 130 | 26 | 26 | 252 | 252 | 252 | 0.006 | 98 | 0.0023333 | 287 | 0.0068333 | 1.362 | A04 | MICL0.00913026/PNC
Build-In Floor | Mini Canal | MICL.00913026/RBL | 9 | 130 | 26 | 26 | 296 | 296 | 296 | 0.0070476 | 115 | 0.0027381 | 337 | 0.0080238 | 1.362 | A04 | MICL0.00913026/RBL
Build-In Floor | Mini Canal | MICL.00913026/RBN | 9 | 130 | 26 | 26 | 287 | 287 | 287 | 0.0068333 | 112 | 0.0026667 | 327 | 0.0077857 | 1.362 | A04 | MICL0.00913026/RBN
Build-In Floor | Mini Canal | MICL.00913026/RBR | 9 | 130 | 26 | 26 | 296 | 296 | 296 | 0.0070476 | 115 | 0.0027381 | 337 | 0.0080238 | 1.362 | A04 | MICL0.00913026/RBR
Build-In Floor | Mini Canal | MICL.00913026/RBV | 9 | 130 | 26 | 26 | 287 | 287 | 287 | 0.0068333 | 112 | 0.0026667 | 327 | 0.0077857 | 1.362 | A04 | MICL0.00913026/RBV
Build-In Floor | Mini Canal | MICL.00913026/RDB | 9 | 130 | 26 | 26 | 296 | 296 | 296 | 0.0070476 | 115 | 0.0027381 | 337 | 0.0080238 | 1.362 | A04 | MICL0.00913026/RDB
Build-In Floor | Mini Canal | MICL.00913026/RMN | 9 | 130 | 26 | 26 | 287 | 287 | 287 | 0.0068333 | 112 | 0.0026667 | 327 | 0.0077857 | 1.362 | A04 | MICL0.00913026/RMN
Build-In Floor | Mini Canal | MICL.00913026/RMV | 9 | 130 | 26 | 26 | 287 | 287 | 287 | 0.0068333 | 112 | 0.0026667 | 327 | 0.0077857 | 1.362 | A04 | MICL0.00913026/RMV
Build-In Floor | Mini Canal | MICL.00913026/RNA | 9 | 130 | 26 | 26 | 296 | 296 | 296 | 0.0070476 | 115 | 0.0027381 | 337 | 0.0080238 | 1.362 | A04 | MICL0.00913026/RNA
Build-In Floor | Mini Canal | MICL.00913026/RON | 9 | 130 | 26 | 26 | 287 | 287 | 287 | 0.0068333 | 112 | 0.0026667 | 327 | 0.0077857 | 1.362 | A04 | MICL0.00913026/RON
Build-In Floor | Mini Canal | MICL.00913026/ROV | 9 | 130 | 26 | 26 | 287 | 287 | 287 | 0.0068333 | 112 | 0.0026667 | 327 | 0.0077857 | 1.362 | A04 | MICL0.00913026/ROV
Build-In Floor | Mini Canal | MICL.00913026/RSS | 9 | 130 | 26 | 26 | 284 | 284 | 284 | 0.0067619 | 110 | 0.002619 | 323 | 0.0076905 | 1.362 | A04 | MICL0.00913026/RSS
Build-In Floor | Mini Canal | MICL.00913026/SBL | 9 | 130 | 26 | 26 | 296 | 296 | 296 | 0.0070476 | 115 | 0.0027381 | 337 | 0.0080238 | 1.362 | A04 | MICL0.00913026/SBL
Build-In Floor | Mini Canal | MICL.00913026/SBR | 9 | 130 | 26 | 26 | 296 | 296 | 296 | 0.0070476 | 115 | 0.0027381 | 337 | 0.0080238 | 1.362 | A04 | MICL0.00913026/SBR
Build-In Floor | Mini Canal | MICL.00913026/SDB | 9 | 130 | 26 | 26 | 296 | 296 | 296 | 0.0070476 | 115 | 0.0027381 | 337 | 0.0080238 | 1.362 | A04 | MICL0.00913026/SDB
Build-In Floor | Mini Canal | MICL.00913026/SNA | 9 | 130 | 26 | 26 | 296 | 296 | 296 | 0.0070476 | 115 | 0.0027381 | 337 | 0.0080238 | 1.362 | A04 | MICL0.00913026/SNA
Build-In Floor | Mini Canal | MICL.00913026/SNC | 9 | 130 | 26 | 26 | 296 | 296 | 296 | 0.0070476 | 115 | 0.0027381 | 337 | 0.0080238 | 1.362 | A04 | MICL0.00913026/SNC
Build-In Floor | Mini Canal | MICL.00913034/ANA | 9 | 130 | 34 | 34 | 289 | 289 | 289 | 0.006881 | 112 | 0.0026667 | 329 | 0.0078333 | 1.362 | A04 | MICL0.00913034/ANA
Build-In Floor | Mini Canal | MICL.00913034/DBL | 9 | 130 | 34 | 34 | 373 | 373 | 373 | 0.008881 | 145 | 0.0034524 | 425 | 0.010119 | 1.362 | A04 | MICL0.00913034/DBL
Build-In Floor | Mini Canal | MICL.00913034/DBN | 9 | 130 | 34 | 34 | 358 | 358 | 358 | 0.0085238 | 139 | 0.0033095 | 408 | 0.0097143 | 1.362 | A04 | MICL0.00913034/DBN
Build-In Floor | Mini Canal | MICL.00913034/DBR | 9 | 130 | 34 | 34 | 373 | 373 | 373 | 0.008881 | 145 | 0.0034524 | 425 | 0.010119 | 1.362 | A04 | MICL0.00913034/DBR
Build-In Floor | Mini Canal | MICL.00913034/DBV | 9 | 130 | 34 | 34 | 358 | 358 | 358 | 0.0085238 | 139 | 0.0033095 | 408 | 0.0097143 | 1.362 | A04 | MICL0.00913034/DBV
Build-In Floor | Mini Canal | MICL.00913034/DDB | 9 | 130 | 34 | 34 | 373 | 373 | 373 | 0.008881 | 145 | 0.0034524 | 425 | 0.010119 | 1.362 | A04 | MICL0.00913034/DDB
Build-In Floor | Mini Canal | MICL.00913034/DMN | 9 | 130 | 34 | 34 | 358 | 358 | 358 | 0.0085238 | 139 | 0.0033095 | 408 | 0.0097143 | 1.362 | A04 | MICL0.00913034/DMN
Build-In Floor | Mini Canal | MICL.00913034/DMV | 9 | 130 | 34 | 34 | 358 | 358 | 358 | 0.0085238 | 139 | 0.0033095 | 408 | 0.0097143 | 1.362 | A04 | MICL0.00913034/DMV
Build-In Floor | Mini Canal | MICL.00913034/DNA | 9 | 130 | 34 | 34 | 373 | 373 | 373 | 0.008881 | 145 | 0.0034524 | 425 | 0.010119 | 1.362 | A04 | MICL0.00913034/DNA
Build-In Floor | Mini Canal | MICL.00913034/DNC | 9 | 130 | 34 | 34 | 373 | 373 | 373 | 0.008881 | 145 | 0.0034524 | 425 | 0.010119 | 1.362 | A04 | MICL0.00913034/DNC
Build-In Floor | Mini Canal | MICL.00913034/DON | 9 | 130 | 34 | 34 | 358 | 358 | 358 | 0.0085238 | 139 | 0.0033095 | 408 | 0.0097143 | 1.362 | A04 | MICL0.00913034/DON
Build-In Floor | Mini Canal | MICL.00913034/DOV | 9 | 130 | 34 | 34 | 358 | 358 | 358 | 0.0085238 | 139 | 0.0033095 | 408 | 0.0097143 | 1.362 | A04 | MICL0.00913034/DOV
Build-In Floor | Mini Canal | MICL.00913034/PNC | 9 | 130 | 34 | 34 | 327 | 327 | 327 | 0.0077857 | 127 | 0.0030238 | 372 | 0.0088571 | 1.362 | A04 | MICL0.00913034/PNC
Build-In Floor | Mini Canal | MICL.00913034/RBL | 9 | 130 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.00913034/RBL
Build-In Floor | Mini Canal | MICL.00913034/RBN | 9 | 130 | 34 | 34 | 373 | 373 | 373 | 0.008881 | 145 | 0.0034524 | 425 | 0.010119 | 1.362 | A04 | MICL0.00913034/RBN
Build-In Floor | Mini Canal | MICL.00913034/RBR | 9 | 130 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.00913034/RBR
Build-In Floor | Mini Canal | MICL.00913034/RBV | 9 | 130 | 34 | 34 | 373 | 373 | 373 | 0.008881 | 145 | 0.0034524 | 425 | 0.010119 | 1.362 | A04 | MICL0.00913034/RBV
Build-In Floor | Mini Canal | MICL.00913034/RDB | 9 | 130 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.00913034/RDB
Build-In Floor | Mini Canal | MICL.00913034/RMN | 9 | 130 | 34 | 34 | 373 | 373 | 373 | 0.008881 | 145 | 0.0034524 | 425 | 0.010119 | 1.362 | A04 | MICL0.00913034/RMN
Build-In Floor | Mini Canal | MICL.00913034/RMV | 9 | 130 | 34 | 34 | 373 | 373 | 373 | 0.008881 | 145 | 0.0034524 | 425 | 0.010119 | 1.362 | A04 | MICL0.00913034/RMV
Build-In Floor | Mini Canal | MICL.00913034/RNA | 9 | 130 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.00913034/RNA
Build-In Floor | Mini Canal | MICL.00913034/RON | 9 | 130 | 34 | 34 | 373 | 373 | 373 | 0.008881 | 145 | 0.0034524 | 425 | 0.010119 | 1.362 | A04 | MICL0.00913034/RON
Build-In Floor | Mini Canal | MICL.00913034/ROV | 9 | 130 | 34 | 34 | 373 | 373 | 373 | 0.008881 | 145 | 0.0034524 | 425 | 0.010119 | 1.362 | A04 | MICL0.00913034/ROV
Build-In Floor | Mini Canal | MICL.00913034/RSS | 9 | 130 | 34 | 34 | 370 | 370 | 370 | 0.0088095 | 144 | 0.0034286 | 421 | 0.010024 | 1.362 | A04 | MICL0.00913034/RSS
Build-In Floor | Mini Canal | MICL.00913034/SBL | 9 | 130 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.00913034/SBL
Build-In Floor | Mini Canal | MICL.00913034/SBR | 9 | 130 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.00913034/SBR
Build-In Floor | Mini Canal | MICL.00913034/SDB | 9 | 130 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.00913034/SDB
Build-In Floor | Mini Canal | MICL.00913034/SNA | 9 | 130 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.00913034/SNA
Build-In Floor | Mini Canal | MICL.00913034/SNC | 9 | 130 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.00913034/SNC
Build-In Floor | Mini Canal | MICL.00913042/ANA | 9 | 130 | 42 | 42 | 416 | 416 | 416 | 0.0099048 | 162 | 0.0038571 | 474 | 0.011286 | 1.362 | A04 | MICL0.00913042/ANA
Build-In Floor | Mini Canal | MICL.00913042/DBL | 9 | 130 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00913042/DBL
Build-In Floor | Mini Canal | MICL.00913042/DBN | 9 | 130 | 42 | 42 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.00913042/DBN
Build-In Floor | Mini Canal | MICL.00913042/DBR | 9 | 130 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00913042/DBR
Build-In Floor | Mini Canal | MICL.00913042/DBV | 9 | 130 | 42 | 42 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.00913042/DBV
Build-In Floor | Mini Canal | MICL.00913042/DDB | 9 | 130 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00913042/DDB
Build-In Floor | Mini Canal | MICL.00913042/DMN | 9 | 130 | 42 | 42 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.00913042/DMN
Build-In Floor | Mini Canal | MICL.00913042/DMV | 9 | 130 | 42 | 42 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.00913042/DMV
Build-In Floor | Mini Canal | MICL.00913042/DNA | 9 | 130 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00913042/DNA
Build-In Floor | Mini Canal | MICL.00913042/DNC | 9 | 130 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00913042/DNC
Build-In Floor | Mini Canal | MICL.00913042/DON | 9 | 130 | 42 | 42 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.00913042/DON
Build-In Floor | Mini Canal | MICL.00913042/DOV | 9 | 130 | 42 | 42 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.00913042/DOV
Build-In Floor | Mini Canal | MICL.00913042/PNC | 9 | 130 | 42 | 42 | 472 | 472 | 472 | 0.011238 | 184 | 0.004381 | 538 | 0.01281 | 1.362 | A04 | MICL0.00913042/PNC
Build-In Floor | Mini Canal | MICL.00913042/RBL | 9 | 130 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.00913042/RBL
Build-In Floor | Mini Canal | MICL.00913042/RBN | 9 | 130 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00913042/RBN
Build-In Floor | Mini Canal | MICL.00913042/RBR | 9 | 130 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.00913042/RBR
Build-In Floor | Mini Canal | MICL.00913042/RBV | 9 | 130 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00913042/RBV
Build-In Floor | Mini Canal | MICL.00913042/RDB | 9 | 130 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.00913042/RDB
Build-In Floor | Mini Canal | MICL.00913042/RMN | 9 | 130 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00913042/RMN
Build-In Floor | Mini Canal | MICL.00913042/RMV | 9 | 130 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00913042/RMV
Build-In Floor | Mini Canal | MICL.00913042/RNA | 9 | 130 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.00913042/RNA
Build-In Floor | Mini Canal | MICL.00913042/RON | 9 | 130 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00913042/RON
Build-In Floor | Mini Canal | MICL.00913042/ROV | 9 | 130 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00913042/ROV
Build-In Floor | Mini Canal | MICL.00913042/RSS | 9 | 130 | 42 | 42 | 533 | 533 | 533 | 0.01269 | 207 | 0.0049286 | 607 | 0.014452 | 1.362 | A04 | MICL0.00913042/RSS
Build-In Floor | Mini Canal | MICL.00913042/SBL | 9 | 130 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.00913042/SBL
Build-In Floor | Mini Canal | MICL.00913042/SBR | 9 | 130 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.00913042/SBR
Build-In Floor | Mini Canal | MICL.00913042/SDB | 9 | 130 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.00913042/SDB
Build-In Floor | Mini Canal | MICL.00913042/SNA | 9 | 130 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.00913042/SNA
Build-In Floor | Mini Canal | MICL.00913042/SNC | 9 | 130 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.00913042/SNC
Build-In Floor | Mini Canal | MICL.00915014/ANA | 9 | 150 | 14 | 14 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.00915014/ANA
Build-In Floor | Mini Canal | MICL.00915014/DBL | 9 | 150 | 14 | 14 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00915014/DBL
Build-In Floor | Mini Canal | MICL.00915014/DBN | 9 | 150 | 14 | 14 | 213 | 213 | 213 | 0.0050714 | 83 | 0.0019762 | 243 | 0.0057857 | 1.362 | A04 | MICL0.00915014/DBN
Build-In Floor | Mini Canal | MICL.00915014/DBR | 9 | 150 | 14 | 14 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00915014/DBR
Build-In Floor | Mini Canal | MICL.00915014/DBV | 9 | 150 | 14 | 14 | 213 | 213 | 213 | 0.0050714 | 83 | 0.0019762 | 243 | 0.0057857 | 1.362 | A04 | MICL0.00915014/DBV
Build-In Floor | Mini Canal | MICL.00915014/DDB | 9 | 150 | 14 | 14 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00915014/DDB
Build-In Floor | Mini Canal | MICL.00915014/DMN | 9 | 150 | 14 | 14 | 213 | 213 | 213 | 0.0050714 | 83 | 0.0019762 | 243 | 0.0057857 | 1.362 | A04 | MICL0.00915014/DMN
Build-In Floor | Mini Canal | MICL.00915014/DMV | 9 | 150 | 14 | 14 | 213 | 213 | 213 | 0.0050714 | 83 | 0.0019762 | 243 | 0.0057857 | 1.362 | A04 | MICL0.00915014/DMV
Build-In Floor | Mini Canal | MICL.00915014/DNA | 9 | 150 | 14 | 14 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00915014/DNA
Build-In Floor | Mini Canal | MICL.00915014/DNC | 9 | 150 | 14 | 14 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00915014/DNC
Build-In Floor | Mini Canal | MICL.00915014/DON | 9 | 150 | 14 | 14 | 213 | 213 | 213 | 0.0050714 | 83 | 0.0019762 | 243 | 0.0057857 | 1.362 | A04 | MICL0.00915014/DON
Build-In Floor | Mini Canal | MICL.00915014/DOV | 9 | 150 | 14 | 14 | 213 | 213 | 213 | 0.0050714 | 83 | 0.0019762 | 243 | 0.0057857 | 1.362 | A04 | MICL0.00915014/DOV
Build-In Floor | Mini Canal | MICL.00915014/RBL | 9 | 150 | 14 | 14 | 229 | 229 | 229 | 0.0054524 | 89 | 0.002119 | 261 | 0.0062143 | 1.362 | A04 | MICL0.00915014/RBL
Build-In Floor | Mini Canal | MICL.00915014/RBN | 9 | 150 | 14 | 14 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00915014/RBN
Build-In Floor | Mini Canal | MICL.00915014/RBR | 9 | 150 | 14 | 14 | 229 | 229 | 229 | 0.0054524 | 89 | 0.002119 | 261 | 0.0062143 | 1.362 | A04 | MICL0.00915014/RBR
Build-In Floor | Mini Canal | MICL.00915014/RBV | 9 | 150 | 14 | 14 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00915014/RBV
Build-In Floor | Mini Canal | MICL.00915014/RDB | 9 | 150 | 14 | 14 | 229 | 229 | 229 | 0.0054524 | 89 | 0.002119 | 261 | 0.0062143 | 1.362 | A04 | MICL0.00915014/RDB
Build-In Floor | Mini Canal | MICL.00915014/RMN | 9 | 150 | 14 | 14 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00915014/RMN
Build-In Floor | Mini Canal | MICL.00915014/RMV | 9 | 150 | 14 | 14 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00915014/RMV
Build-In Floor | Mini Canal | MICL.00915014/RNA | 9 | 150 | 14 | 14 | 229 | 229 | 229 | 0.0054524 | 89 | 0.002119 | 261 | 0.0062143 | 1.362 | A04 | MICL0.00915014/RNA
Build-In Floor | Mini Canal | MICL.00915014/RON | 9 | 150 | 14 | 14 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00915014/RON
Build-In Floor | Mini Canal | MICL.00915014/ROV | 9 | 150 | 14 | 14 | 222 | 222 | 222 | 0.0052857 | 86 | 0.0020476 | 253 | 0.0060238 | 1.362 | A04 | MICL0.00915014/ROV
Build-In Floor | Mini Canal | MICL.00915014/RSS | 9 | 150 | 14 | 14 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.00915014/RSS
Build-In Floor | Mini Canal | MICL.00915014/SBL | 9 | 150 | 14 | 14 | 229 | 229 | 229 | 0.0054524 | 89 | 0.002119 | 261 | 0.0062143 | 1.362 | A04 | MICL0.00915014/SBL
Build-In Floor | Mini Canal | MICL.00915014/SBR | 9 | 150 | 14 | 14 | 229 | 229 | 229 | 0.0054524 | 89 | 0.002119 | 261 | 0.0062143 | 1.362 | A04 | MICL0.00915014/SBR
Build-In Floor | Mini Canal | MICL.00915014/SDB | 9 | 150 | 14 | 14 | 229 | 229 | 229 | 0.0054524 | 89 | 0.002119 | 261 | 0.0062143 | 1.362 | A04 | MICL0.00915014/SDB
Build-In Floor | Mini Canal | MICL.00915014/SNA | 9 | 150 | 14 | 14 | 229 | 229 | 229 | 0.0054524 | 89 | 0.002119 | 261 | 0.0062143 | 1.362 | A04 | MICL0.00915014/SNA
Build-In Floor | Mini Canal | MICL.00915014/SNC | 9 | 150 | 14 | 14 | 229 | 229 | 229 | 0.0054524 | 89 | 0.002119 | 261 | 0.0062143 | 1.362 | A04 | MICL0.00915014/SNC
Build-In Floor | Mini Canal | MICL.00915018/ANA | 9 | 150 | 18 | 18 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.00915018/ANA
Build-In Floor | Mini Canal | MICL.00915018/DBL | 9 | 150 | 18 | 18 | 263 | 263 | 263 | 0.0062619 | 102 | 0.0024286 | 300 | 0.0071429 | 1.362 | A04 | MICL0.00915018/DBL
Build-In Floor | Mini Canal | MICL.00915018/DBN | 9 | 150 | 18 | 18 | 252 | 252 | 252 | 0.006 | 98 | 0.0023333 | 287 | 0.0068333 | 1.362 | A04 | MICL0.00915018/DBN
Build-In Floor | Mini Canal | MICL.00915018/DBR | 9 | 150 | 18 | 18 | 263 | 263 | 263 | 0.0062619 | 102 | 0.0024286 | 300 | 0.0071429 | 1.362 | A04 | MICL0.00915018/DBR
Build-In Floor | Mini Canal | MICL.00915018/DBV | 9 | 150 | 18 | 18 | 252 | 252 | 252 | 0.006 | 98 | 0.0023333 | 287 | 0.0068333 | 1.362 | A04 | MICL0.00915018/DBV
Build-In Floor | Mini Canal | MICL.00915018/DDB | 9 | 150 | 18 | 18 | 263 | 263 | 263 | 0.0062619 | 102 | 0.0024286 | 300 | 0.0071429 | 1.362 | A04 | MICL0.00915018/DDB
Build-In Floor | Mini Canal | MICL.00915018/DMN | 9 | 150 | 18 | 18 | 252 | 252 | 252 | 0.006 | 98 | 0.0023333 | 287 | 0.0068333 | 1.362 | A04 | MICL0.00915018/DMN
Build-In Floor | Mini Canal | MICL.00915018/DMV | 9 | 150 | 18 | 18 | 252 | 252 | 252 | 0.006 | 98 | 0.0023333 | 287 | 0.0068333 | 1.362 | A04 | MICL0.00915018/DMV
Build-In Floor | Mini Canal | MICL.00915018/DNA | 9 | 150 | 18 | 18 | 263 | 263 | 263 | 0.0062619 | 102 | 0.0024286 | 300 | 0.0071429 | 1.362 | A04 | MICL0.00915018/DNA
Build-In Floor | Mini Canal | MICL.00915018/DNC | 9 | 150 | 18 | 18 | 263 | 263 | 263 | 0.0062619 | 102 | 0.0024286 | 300 | 0.0071429 | 1.362 | A04 | MICL0.00915018/DNC
Build-In Floor | Mini Canal | MICL.00915018/DON | 9 | 150 | 18 | 18 | 252 | 252 | 252 | 0.006 | 98 | 0.0023333 | 287 | 0.0068333 | 1.362 | A04 | MICL0.00915018/DON
Build-In Floor | Mini Canal | MICL.00915018/DOV | 9 | 150 | 18 | 18 | 252 | 252 | 252 | 0.006 | 98 | 0.0023333 | 287 | 0.0068333 | 1.362 | A04 | MICL0.00915018/DOV
Build-In Floor | Mini Canal | MICL.00915018/RBL | 9 | 150 | 18 | 18 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.00915018/RBL
Build-In Floor | Mini Canal | MICL.00915018/RBN | 9 | 150 | 18 | 18 | 263 | 263 | 263 | 0.0062619 | 102 | 0.0024286 | 300 | 0.0071429 | 1.362 | A04 | MICL0.00915018/RBN
Build-In Floor | Mini Canal | MICL.00915018/RBR | 9 | 150 | 18 | 18 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.00915018/RBR
Build-In Floor | Mini Canal | MICL.00915018/RBV | 9 | 150 | 18 | 18 | 263 | 263 | 263 | 0.0062619 | 102 | 0.0024286 | 300 | 0.0071429 | 1.362 | A04 | MICL0.00915018/RBV
Build-In Floor | Mini Canal | MICL.00915018/RDB | 9 | 150 | 18 | 18 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.00915018/RDB
Build-In Floor | Mini Canal | MICL.00915018/RMN | 9 | 150 | 18 | 18 | 263 | 263 | 263 | 0.0062619 | 102 | 0.0024286 | 300 | 0.0071429 | 1.362 | A04 | MICL0.00915018/RMN
Build-In Floor | Mini Canal | MICL.00915018/RMV | 9 | 150 | 18 | 18 | 263 | 263 | 263 | 0.0062619 | 102 | 0.0024286 | 300 | 0.0071429 | 1.362 | A04 | MICL0.00915018/RMV
Build-In Floor | Mini Canal | MICL.00915018/RNA | 9 | 150 | 18 | 18 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.00915018/RNA
Build-In Floor | Mini Canal | MICL.00915018/RON | 9 | 150 | 18 | 18 | 263 | 263 | 263 | 0.0062619 | 102 | 0.0024286 | 300 | 0.0071429 | 1.362 | A04 | MICL0.00915018/RON
Build-In Floor | Mini Canal | MICL.00915018/ROV | 9 | 150 | 18 | 18 | 263 | 263 | 263 | 0.0062619 | 102 | 0.0024286 | 300 | 0.0071429 | 1.362 | A04 | MICL0.00915018/ROV
Build-In Floor | Mini Canal | MICL.00915018/RSS | 9 | 150 | 18 | 18 | 260 | 260 | 260 | 0.0061905 | 101 | 0.0024048 | 296 | 0.0070476 | 1.362 | A04 | MICL0.00915018/RSS
Build-In Floor | Mini Canal | MICL.00915018/SBL | 9 | 150 | 18 | 18 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.00915018/SBL
Build-In Floor | Mini Canal | MICL.00915018/SBR | 9 | 150 | 18 | 18 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.00915018/SBR
Build-In Floor | Mini Canal | MICL.00915018/SDB | 9 | 150 | 18 | 18 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.00915018/SDB
Build-In Floor | Mini Canal | MICL.00915018/SNA | 9 | 150 | 18 | 18 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.00915018/SNA
Build-In Floor | Mini Canal | MICL.00915018/SNC | 9 | 150 | 18 | 18 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.00915018/SNC
Build-In Floor | Mini Canal | MICL.00915026/ANA | 9 | 150 | 26 | 26 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00915026/ANA
Build-In Floor | Mini Canal | MICL.00915026/DBL | 9 | 150 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.00915026/DBL
Build-In Floor | Mini Canal | MICL.00915026/DBN | 9 | 150 | 26 | 26 | 331 | 331 | 331 | 0.007881 | 129 | 0.0030714 | 377 | 0.0089762 | 1.362 | A04 | MICL0.00915026/DBN
Build-In Floor | Mini Canal | MICL.00915026/DBR | 9 | 150 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.00915026/DBR
Build-In Floor | Mini Canal | MICL.00915026/DBV | 9 | 150 | 26 | 26 | 331 | 331 | 331 | 0.007881 | 129 | 0.0030714 | 377 | 0.0089762 | 1.362 | A04 | MICL0.00915026/DBV
Build-In Floor | Mini Canal | MICL.00915026/DDB | 9 | 150 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.00915026/DDB
Build-In Floor | Mini Canal | MICL.00915026/DMN | 9 | 150 | 26 | 26 | 331 | 331 | 331 | 0.007881 | 129 | 0.0030714 | 377 | 0.0089762 | 1.362 | A04 | MICL0.00915026/DMN
Build-In Floor | Mini Canal | MICL.00915026/DMV | 9 | 150 | 26 | 26 | 331 | 331 | 331 | 0.007881 | 129 | 0.0030714 | 377 | 0.0089762 | 1.362 | A04 | MICL0.00915026/DMV
Build-In Floor | Mini Canal | MICL.00915026/DNA | 9 | 150 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.00915026/DNA
Build-In Floor | Mini Canal | MICL.00915026/DNC | 9 | 150 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.00915026/DNC
Build-In Floor | Mini Canal | MICL.00915026/DON | 9 | 150 | 26 | 26 | 331 | 331 | 331 | 0.007881 | 129 | 0.0030714 | 377 | 0.0089762 | 1.362 | A04 | MICL0.00915026/DON
Build-In Floor | Mini Canal | MICL.00915026/DOV | 9 | 150 | 26 | 26 | 331 | 331 | 331 | 0.007881 | 129 | 0.0030714 | 377 | 0.0089762 | 1.362 | A04 | MICL0.00915026/DOV
Build-In Floor | Mini Canal | MICL.00915026/PNC | 9 | 150 | 26 | 26 | 303 | 303 | 303 | 0.0072143 | 118 | 0.0028095 | 345 | 0.0082143 | 1.362 | A04 | MICL0.00915026/PNC
Build-In Floor | Mini Canal | MICL.00915026/RBL | 9 | 150 | 26 | 26 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.00915026/RBL
Build-In Floor | Mini Canal | MICL.00915026/RBN | 9 | 150 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.00915026/RBN
Build-In Floor | Mini Canal | MICL.00915026/RBR | 9 | 150 | 26 | 26 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.00915026/RBR
Build-In Floor | Mini Canal | MICL.00915026/RBV | 9 | 150 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.00915026/RBV
Build-In Floor | Mini Canal | MICL.00915026/RDB | 9 | 150 | 26 | 26 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.00915026/RDB
Build-In Floor | Mini Canal | MICL.00915026/RMN | 9 | 150 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.00915026/RMN
Build-In Floor | Mini Canal | MICL.00915026/RMV | 9 | 150 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.00915026/RMV
Build-In Floor | Mini Canal | MICL.00915026/RNA | 9 | 150 | 26 | 26 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.00915026/RNA
Build-In Floor | Mini Canal | MICL.00915026/RON | 9 | 150 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.00915026/RON
Build-In Floor | Mini Canal | MICL.00915026/ROV | 9 | 150 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.00915026/ROV
Build-In Floor | Mini Canal | MICL.00915026/RSS | 9 | 150 | 26 | 26 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.00915026/RSS
Build-In Floor | Mini Canal | MICL.00915026/SBL | 9 | 150 | 26 | 26 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.00915026/SBL
Build-In Floor | Mini Canal | MICL.00915026/SBR | 9 | 150 | 26 | 26 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.00915026/SBR
Build-In Floor | Mini Canal | MICL.00915026/SDB | 9 | 150 | 26 | 26 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.00915026/SDB
Build-In Floor | Mini Canal | MICL.00915026/SNA | 9 | 150 | 26 | 26 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.00915026/SNA
Build-In Floor | Mini Canal | MICL.00915026/SNC | 9 | 150 | 26 | 26 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.00915026/SNC
Build-In Floor | Mini Canal | MICL.00915034/ANA | 9 | 150 | 34 | 34 | 347 | 347 | 347 | 0.0082619 | 135 | 0.0032143 | 395 | 0.0094048 | 1.362 | A04 | MICL0.00915034/ANA
Build-In Floor | Mini Canal | MICL.00915034/DBL | 9 | 150 | 34 | 34 | 448 | 448 | 448 | 0.010667 | 174 | 0.0041429 | 510 | 0.012143 | 1.362 | A04 | MICL0.00915034/DBL
Build-In Floor | Mini Canal | MICL.00915034/DBN | 9 | 150 | 34 | 34 | 430 | 430 | 430 | 0.010238 | 167 | 0.0039762 | 490 | 0.011667 | 1.362 | A04 | MICL0.00915034/DBN
Build-In Floor | Mini Canal | MICL.00915034/DBR | 9 | 150 | 34 | 34 | 448 | 448 | 448 | 0.010667 | 174 | 0.0041429 | 510 | 0.012143 | 1.362 | A04 | MICL0.00915034/DBR
Build-In Floor | Mini Canal | MICL.00915034/DBV | 9 | 150 | 34 | 34 | 430 | 430 | 430 | 0.010238 | 167 | 0.0039762 | 490 | 0.011667 | 1.362 | A04 | MICL0.00915034/DBV
Build-In Floor | Mini Canal | MICL.00915034/DDB | 9 | 150 | 34 | 34 | 448 | 448 | 448 | 0.010667 | 174 | 0.0041429 | 510 | 0.012143 | 1.362 | A04 | MICL0.00915034/DDB
Build-In Floor | Mini Canal | MICL.00915034/DMN | 9 | 150 | 34 | 34 | 430 | 430 | 430 | 0.010238 | 167 | 0.0039762 | 490 | 0.011667 | 1.362 | A04 | MICL0.00915034/DMN
Build-In Floor | Mini Canal | MICL.00915034/DMV | 9 | 150 | 34 | 34 | 430 | 430 | 430 | 0.010238 | 167 | 0.0039762 | 490 | 0.011667 | 1.362 | A04 | MICL0.00915034/DMV
Build-In Floor | Mini Canal | MICL.00915034/DNA | 9 | 150 | 34 | 34 | 448 | 448 | 448 | 0.010667 | 174 | 0.0041429 | 510 | 0.012143 | 1.362 | A04 | MICL0.00915034/DNA
Build-In Floor | Mini Canal | MICL.00915034/DNC | 9 | 150 | 34 | 34 | 448 | 448 | 448 | 0.010667 | 174 | 0.0041429 | 510 | 0.012143 | 1.362 | A04 | MICL0.00915034/DNC
Build-In Floor | Mini Canal | MICL.00915034/DON | 9 | 150 | 34 | 34 | 430 | 430 | 430 | 0.010238 | 167 | 0.0039762 | 490 | 0.011667 | 1.362 | A04 | MICL0.00915034/DON
Build-In Floor | Mini Canal | MICL.00915034/DOV | 9 | 150 | 34 | 34 | 430 | 430 | 430 | 0.010238 | 167 | 0.0039762 | 490 | 0.011667 | 1.362 | A04 | MICL0.00915034/DOV
Build-In Floor | Mini Canal | MICL.00915034/PNC | 9 | 150 | 34 | 34 | 393 | 393 | 393 | 0.0093571 | 153 | 0.0036429 | 448 | 0.010667 | 1.362 | A04 | MICL0.00915034/PNC
Build-In Floor | Mini Canal | MICL.00915034/RBL | 9 | 150 | 34 | 34 | 462 | 462 | 462 | 0.011 | 180 | 0.0042857 | 526 | 0.012524 | 1.362 | A04 | MICL0.00915034/RBL
Build-In Floor | Mini Canal | MICL.00915034/RBN | 9 | 150 | 34 | 34 | 448 | 448 | 448 | 0.010667 | 174 | 0.0041429 | 510 | 0.012143 | 1.362 | A04 | MICL0.00915034/RBN
Build-In Floor | Mini Canal | MICL.00915034/RBR | 9 | 150 | 34 | 34 | 462 | 462 | 462 | 0.011 | 180 | 0.0042857 | 526 | 0.012524 | 1.362 | A04 | MICL0.00915034/RBR
Build-In Floor | Mini Canal | MICL.00915034/RBV | 9 | 150 | 34 | 34 | 448 | 448 | 448 | 0.010667 | 174 | 0.0041429 | 510 | 0.012143 | 1.362 | A04 | MICL0.00915034/RBV
Build-In Floor | Mini Canal | MICL.00915034/RDB | 9 | 150 | 34 | 34 | 462 | 462 | 462 | 0.011 | 180 | 0.0042857 | 526 | 0.012524 | 1.362 | A04 | MICL0.00915034/RDB
Build-In Floor | Mini Canal | MICL.00915034/RMN | 9 | 150 | 34 | 34 | 448 | 448 | 448 | 0.010667 | 174 | 0.0041429 | 510 | 0.012143 | 1.362 | A04 | MICL0.00915034/RMN
Build-In Floor | Mini Canal | MICL.00915034/RMV | 9 | 150 | 34 | 34 | 448 | 448 | 448 | 0.010667 | 174 | 0.0041429 | 510 | 0.012143 | 1.362 | A04 | MICL0.00915034/RMV
Build-In Floor | Mini Canal | MICL.00915034/RNA | 9 | 150 | 34 | 34 | 462 | 462 | 462 | 0.011 | 180 | 0.0042857 | 526 | 0.012524 | 1.362 | A04 | MICL0.00915034/RNA
Build-In Floor | Mini Canal | MICL.00915034/RON | 9 | 150 | 34 | 34 | 448 | 448 | 448 | 0.010667 | 174 | 0.0041429 | 510 | 0.012143 | 1.362 | A04 | MICL0.00915034/RON
Build-In Floor | Mini Canal | MICL.00915034/ROV | 9 | 150 | 34 | 34 | 448 | 448 | 448 | 0.010667 | 174 | 0.0041429 | 510 | 0.012143 | 1.362 | A04 | MICL0.00915034/ROV
Build-In Floor | Mini Canal | MICL.00915034/RSS | 9 | 150 | 34 | 34 | 444 | 444 | 444 | 0.010571 | 173 | 0.004119 | 506 | 0.012048 | 1.362 | A04 | MICL0.00915034/RSS
Build-In Floor | Mini Canal | MICL.00915034/SBL | 9 | 150 | 34 | 34 | 462 | 462 | 462 | 0.011 | 180 | 0.0042857 | 526 | 0.012524 | 1.362 | A04 | MICL0.00915034/SBL
Build-In Floor | Mini Canal | MICL.00915034/SBR | 9 | 150 | 34 | 34 | 462 | 462 | 462 | 0.011 | 180 | 0.0042857 | 526 | 0.012524 | 1.362 | A04 | MICL0.00915034/SBR
Build-In Floor | Mini Canal | MICL.00915034/SDB | 9 | 150 | 34 | 34 | 462 | 462 | 462 | 0.011 | 180 | 0.0042857 | 526 | 0.012524 | 1.362 | A04 | MICL0.00915034/SDB
Build-In Floor | Mini Canal | MICL.00915034/SNA | 9 | 150 | 34 | 34 | 462 | 462 | 462 | 0.011 | 180 | 0.0042857 | 526 | 0.012524 | 1.362 | A04 | MICL0.00915034/SNA
Build-In Floor | Mini Canal | MICL.00915034/SNC | 9 | 150 | 34 | 34 | 462 | 462 | 462 | 0.011 | 180 | 0.0042857 | 526 | 0.012524 | 1.362 | A04 | MICL0.00915034/SNC
Build-In Floor | Mini Canal | MICL.00915042/ANA | 9 | 150 | 42 | 42 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00915042/ANA
Build-In Floor | Mini Canal | MICL.00915042/DBL | 9 | 150 | 42 | 42 | 646 | 646 | 646 | 0.015381 | 251 | 0.0059762 | 736 | 0.017524 | 1.362 | A04 | MICL0.00915042/DBL
Build-In Floor | Mini Canal | MICL.00915042/DBN | 9 | 150 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.00915042/DBN
Build-In Floor | Mini Canal | MICL.00915042/DBR | 9 | 150 | 42 | 42 | 646 | 646 | 646 | 0.015381 | 251 | 0.0059762 | 736 | 0.017524 | 1.362 | A04 | MICL0.00915042/DBR
Build-In Floor | Mini Canal | MICL.00915042/DBV | 9 | 150 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.00915042/DBV
Build-In Floor | Mini Canal | MICL.00915042/DDB | 9 | 150 | 42 | 42 | 646 | 646 | 646 | 0.015381 | 251 | 0.0059762 | 736 | 0.017524 | 1.362 | A04 | MICL0.00915042/DDB
Build-In Floor | Mini Canal | MICL.00915042/DMN | 9 | 150 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.00915042/DMN
Build-In Floor | Mini Canal | MICL.00915042/DMV | 9 | 150 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.00915042/DMV
Build-In Floor | Mini Canal | MICL.00915042/DNA | 9 | 150 | 42 | 42 | 646 | 646 | 646 | 0.015381 | 251 | 0.0059762 | 736 | 0.017524 | 1.362 | A04 | MICL0.00915042/DNA
Build-In Floor | Mini Canal | MICL.00915042/DNC | 9 | 150 | 42 | 42 | 646 | 646 | 646 | 0.015381 | 251 | 0.0059762 | 736 | 0.017524 | 1.362 | A04 | MICL0.00915042/DNC
Build-In Floor | Mini Canal | MICL.00915042/DON | 9 | 150 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.00915042/DON
Build-In Floor | Mini Canal | MICL.00915042/DOV | 9 | 150 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.00915042/DOV
Build-In Floor | Mini Canal | MICL.00915042/PNC | 9 | 150 | 42 | 42 | 566 | 566 | 566 | 0.013476 | 220 | 0.0052381 | 645 | 0.015357 | 1.362 | A04 | MICL0.00915042/PNC
Build-In Floor | Mini Canal | MICL.00915042/RBL | 9 | 150 | 42 | 42 | 666 | 666 | 666 | 0.015857 | 259 | 0.0061667 | 759 | 0.018071 | 1.362 | A04 | MICL0.00915042/RBL
Build-In Floor | Mini Canal | MICL.00915042/RBN | 9 | 150 | 42 | 42 | 646 | 646 | 646 | 0.015381 | 251 | 0.0059762 | 736 | 0.017524 | 1.362 | A04 | MICL0.00915042/RBN
Build-In Floor | Mini Canal | MICL.00915042/RBR | 9 | 150 | 42 | 42 | 666 | 666 | 666 | 0.015857 | 259 | 0.0061667 | 759 | 0.018071 | 1.362 | A04 | MICL0.00915042/RBR
Build-In Floor | Mini Canal | MICL.00915042/RBV | 9 | 150 | 42 | 42 | 646 | 646 | 646 | 0.015381 | 251 | 0.0059762 | 736 | 0.017524 | 1.362 | A04 | MICL0.00915042/RBV
Build-In Floor | Mini Canal | MICL.00915042/RDB | 9 | 150 | 42 | 42 | 666 | 666 | 666 | 0.015857 | 259 | 0.0061667 | 759 | 0.018071 | 1.362 | A04 | MICL0.00915042/RDB
Build-In Floor | Mini Canal | MICL.00915042/RMN | 9 | 150 | 42 | 42 | 646 | 646 | 646 | 0.015381 | 251 | 0.0059762 | 736 | 0.017524 | 1.362 | A04 | MICL0.00915042/RMN
Build-In Floor | Mini Canal | MICL.00915042/RMV | 9 | 150 | 42 | 42 | 646 | 646 | 646 | 0.015381 | 251 | 0.0059762 | 736 | 0.017524 | 1.362 | A04 | MICL0.00915042/RMV
Build-In Floor | Mini Canal | MICL.00915042/RNA | 9 | 150 | 42 | 42 | 666 | 666 | 666 | 0.015857 | 259 | 0.0061667 | 759 | 0.018071 | 1.362 | A04 | MICL0.00915042/RNA
Build-In Floor | Mini Canal | MICL.00915042/RON | 9 | 150 | 42 | 42 | 646 | 646 | 646 | 0.015381 | 251 | 0.0059762 | 736 | 0.017524 | 1.362 | A04 | MICL0.00915042/RON
Build-In Floor | Mini Canal | MICL.00915042/ROV | 9 | 150 | 42 | 42 | 646 | 646 | 646 | 0.015381 | 251 | 0.0059762 | 736 | 0.017524 | 1.362 | A04 | MICL0.00915042/ROV
Build-In Floor | Mini Canal | MICL.00915042/RSS | 9 | 150 | 42 | 42 | 639 | 639 | 639 | 0.015214 | 249 | 0.0059286 | 728 | 0.017333 | 1.362 | A04 | MICL0.00915042/RSS
Build-In Floor | Mini Canal | MICL.00915042/SBL | 9 | 150 | 42 | 42 | 666 | 666 | 666 | 0.015857 | 259 | 0.0061667 | 759 | 0.018071 | 1.362 | A04 | MICL0.00915042/SBL
Build-In Floor | Mini Canal | MICL.00915042/SBR | 9 | 150 | 42 | 42 | 666 | 666 | 666 | 0.015857 | 259 | 0.0061667 | 759 | 0.018071 | 1.362 | A04 | MICL0.00915042/SBR
Build-In Floor | Mini Canal | MICL.00915042/SDB | 9 | 150 | 42 | 42 | 666 | 666 | 666 | 0.015857 | 259 | 0.0061667 | 759 | 0.018071 | 1.362 | A04 | MICL0.00915042/SDB
Build-In Floor | Mini Canal | MICL.00915042/SNA | 9 | 150 | 42 | 42 | 666 | 666 | 666 | 0.015857 | 259 | 0.0061667 | 759 | 0.018071 | 1.362 | A04 | MICL0.00915042/SNA
Build-In Floor | Mini Canal | MICL.00915042/SNC | 9 | 150 | 42 | 42 | 666 | 666 | 666 | 0.015857 | 259 | 0.0061667 | 759 | 0.018071 | 1.362 | A04 | MICL0.00915042/SNC
Build-In Floor | Mini Canal | MICL.00917014/ANA | 9 | 170 | 14 | 14 | 200 | 200 | 200 | 0.0047619 | 78 | 0.0018571 | 228 | 0.0054286 | 1.362 | A04 | MICL0.00917014/ANA
Build-In Floor | Mini Canal | MICL.00917014/DBL | 9 | 170 | 14 | 14 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00917014/DBL
Build-In Floor | Mini Canal | MICL.00917014/DBN | 9 | 170 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.00917014/DBN
Build-In Floor | Mini Canal | MICL.00917014/DBR | 9 | 170 | 14 | 14 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00917014/DBR
Build-In Floor | Mini Canal | MICL.00917014/DBV | 9 | 170 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.00917014/DBV
Build-In Floor | Mini Canal | MICL.00917014/DDB | 9 | 170 | 14 | 14 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00917014/DDB
Build-In Floor | Mini Canal | MICL.00917014/DMN | 9 | 170 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.00917014/DMN
Build-In Floor | Mini Canal | MICL.00917014/DMV | 9 | 170 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.00917014/DMV
Build-In Floor | Mini Canal | MICL.00917014/DNA | 9 | 170 | 14 | 14 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00917014/DNA
Build-In Floor | Mini Canal | MICL.00917014/DNC | 9 | 170 | 14 | 14 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00917014/DNC
Build-In Floor | Mini Canal | MICL.00917014/DON | 9 | 170 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.00917014/DON
Build-In Floor | Mini Canal | MICL.00917014/DOV | 9 | 170 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.00917014/DOV
Build-In Floor | Mini Canal | MICL.00917014/RBL | 9 | 170 | 14 | 14 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00917014/RBL
Build-In Floor | Mini Canal | MICL.00917014/RBN | 9 | 170 | 14 | 14 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00917014/RBN
Build-In Floor | Mini Canal | MICL.00917014/RBR | 9 | 170 | 14 | 14 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00917014/RBR
Build-In Floor | Mini Canal | MICL.00917014/RBV | 9 | 170 | 14 | 14 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00917014/RBV
Build-In Floor | Mini Canal | MICL.00917014/RDB | 9 | 170 | 14 | 14 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00917014/RDB
Build-In Floor | Mini Canal | MICL.00917014/RMN | 9 | 170 | 14 | 14 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00917014/RMN
Build-In Floor | Mini Canal | MICL.00917014/RMV | 9 | 170 | 14 | 14 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00917014/RMV
Build-In Floor | Mini Canal | MICL.00917014/RNA | 9 | 170 | 14 | 14 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00917014/RNA
Build-In Floor | Mini Canal | MICL.00917014/RON | 9 | 170 | 14 | 14 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00917014/RON
Build-In Floor | Mini Canal | MICL.00917014/ROV | 9 | 170 | 14 | 14 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.00917014/ROV
Build-In Floor | Mini Canal | MICL.00917014/RSS | 9 | 170 | 14 | 14 | 256 | 256 | 256 | 0.0060952 | 100 | 0.002381 | 292 | 0.0069524 | 1.362 | A04 | MICL0.00917014/RSS
Build-In Floor | Mini Canal | MICL.00917014/SBL | 9 | 170 | 14 | 14 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00917014/SBL
Build-In Floor | Mini Canal | MICL.00917014/SBR | 9 | 170 | 14 | 14 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00917014/SBR
Build-In Floor | Mini Canal | MICL.00917014/SDB | 9 | 170 | 14 | 14 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00917014/SDB
Build-In Floor | Mini Canal | MICL.00917014/SNA | 9 | 170 | 14 | 14 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00917014/SNA
Build-In Floor | Mini Canal | MICL.00917014/SNC | 9 | 170 | 14 | 14 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.00917014/SNC
Build-In Floor | Mini Canal | MICL.00917018/ANA | 9 | 170 | 18 | 18 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.00917018/ANA
Build-In Floor | Mini Canal | MICL.00917018/DBL | 9 | 170 | 18 | 18 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00917018/DBL
Build-In Floor | Mini Canal | MICL.00917018/DBN | 9 | 170 | 18 | 18 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.00917018/DBN
Build-In Floor | Mini Canal | MICL.00917018/DBR | 9 | 170 | 18 | 18 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00917018/DBR
Build-In Floor | Mini Canal | MICL.00917018/DBV | 9 | 170 | 18 | 18 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.00917018/DBV
Build-In Floor | Mini Canal | MICL.00917018/DDB | 9 | 170 | 18 | 18 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00917018/DDB
Build-In Floor | Mini Canal | MICL.00917018/DMN | 9 | 170 | 18 | 18 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.00917018/DMN
Build-In Floor | Mini Canal | MICL.00917018/DMV | 9 | 170 | 18 | 18 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.00917018/DMV
Build-In Floor | Mini Canal | MICL.00917018/DNA | 9 | 170 | 18 | 18 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00917018/DNA
Build-In Floor | Mini Canal | MICL.00917018/DNC | 9 | 170 | 18 | 18 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00917018/DNC
Build-In Floor | Mini Canal | MICL.00917018/DON | 9 | 170 | 18 | 18 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.00917018/DON
Build-In Floor | Mini Canal | MICL.00917018/DOV | 9 | 170 | 18 | 18 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.00917018/DOV
Build-In Floor | Mini Canal | MICL.00917018/RBL | 9 | 170 | 18 | 18 | 316 | 316 | 316 | 0.0075238 | 123 | 0.0029286 | 360 | 0.0085714 | 1.362 | A04 | MICL0.00917018/RBL
Build-In Floor | Mini Canal | MICL.00917018/RBN | 9 | 170 | 18 | 18 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00917018/RBN
Build-In Floor | Mini Canal | MICL.00917018/RBR | 9 | 170 | 18 | 18 | 316 | 316 | 316 | 0.0075238 | 123 | 0.0029286 | 360 | 0.0085714 | 1.362 | A04 | MICL0.00917018/RBR
Build-In Floor | Mini Canal | MICL.00917018/RBV | 9 | 170 | 18 | 18 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00917018/RBV
Build-In Floor | Mini Canal | MICL.00917018/RDB | 9 | 170 | 18 | 18 | 316 | 316 | 316 | 0.0075238 | 123 | 0.0029286 | 360 | 0.0085714 | 1.362 | A04 | MICL0.00917018/RDB
Build-In Floor | Mini Canal | MICL.00917018/RMN | 9 | 170 | 18 | 18 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00917018/RMN
Build-In Floor | Mini Canal | MICL.00917018/RMV | 9 | 170 | 18 | 18 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00917018/RMV
Build-In Floor | Mini Canal | MICL.00917018/RNA | 9 | 170 | 18 | 18 | 316 | 316 | 316 | 0.0075238 | 123 | 0.0029286 | 360 | 0.0085714 | 1.362 | A04 | MICL0.00917018/RNA
Build-In Floor | Mini Canal | MICL.00917018/RON | 9 | 170 | 18 | 18 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00917018/RON
Build-In Floor | Mini Canal | MICL.00917018/ROV | 9 | 170 | 18 | 18 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.00917018/ROV
Build-In Floor | Mini Canal | MICL.00917018/RSS | 9 | 170 | 18 | 18 | 303 | 303 | 303 | 0.0072143 | 118 | 0.0028095 | 345 | 0.0082143 | 1.362 | A04 | MICL0.00917018/RSS
Build-In Floor | Mini Canal | MICL.00917018/SBL | 9 | 170 | 18 | 18 | 316 | 316 | 316 | 0.0075238 | 123 | 0.0029286 | 360 | 0.0085714 | 1.362 | A04 | MICL0.00917018/SBL
Build-In Floor | Mini Canal | MICL.00917018/SBR | 9 | 170 | 18 | 18 | 316 | 316 | 316 | 0.0075238 | 123 | 0.0029286 | 360 | 0.0085714 | 1.362 | A04 | MICL0.00917018/SBR
Build-In Floor | Mini Canal | MICL.00917018/SDB | 9 | 170 | 18 | 18 | 316 | 316 | 316 | 0.0075238 | 123 | 0.0029286 | 360 | 0.0085714 | 1.362 | A04 | MICL0.00917018/SDB
Build-In Floor | Mini Canal | MICL.00917018/SNA | 9 | 170 | 18 | 18 | 316 | 316 | 316 | 0.0075238 | 123 | 0.0029286 | 360 | 0.0085714 | 1.362 | A04 | MICL0.00917018/SNA
Build-In Floor | Mini Canal | MICL.00917018/SNC | 9 | 170 | 18 | 18 | 316 | 316 | 316 | 0.0075238 | 123 | 0.0029286 | 360 | 0.0085714 | 1.362 | A04 | MICL0.00917018/SNC
Build-In Floor | Mini Canal | MICL.00917026/ANA | 9 | 170 | 26 | 26 | 311 | 311 | 311 | 0.0074048 | 121 | 0.002881 | 354 | 0.0084286 | 1.362 | A04 | MICL0.00917026/ANA
Build-In Floor | Mini Canal | MICL.00917026/DBL | 9 | 170 | 26 | 26 | 403 | 403 | 403 | 0.0095952 | 157 | 0.0037381 | 459 | 0.010929 | 1.362 | A04 | MICL0.00917026/DBL
Build-In Floor | Mini Canal | MICL.00917026/DBN | 9 | 170 | 26 | 26 | 386 | 386 | 386 | 0.0091905 | 150 | 0.0035714 | 440 | 0.010476 | 1.362 | A04 | MICL0.00917026/DBN
Build-In Floor | Mini Canal | MICL.00917026/DBR | 9 | 170 | 26 | 26 | 403 | 403 | 403 | 0.0095952 | 157 | 0.0037381 | 459 | 0.010929 | 1.362 | A04 | MICL0.00917026/DBR
Build-In Floor | Mini Canal | MICL.00917026/DBV | 9 | 170 | 26 | 26 | 386 | 386 | 386 | 0.0091905 | 150 | 0.0035714 | 440 | 0.010476 | 1.362 | A04 | MICL0.00917026/DBV
Build-In Floor | Mini Canal | MICL.00917026/DDB | 9 | 170 | 26 | 26 | 403 | 403 | 403 | 0.0095952 | 157 | 0.0037381 | 459 | 0.010929 | 1.362 | A04 | MICL0.00917026/DDB
Build-In Floor | Mini Canal | MICL.00917026/DMN | 9 | 170 | 26 | 26 | 386 | 386 | 386 | 0.0091905 | 150 | 0.0035714 | 440 | 0.010476 | 1.362 | A04 | MICL0.00917026/DMN
Build-In Floor | Mini Canal | MICL.00917026/DMV | 9 | 170 | 26 | 26 | 386 | 386 | 386 | 0.0091905 | 150 | 0.0035714 | 440 | 0.010476 | 1.362 | A04 | MICL0.00917026/DMV
Build-In Floor | Mini Canal | MICL.00917026/DNA | 9 | 170 | 26 | 26 | 403 | 403 | 403 | 0.0095952 | 157 | 0.0037381 | 459 | 0.010929 | 1.362 | A04 | MICL0.00917026/DNA
Build-In Floor | Mini Canal | MICL.00917026/DNC | 9 | 170 | 26 | 26 | 403 | 403 | 403 | 0.0095952 | 157 | 0.0037381 | 459 | 0.010929 | 1.362 | A04 | MICL0.00917026/DNC
Build-In Floor | Mini Canal | MICL.00917026/DON | 9 | 170 | 26 | 26 | 386 | 386 | 386 | 0.0091905 | 150 | 0.0035714 | 440 | 0.010476 | 1.362 | A04 | MICL0.00917026/DON
Build-In Floor | Mini Canal | MICL.00917026/DOV | 9 | 170 | 26 | 26 | 386 | 386 | 386 | 0.0091905 | 150 | 0.0035714 | 440 | 0.010476 | 1.362 | A04 | MICL0.00917026/DOV
Build-In Floor | Mini Canal | MICL.00917026/PNC | 9 | 170 | 26 | 26 | 353 | 353 | 353 | 0.0084048 | 137 | 0.0032619 | 402 | 0.0095714 | 1.362 | A04 | MICL0.00917026/PNC
Build-In Floor | Mini Canal | MICL.00917026/RBL | 9 | 170 | 26 | 26 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.00917026/RBL
Build-In Floor | Mini Canal | MICL.00917026/RBN | 9 | 170 | 26 | 26 | 403 | 403 | 403 | 0.0095952 | 157 | 0.0037381 | 459 | 0.010929 | 1.362 | A04 | MICL0.00917026/RBN
Build-In Floor | Mini Canal | MICL.00917026/RBR | 9 | 170 | 26 | 26 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.00917026/RBR
Build-In Floor | Mini Canal | MICL.00917026/RBV | 9 | 170 | 26 | 26 | 403 | 403 | 403 | 0.0095952 | 157 | 0.0037381 | 459 | 0.010929 | 1.362 | A04 | MICL0.00917026/RBV
Build-In Floor | Mini Canal | MICL.00917026/RDB | 9 | 170 | 26 | 26 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.00917026/RDB
Build-In Floor | Mini Canal | MICL.00917026/RMN | 9 | 170 | 26 | 26 | 403 | 403 | 403 | 0.0095952 | 157 | 0.0037381 | 459 | 0.010929 | 1.362 | A04 | MICL0.00917026/RMN
Build-In Floor | Mini Canal | MICL.00917026/RMV | 9 | 170 | 26 | 26 | 403 | 403 | 403 | 0.0095952 | 157 | 0.0037381 | 459 | 0.010929 | 1.362 | A04 | MICL0.00917026/RMV
Build-In Floor | Mini Canal | MICL.00917026/RNA | 9 | 170 | 26 | 26 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.00917026/RNA
Build-In Floor | Mini Canal | MICL.00917026/RON | 9 | 170 | 26 | 26 | 403 | 403 | 403 | 0.0095952 | 157 | 0.0037381 | 459 | 0.010929 | 1.362 | A04 | MICL0.00917026/RON
Build-In Floor | Mini Canal | MICL.00917026/ROV | 9 | 170 | 26 | 26 | 403 | 403 | 403 | 0.0095952 | 157 | 0.0037381 | 459 | 0.010929 | 1.362 | A04 | MICL0.00917026/ROV
Build-In Floor | Mini Canal | MICL.00917026/RSS | 9 | 170 | 26 | 26 | 398 | 398 | 398 | 0.0094762 | 155 | 0.0036905 | 453 | 0.010786 | 1.362 | A04 | MICL0.00917026/RSS
Build-In Floor | Mini Canal | MICL.00917026/SBL | 9 | 170 | 26 | 26 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.00917026/SBL
Build-In Floor | Mini Canal | MICL.00917026/SBR | 9 | 170 | 26 | 26 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.00917026/SBR
Build-In Floor | Mini Canal | MICL.00917026/SDB | 9 | 170 | 26 | 26 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.00917026/SDB
Build-In Floor | Mini Canal | MICL.00917026/SNA | 9 | 170 | 26 | 26 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.00917026/SNA
Build-In Floor | Mini Canal | MICL.00917026/SNC | 9 | 170 | 26 | 26 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.00917026/SNC
Build-In Floor | Mini Canal | MICL.00917034/ANA | 9 | 170 | 34 | 34 | 404 | 404 | 404 | 0.009619 | 157 | 0.0037381 | 460 | 0.010952 | 1.362 | A04 | MICL0.00917034/ANA
Build-In Floor | Mini Canal | MICL.00917034/DBL | 9 | 170 | 34 | 34 | 522 | 522 | 522 | 0.012429 | 203 | 0.0048333 | 595 | 0.014167 | 1.362 | A04 | MICL0.00917034/DBL
Build-In Floor | Mini Canal | MICL.00917034/DBN | 9 | 170 | 34 | 34 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00917034/DBN
Build-In Floor | Mini Canal | MICL.00917034/DBR | 9 | 170 | 34 | 34 | 522 | 522 | 522 | 0.012429 | 203 | 0.0048333 | 595 | 0.014167 | 1.362 | A04 | MICL0.00917034/DBR
Build-In Floor | Mini Canal | MICL.00917034/DBV | 9 | 170 | 34 | 34 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00917034/DBV
Build-In Floor | Mini Canal | MICL.00917034/DDB | 9 | 170 | 34 | 34 | 522 | 522 | 522 | 0.012429 | 203 | 0.0048333 | 595 | 0.014167 | 1.362 | A04 | MICL0.00917034/DDB
Build-In Floor | Mini Canal | MICL.00917034/DMN | 9 | 170 | 34 | 34 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00917034/DMN
Build-In Floor | Mini Canal | MICL.00917034/DMV | 9 | 170 | 34 | 34 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00917034/DMV
Build-In Floor | Mini Canal | MICL.00917034/DNA | 9 | 170 | 34 | 34 | 522 | 522 | 522 | 0.012429 | 203 | 0.0048333 | 595 | 0.014167 | 1.362 | A04 | MICL0.00917034/DNA
Build-In Floor | Mini Canal | MICL.00917034/DNC | 9 | 170 | 34 | 34 | 522 | 522 | 522 | 0.012429 | 203 | 0.0048333 | 595 | 0.014167 | 1.362 | A04 | MICL0.00917034/DNC
Build-In Floor | Mini Canal | MICL.00917034/DON | 9 | 170 | 34 | 34 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00917034/DON
Build-In Floor | Mini Canal | MICL.00917034/DOV | 9 | 170 | 34 | 34 | 500 | 500 | 500 | 0.011905 | 195 | 0.0046429 | 570 | 0.013571 | 1.362 | A04 | MICL0.00917034/DOV
Build-In Floor | Mini Canal | MICL.00917034/PNC | 9 | 170 | 34 | 34 | 457 | 457 | 457 | 0.010881 | 178 | 0.0042381 | 521 | 0.012405 | 1.362 | A04 | MICL0.00917034/PNC
Build-In Floor | Mini Canal | MICL.00917034/RBL | 9 | 170 | 34 | 34 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00917034/RBL
Build-In Floor | Mini Canal | MICL.00917034/RBN | 9 | 170 | 34 | 34 | 522 | 522 | 522 | 0.012429 | 203 | 0.0048333 | 595 | 0.014167 | 1.362 | A04 | MICL0.00917034/RBN
Build-In Floor | Mini Canal | MICL.00917034/RBR | 9 | 170 | 34 | 34 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00917034/RBR
Build-In Floor | Mini Canal | MICL.00917034/RBV | 9 | 170 | 34 | 34 | 522 | 522 | 522 | 0.012429 | 203 | 0.0048333 | 595 | 0.014167 | 1.362 | A04 | MICL0.00917034/RBV
Build-In Floor | Mini Canal | MICL.00917034/RDB | 9 | 170 | 34 | 34 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00917034/RDB
Build-In Floor | Mini Canal | MICL.00917034/RMN | 9 | 170 | 34 | 34 | 522 | 522 | 522 | 0.012429 | 203 | 0.0048333 | 595 | 0.014167 | 1.362 | A04 | MICL0.00917034/RMN
Build-In Floor | Mini Canal | MICL.00917034/RMV | 9 | 170 | 34 | 34 | 522 | 522 | 522 | 0.012429 | 203 | 0.0048333 | 595 | 0.014167 | 1.362 | A04 | MICL0.00917034/RMV
Build-In Floor | Mini Canal | MICL.00917034/RNA | 9 | 170 | 34 | 34 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00917034/RNA
Build-In Floor | Mini Canal | MICL.00917034/RON | 9 | 170 | 34 | 34 | 522 | 522 | 522 | 0.012429 | 203 | 0.0048333 | 595 | 0.014167 | 1.362 | A04 | MICL0.00917034/RON
Build-In Floor | Mini Canal | MICL.00917034/ROV | 9 | 170 | 34 | 34 | 522 | 522 | 522 | 0.012429 | 203 | 0.0048333 | 595 | 0.014167 | 1.362 | A04 | MICL0.00917034/ROV
Build-In Floor | Mini Canal | MICL.00917034/RSS | 9 | 170 | 34 | 34 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.00917034/RSS
Build-In Floor | Mini Canal | MICL.00917034/SBL | 9 | 170 | 34 | 34 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00917034/SBL
Build-In Floor | Mini Canal | MICL.00917034/SBR | 9 | 170 | 34 | 34 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00917034/SBR
Build-In Floor | Mini Canal | MICL.00917034/SDB | 9 | 170 | 34 | 34 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00917034/SDB
Build-In Floor | Mini Canal | MICL.00917034/SNA | 9 | 170 | 34 | 34 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00917034/SNA
Build-In Floor | Mini Canal | MICL.00917034/SNC | 9 | 170 | 34 | 34 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.00917034/SNC
Build-In Floor | Mini Canal | MICL.00917042/ANA | 9 | 170 | 42 | 42 | 584 | 584 | 584 | 0.013905 | 227 | 0.0054048 | 665 | 0.015833 | 1.362 | A04 | MICL0.00917042/ANA
Build-In Floor | Mini Canal | MICL.00917042/DBL | 9 | 170 | 42 | 42 | 755 | 755 | 755 | 0.017976 | 294 | 0.007 | 860 | 0.020476 | 1.362 | A04 | MICL0.00917042/DBL
Build-In Floor | Mini Canal | MICL.00917042/DBN | 9 | 170 | 42 | 42 | 724 | 724 | 724 | 0.017238 | 282 | 0.0067143 | 825 | 0.019643 | 1.362 | A04 | MICL0.00917042/DBN
Build-In Floor | Mini Canal | MICL.00917042/DBR | 9 | 170 | 42 | 42 | 755 | 755 | 755 | 0.017976 | 294 | 0.007 | 860 | 0.020476 | 1.362 | A04 | MICL0.00917042/DBR
Build-In Floor | Mini Canal | MICL.00917042/DBV | 9 | 170 | 42 | 42 | 724 | 724 | 724 | 0.017238 | 282 | 0.0067143 | 825 | 0.019643 | 1.362 | A04 | MICL0.00917042/DBV
Build-In Floor | Mini Canal | MICL.00917042/DDB | 9 | 170 | 42 | 42 | 755 | 755 | 755 | 0.017976 | 294 | 0.007 | 860 | 0.020476 | 1.362 | A04 | MICL0.00917042/DDB
Build-In Floor | Mini Canal | MICL.00917042/DMN | 9 | 170 | 42 | 42 | 724 | 724 | 724 | 0.017238 | 282 | 0.0067143 | 825 | 0.019643 | 1.362 | A04 | MICL0.00917042/DMN
Build-In Floor | Mini Canal | MICL.00917042/DMV | 9 | 170 | 42 | 42 | 724 | 724 | 724 | 0.017238 | 282 | 0.0067143 | 825 | 0.019643 | 1.362 | A04 | MICL0.00917042/DMV
Build-In Floor | Mini Canal | MICL.00917042/DNA | 9 | 170 | 42 | 42 | 755 | 755 | 755 | 0.017976 | 294 | 0.007 | 860 | 0.020476 | 1.362 | A04 | MICL0.00917042/DNA
Build-In Floor | Mini Canal | MICL.00917042/DNC | 9 | 170 | 42 | 42 | 755 | 755 | 755 | 0.017976 | 294 | 0.007 | 860 | 0.020476 | 1.362 | A04 | MICL0.00917042/DNC
Build-In Floor | Mini Canal | MICL.00917042/DON | 9 | 170 | 42 | 42 | 724 | 724 | 724 | 0.017238 | 282 | 0.0067143 | 825 | 0.019643 | 1.362 | A04 | MICL0.00917042/DON
Build-In Floor | Mini Canal | MICL.00917042/DOV | 9 | 170 | 42 | 42 | 724 | 724 | 724 | 0.017238 | 282 | 0.0067143 | 825 | 0.019643 | 1.362 | A04 | MICL0.00917042/DOV
Build-In Floor | Mini Canal | MICL.00917042/PNC | 9 | 170 | 42 | 42 | 661 | 661 | 661 | 0.015738 | 257 | 0.006119 | 753 | 0.017929 | 1.362 | A04 | MICL0.00917042/PNC
Build-In Floor | Mini Canal | MICL.00917042/RBL | 9 | 170 | 42 | 42 | 778 | 778 | 778 | 0.018524 | 303 | 0.0072143 | 886 | 0.021095 | 1.362 | A04 | MICL0.00917042/RBL
Build-In Floor | Mini Canal | MICL.00917042/RBN | 9 | 170 | 42 | 42 | 755 | 755 | 755 | 0.017976 | 294 | 0.007 | 860 | 0.020476 | 1.362 | A04 | MICL0.00917042/RBN
Build-In Floor | Mini Canal | MICL.00917042/RBR | 9 | 170 | 42 | 42 | 778 | 778 | 778 | 0.018524 | 303 | 0.0072143 | 886 | 0.021095 | 1.362 | A04 | MICL0.00917042/RBR
Build-In Floor | Mini Canal | MICL.00917042/RBV | 9 | 170 | 42 | 42 | 755 | 755 | 755 | 0.017976 | 294 | 0.007 | 860 | 0.020476 | 1.362 | A04 | MICL0.00917042/RBV
Build-In Floor | Mini Canal | MICL.00917042/RDB | 9 | 170 | 42 | 42 | 778 | 778 | 778 | 0.018524 | 303 | 0.0072143 | 886 | 0.021095 | 1.362 | A04 | MICL0.00917042/RDB
Build-In Floor | Mini Canal | MICL.00917042/RMN | 9 | 170 | 42 | 42 | 755 | 755 | 755 | 0.017976 | 294 | 0.007 | 860 | 0.020476 | 1.362 | A04 | MICL0.00917042/RMN
Build-In Floor | Mini Canal | MICL.00917042/RMV | 9 | 170 | 42 | 42 | 755 | 755 | 755 | 0.017976 | 294 | 0.007 | 860 | 0.020476 | 1.362 | A04 | MICL0.00917042/RMV
Build-In Floor | Mini Canal | MICL.00917042/RNA | 9 | 170 | 42 | 42 | 778 | 778 | 778 | 0.018524 | 303 | 0.0072143 | 886 | 0.021095 | 1.362 | A04 | MICL0.00917042/RNA
Build-In Floor | Mini Canal | MICL.00917042/RON | 9 | 170 | 42 | 42 | 755 | 755 | 755 | 0.017976 | 294 | 0.007 | 860 | 0.020476 | 1.362 | A04 | MICL0.00917042/RON
Build-In Floor | Mini Canal | MICL.00917042/ROV | 9 | 170 | 42 | 42 | 755 | 755 | 755 | 0.017976 | 294 | 0.007 | 860 | 0.020476 | 1.362 | A04 | MICL0.00917042/ROV
Build-In Floor | Mini Canal | MICL.00917042/RSS | 9 | 170 | 42 | 42 | 747 | 747 | 747 | 0.017786 | 291 | 0.0069286 | 851 | 0.020262 | 1.362 | A04 | MICL0.00917042/RSS
Build-In Floor | Mini Canal | MICL.00917042/SBL | 9 | 170 | 42 | 42 | 778 | 778 | 778 | 0.018524 | 303 | 0.0072143 | 886 | 0.021095 | 1.362 | A04 | MICL0.00917042/SBL
Build-In Floor | Mini Canal | MICL.00917042/SBR | 9 | 170 | 42 | 42 | 778 | 778 | 778 | 0.018524 | 303 | 0.0072143 | 886 | 0.021095 | 1.362 | A04 | MICL0.00917042/SBR
Build-In Floor | Mini Canal | MICL.00917042/SDB | 9 | 170 | 42 | 42 | 778 | 778 | 778 | 0.018524 | 303 | 0.0072143 | 886 | 0.021095 | 1.362 | A04 | MICL0.00917042/SDB
Build-In Floor | Mini Canal | MICL.00917042/SNA | 9 | 170 | 42 | 42 | 778 | 778 | 778 | 0.018524 | 303 | 0.0072143 | 886 | 0.021095 | 1.362 | A04 | MICL0.00917042/SNA
Build-In Floor | Mini Canal | MICL.00917042/SNC | 9 | 170 | 42 | 42 | 778 | 778 | 778 | 0.018524 | 303 | 0.0072143 | 886 | 0.021095 | 1.362 | A04 | MICL0.00917042/SNC
Build-In Floor | Mini Canal | MICL.00919014/ANA | 9 | 190 | 14 | 14 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.00919014/ANA
Build-In Floor | Mini Canal | MICL.00919014/DBL | 9 | 190 | 14 | 14 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.00919014/DBL
Build-In Floor | Mini Canal | MICL.00919014/DBN | 9 | 190 | 14 | 14 | 283 | 283 | 283 | 0.0067381 | 110 | 0.002619 | 322 | 0.0076667 | 1.362 | A04 | MICL0.00919014/DBN
Build-In Floor | Mini Canal | MICL.00919014/DBR | 9 | 190 | 14 | 14 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.00919014/DBR
Build-In Floor | Mini Canal | MICL.00919014/DBV | 9 | 190 | 14 | 14 | 283 | 283 | 283 | 0.0067381 | 110 | 0.002619 | 322 | 0.0076667 | 1.362 | A04 | MICL0.00919014/DBV
Build-In Floor | Mini Canal | MICL.00919014/DDB | 9 | 190 | 14 | 14 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.00919014/DDB
Build-In Floor | Mini Canal | MICL.00919014/DMN | 9 | 190 | 14 | 14 | 283 | 283 | 283 | 0.0067381 | 110 | 0.002619 | 322 | 0.0076667 | 1.362 | A04 | MICL0.00919014/DMN
Build-In Floor | Mini Canal | MICL.00919014/DMV | 9 | 190 | 14 | 14 | 283 | 283 | 283 | 0.0067381 | 110 | 0.002619 | 322 | 0.0076667 | 1.362 | A04 | MICL0.00919014/DMV
Build-In Floor | Mini Canal | MICL.00919014/DNA | 9 | 190 | 14 | 14 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.00919014/DNA
Build-In Floor | Mini Canal | MICL.00919014/DNC | 9 | 190 | 14 | 14 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.00919014/DNC
Build-In Floor | Mini Canal | MICL.00919014/DON | 9 | 190 | 14 | 14 | 283 | 283 | 283 | 0.0067381 | 110 | 0.002619 | 322 | 0.0076667 | 1.362 | A04 | MICL0.00919014/DON
Build-In Floor | Mini Canal | MICL.00919014/DOV | 9 | 190 | 14 | 14 | 283 | 283 | 283 | 0.0067381 | 110 | 0.002619 | 322 | 0.0076667 | 1.362 | A04 | MICL0.00919014/DOV
Build-In Floor | Mini Canal | MICL.00919014/RBL | 9 | 190 | 14 | 14 | 304 | 304 | 304 | 0.0072381 | 118 | 0.0028095 | 346 | 0.0082381 | 1.362 | A04 | MICL0.00919014/RBL
Build-In Floor | Mini Canal | MICL.00919014/RBN | 9 | 190 | 14 | 14 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.00919014/RBN
Build-In Floor | Mini Canal | MICL.00919014/RBR | 9 | 190 | 14 | 14 | 304 | 304 | 304 | 0.0072381 | 118 | 0.0028095 | 346 | 0.0082381 | 1.362 | A04 | MICL0.00919014/RBR
Build-In Floor | Mini Canal | MICL.00919014/RBV | 9 | 190 | 14 | 14 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.00919014/RBV
Build-In Floor | Mini Canal | MICL.00919014/RDB | 9 | 190 | 14 | 14 | 304 | 304 | 304 | 0.0072381 | 118 | 0.0028095 | 346 | 0.0082381 | 1.362 | A04 | MICL0.00919014/RDB
Build-In Floor | Mini Canal | MICL.00919014/RMN | 9 | 190 | 14 | 14 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.00919014/RMN
Build-In Floor | Mini Canal | MICL.00919014/RMV | 9 | 190 | 14 | 14 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.00919014/RMV
Build-In Floor | Mini Canal | MICL.00919014/RNA | 9 | 190 | 14 | 14 | 304 | 304 | 304 | 0.0072381 | 118 | 0.0028095 | 346 | 0.0082381 | 1.362 | A04 | MICL0.00919014/RNA
Build-In Floor | Mini Canal | MICL.00919014/RON | 9 | 190 | 14 | 14 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.00919014/RON
Build-In Floor | Mini Canal | MICL.00919014/ROV | 9 | 190 | 14 | 14 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.00919014/ROV
Build-In Floor | Mini Canal | MICL.00919014/RSS | 9 | 190 | 14 | 14 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.00919014/RSS
Build-In Floor | Mini Canal | MICL.00919014/SBL | 9 | 190 | 14 | 14 | 304 | 304 | 304 | 0.0072381 | 118 | 0.0028095 | 346 | 0.0082381 | 1.362 | A04 | MICL0.00919014/SBL
Build-In Floor | Mini Canal | MICL.00919014/SBR | 9 | 190 | 14 | 14 | 304 | 304 | 304 | 0.0072381 | 118 | 0.0028095 | 346 | 0.0082381 | 1.362 | A04 | MICL0.00919014/SBR
Build-In Floor | Mini Canal | MICL.00919014/SDB | 9 | 190 | 14 | 14 | 304 | 304 | 304 | 0.0072381 | 118 | 0.0028095 | 346 | 0.0082381 | 1.362 | A04 | MICL0.00919014/SDB
Build-In Floor | Mini Canal | MICL.00919014/SNA | 9 | 190 | 14 | 14 | 304 | 304 | 304 | 0.0072381 | 118 | 0.0028095 | 346 | 0.0082381 | 1.362 | A04 | MICL0.00919014/SNA
Build-In Floor | Mini Canal | MICL.00919014/SNC | 9 | 190 | 14 | 14 | 304 | 304 | 304 | 0.0072381 | 118 | 0.0028095 | 346 | 0.0082381 | 1.362 | A04 | MICL0.00919014/SNC
Build-In Floor | Mini Canal | MICL.00919018/ANA | 9 | 190 | 18 | 18 | 270 | 270 | 270 | 0.0064286 | 105 | 0.0025 | 308 | 0.0073333 | 1.362 | A04 | MICL0.00919018/ANA
Build-In Floor | Mini Canal | MICL.00919018/DBL | 9 | 190 | 18 | 18 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.00919018/DBL
Build-In Floor | Mini Canal | MICL.00919018/DBN | 9 | 190 | 18 | 18 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.00919018/DBN
Build-In Floor | Mini Canal | MICL.00919018/DBR | 9 | 190 | 18 | 18 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.00919018/DBR
Build-In Floor | Mini Canal | MICL.00919018/DBV | 9 | 190 | 18 | 18 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.00919018/DBV
Build-In Floor | Mini Canal | MICL.00919018/DDB | 9 | 190 | 18 | 18 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.00919018/DDB
Build-In Floor | Mini Canal | MICL.00919018/DMN | 9 | 190 | 18 | 18 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.00919018/DMN
Build-In Floor | Mini Canal | MICL.00919018/DMV | 9 | 190 | 18 | 18 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.00919018/DMV
Build-In Floor | Mini Canal | MICL.00919018/DNA | 9 | 190 | 18 | 18 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.00919018/DNA
Build-In Floor | Mini Canal | MICL.00919018/DNC | 9 | 190 | 18 | 18 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.00919018/DNC
Build-In Floor | Mini Canal | MICL.00919018/DON | 9 | 190 | 18 | 18 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.00919018/DON
Build-In Floor | Mini Canal | MICL.00919018/DOV | 9 | 190 | 18 | 18 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.00919018/DOV
Build-In Floor | Mini Canal | MICL.00919018/RBL | 9 | 190 | 18 | 18 | 360 | 360 | 360 | 0.0085714 | 140 | 0.0033333 | 410 | 0.0097619 | 1.362 | A04 | MICL0.00919018/RBL
Build-In Floor | Mini Canal | MICL.00919018/RBN | 9 | 190 | 18 | 18 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.00919018/RBN
Build-In Floor | Mini Canal | MICL.00919018/RBR | 9 | 190 | 18 | 18 | 360 | 360 | 360 | 0.0085714 | 140 | 0.0033333 | 410 | 0.0097619 | 1.362 | A04 | MICL0.00919018/RBR
Build-In Floor | Mini Canal | MICL.00919018/RBV | 9 | 190 | 18 | 18 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.00919018/RBV
Build-In Floor | Mini Canal | MICL.00919018/RDB | 9 | 190 | 18 | 18 | 360 | 360 | 360 | 0.0085714 | 140 | 0.0033333 | 410 | 0.0097619 | 1.362 | A04 | MICL0.00919018/RDB
Build-In Floor | Mini Canal | MICL.00919018/RMN | 9 | 190 | 18 | 18 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.00919018/RMN
Build-In Floor | Mini Canal | MICL.00919018/RMV | 9 | 190 | 18 | 18 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.00919018/RMV
Build-In Floor | Mini Canal | MICL.00919018/RNA | 9 | 190 | 18 | 18 | 360 | 360 | 360 | 0.0085714 | 140 | 0.0033333 | 410 | 0.0097619 | 1.362 | A04 | MICL0.00919018/RNA
Build-In Floor | Mini Canal | MICL.00919018/RON | 9 | 190 | 18 | 18 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.00919018/RON
Build-In Floor | Mini Canal | MICL.00919018/ROV | 9 | 190 | 18 | 18 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.00919018/ROV
Build-In Floor | Mini Canal | MICL.00919018/RSS | 9 | 190 | 18 | 18 | 346 | 346 | 346 | 0.0082381 | 135 | 0.0032143 | 394 | 0.009381 | 1.362 | A04 | MICL0.00919018/RSS
Build-In Floor | Mini Canal | MICL.00919018/SBL | 9 | 190 | 18 | 18 | 360 | 360 | 360 | 0.0085714 | 140 | 0.0033333 | 410 | 0.0097619 | 1.362 | A04 | MICL0.00919018/SBL
Build-In Floor | Mini Canal | MICL.00919018/SBR | 9 | 190 | 18 | 18 | 360 | 360 | 360 | 0.0085714 | 140 | 0.0033333 | 410 | 0.0097619 | 1.362 | A04 | MICL0.00919018/SBR
Build-In Floor | Mini Canal | MICL.00919018/SDB | 9 | 190 | 18 | 18 | 360 | 360 | 360 | 0.0085714 | 140 | 0.0033333 | 410 | 0.0097619 | 1.362 | A04 | MICL0.00919018/SDB
Build-In Floor | Mini Canal | MICL.00919018/SNA | 9 | 190 | 18 | 18 | 360 | 360 | 360 | 0.0085714 | 140 | 0.0033333 | 410 | 0.0097619 | 1.362 | A04 | MICL0.00919018/SNA
Build-In Floor | Mini Canal | MICL.00919018/SNC | 9 | 190 | 18 | 18 | 360 | 360 | 360 | 0.0085714 | 140 | 0.0033333 | 410 | 0.0097619 | 1.362 | A04 | MICL0.00919018/SNC
Build-In Floor | Mini Canal | MICL.00919026/ANA | 9 | 190 | 26 | 26 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.00919026/ANA
Build-In Floor | Mini Canal | MICL.00919026/DBL | 9 | 190 | 26 | 26 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00919026/DBL
Build-In Floor | Mini Canal | MICL.00919026/DBN | 9 | 190 | 26 | 26 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.00919026/DBN
Build-In Floor | Mini Canal | MICL.00919026/DBR | 9 | 190 | 26 | 26 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00919026/DBR
Build-In Floor | Mini Canal | MICL.00919026/DBV | 9 | 190 | 26 | 26 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.00919026/DBV
Build-In Floor | Mini Canal | MICL.00919026/DDB | 9 | 190 | 26 | 26 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00919026/DDB
Build-In Floor | Mini Canal | MICL.00919026/DMN | 9 | 190 | 26 | 26 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.00919026/DMN
Build-In Floor | Mini Canal | MICL.00919026/DMV | 9 | 190 | 26 | 26 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.00919026/DMV
Build-In Floor | Mini Canal | MICL.00919026/DNA | 9 | 190 | 26 | 26 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00919026/DNA
Build-In Floor | Mini Canal | MICL.00919026/DNC | 9 | 190 | 26 | 26 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00919026/DNC
Build-In Floor | Mini Canal | MICL.00919026/DON | 9 | 190 | 26 | 26 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.00919026/DON
Build-In Floor | Mini Canal | MICL.00919026/DOV | 9 | 190 | 26 | 26 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.00919026/DOV
Build-In Floor | Mini Canal | MICL.00919026/PNC | 9 | 190 | 26 | 26 | 403 | 403 | 403 | 0.0095952 | 157 | 0.0037381 | 459 | 0.010929 | 1.362 | A04 | MICL0.00919026/PNC
Build-In Floor | Mini Canal | MICL.00919026/RBL | 9 | 190 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.00919026/RBL
Build-In Floor | Mini Canal | MICL.00919026/RBN | 9 | 190 | 26 | 26 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00919026/RBN
Build-In Floor | Mini Canal | MICL.00919026/RBR | 9 | 190 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.00919026/RBR
Build-In Floor | Mini Canal | MICL.00919026/RBV | 9 | 190 | 26 | 26 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00919026/RBV
Build-In Floor | Mini Canal | MICL.00919026/RDB | 9 | 190 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.00919026/RDB
Build-In Floor | Mini Canal | MICL.00919026/RMN | 9 | 190 | 26 | 26 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00919026/RMN
Build-In Floor | Mini Canal | MICL.00919026/RMV | 9 | 190 | 26 | 26 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00919026/RMV
Build-In Floor | Mini Canal | MICL.00919026/RNA | 9 | 190 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.00919026/RNA
Build-In Floor | Mini Canal | MICL.00919026/RON | 9 | 190 | 26 | 26 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00919026/RON
Build-In Floor | Mini Canal | MICL.00919026/ROV | 9 | 190 | 26 | 26 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00919026/ROV
Build-In Floor | Mini Canal | MICL.00919026/RSS | 9 | 190 | 26 | 26 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.00919026/RSS
Build-In Floor | Mini Canal | MICL.00919026/SBL | 9 | 190 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.00919026/SBL
Build-In Floor | Mini Canal | MICL.00919026/SBR | 9 | 190 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.00919026/SBR
Build-In Floor | Mini Canal | MICL.00919026/SDB | 9 | 190 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.00919026/SDB
Build-In Floor | Mini Canal | MICL.00919026/SNA | 9 | 190 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.00919026/SNA
Build-In Floor | Mini Canal | MICL.00919026/SNC | 9 | 190 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.00919026/SNC
Build-In Floor | Mini Canal | MICL.00919034/ANA | 9 | 190 | 34 | 34 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.00919034/ANA
Build-In Floor | Mini Canal | MICL.00919034/DBL | 9 | 190 | 34 | 34 | 597 | 597 | 597 | 0.014214 | 232 | 0.0055238 | 680 | 0.01619 | 1.362 | A04 | MICL0.00919034/DBL
Build-In Floor | Mini Canal | MICL.00919034/DBN | 9 | 190 | 34 | 34 | 572 | 572 | 572 | 0.013619 | 223 | 0.0053095 | 652 | 0.015524 | 1.362 | A04 | MICL0.00919034/DBN
Build-In Floor | Mini Canal | MICL.00919034/DBR | 9 | 190 | 34 | 34 | 597 | 597 | 597 | 0.014214 | 232 | 0.0055238 | 680 | 0.01619 | 1.362 | A04 | MICL0.00919034/DBR
Build-In Floor | Mini Canal | MICL.00919034/DBV | 9 | 190 | 34 | 34 | 572 | 572 | 572 | 0.013619 | 223 | 0.0053095 | 652 | 0.015524 | 1.362 | A04 | MICL0.00919034/DBV
Build-In Floor | Mini Canal | MICL.00919034/DDB | 9 | 190 | 34 | 34 | 597 | 597 | 597 | 0.014214 | 232 | 0.0055238 | 680 | 0.01619 | 1.362 | A04 | MICL0.00919034/DDB
Build-In Floor | Mini Canal | MICL.00919034/DMN | 9 | 190 | 34 | 34 | 572 | 572 | 572 | 0.013619 | 223 | 0.0053095 | 652 | 0.015524 | 1.362 | A04 | MICL0.00919034/DMN
Build-In Floor | Mini Canal | MICL.00919034/DMV | 9 | 190 | 34 | 34 | 572 | 572 | 572 | 0.013619 | 223 | 0.0053095 | 652 | 0.015524 | 1.362 | A04 | MICL0.00919034/DMV
Build-In Floor | Mini Canal | MICL.00919034/DNA | 9 | 190 | 34 | 34 | 597 | 597 | 597 | 0.014214 | 232 | 0.0055238 | 680 | 0.01619 | 1.362 | A04 | MICL0.00919034/DNA
Build-In Floor | Mini Canal | MICL.00919034/DNC | 9 | 190 | 34 | 34 | 597 | 597 | 597 | 0.014214 | 232 | 0.0055238 | 680 | 0.01619 | 1.362 | A04 | MICL0.00919034/DNC
Build-In Floor | Mini Canal | MICL.00919034/DON | 9 | 190 | 34 | 34 | 572 | 572 | 572 | 0.013619 | 223 | 0.0053095 | 652 | 0.015524 | 1.362 | A04 | MICL0.00919034/DON
Build-In Floor | Mini Canal | MICL.00919034/DOV | 9 | 190 | 34 | 34 | 572 | 572 | 572 | 0.013619 | 223 | 0.0053095 | 652 | 0.015524 | 1.362 | A04 | MICL0.00919034/DOV
Build-In Floor | Mini Canal | MICL.00919034/PNC | 9 | 190 | 34 | 34 | 523 | 523 | 523 | 0.012452 | 203 | 0.0048333 | 596 | 0.01419 | 1.362 | A04 | MICL0.00919034/PNC
Build-In Floor | Mini Canal | MICL.00919034/RBL | 9 | 190 | 34 | 34 | 615 | 615 | 615 | 0.014643 | 239 | 0.0056905 | 700 | 0.016667 | 1.362 | A04 | MICL0.00919034/RBL
Build-In Floor | Mini Canal | MICL.00919034/RBN | 9 | 190 | 34 | 34 | 597 | 597 | 597 | 0.014214 | 232 | 0.0055238 | 680 | 0.01619 | 1.362 | A04 | MICL0.00919034/RBN
Build-In Floor | Mini Canal | MICL.00919034/RBR | 9 | 190 | 34 | 34 | 615 | 615 | 615 | 0.014643 | 239 | 0.0056905 | 700 | 0.016667 | 1.362 | A04 | MICL0.00919034/RBR
Build-In Floor | Mini Canal | MICL.00919034/RBV | 9 | 190 | 34 | 34 | 597 | 597 | 597 | 0.014214 | 232 | 0.0055238 | 680 | 0.01619 | 1.362 | A04 | MICL0.00919034/RBV
Build-In Floor | Mini Canal | MICL.00919034/RDB | 9 | 190 | 34 | 34 | 615 | 615 | 615 | 0.014643 | 239 | 0.0056905 | 700 | 0.016667 | 1.362 | A04 | MICL0.00919034/RDB
Build-In Floor | Mini Canal | MICL.00919034/RMN | 9 | 190 | 34 | 34 | 597 | 597 | 597 | 0.014214 | 232 | 0.0055238 | 680 | 0.01619 | 1.362 | A04 | MICL0.00919034/RMN
Build-In Floor | Mini Canal | MICL.00919034/RMV | 9 | 190 | 34 | 34 | 597 | 597 | 597 | 0.014214 | 232 | 0.0055238 | 680 | 0.01619 | 1.362 | A04 | MICL0.00919034/RMV
Build-In Floor | Mini Canal | MICL.00919034/RNA | 9 | 190 | 34 | 34 | 615 | 615 | 615 | 0.014643 | 239 | 0.0056905 | 700 | 0.016667 | 1.362 | A04 | MICL0.00919034/RNA
Build-In Floor | Mini Canal | MICL.00919034/RON | 9 | 190 | 34 | 34 | 597 | 597 | 597 | 0.014214 | 232 | 0.0055238 | 680 | 0.01619 | 1.362 | A04 | MICL0.00919034/RON
Build-In Floor | Mini Canal | MICL.00919034/ROV | 9 | 190 | 34 | 34 | 597 | 597 | 597 | 0.014214 | 232 | 0.0055238 | 680 | 0.01619 | 1.362 | A04 | MICL0.00919034/ROV
Build-In Floor | Mini Canal | MICL.00919034/RSS | 9 | 190 | 34 | 34 | 590 | 590 | 590 | 0.014048 | 230 | 0.0054762 | 672 | 0.016 | 1.362 | A04 | MICL0.00919034/RSS
Build-In Floor | Mini Canal | MICL.00919034/SBL | 9 | 190 | 34 | 34 | 615 | 615 | 615 | 0.014643 | 239 | 0.0056905 | 700 | 0.016667 | 1.362 | A04 | MICL0.00919034/SBL
Build-In Floor | Mini Canal | MICL.00919034/SBR | 9 | 190 | 34 | 34 | 615 | 615 | 615 | 0.014643 | 239 | 0.0056905 | 700 | 0.016667 | 1.362 | A04 | MICL0.00919034/SBR
Build-In Floor | Mini Canal | MICL.00919034/SDB | 9 | 190 | 34 | 34 | 615 | 615 | 615 | 0.014643 | 239 | 0.0056905 | 700 | 0.016667 | 1.362 | A04 | MICL0.00919034/SDB
Build-In Floor | Mini Canal | MICL.00919034/SNA | 9 | 190 | 34 | 34 | 615 | 615 | 615 | 0.014643 | 239 | 0.0056905 | 700 | 0.016667 | 1.362 | A04 | MICL0.00919034/SNA
Build-In Floor | Mini Canal | MICL.00919034/SNC | 9 | 190 | 34 | 34 | 615 | 615 | 615 | 0.014643 | 239 | 0.0056905 | 700 | 0.016667 | 1.362 | A04 | MICL0.00919034/SNC
Build-In Floor | Mini Canal | MICL.00919042/ANA | 9 | 190 | 42 | 42 | 666 | 666 | 666 | 0.015857 | 259 | 0.0061667 | 759 | 0.018071 | 1.362 | A04 | MICL0.00919042/ANA
Build-In Floor | Mini Canal | MICL.00919042/DBL | 9 | 190 | 42 | 42 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.00919042/DBL
Build-In Floor | Mini Canal | MICL.00919042/DBN | 9 | 190 | 42 | 42 | 826 | 826 | 826 | 0.019667 | 321 | 0.0076429 | 941 | 0.022405 | 1.362 | A04 | MICL0.00919042/DBN
Build-In Floor | Mini Canal | MICL.00919042/DBR | 9 | 190 | 42 | 42 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.00919042/DBR
Build-In Floor | Mini Canal | MICL.00919042/DBV | 9 | 190 | 42 | 42 | 826 | 826 | 826 | 0.019667 | 321 | 0.0076429 | 941 | 0.022405 | 1.362 | A04 | MICL0.00919042/DBV
Build-In Floor | Mini Canal | MICL.00919042/DDB | 9 | 190 | 42 | 42 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.00919042/DDB
Build-In Floor | Mini Canal | MICL.00919042/DMN | 9 | 190 | 42 | 42 | 826 | 826 | 826 | 0.019667 | 321 | 0.0076429 | 941 | 0.022405 | 1.362 | A04 | MICL0.00919042/DMN
Build-In Floor | Mini Canal | MICL.00919042/DMV | 9 | 190 | 42 | 42 | 826 | 826 | 826 | 0.019667 | 321 | 0.0076429 | 941 | 0.022405 | 1.362 | A04 | MICL0.00919042/DMV
Build-In Floor | Mini Canal | MICL.00919042/DNA | 9 | 190 | 42 | 42 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.00919042/DNA
Build-In Floor | Mini Canal | MICL.00919042/DNC | 9 | 190 | 42 | 42 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.00919042/DNC
Build-In Floor | Mini Canal | MICL.00919042/DON | 9 | 190 | 42 | 42 | 826 | 826 | 826 | 0.019667 | 321 | 0.0076429 | 941 | 0.022405 | 1.362 | A04 | MICL0.00919042/DON
Build-In Floor | Mini Canal | MICL.00919042/DOV | 9 | 190 | 42 | 42 | 826 | 826 | 826 | 0.019667 | 321 | 0.0076429 | 941 | 0.022405 | 1.362 | A04 | MICL0.00919042/DOV
Build-In Floor | Mini Canal | MICL.00919042/PNC | 9 | 190 | 42 | 42 | 755 | 755 | 755 | 0.017976 | 294 | 0.007 | 860 | 0.020476 | 1.362 | A04 | MICL0.00919042/PNC
Build-In Floor | Mini Canal | MICL.00919042/RBL | 9 | 190 | 42 | 42 | 888 | 888 | 888 | 0.021143 | 345 | 0.0082143 | 1011 | 0.024071 | 1.362 | A04 | MICL0.00919042/RBL
Build-In Floor | Mini Canal | MICL.00919042/RBN | 9 | 190 | 42 | 42 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.00919042/RBN
Build-In Floor | Mini Canal | MICL.00919042/RBR | 9 | 190 | 42 | 42 | 888 | 888 | 888 | 0.021143 | 345 | 0.0082143 | 1011 | 0.024071 | 1.362 | A04 | MICL0.00919042/RBR
Build-In Floor | Mini Canal | MICL.00919042/RBV | 9 | 190 | 42 | 42 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.00919042/RBV
Build-In Floor | Mini Canal | MICL.00919042/RDB | 9 | 190 | 42 | 42 | 888 | 888 | 888 | 0.021143 | 345 | 0.0082143 | 1011 | 0.024071 | 1.362 | A04 | MICL0.00919042/RDB
Build-In Floor | Mini Canal | MICL.00919042/RMN | 9 | 190 | 42 | 42 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.00919042/RMN
Build-In Floor | Mini Canal | MICL.00919042/RMV | 9 | 190 | 42 | 42 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.00919042/RMV
Build-In Floor | Mini Canal | MICL.00919042/RNA | 9 | 190 | 42 | 42 | 888 | 888 | 888 | 0.021143 | 345 | 0.0082143 | 1011 | 0.024071 | 1.362 | A04 | MICL0.00919042/RNA
Build-In Floor | Mini Canal | MICL.00919042/RON | 9 | 190 | 42 | 42 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.00919042/RON
Build-In Floor | Mini Canal | MICL.00919042/ROV | 9 | 190 | 42 | 42 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.00919042/ROV
Build-In Floor | Mini Canal | MICL.00919042/RSS | 9 | 190 | 42 | 42 | 852 | 852 | 852 | 0.020286 | 331 | 0.007881 | 970 | 0.023095 | 1.362 | A04 | MICL0.00919042/RSS
Build-In Floor | Mini Canal | MICL.00919042/SBL | 9 | 190 | 42 | 42 | 888 | 888 | 888 | 0.021143 | 345 | 0.0082143 | 1011 | 0.024071 | 1.362 | A04 | MICL0.00919042/SBL
Build-In Floor | Mini Canal | MICL.00919042/SBR | 9 | 190 | 42 | 42 | 888 | 888 | 888 | 0.021143 | 345 | 0.0082143 | 1011 | 0.024071 | 1.362 | A04 | MICL0.00919042/SBR
Build-In Floor | Mini Canal | MICL.00919042/SDB | 9 | 190 | 42 | 42 | 888 | 888 | 888 | 0.021143 | 345 | 0.0082143 | 1011 | 0.024071 | 1.362 | A04 | MICL0.00919042/SDB
Build-In Floor | Mini Canal | MICL.00919042/SNA | 9 | 190 | 42 | 42 | 888 | 888 | 888 | 0.021143 | 345 | 0.0082143 | 1011 | 0.024071 | 1.362 | A04 | MICL0.00919042/SNA
Build-In Floor | Mini Canal | MICL.00919042/SNC | 9 | 190 | 42 | 42 | 888 | 888 | 888 | 0.021143 | 345 | 0.0082143 | 1011 | 0.024071 | 1.362 | A04 | MICL0.00919042/SNC
Build-In Floor | Mini Canal | MICL.00921014/ANA | 9 | 210 | 14 | 14 | 257 | 257 | 257 | 0.006119 | 100 | 0.002381 | 293 | 0.0069762 | 1.362 | A04 | MICL0.00921014/ANA
Build-In Floor | Mini Canal | MICL.00921014/DBL | 9 | 210 | 14 | 14 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.00921014/DBL
Build-In Floor | Mini Canal | MICL.00921014/DBN | 9 | 210 | 14 | 14 | 318 | 318 | 318 | 0.0075714 | 124 | 0.0029524 | 362 | 0.008619 | 1.362 | A04 | MICL0.00921014/DBN
Build-In Floor | Mini Canal | MICL.00921014/DBR | 9 | 210 | 14 | 14 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.00921014/DBR
Build-In Floor | Mini Canal | MICL.00921014/DBV | 9 | 210 | 14 | 14 | 318 | 318 | 318 | 0.0075714 | 124 | 0.0029524 | 362 | 0.008619 | 1.362 | A04 | MICL0.00921014/DBV
Build-In Floor | Mini Canal | MICL.00921014/DDB | 9 | 210 | 14 | 14 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.00921014/DDB
Build-In Floor | Mini Canal | MICL.00921014/DMN | 9 | 210 | 14 | 14 | 318 | 318 | 318 | 0.0075714 | 124 | 0.0029524 | 362 | 0.008619 | 1.362 | A04 | MICL0.00921014/DMN
Build-In Floor | Mini Canal | MICL.00921014/DMV | 9 | 210 | 14 | 14 | 318 | 318 | 318 | 0.0075714 | 124 | 0.0029524 | 362 | 0.008619 | 1.362 | A04 | MICL0.00921014/DMV
Build-In Floor | Mini Canal | MICL.00921014/DNA | 9 | 210 | 14 | 14 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.00921014/DNA
Build-In Floor | Mini Canal | MICL.00921014/DNC | 9 | 210 | 14 | 14 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.00921014/DNC
Build-In Floor | Mini Canal | MICL.00921014/DON | 9 | 210 | 14 | 14 | 318 | 318 | 318 | 0.0075714 | 124 | 0.0029524 | 362 | 0.008619 | 1.362 | A04 | MICL0.00921014/DON
Build-In Floor | Mini Canal | MICL.00921014/DOV | 9 | 210 | 14 | 14 | 318 | 318 | 318 | 0.0075714 | 124 | 0.0029524 | 362 | 0.008619 | 1.362 | A04 | MICL0.00921014/DOV
Build-In Floor | Mini Canal | MICL.00921014/RBL | 9 | 210 | 14 | 14 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.00921014/RBL
Build-In Floor | Mini Canal | MICL.00921014/RBN | 9 | 210 | 14 | 14 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.00921014/RBN
Build-In Floor | Mini Canal | MICL.00921014/RBR | 9 | 210 | 14 | 14 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.00921014/RBR
Build-In Floor | Mini Canal | MICL.00921014/RBV | 9 | 210 | 14 | 14 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.00921014/RBV
Build-In Floor | Mini Canal | MICL.00921014/RDB | 9 | 210 | 14 | 14 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.00921014/RDB
Build-In Floor | Mini Canal | MICL.00921014/RMN | 9 | 210 | 14 | 14 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.00921014/RMN
Build-In Floor | Mini Canal | MICL.00921014/RMV | 9 | 210 | 14 | 14 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.00921014/RMV
Build-In Floor | Mini Canal | MICL.00921014/RNA | 9 | 210 | 14 | 14 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.00921014/RNA
Build-In Floor | Mini Canal | MICL.00921014/RON | 9 | 210 | 14 | 14 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.00921014/RON
Build-In Floor | Mini Canal | MICL.00921014/ROV | 9 | 210 | 14 | 14 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.00921014/ROV
Build-In Floor | Mini Canal | MICL.00921014/RSS | 9 | 210 | 14 | 14 | 328 | 328 | 328 | 0.0078095 | 128 | 0.0030476 | 374 | 0.0089048 | 1.362 | A04 | MICL0.00921014/RSS
Build-In Floor | Mini Canal | MICL.00921014/SBL | 9 | 210 | 14 | 14 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.00921014/SBL
Build-In Floor | Mini Canal | MICL.00921014/SBR | 9 | 210 | 14 | 14 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.00921014/SBR
Build-In Floor | Mini Canal | MICL.00921014/SDB | 9 | 210 | 14 | 14 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.00921014/SDB
Build-In Floor | Mini Canal | MICL.00921014/SNA | 9 | 210 | 14 | 14 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.00921014/SNA
Build-In Floor | Mini Canal | MICL.00921014/SNC | 9 | 210 | 14 | 14 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.00921014/SNC
Build-In Floor | Mini Canal | MICL.00921018/ANA | 9 | 210 | 18 | 18 | 305 | 305 | 305 | 0.0072619 | 119 | 0.0028333 | 347 | 0.0082619 | 1.362 | A04 | MICL0.00921018/ANA
Build-In Floor | Mini Canal | MICL.00921018/DBL | 9 | 210 | 18 | 18 | 394 | 394 | 394 | 0.009381 | 153 | 0.0036429 | 449 | 0.01069 | 1.362 | A04 | MICL0.00921018/DBL
Build-In Floor | Mini Canal | MICL.00921018/DBN | 9 | 210 | 18 | 18 | 378 | 378 | 378 | 0.009 | 147 | 0.0035 | 431 | 0.010262 | 1.362 | A04 | MICL0.00921018/DBN
Build-In Floor | Mini Canal | MICL.00921018/DBR | 9 | 210 | 18 | 18 | 394 | 394 | 394 | 0.009381 | 153 | 0.0036429 | 449 | 0.01069 | 1.362 | A04 | MICL0.00921018/DBR
Build-In Floor | Mini Canal | MICL.00921018/DBV | 9 | 210 | 18 | 18 | 378 | 378 | 378 | 0.009 | 147 | 0.0035 | 431 | 0.010262 | 1.362 | A04 | MICL0.00921018/DBV
Build-In Floor | Mini Canal | MICL.00921018/DDB | 9 | 210 | 18 | 18 | 394 | 394 | 394 | 0.009381 | 153 | 0.0036429 | 449 | 0.01069 | 1.362 | A04 | MICL0.00921018/DDB
Build-In Floor | Mini Canal | MICL.00921018/DMN | 9 | 210 | 18 | 18 | 378 | 378 | 378 | 0.009 | 147 | 0.0035 | 431 | 0.010262 | 1.362 | A04 | MICL0.00921018/DMN
Build-In Floor | Mini Canal | MICL.00921018/DMV | 9 | 210 | 18 | 18 | 378 | 378 | 378 | 0.009 | 147 | 0.0035 | 431 | 0.010262 | 1.362 | A04 | MICL0.00921018/DMV
Build-In Floor | Mini Canal | MICL.00921018/DNA | 9 | 210 | 18 | 18 | 394 | 394 | 394 | 0.009381 | 153 | 0.0036429 | 449 | 0.01069 | 1.362 | A04 | MICL0.00921018/DNA
Build-In Floor | Mini Canal | MICL.00921018/DNC | 9 | 210 | 18 | 18 | 394 | 394 | 394 | 0.009381 | 153 | 0.0036429 | 449 | 0.01069 | 1.362 | A04 | MICL0.00921018/DNC
Build-In Floor | Mini Canal | MICL.00921018/DON | 9 | 210 | 18 | 18 | 378 | 378 | 378 | 0.009 | 147 | 0.0035 | 431 | 0.010262 | 1.362 | A04 | MICL0.00921018/DON
Build-In Floor | Mini Canal | MICL.00921018/DOV | 9 | 210 | 18 | 18 | 378 | 378 | 378 | 0.009 | 147 | 0.0035 | 431 | 0.010262 | 1.362 | A04 | MICL0.00921018/DOV
Build-In Floor | Mini Canal | MICL.00921018/RBL | 9 | 210 | 18 | 18 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00921018/RBL
Build-In Floor | Mini Canal | MICL.00921018/RBN | 9 | 210 | 18 | 18 | 394 | 394 | 394 | 0.009381 | 153 | 0.0036429 | 449 | 0.01069 | 1.362 | A04 | MICL0.00921018/RBN
Build-In Floor | Mini Canal | MICL.00921018/RBR | 9 | 210 | 18 | 18 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00921018/RBR
Build-In Floor | Mini Canal | MICL.00921018/RBV | 9 | 210 | 18 | 18 | 394 | 394 | 394 | 0.009381 | 153 | 0.0036429 | 449 | 0.01069 | 1.362 | A04 | MICL0.00921018/RBV
Build-In Floor | Mini Canal | MICL.00921018/RDB | 9 | 210 | 18 | 18 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00921018/RDB
Build-In Floor | Mini Canal | MICL.00921018/RMN | 9 | 210 | 18 | 18 | 394 | 394 | 394 | 0.009381 | 153 | 0.0036429 | 449 | 0.01069 | 1.362 | A04 | MICL0.00921018/RMN
Build-In Floor | Mini Canal | MICL.00921018/RMV | 9 | 210 | 18 | 18 | 394 | 394 | 394 | 0.009381 | 153 | 0.0036429 | 449 | 0.01069 | 1.362 | A04 | MICL0.00921018/RMV
Build-In Floor | Mini Canal | MICL.00921018/RNA | 9 | 210 | 18 | 18 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00921018/RNA
Build-In Floor | Mini Canal | MICL.00921018/RON | 9 | 210 | 18 | 18 | 394 | 394 | 394 | 0.009381 | 153 | 0.0036429 | 449 | 0.01069 | 1.362 | A04 | MICL0.00921018/RON
Build-In Floor | Mini Canal | MICL.00921018/ROV | 9 | 210 | 18 | 18 | 394 | 394 | 394 | 0.009381 | 153 | 0.0036429 | 449 | 0.01069 | 1.362 | A04 | MICL0.00921018/ROV
Build-In Floor | Mini Canal | MICL.00921018/RSS | 9 | 210 | 18 | 18 | 390 | 390 | 390 | 0.0092857 | 152 | 0.003619 | 444 | 0.010571 | 1.362 | A04 | MICL0.00921018/RSS
Build-In Floor | Mini Canal | MICL.00921018/SBL | 9 | 210 | 18 | 18 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00921018/SBL
Build-In Floor | Mini Canal | MICL.00921018/SBR | 9 | 210 | 18 | 18 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00921018/SBR
Build-In Floor | Mini Canal | MICL.00921018/SDB | 9 | 210 | 18 | 18 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00921018/SDB
Build-In Floor | Mini Canal | MICL.00921018/SNA | 9 | 210 | 18 | 18 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00921018/SNA
Build-In Floor | Mini Canal | MICL.00921018/SNC | 9 | 210 | 18 | 18 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00921018/SNC
Build-In Floor | Mini Canal | MICL.00921026/ANA | 9 | 210 | 26 | 26 | 401 | 401 | 401 | 0.0095476 | 156 | 0.0037143 | 457 | 0.010881 | 1.362 | A04 | MICL0.00921026/ANA
Build-In Floor | Mini Canal | MICL.00921026/DBL | 9 | 210 | 26 | 26 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.00921026/DBL
Build-In Floor | Mini Canal | MICL.00921026/DBN | 9 | 210 | 26 | 26 | 497 | 497 | 497 | 0.011833 | 193 | 0.0045952 | 566 | 0.013476 | 1.362 | A04 | MICL0.00921026/DBN
Build-In Floor | Mini Canal | MICL.00921026/DBR | 9 | 210 | 26 | 26 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.00921026/DBR
Build-In Floor | Mini Canal | MICL.00921026/DBV | 9 | 210 | 26 | 26 | 497 | 497 | 497 | 0.011833 | 193 | 0.0045952 | 566 | 0.013476 | 1.362 | A04 | MICL0.00921026/DBV
Build-In Floor | Mini Canal | MICL.00921026/DDB | 9 | 210 | 26 | 26 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.00921026/DDB
Build-In Floor | Mini Canal | MICL.00921026/DMN | 9 | 210 | 26 | 26 | 497 | 497 | 497 | 0.011833 | 193 | 0.0045952 | 566 | 0.013476 | 1.362 | A04 | MICL0.00921026/DMN
Build-In Floor | Mini Canal | MICL.00921026/DMV | 9 | 210 | 26 | 26 | 497 | 497 | 497 | 0.011833 | 193 | 0.0045952 | 566 | 0.013476 | 1.362 | A04 | MICL0.00921026/DMV
Build-In Floor | Mini Canal | MICL.00921026/DNA | 9 | 210 | 26 | 26 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.00921026/DNA
Build-In Floor | Mini Canal | MICL.00921026/DNC | 9 | 210 | 26 | 26 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.00921026/DNC
Build-In Floor | Mini Canal | MICL.00921026/DON | 9 | 210 | 26 | 26 | 497 | 497 | 497 | 0.011833 | 193 | 0.0045952 | 566 | 0.013476 | 1.362 | A04 | MICL0.00921026/DON
Build-In Floor | Mini Canal | MICL.00921026/DOV | 9 | 210 | 26 | 26 | 497 | 497 | 497 | 0.011833 | 193 | 0.0045952 | 566 | 0.013476 | 1.362 | A04 | MICL0.00921026/DOV
Build-In Floor | Mini Canal | MICL.00921026/PNC | 9 | 210 | 26 | 26 | 454 | 454 | 454 | 0.01081 | 177 | 0.0042143 | 517 | 0.01231 | 1.362 | A04 | MICL0.00921026/PNC
Build-In Floor | Mini Canal | MICL.00921026/RBL | 9 | 210 | 26 | 26 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.00921026/RBL
Build-In Floor | Mini Canal | MICL.00921026/RBN | 9 | 210 | 26 | 26 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.00921026/RBN
Build-In Floor | Mini Canal | MICL.00921026/RBR | 9 | 210 | 26 | 26 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.00921026/RBR
Build-In Floor | Mini Canal | MICL.00921026/RBV | 9 | 210 | 26 | 26 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.00921026/RBV
Build-In Floor | Mini Canal | MICL.00921026/RDB | 9 | 210 | 26 | 26 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.00921026/RDB
Build-In Floor | Mini Canal | MICL.00921026/RMN | 9 | 210 | 26 | 26 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.00921026/RMN
Build-In Floor | Mini Canal | MICL.00921026/RMV | 9 | 210 | 26 | 26 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.00921026/RMV
Build-In Floor | Mini Canal | MICL.00921026/RNA | 9 | 210 | 26 | 26 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.00921026/RNA
Build-In Floor | Mini Canal | MICL.00921026/RON | 9 | 210 | 26 | 26 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.00921026/RON
Build-In Floor | Mini Canal | MICL.00921026/ROV | 9 | 210 | 26 | 26 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.00921026/ROV
Build-In Floor | Mini Canal | MICL.00921026/RSS | 9 | 210 | 26 | 26 | 513 | 513 | 513 | 0.012214 | 200 | 0.0047619 | 584 | 0.013905 | 1.362 | A04 | MICL0.00921026/RSS
Build-In Floor | Mini Canal | MICL.00921026/SBL | 9 | 210 | 26 | 26 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.00921026/SBL
Build-In Floor | Mini Canal | MICL.00921026/SBR | 9 | 210 | 26 | 26 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.00921026/SBR
Build-In Floor | Mini Canal | MICL.00921026/SDB | 9 | 210 | 26 | 26 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.00921026/SDB
Build-In Floor | Mini Canal | MICL.00921026/SNA | 9 | 210 | 26 | 26 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.00921026/SNA
Build-In Floor | Mini Canal | MICL.00921026/SNC | 9 | 210 | 26 | 26 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.00921026/SNC
Build-In Floor | Mini Canal | MICL.00921034/ANA | 9 | 210 | 34 | 34 | 519 | 519 | 519 | 0.012357 | 202 | 0.0048095 | 591 | 0.014071 | 1.362 | A04 | MICL0.00921034/ANA
Build-In Floor | Mini Canal | MICL.00921034/DBL | 9 | 210 | 34 | 34 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00921034/DBL
Build-In Floor | Mini Canal | MICL.00921034/DBN | 9 | 210 | 34 | 34 | 644 | 644 | 644 | 0.015333 | 251 | 0.0059762 | 734 | 0.017476 | 1.362 | A04 | MICL0.00921034/DBN
Build-In Floor | Mini Canal | MICL.00921034/DBR | 9 | 210 | 34 | 34 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00921034/DBR
Build-In Floor | Mini Canal | MICL.00921034/DBV | 9 | 210 | 34 | 34 | 644 | 644 | 644 | 0.015333 | 251 | 0.0059762 | 734 | 0.017476 | 1.362 | A04 | MICL0.00921034/DBV
Build-In Floor | Mini Canal | MICL.00921034/DDB | 9 | 210 | 34 | 34 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00921034/DDB
Build-In Floor | Mini Canal | MICL.00921034/DMN | 9 | 210 | 34 | 34 | 644 | 644 | 644 | 0.015333 | 251 | 0.0059762 | 734 | 0.017476 | 1.362 | A04 | MICL0.00921034/DMN
Build-In Floor | Mini Canal | MICL.00921034/DMV | 9 | 210 | 34 | 34 | 644 | 644 | 644 | 0.015333 | 251 | 0.0059762 | 734 | 0.017476 | 1.362 | A04 | MICL0.00921034/DMV
Build-In Floor | Mini Canal | MICL.00921034/DNA | 9 | 210 | 34 | 34 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00921034/DNA
Build-In Floor | Mini Canal | MICL.00921034/DNC | 9 | 210 | 34 | 34 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00921034/DNC
Build-In Floor | Mini Canal | MICL.00921034/DON | 9 | 210 | 34 | 34 | 644 | 644 | 644 | 0.015333 | 251 | 0.0059762 | 734 | 0.017476 | 1.362 | A04 | MICL0.00921034/DON
Build-In Floor | Mini Canal | MICL.00921034/DOV | 9 | 210 | 34 | 34 | 644 | 644 | 644 | 0.015333 | 251 | 0.0059762 | 734 | 0.017476 | 1.362 | A04 | MICL0.00921034/DOV
Build-In Floor | Mini Canal | MICL.00921034/PNC | 9 | 210 | 34 | 34 | 588 | 588 | 588 | 0.014 | 229 | 0.0054524 | 670 | 0.015952 | 1.362 | A04 | MICL0.00921034/PNC
Build-In Floor | Mini Canal | MICL.00921034/RBL | 9 | 210 | 34 | 34 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.00921034/RBL
Build-In Floor | Mini Canal | MICL.00921034/RBN | 9 | 210 | 34 | 34 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00921034/RBN
Build-In Floor | Mini Canal | MICL.00921034/RBR | 9 | 210 | 34 | 34 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.00921034/RBR
Build-In Floor | Mini Canal | MICL.00921034/RBV | 9 | 210 | 34 | 34 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00921034/RBV
Build-In Floor | Mini Canal | MICL.00921034/RDB | 9 | 210 | 34 | 34 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.00921034/RDB
Build-In Floor | Mini Canal | MICL.00921034/RMN | 9 | 210 | 34 | 34 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00921034/RMN
Build-In Floor | Mini Canal | MICL.00921034/RMV | 9 | 210 | 34 | 34 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00921034/RMV
Build-In Floor | Mini Canal | MICL.00921034/RNA | 9 | 210 | 34 | 34 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.00921034/RNA
Build-In Floor | Mini Canal | MICL.00921034/RON | 9 | 210 | 34 | 34 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00921034/RON
Build-In Floor | Mini Canal | MICL.00921034/ROV | 9 | 210 | 34 | 34 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00921034/ROV
Build-In Floor | Mini Canal | MICL.00921034/RSS | 9 | 210 | 34 | 34 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.00921034/RSS
Build-In Floor | Mini Canal | MICL.00921034/SBL | 9 | 210 | 34 | 34 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.00921034/SBL
Build-In Floor | Mini Canal | MICL.00921034/SBR | 9 | 210 | 34 | 34 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.00921034/SBR
Build-In Floor | Mini Canal | MICL.00921034/SDB | 9 | 210 | 34 | 34 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.00921034/SDB
Build-In Floor | Mini Canal | MICL.00921034/SNA | 9 | 210 | 34 | 34 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.00921034/SNA
Build-In Floor | Mini Canal | MICL.00921034/SNC | 9 | 210 | 34 | 34 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.00921034/SNC
Build-In Floor | Mini Canal | MICL.00921042/ANA | 9 | 210 | 42 | 42 | 750 | 750 | 750 | 0.017857 | 292 | 0.0069524 | 854 | 0.020333 | 1.362 | A04 | MICL0.00921042/ANA
Build-In Floor | Mini Canal | MICL.00921042/DBL | 9 | 210 | 42 | 42 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00921042/DBL
Build-In Floor | Mini Canal | MICL.00921042/DBN | 9 | 210 | 42 | 42 | 930 | 930 | 930 | 0.022143 | 362 | 0.008619 | 1059 | 0.025214 | 1.362 | A04 | MICL0.00921042/DBN
Build-In Floor | Mini Canal | MICL.00921042/DBR | 9 | 210 | 42 | 42 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00921042/DBR
Build-In Floor | Mini Canal | MICL.00921042/DBV | 9 | 210 | 42 | 42 | 930 | 930 | 930 | 0.022143 | 362 | 0.008619 | 1059 | 0.025214 | 1.362 | A04 | MICL0.00921042/DBV
Build-In Floor | Mini Canal | MICL.00921042/DDB | 9 | 210 | 42 | 42 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00921042/DDB
Build-In Floor | Mini Canal | MICL.00921042/DMN | 9 | 210 | 42 | 42 | 930 | 930 | 930 | 0.022143 | 362 | 0.008619 | 1059 | 0.025214 | 1.362 | A04 | MICL0.00921042/DMN
Build-In Floor | Mini Canal | MICL.00921042/DMV | 9 | 210 | 42 | 42 | 930 | 930 | 930 | 0.022143 | 362 | 0.008619 | 1059 | 0.025214 | 1.362 | A04 | MICL0.00921042/DMV
Build-In Floor | Mini Canal | MICL.00921042/DNA | 9 | 210 | 42 | 42 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00921042/DNA
Build-In Floor | Mini Canal | MICL.00921042/DNC | 9 | 210 | 42 | 42 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00921042/DNC
Build-In Floor | Mini Canal | MICL.00921042/DON | 9 | 210 | 42 | 42 | 930 | 930 | 930 | 0.022143 | 362 | 0.008619 | 1059 | 0.025214 | 1.362 | A04 | MICL0.00921042/DON
Build-In Floor | Mini Canal | MICL.00921042/DOV | 9 | 210 | 42 | 42 | 930 | 930 | 930 | 0.022143 | 362 | 0.008619 | 1059 | 0.025214 | 1.362 | A04 | MICL0.00921042/DOV
Build-In Floor | Mini Canal | MICL.00921042/PNC | 9 | 210 | 42 | 42 | 850 | 850 | 850 | 0.020238 | 331 | 0.007881 | 968 | 0.023048 | 1.362 | A04 | MICL0.00921042/PNC
Build-In Floor | Mini Canal | MICL.00921042/RBL | 9 | 210 | 42 | 42 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00921042/RBL
Build-In Floor | Mini Canal | MICL.00921042/RBN | 9 | 210 | 42 | 42 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00921042/RBN
Build-In Floor | Mini Canal | MICL.00921042/RBR | 9 | 210 | 42 | 42 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00921042/RBR
Build-In Floor | Mini Canal | MICL.00921042/RBV | 9 | 210 | 42 | 42 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00921042/RBV
Build-In Floor | Mini Canal | MICL.00921042/RDB | 9 | 210 | 42 | 42 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00921042/RDB
Build-In Floor | Mini Canal | MICL.00921042/RMN | 9 | 210 | 42 | 42 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00921042/RMN
Build-In Floor | Mini Canal | MICL.00921042/RMV | 9 | 210 | 42 | 42 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00921042/RMV
Build-In Floor | Mini Canal | MICL.00921042/RNA | 9 | 210 | 42 | 42 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00921042/RNA
Build-In Floor | Mini Canal | MICL.00921042/RON | 9 | 210 | 42 | 42 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00921042/RON
Build-In Floor | Mini Canal | MICL.00921042/ROV | 9 | 210 | 42 | 42 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00921042/ROV
Build-In Floor | Mini Canal | MICL.00921042/RSS | 9 | 210 | 42 | 42 | 960 | 960 | 960 | 0.022857 | 373 | 0.008881 | 1093 | 0.026024 | 1.362 | A04 | MICL0.00921042/RSS
Build-In Floor | Mini Canal | MICL.00921042/SBL | 9 | 210 | 42 | 42 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00921042/SBL
Build-In Floor | Mini Canal | MICL.00921042/SBR | 9 | 210 | 42 | 42 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00921042/SBR
Build-In Floor | Mini Canal | MICL.00921042/SDB | 9 | 210 | 42 | 42 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00921042/SDB
Build-In Floor | Mini Canal | MICL.00921042/SNA | 9 | 210 | 42 | 42 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00921042/SNA
Build-In Floor | Mini Canal | MICL.00921042/SNC | 9 | 210 | 42 | 42 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00921042/SNC
Build-In Floor | Mini Canal | MICL.00923014/ANA | 9 | 230 | 14 | 14 | 286 | 286 | 286 | 0.0068095 | 111 | 0.0026429 | 326 | 0.0077619 | 1.362 | A04 | MICL0.00923014/ANA
Build-In Floor | Mini Canal | MICL.00923014/DBL | 9 | 230 | 14 | 14 | 370 | 370 | 370 | 0.0088095 | 144 | 0.0034286 | 421 | 0.010024 | 1.362 | A04 | MICL0.00923014/DBL
Build-In Floor | Mini Canal | MICL.00923014/DBN | 9 | 230 | 14 | 14 | 354 | 354 | 354 | 0.0084286 | 138 | 0.0032857 | 403 | 0.0095952 | 1.362 | A04 | MICL0.00923014/DBN
Build-In Floor | Mini Canal | MICL.00923014/DBR | 9 | 230 | 14 | 14 | 370 | 370 | 370 | 0.0088095 | 144 | 0.0034286 | 421 | 0.010024 | 1.362 | A04 | MICL0.00923014/DBR
Build-In Floor | Mini Canal | MICL.00923014/DBV | 9 | 230 | 14 | 14 | 354 | 354 | 354 | 0.0084286 | 138 | 0.0032857 | 403 | 0.0095952 | 1.362 | A04 | MICL0.00923014/DBV
Build-In Floor | Mini Canal | MICL.00923014/DDB | 9 | 230 | 14 | 14 | 370 | 370 | 370 | 0.0088095 | 144 | 0.0034286 | 421 | 0.010024 | 1.362 | A04 | MICL0.00923014/DDB
Build-In Floor | Mini Canal | MICL.00923014/DMN | 9 | 230 | 14 | 14 | 354 | 354 | 354 | 0.0084286 | 138 | 0.0032857 | 403 | 0.0095952 | 1.362 | A04 | MICL0.00923014/DMN
Build-In Floor | Mini Canal | MICL.00923014/DMV | 9 | 230 | 14 | 14 | 354 | 354 | 354 | 0.0084286 | 138 | 0.0032857 | 403 | 0.0095952 | 1.362 | A04 | MICL0.00923014/DMV
Build-In Floor | Mini Canal | MICL.00923014/DNA | 9 | 230 | 14 | 14 | 370 | 370 | 370 | 0.0088095 | 144 | 0.0034286 | 421 | 0.010024 | 1.362 | A04 | MICL0.00923014/DNA
Build-In Floor | Mini Canal | MICL.00923014/DNC | 9 | 230 | 14 | 14 | 370 | 370 | 370 | 0.0088095 | 144 | 0.0034286 | 421 | 0.010024 | 1.362 | A04 | MICL0.00923014/DNC
Build-In Floor | Mini Canal | MICL.00923014/DON | 9 | 230 | 14 | 14 | 354 | 354 | 354 | 0.0084286 | 138 | 0.0032857 | 403 | 0.0095952 | 1.362 | A04 | MICL0.00923014/DON
Build-In Floor | Mini Canal | MICL.00923014/DOV | 9 | 230 | 14 | 14 | 354 | 354 | 354 | 0.0084286 | 138 | 0.0032857 | 403 | 0.0095952 | 1.362 | A04 | MICL0.00923014/DOV
Build-In Floor | Mini Canal | MICL.00923014/RBL | 9 | 230 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.00923014/RBL
Build-In Floor | Mini Canal | MICL.00923014/RBN | 9 | 230 | 14 | 14 | 370 | 370 | 370 | 0.0088095 | 144 | 0.0034286 | 421 | 0.010024 | 1.362 | A04 | MICL0.00923014/RBN
Build-In Floor | Mini Canal | MICL.00923014/RBR | 9 | 230 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.00923014/RBR
Build-In Floor | Mini Canal | MICL.00923014/RBV | 9 | 230 | 14 | 14 | 370 | 370 | 370 | 0.0088095 | 144 | 0.0034286 | 421 | 0.010024 | 1.362 | A04 | MICL0.00923014/RBV
Build-In Floor | Mini Canal | MICL.00923014/RDB | 9 | 230 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.00923014/RDB
Build-In Floor | Mini Canal | MICL.00923014/RMN | 9 | 230 | 14 | 14 | 370 | 370 | 370 | 0.0088095 | 144 | 0.0034286 | 421 | 0.010024 | 1.362 | A04 | MICL0.00923014/RMN
Build-In Floor | Mini Canal | MICL.00923014/RMV | 9 | 230 | 14 | 14 | 370 | 370 | 370 | 0.0088095 | 144 | 0.0034286 | 421 | 0.010024 | 1.362 | A04 | MICL0.00923014/RMV
Build-In Floor | Mini Canal | MICL.00923014/RNA | 9 | 230 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.00923014/RNA
Build-In Floor | Mini Canal | MICL.00923014/RON | 9 | 230 | 14 | 14 | 370 | 370 | 370 | 0.0088095 | 144 | 0.0034286 | 421 | 0.010024 | 1.362 | A04 | MICL0.00923014/RON
Build-In Floor | Mini Canal | MICL.00923014/ROV | 9 | 230 | 14 | 14 | 370 | 370 | 370 | 0.0088095 | 144 | 0.0034286 | 421 | 0.010024 | 1.362 | A04 | MICL0.00923014/ROV
Build-In Floor | Mini Canal | MICL.00923014/RSS | 9 | 230 | 14 | 14 | 366 | 366 | 366 | 0.0087143 | 142 | 0.003381 | 417 | 0.0099286 | 1.362 | A04 | MICL0.00923014/RSS
Build-In Floor | Mini Canal | MICL.00923014/SBL | 9 | 230 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.00923014/SBL
Build-In Floor | Mini Canal | MICL.00923014/SBR | 9 | 230 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.00923014/SBR
Build-In Floor | Mini Canal | MICL.00923014/SDB | 9 | 230 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.00923014/SDB
Build-In Floor | Mini Canal | MICL.00923014/SNA | 9 | 230 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.00923014/SNA
Build-In Floor | Mini Canal | MICL.00923014/SNC | 9 | 230 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.00923014/SNC
Build-In Floor | Mini Canal | MICL.00923018/ANA | 9 | 230 | 18 | 18 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.00923018/ANA
Build-In Floor | Mini Canal | MICL.00923018/DBL | 9 | 230 | 18 | 18 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.00923018/DBL
Build-In Floor | Mini Canal | MICL.00923018/DBN | 9 | 230 | 18 | 18 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00923018/DBN
Build-In Floor | Mini Canal | MICL.00923018/DBR | 9 | 230 | 18 | 18 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.00923018/DBR
Build-In Floor | Mini Canal | MICL.00923018/DBV | 9 | 230 | 18 | 18 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00923018/DBV
Build-In Floor | Mini Canal | MICL.00923018/DDB | 9 | 230 | 18 | 18 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.00923018/DDB
Build-In Floor | Mini Canal | MICL.00923018/DMN | 9 | 230 | 18 | 18 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00923018/DMN
Build-In Floor | Mini Canal | MICL.00923018/DMV | 9 | 230 | 18 | 18 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00923018/DMV
Build-In Floor | Mini Canal | MICL.00923018/DNA | 9 | 230 | 18 | 18 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.00923018/DNA
Build-In Floor | Mini Canal | MICL.00923018/DNC | 9 | 230 | 18 | 18 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.00923018/DNC
Build-In Floor | Mini Canal | MICL.00923018/DON | 9 | 230 | 18 | 18 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00923018/DON
Build-In Floor | Mini Canal | MICL.00923018/DOV | 9 | 230 | 18 | 18 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00923018/DOV
Build-In Floor | Mini Canal | MICL.00923018/RBL | 9 | 230 | 18 | 18 | 451 | 451 | 451 | 0.010738 | 175 | 0.0041667 | 514 | 0.012238 | 1.362 | A04 | MICL0.00923018/RBL
Build-In Floor | Mini Canal | MICL.00923018/RBN | 9 | 230 | 18 | 18 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.00923018/RBN
Build-In Floor | Mini Canal | MICL.00923018/RBR | 9 | 230 | 18 | 18 | 451 | 451 | 451 | 0.010738 | 175 | 0.0041667 | 514 | 0.012238 | 1.362 | A04 | MICL0.00923018/RBR
Build-In Floor | Mini Canal | MICL.00923018/RBV | 9 | 230 | 18 | 18 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.00923018/RBV
Build-In Floor | Mini Canal | MICL.00923018/RDB | 9 | 230 | 18 | 18 | 451 | 451 | 451 | 0.010738 | 175 | 0.0041667 | 514 | 0.012238 | 1.362 | A04 | MICL0.00923018/RDB
Build-In Floor | Mini Canal | MICL.00923018/RMN | 9 | 230 | 18 | 18 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.00923018/RMN
Build-In Floor | Mini Canal | MICL.00923018/RMV | 9 | 230 | 18 | 18 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.00923018/RMV
Build-In Floor | Mini Canal | MICL.00923018/RNA | 9 | 230 | 18 | 18 | 451 | 451 | 451 | 0.010738 | 175 | 0.0041667 | 514 | 0.012238 | 1.362 | A04 | MICL0.00923018/RNA
Build-In Floor | Mini Canal | MICL.00923018/RON | 9 | 230 | 18 | 18 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.00923018/RON
Build-In Floor | Mini Canal | MICL.00923018/ROV | 9 | 230 | 18 | 18 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.00923018/ROV
Build-In Floor | Mini Canal | MICL.00923018/RSS | 9 | 230 | 18 | 18 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.00923018/RSS
Build-In Floor | Mini Canal | MICL.00923018/SBL | 9 | 230 | 18 | 18 | 451 | 451 | 451 | 0.010738 | 175 | 0.0041667 | 514 | 0.012238 | 1.362 | A04 | MICL0.00923018/SBL
Build-In Floor | Mini Canal | MICL.00923018/SBR | 9 | 230 | 18 | 18 | 451 | 451 | 451 | 0.010738 | 175 | 0.0041667 | 514 | 0.012238 | 1.362 | A04 | MICL0.00923018/SBR
Build-In Floor | Mini Canal | MICL.00923018/SDB | 9 | 230 | 18 | 18 | 451 | 451 | 451 | 0.010738 | 175 | 0.0041667 | 514 | 0.012238 | 1.362 | A04 | MICL0.00923018/SDB
Build-In Floor | Mini Canal | MICL.00923018/SNA | 9 | 230 | 18 | 18 | 451 | 451 | 451 | 0.010738 | 175 | 0.0041667 | 514 | 0.012238 | 1.362 | A04 | MICL0.00923018/SNA
Build-In Floor | Mini Canal | MICL.00923018/SNC | 9 | 230 | 18 | 18 | 451 | 451 | 451 | 0.010738 | 175 | 0.0041667 | 514 | 0.012238 | 1.362 | A04 | MICL0.00923018/SNC
Build-In Floor | Mini Canal | MICL.00923026/ANA | 9 | 230 | 26 | 26 | 445 | 445 | 445 | 0.010595 | 173 | 0.004119 | 507 | 0.012071 | 1.362 | A04 | MICL0.00923026/ANA
Build-In Floor | Mini Canal | MICL.00923026/DBL | 9 | 230 | 26 | 26 | 575 | 575 | 575 | 0.01369 | 224 | 0.0053333 | 655 | 0.015595 | 1.362 | A04 | MICL0.00923026/DBL
Build-In Floor | Mini Canal | MICL.00923026/DBN | 9 | 230 | 26 | 26 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.00923026/DBN
Build-In Floor | Mini Canal | MICL.00923026/DBR | 9 | 230 | 26 | 26 | 575 | 575 | 575 | 0.01369 | 224 | 0.0053333 | 655 | 0.015595 | 1.362 | A04 | MICL0.00923026/DBR
Build-In Floor | Mini Canal | MICL.00923026/DBV | 9 | 230 | 26 | 26 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.00923026/DBV
Build-In Floor | Mini Canal | MICL.00923026/DDB | 9 | 230 | 26 | 26 | 575 | 575 | 575 | 0.01369 | 224 | 0.0053333 | 655 | 0.015595 | 1.362 | A04 | MICL0.00923026/DDB
Build-In Floor | Mini Canal | MICL.00923026/DMN | 9 | 230 | 26 | 26 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.00923026/DMN
Build-In Floor | Mini Canal | MICL.00923026/DMV | 9 | 230 | 26 | 26 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.00923026/DMV
Build-In Floor | Mini Canal | MICL.00923026/DNA | 9 | 230 | 26 | 26 | 575 | 575 | 575 | 0.01369 | 224 | 0.0053333 | 655 | 0.015595 | 1.362 | A04 | MICL0.00923026/DNA
Build-In Floor | Mini Canal | MICL.00923026/DNC | 9 | 230 | 26 | 26 | 575 | 575 | 575 | 0.01369 | 224 | 0.0053333 | 655 | 0.015595 | 1.362 | A04 | MICL0.00923026/DNC
Build-In Floor | Mini Canal | MICL.00923026/DON | 9 | 230 | 26 | 26 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.00923026/DON
Build-In Floor | Mini Canal | MICL.00923026/DOV | 9 | 230 | 26 | 26 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.00923026/DOV
Build-In Floor | Mini Canal | MICL.00923026/PNC | 9 | 230 | 26 | 26 | 504 | 504 | 504 | 0.012 | 196 | 0.0046667 | 574 | 0.013667 | 1.362 | A04 | MICL0.00923026/PNC
Build-In Floor | Mini Canal | MICL.00923026/RBL | 9 | 230 | 26 | 26 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.00923026/RBL
Build-In Floor | Mini Canal | MICL.00923026/RBN | 9 | 230 | 26 | 26 | 575 | 575 | 575 | 0.01369 | 224 | 0.0053333 | 655 | 0.015595 | 1.362 | A04 | MICL0.00923026/RBN
Build-In Floor | Mini Canal | MICL.00923026/RBR | 9 | 230 | 26 | 26 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.00923026/RBR
Build-In Floor | Mini Canal | MICL.00923026/RBV | 9 | 230 | 26 | 26 | 575 | 575 | 575 | 0.01369 | 224 | 0.0053333 | 655 | 0.015595 | 1.362 | A04 | MICL0.00923026/RBV
Build-In Floor | Mini Canal | MICL.00923026/RDB | 9 | 230 | 26 | 26 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.00923026/RDB
Build-In Floor | Mini Canal | MICL.00923026/RMN | 9 | 230 | 26 | 26 | 575 | 575 | 575 | 0.01369 | 224 | 0.0053333 | 655 | 0.015595 | 1.362 | A04 | MICL0.00923026/RMN
Build-In Floor | Mini Canal | MICL.00923026/RMV | 9 | 230 | 26 | 26 | 575 | 575 | 575 | 0.01369 | 224 | 0.0053333 | 655 | 0.015595 | 1.362 | A04 | MICL0.00923026/RMV
Build-In Floor | Mini Canal | MICL.00923026/RNA | 9 | 230 | 26 | 26 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.00923026/RNA
Build-In Floor | Mini Canal | MICL.00923026/RON | 9 | 230 | 26 | 26 | 575 | 575 | 575 | 0.01369 | 224 | 0.0053333 | 655 | 0.015595 | 1.362 | A04 | MICL0.00923026/RON
Build-In Floor | Mini Canal | MICL.00923026/ROV | 9 | 230 | 26 | 26 | 575 | 575 | 575 | 0.01369 | 224 | 0.0053333 | 655 | 0.015595 | 1.362 | A04 | MICL0.00923026/ROV
Build-In Floor | Mini Canal | MICL.00923026/RSS | 9 | 230 | 26 | 26 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.00923026/RSS
Build-In Floor | Mini Canal | MICL.00923026/SBL | 9 | 230 | 26 | 26 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.00923026/SBL
Build-In Floor | Mini Canal | MICL.00923026/SBR | 9 | 230 | 26 | 26 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.00923026/SBR
Build-In Floor | Mini Canal | MICL.00923026/SDB | 9 | 230 | 26 | 26 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.00923026/SDB
Build-In Floor | Mini Canal | MICL.00923026/SNA | 9 | 230 | 26 | 26 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.00923026/SNA
Build-In Floor | Mini Canal | MICL.00923026/SNC | 9 | 230 | 26 | 26 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.00923026/SNC
Build-In Floor | Mini Canal | MICL.00923034/ANA | 9 | 230 | 34 | 34 | 577 | 577 | 577 | 0.013738 | 224 | 0.0053333 | 657 | 0.015643 | 1.362 | A04 | MICL0.00923034/ANA
Build-In Floor | Mini Canal | MICL.00923034/DBL | 9 | 230 | 34 | 34 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.00923034/DBL
Build-In Floor | Mini Canal | MICL.00923034/DBN | 9 | 230 | 34 | 34 | 715 | 715 | 715 | 0.017024 | 278 | 0.006619 | 814 | 0.019381 | 1.362 | A04 | MICL0.00923034/DBN
Build-In Floor | Mini Canal | MICL.00923034/DBR | 9 | 230 | 34 | 34 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.00923034/DBR
Build-In Floor | Mini Canal | MICL.00923034/DBV | 9 | 230 | 34 | 34 | 715 | 715 | 715 | 0.017024 | 278 | 0.006619 | 814 | 0.019381 | 1.362 | A04 | MICL0.00923034/DBV
Build-In Floor | Mini Canal | MICL.00923034/DDB | 9 | 230 | 34 | 34 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.00923034/DDB
Build-In Floor | Mini Canal | MICL.00923034/DMN | 9 | 230 | 34 | 34 | 715 | 715 | 715 | 0.017024 | 278 | 0.006619 | 814 | 0.019381 | 1.362 | A04 | MICL0.00923034/DMN
Build-In Floor | Mini Canal | MICL.00923034/DMV | 9 | 230 | 34 | 34 | 715 | 715 | 715 | 0.017024 | 278 | 0.006619 | 814 | 0.019381 | 1.362 | A04 | MICL0.00923034/DMV
Build-In Floor | Mini Canal | MICL.00923034/DNA | 9 | 230 | 34 | 34 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.00923034/DNA
Build-In Floor | Mini Canal | MICL.00923034/DNC | 9 | 230 | 34 | 34 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.00923034/DNC
Build-In Floor | Mini Canal | MICL.00923034/DON | 9 | 230 | 34 | 34 | 715 | 715 | 715 | 0.017024 | 278 | 0.006619 | 814 | 0.019381 | 1.362 | A04 | MICL0.00923034/DON
Build-In Floor | Mini Canal | MICL.00923034/DOV | 9 | 230 | 34 | 34 | 715 | 715 | 715 | 0.017024 | 278 | 0.006619 | 814 | 0.019381 | 1.362 | A04 | MICL0.00923034/DOV
Build-In Floor | Mini Canal | MICL.00923034/PNC | 9 | 230 | 34 | 34 | 654 | 654 | 654 | 0.015571 | 254 | 0.0060476 | 745 | 0.017738 | 1.362 | A04 | MICL0.00923034/PNC
Build-In Floor | Mini Canal | MICL.00923034/RBL | 9 | 230 | 34 | 34 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.00923034/RBL
Build-In Floor | Mini Canal | MICL.00923034/RBN | 9 | 230 | 34 | 34 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.00923034/RBN
Build-In Floor | Mini Canal | MICL.00923034/RBR | 9 | 230 | 34 | 34 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.00923034/RBR
Build-In Floor | Mini Canal | MICL.00923034/RBV | 9 | 230 | 34 | 34 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.00923034/RBV
Build-In Floor | Mini Canal | MICL.00923034/RDB | 9 | 230 | 34 | 34 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.00923034/RDB
Build-In Floor | Mini Canal | MICL.00923034/RMN | 9 | 230 | 34 | 34 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.00923034/RMN
Build-In Floor | Mini Canal | MICL.00923034/RMV | 9 | 230 | 34 | 34 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.00923034/RMV
Build-In Floor | Mini Canal | MICL.00923034/RNA | 9 | 230 | 34 | 34 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.00923034/RNA
Build-In Floor | Mini Canal | MICL.00923034/RON | 9 | 230 | 34 | 34 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.00923034/RON
Build-In Floor | Mini Canal | MICL.00923034/ROV | 9 | 230 | 34 | 34 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.00923034/ROV
Build-In Floor | Mini Canal | MICL.00923034/RSS | 9 | 230 | 34 | 34 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.00923034/RSS
Build-In Floor | Mini Canal | MICL.00923034/SBL | 9 | 230 | 34 | 34 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.00923034/SBL
Build-In Floor | Mini Canal | MICL.00923034/SBR | 9 | 230 | 34 | 34 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.00923034/SBR
Build-In Floor | Mini Canal | MICL.00923034/SDB | 9 | 230 | 34 | 34 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.00923034/SDB
Build-In Floor | Mini Canal | MICL.00923034/SNA | 9 | 230 | 34 | 34 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.00923034/SNA
Build-In Floor | Mini Canal | MICL.00923034/SNC | 9 | 230 | 34 | 34 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.00923034/SNC
Build-In Floor | Mini Canal | MICL.00923042/ANA | 9 | 230 | 42 | 42 | 833 | 833 | 833 | 0.019833 | 324 | 0.0077143 | 949 | 0.022595 | 1.362 | A04 | MICL0.00923042/ANA
Build-In Floor | Mini Canal | MICL.00923042/DBL | 9 | 230 | 42 | 42 | 1078 | 1078 | 1078 | 0.025667 | 419 | 0.0099762 | 1228 | 0.029238 | 1.362 | A04 | MICL0.00923042/DBL
Build-In Floor | Mini Canal | MICL.00923042/DBN | 9 | 230 | 42 | 42 | 1033 | 1033 | 1033 | 0.024595 | 402 | 0.0095714 | 1177 | 0.028024 | 1.362 | A04 | MICL0.00923042/DBN
Build-In Floor | Mini Canal | MICL.00923042/DBR | 9 | 230 | 42 | 42 | 1078 | 1078 | 1078 | 0.025667 | 419 | 0.0099762 | 1228 | 0.029238 | 1.362 | A04 | MICL0.00923042/DBR
Build-In Floor | Mini Canal | MICL.00923042/DBV | 9 | 230 | 42 | 42 | 1033 | 1033 | 1033 | 0.024595 | 402 | 0.0095714 | 1177 | 0.028024 | 1.362 | A04 | MICL0.00923042/DBV
Build-In Floor | Mini Canal | MICL.00923042/DDB | 9 | 230 | 42 | 42 | 1078 | 1078 | 1078 | 0.025667 | 419 | 0.0099762 | 1228 | 0.029238 | 1.362 | A04 | MICL0.00923042/DDB
Build-In Floor | Mini Canal | MICL.00923042/DMN | 9 | 230 | 42 | 42 | 1033 | 1033 | 1033 | 0.024595 | 402 | 0.0095714 | 1177 | 0.028024 | 1.362 | A04 | MICL0.00923042/DMN
Build-In Floor | Mini Canal | MICL.00923042/DMV | 9 | 230 | 42 | 42 | 1033 | 1033 | 1033 | 0.024595 | 402 | 0.0095714 | 1177 | 0.028024 | 1.362 | A04 | MICL0.00923042/DMV
Build-In Floor | Mini Canal | MICL.00923042/DNA | 9 | 230 | 42 | 42 | 1078 | 1078 | 1078 | 0.025667 | 419 | 0.0099762 | 1228 | 0.029238 | 1.362 | A04 | MICL0.00923042/DNA
Build-In Floor | Mini Canal | MICL.00923042/DNC | 9 | 230 | 42 | 42 | 1078 | 1078 | 1078 | 0.025667 | 419 | 0.0099762 | 1228 | 0.029238 | 1.362 | A04 | MICL0.00923042/DNC
Build-In Floor | Mini Canal | MICL.00923042/DON | 9 | 230 | 42 | 42 | 1033 | 1033 | 1033 | 0.024595 | 402 | 0.0095714 | 1177 | 0.028024 | 1.362 | A04 | MICL0.00923042/DON
Build-In Floor | Mini Canal | MICL.00923042/DOV | 9 | 230 | 42 | 42 | 1033 | 1033 | 1033 | 0.024595 | 402 | 0.0095714 | 1177 | 0.028024 | 1.362 | A04 | MICL0.00923042/DOV
Build-In Floor | Mini Canal | MICL.00923042/PNC | 9 | 230 | 42 | 42 | 944 | 944 | 944 | 0.022476 | 367 | 0.0087381 | 1075 | 0.025595 | 1.362 | A04 | MICL0.00923042/PNC
Build-In Floor | Mini Canal | MICL.00923042/RBL | 9 | 230 | 42 | 42 | 1111 | 1111 | 1111 | 0.026452 | 432 | 0.010286 | 1265 | 0.030119 | 1.362 | A04 | MICL0.00923042/RBL
Build-In Floor | Mini Canal | MICL.00923042/RBN | 9 | 230 | 42 | 42 | 1078 | 1078 | 1078 | 0.025667 | 419 | 0.0099762 | 1228 | 0.029238 | 1.362 | A04 | MICL0.00923042/RBN
Build-In Floor | Mini Canal | MICL.00923042/RBR | 9 | 230 | 42 | 42 | 1111 | 1111 | 1111 | 0.026452 | 432 | 0.010286 | 1265 | 0.030119 | 1.362 | A04 | MICL0.00923042/RBR
Build-In Floor | Mini Canal | MICL.00923042/RBV | 9 | 230 | 42 | 42 | 1078 | 1078 | 1078 | 0.025667 | 419 | 0.0099762 | 1228 | 0.029238 | 1.362 | A04 | MICL0.00923042/RBV
Build-In Floor | Mini Canal | MICL.00923042/RDB | 9 | 230 | 42 | 42 | 1111 | 1111 | 1111 | 0.026452 | 432 | 0.010286 | 1265 | 0.030119 | 1.362 | A04 | MICL0.00923042/RDB
Build-In Floor | Mini Canal | MICL.00923042/RMN | 9 | 230 | 42 | 42 | 1078 | 1078 | 1078 | 0.025667 | 419 | 0.0099762 | 1228 | 0.029238 | 1.362 | A04 | MICL0.00923042/RMN
Build-In Floor | Mini Canal | MICL.00923042/RMV | 9 | 230 | 42 | 42 | 1078 | 1078 | 1078 | 0.025667 | 419 | 0.0099762 | 1228 | 0.029238 | 1.362 | A04 | MICL0.00923042/RMV
Build-In Floor | Mini Canal | MICL.00923042/RNA | 9 | 230 | 42 | 42 | 1111 | 1111 | 1111 | 0.026452 | 432 | 0.010286 | 1265 | 0.030119 | 1.362 | A04 | MICL0.00923042/RNA
Build-In Floor | Mini Canal | MICL.00923042/RON | 9 | 230 | 42 | 42 | 1078 | 1078 | 1078 | 0.025667 | 419 | 0.0099762 | 1228 | 0.029238 | 1.362 | A04 | MICL0.00923042/RON
Build-In Floor | Mini Canal | MICL.00923042/ROV | 9 | 230 | 42 | 42 | 1078 | 1078 | 1078 | 0.025667 | 419 | 0.0099762 | 1228 | 0.029238 | 1.362 | A04 | MICL0.00923042/ROV
Build-In Floor | Mini Canal | MICL.00923042/RSS | 9 | 230 | 42 | 42 | 1067 | 1067 | 1067 | 0.025405 | 415 | 0.009881 | 1215 | 0.028929 | 1.362 | A04 | MICL0.00923042/RSS
Build-In Floor | Mini Canal | MICL.00923042/SBL | 9 | 230 | 42 | 42 | 1111 | 1111 | 1111 | 0.026452 | 432 | 0.010286 | 1265 | 0.030119 | 1.362 | A04 | MICL0.00923042/SBL
Build-In Floor | Mini Canal | MICL.00923042/SBR | 9 | 230 | 42 | 42 | 1111 | 1111 | 1111 | 0.026452 | 432 | 0.010286 | 1265 | 0.030119 | 1.362 | A04 | MICL0.00923042/SBR
Build-In Floor | Mini Canal | MICL.00923042/SDB | 9 | 230 | 42 | 42 | 1111 | 1111 | 1111 | 0.026452 | 432 | 0.010286 | 1265 | 0.030119 | 1.362 | A04 | MICL0.00923042/SDB
Build-In Floor | Mini Canal | MICL.00923042/SNA | 9 | 230 | 42 | 42 | 1111 | 1111 | 1111 | 0.026452 | 432 | 0.010286 | 1265 | 0.030119 | 1.362 | A04 | MICL0.00923042/SNA
Build-In Floor | Mini Canal | MICL.00923042/SNC | 9 | 230 | 42 | 42 | 1111 | 1111 | 1111 | 0.026452 | 432 | 0.010286 | 1265 | 0.030119 | 1.362 | A04 | MICL0.00923042/SNC
Build-In Floor | Mini Canal | MICL.00925014/ANA | 9 | 250 | 14 | 14 | 314 | 314 | 314 | 0.0074762 | 122 | 0.0029048 | 358 | 0.0085238 | 1.362 | A04 | MICL0.00925014/ANA
Build-In Floor | Mini Canal | MICL.00925014/DBL | 9 | 250 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00925014/DBL
Build-In Floor | Mini Canal | MICL.00925014/DBN | 9 | 250 | 14 | 14 | 390 | 390 | 390 | 0.0092857 | 152 | 0.003619 | 444 | 0.010571 | 1.362 | A04 | MICL0.00925014/DBN
Build-In Floor | Mini Canal | MICL.00925014/DBR | 9 | 250 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00925014/DBR
Build-In Floor | Mini Canal | MICL.00925014/DBV | 9 | 250 | 14 | 14 | 390 | 390 | 390 | 0.0092857 | 152 | 0.003619 | 444 | 0.010571 | 1.362 | A04 | MICL0.00925014/DBV
Build-In Floor | Mini Canal | MICL.00925014/DDB | 9 | 250 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00925014/DDB
Build-In Floor | Mini Canal | MICL.00925014/DMN | 9 | 250 | 14 | 14 | 390 | 390 | 390 | 0.0092857 | 152 | 0.003619 | 444 | 0.010571 | 1.362 | A04 | MICL0.00925014/DMN
Build-In Floor | Mini Canal | MICL.00925014/DMV | 9 | 250 | 14 | 14 | 390 | 390 | 390 | 0.0092857 | 152 | 0.003619 | 444 | 0.010571 | 1.362 | A04 | MICL0.00925014/DMV
Build-In Floor | Mini Canal | MICL.00925014/DNA | 9 | 250 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00925014/DNA
Build-In Floor | Mini Canal | MICL.00925014/DNC | 9 | 250 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00925014/DNC
Build-In Floor | Mini Canal | MICL.00925014/DON | 9 | 250 | 14 | 14 | 390 | 390 | 390 | 0.0092857 | 152 | 0.003619 | 444 | 0.010571 | 1.362 | A04 | MICL0.00925014/DON
Build-In Floor | Mini Canal | MICL.00925014/DOV | 9 | 250 | 14 | 14 | 390 | 390 | 390 | 0.0092857 | 152 | 0.003619 | 444 | 0.010571 | 1.362 | A04 | MICL0.00925014/DOV
Build-In Floor | Mini Canal | MICL.00925014/RBL | 9 | 250 | 14 | 14 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00925014/RBL
Build-In Floor | Mini Canal | MICL.00925014/RBN | 9 | 250 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00925014/RBN
Build-In Floor | Mini Canal | MICL.00925014/RBR | 9 | 250 | 14 | 14 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00925014/RBR
Build-In Floor | Mini Canal | MICL.00925014/RBV | 9 | 250 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00925014/RBV
Build-In Floor | Mini Canal | MICL.00925014/RDB | 9 | 250 | 14 | 14 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00925014/RDB
Build-In Floor | Mini Canal | MICL.00925014/RMN | 9 | 250 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00925014/RMN
Build-In Floor | Mini Canal | MICL.00925014/RMV | 9 | 250 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00925014/RMV
Build-In Floor | Mini Canal | MICL.00925014/RNA | 9 | 250 | 14 | 14 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00925014/RNA
Build-In Floor | Mini Canal | MICL.00925014/RON | 9 | 250 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00925014/RON
Build-In Floor | Mini Canal | MICL.00925014/ROV | 9 | 250 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00925014/ROV
Build-In Floor | Mini Canal | MICL.00925014/RSS | 9 | 250 | 14 | 14 | 402 | 402 | 402 | 0.0095714 | 156 | 0.0037143 | 458 | 0.010905 | 1.362 | A04 | MICL0.00925014/RSS
Build-In Floor | Mini Canal | MICL.00925014/SBL | 9 | 250 | 14 | 14 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00925014/SBL
Build-In Floor | Mini Canal | MICL.00925014/SBR | 9 | 250 | 14 | 14 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00925014/SBR
Build-In Floor | Mini Canal | MICL.00925014/SDB | 9 | 250 | 14 | 14 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00925014/SDB
Build-In Floor | Mini Canal | MICL.00925014/SNA | 9 | 250 | 14 | 14 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00925014/SNA
Build-In Floor | Mini Canal | MICL.00925014/SNC | 9 | 250 | 14 | 14 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.00925014/SNC
Build-In Floor | Mini Canal | MICL.00925018/ANA | 9 | 250 | 18 | 18 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.00925018/ANA
Build-In Floor | Mini Canal | MICL.00925018/DBL | 9 | 250 | 18 | 18 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.00925018/DBL
Build-In Floor | Mini Canal | MICL.00925018/DBN | 9 | 250 | 18 | 18 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.00925018/DBN
Build-In Floor | Mini Canal | MICL.00925018/DBR | 9 | 250 | 18 | 18 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.00925018/DBR
Build-In Floor | Mini Canal | MICL.00925018/DBV | 9 | 250 | 18 | 18 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.00925018/DBV
Build-In Floor | Mini Canal | MICL.00925018/DDB | 9 | 250 | 18 | 18 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.00925018/DDB
Build-In Floor | Mini Canal | MICL.00925018/DMN | 9 | 250 | 18 | 18 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.00925018/DMN
Build-In Floor | Mini Canal | MICL.00925018/DMV | 9 | 250 | 18 | 18 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.00925018/DMV
Build-In Floor | Mini Canal | MICL.00925018/DNA | 9 | 250 | 18 | 18 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.00925018/DNA
Build-In Floor | Mini Canal | MICL.00925018/DNC | 9 | 250 | 18 | 18 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.00925018/DNC
Build-In Floor | Mini Canal | MICL.00925018/DON | 9 | 250 | 18 | 18 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.00925018/DON
Build-In Floor | Mini Canal | MICL.00925018/DOV | 9 | 250 | 18 | 18 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.00925018/DOV
Build-In Floor | Mini Canal | MICL.00925018/RBL | 9 | 250 | 18 | 18 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00925018/RBL
Build-In Floor | Mini Canal | MICL.00925018/RBN | 9 | 250 | 18 | 18 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.00925018/RBN
Build-In Floor | Mini Canal | MICL.00925018/RBR | 9 | 250 | 18 | 18 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00925018/RBR
Build-In Floor | Mini Canal | MICL.00925018/RBV | 9 | 250 | 18 | 18 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.00925018/RBV
Build-In Floor | Mini Canal | MICL.00925018/RDB | 9 | 250 | 18 | 18 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00925018/RDB
Build-In Floor | Mini Canal | MICL.00925018/RMN | 9 | 250 | 18 | 18 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.00925018/RMN
Build-In Floor | Mini Canal | MICL.00925018/RMV | 9 | 250 | 18 | 18 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.00925018/RMV
Build-In Floor | Mini Canal | MICL.00925018/RNA | 9 | 250 | 18 | 18 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00925018/RNA
Build-In Floor | Mini Canal | MICL.00925018/RON | 9 | 250 | 18 | 18 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.00925018/RON
Build-In Floor | Mini Canal | MICL.00925018/ROV | 9 | 250 | 18 | 18 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.00925018/ROV
Build-In Floor | Mini Canal | MICL.00925018/RSS | 9 | 250 | 18 | 18 | 476 | 476 | 476 | 0.011333 | 185 | 0.0044048 | 542 | 0.012905 | 1.362 | A04 | MICL0.00925018/RSS
Build-In Floor | Mini Canal | MICL.00925018/SBL | 9 | 250 | 18 | 18 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00925018/SBL
Build-In Floor | Mini Canal | MICL.00925018/SBR | 9 | 250 | 18 | 18 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00925018/SBR
Build-In Floor | Mini Canal | MICL.00925018/SDB | 9 | 250 | 18 | 18 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00925018/SDB
Build-In Floor | Mini Canal | MICL.00925018/SNA | 9 | 250 | 18 | 18 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00925018/SNA
Build-In Floor | Mini Canal | MICL.00925018/SNC | 9 | 250 | 18 | 18 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00925018/SNC
Build-In Floor | Mini Canal | MICL.00925026/ANA | 9 | 250 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.00925026/ANA
Build-In Floor | Mini Canal | MICL.00925026/DBL | 9 | 250 | 26 | 26 | 632 | 632 | 632 | 0.015048 | 246 | 0.0058571 | 720 | 0.017143 | 1.362 | A04 | MICL0.00925026/DBL
Build-In Floor | Mini Canal | MICL.00925026/DBN | 9 | 250 | 26 | 26 | 606 | 606 | 606 | 0.014429 | 236 | 0.005619 | 690 | 0.016429 | 1.362 | A04 | MICL0.00925026/DBN
Build-In Floor | Mini Canal | MICL.00925026/DBR | 9 | 250 | 26 | 26 | 632 | 632 | 632 | 0.015048 | 246 | 0.0058571 | 720 | 0.017143 | 1.362 | A04 | MICL0.00925026/DBR
Build-In Floor | Mini Canal | MICL.00925026/DBV | 9 | 250 | 26 | 26 | 606 | 606 | 606 | 0.014429 | 236 | 0.005619 | 690 | 0.016429 | 1.362 | A04 | MICL0.00925026/DBV
Build-In Floor | Mini Canal | MICL.00925026/DDB | 9 | 250 | 26 | 26 | 632 | 632 | 632 | 0.015048 | 246 | 0.0058571 | 720 | 0.017143 | 1.362 | A04 | MICL0.00925026/DDB
Build-In Floor | Mini Canal | MICL.00925026/DMN | 9 | 250 | 26 | 26 | 606 | 606 | 606 | 0.014429 | 236 | 0.005619 | 690 | 0.016429 | 1.362 | A04 | MICL0.00925026/DMN
Build-In Floor | Mini Canal | MICL.00925026/DMV | 9 | 250 | 26 | 26 | 606 | 606 | 606 | 0.014429 | 236 | 0.005619 | 690 | 0.016429 | 1.362 | A04 | MICL0.00925026/DMV
Build-In Floor | Mini Canal | MICL.00925026/DNA | 9 | 250 | 26 | 26 | 632 | 632 | 632 | 0.015048 | 246 | 0.0058571 | 720 | 0.017143 | 1.362 | A04 | MICL0.00925026/DNA
Build-In Floor | Mini Canal | MICL.00925026/DNC | 9 | 250 | 26 | 26 | 632 | 632 | 632 | 0.015048 | 246 | 0.0058571 | 720 | 0.017143 | 1.362 | A04 | MICL0.00925026/DNC
Build-In Floor | Mini Canal | MICL.00925026/DON | 9 | 250 | 26 | 26 | 606 | 606 | 606 | 0.014429 | 236 | 0.005619 | 690 | 0.016429 | 1.362 | A04 | MICL0.00925026/DON
Build-In Floor | Mini Canal | MICL.00925026/DOV | 9 | 250 | 26 | 26 | 606 | 606 | 606 | 0.014429 | 236 | 0.005619 | 690 | 0.016429 | 1.362 | A04 | MICL0.00925026/DOV
Build-In Floor | Mini Canal | MICL.00925026/PNC | 9 | 250 | 26 | 26 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.00925026/PNC
Build-In Floor | Mini Canal | MICL.00925026/RBL | 9 | 250 | 26 | 26 | 652 | 652 | 652 | 0.015524 | 254 | 0.0060476 | 743 | 0.01769 | 1.362 | A04 | MICL0.00925026/RBL
Build-In Floor | Mini Canal | MICL.00925026/RBN | 9 | 250 | 26 | 26 | 632 | 632 | 632 | 0.015048 | 246 | 0.0058571 | 720 | 0.017143 | 1.362 | A04 | MICL0.00925026/RBN
Build-In Floor | Mini Canal | MICL.00925026/RBR | 9 | 250 | 26 | 26 | 652 | 652 | 652 | 0.015524 | 254 | 0.0060476 | 743 | 0.01769 | 1.362 | A04 | MICL0.00925026/RBR
Build-In Floor | Mini Canal | MICL.00925026/RBV | 9 | 250 | 26 | 26 | 632 | 632 | 632 | 0.015048 | 246 | 0.0058571 | 720 | 0.017143 | 1.362 | A04 | MICL0.00925026/RBV
Build-In Floor | Mini Canal | MICL.00925026/RDB | 9 | 250 | 26 | 26 | 652 | 652 | 652 | 0.015524 | 254 | 0.0060476 | 743 | 0.01769 | 1.362 | A04 | MICL0.00925026/RDB
Build-In Floor | Mini Canal | MICL.00925026/RMN | 9 | 250 | 26 | 26 | 632 | 632 | 632 | 0.015048 | 246 | 0.0058571 | 720 | 0.017143 | 1.362 | A04 | MICL0.00925026/RMN
Build-In Floor | Mini Canal | MICL.00925026/RMV | 9 | 250 | 26 | 26 | 632 | 632 | 632 | 0.015048 | 246 | 0.0058571 | 720 | 0.017143 | 1.362 | A04 | MICL0.00925026/RMV
Build-In Floor | Mini Canal | MICL.00925026/RNA | 9 | 250 | 26 | 26 | 652 | 652 | 652 | 0.015524 | 254 | 0.0060476 | 743 | 0.01769 | 1.362 | A04 | MICL0.00925026/RNA
Build-In Floor | Mini Canal | MICL.00925026/RON | 9 | 250 | 26 | 26 | 632 | 632 | 632 | 0.015048 | 246 | 0.0058571 | 720 | 0.017143 | 1.362 | A04 | MICL0.00925026/RON
Build-In Floor | Mini Canal | MICL.00925026/ROV | 9 | 250 | 26 | 26 | 632 | 632 | 632 | 0.015048 | 246 | 0.0058571 | 720 | 0.017143 | 1.362 | A04 | MICL0.00925026/ROV
Build-In Floor | Mini Canal | MICL.00925026/RSS | 9 | 250 | 26 | 26 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.00925026/RSS
Build-In Floor | Mini Canal | MICL.00925026/SBL | 9 | 250 | 26 | 26 | 652 | 652 | 652 | 0.015524 | 254 | 0.0060476 | 743 | 0.01769 | 1.362 | A04 | MICL0.00925026/SBL
Build-In Floor | Mini Canal | MICL.00925026/SBR | 9 | 250 | 26 | 26 | 652 | 652 | 652 | 0.015524 | 254 | 0.0060476 | 743 | 0.01769 | 1.362 | A04 | MICL0.00925026/SBR
Build-In Floor | Mini Canal | MICL.00925026/SDB | 9 | 250 | 26 | 26 | 652 | 652 | 652 | 0.015524 | 254 | 0.0060476 | 743 | 0.01769 | 1.362 | A04 | MICL0.00925026/SDB
Build-In Floor | Mini Canal | MICL.00925026/SNA | 9 | 250 | 26 | 26 | 652 | 652 | 652 | 0.015524 | 254 | 0.0060476 | 743 | 0.01769 | 1.362 | A04 | MICL0.00925026/SNA
Build-In Floor | Mini Canal | MICL.00925026/SNC | 9 | 250 | 26 | 26 | 652 | 652 | 652 | 0.015524 | 254 | 0.0060476 | 743 | 0.01769 | 1.362 | A04 | MICL0.00925026/SNC
Build-In Floor | Mini Canal | MICL.00925034/ANA | 9 | 250 | 34 | 34 | 635 | 635 | 635 | 0.015119 | 247 | 0.005881 | 723 | 0.017214 | 1.362 | A04 | MICL0.00925034/ANA
Build-In Floor | Mini Canal | MICL.00925034/DBL | 9 | 250 | 34 | 34 | 821 | 821 | 821 | 0.019548 | 319 | 0.0075952 | 935 | 0.022262 | 1.362 | A04 | MICL0.00925034/DBL
Build-In Floor | Mini Canal | MICL.00925034/DBN | 9 | 250 | 34 | 34 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00925034/DBN
Build-In Floor | Mini Canal | MICL.00925034/DBR | 9 | 250 | 34 | 34 | 821 | 821 | 821 | 0.019548 | 319 | 0.0075952 | 935 | 0.022262 | 1.362 | A04 | MICL0.00925034/DBR
Build-In Floor | Mini Canal | MICL.00925034/DBV | 9 | 250 | 34 | 34 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00925034/DBV
Build-In Floor | Mini Canal | MICL.00925034/DDB | 9 | 250 | 34 | 34 | 821 | 821 | 821 | 0.019548 | 319 | 0.0075952 | 935 | 0.022262 | 1.362 | A04 | MICL0.00925034/DDB
Build-In Floor | Mini Canal | MICL.00925034/DMN | 9 | 250 | 34 | 34 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00925034/DMN
Build-In Floor | Mini Canal | MICL.00925034/DMV | 9 | 250 | 34 | 34 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00925034/DMV
Build-In Floor | Mini Canal | MICL.00925034/DNA | 9 | 250 | 34 | 34 | 821 | 821 | 821 | 0.019548 | 319 | 0.0075952 | 935 | 0.022262 | 1.362 | A04 | MICL0.00925034/DNA
Build-In Floor | Mini Canal | MICL.00925034/DNC | 9 | 250 | 34 | 34 | 821 | 821 | 821 | 0.019548 | 319 | 0.0075952 | 935 | 0.022262 | 1.362 | A04 | MICL0.00925034/DNC
Build-In Floor | Mini Canal | MICL.00925034/DON | 9 | 250 | 34 | 34 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00925034/DON
Build-In Floor | Mini Canal | MICL.00925034/DOV | 9 | 250 | 34 | 34 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00925034/DOV
Build-In Floor | Mini Canal | MICL.00925034/PNC | 9 | 250 | 34 | 34 | 719 | 719 | 719 | 0.017119 | 280 | 0.0066667 | 819 | 0.0195 | 1.362 | A04 | MICL0.00925034/PNC
Build-In Floor | Mini Canal | MICL.00925034/RBL | 9 | 250 | 34 | 34 | 846 | 846 | 846 | 0.020143 | 329 | 0.0078333 | 964 | 0.022952 | 1.362 | A04 | MICL0.00925034/RBL
Build-In Floor | Mini Canal | MICL.00925034/RBN | 9 | 250 | 34 | 34 | 821 | 821 | 821 | 0.019548 | 319 | 0.0075952 | 935 | 0.022262 | 1.362 | A04 | MICL0.00925034/RBN
Build-In Floor | Mini Canal | MICL.00925034/RBR | 9 | 250 | 34 | 34 | 846 | 846 | 846 | 0.020143 | 329 | 0.0078333 | 964 | 0.022952 | 1.362 | A04 | MICL0.00925034/RBR
Build-In Floor | Mini Canal | MICL.00925034/RBV | 9 | 250 | 34 | 34 | 821 | 821 | 821 | 0.019548 | 319 | 0.0075952 | 935 | 0.022262 | 1.362 | A04 | MICL0.00925034/RBV
Build-In Floor | Mini Canal | MICL.00925034/RDB | 9 | 250 | 34 | 34 | 846 | 846 | 846 | 0.020143 | 329 | 0.0078333 | 964 | 0.022952 | 1.362 | A04 | MICL0.00925034/RDB
Build-In Floor | Mini Canal | MICL.00925034/RMN | 9 | 250 | 34 | 34 | 821 | 821 | 821 | 0.019548 | 319 | 0.0075952 | 935 | 0.022262 | 1.362 | A04 | MICL0.00925034/RMN
Build-In Floor | Mini Canal | MICL.00925034/RMV | 9 | 250 | 34 | 34 | 821 | 821 | 821 | 0.019548 | 319 | 0.0075952 | 935 | 0.022262 | 1.362 | A04 | MICL0.00925034/RMV
Build-In Floor | Mini Canal | MICL.00925034/RNA | 9 | 250 | 34 | 34 | 846 | 846 | 846 | 0.020143 | 329 | 0.0078333 | 964 | 0.022952 | 1.362 | A04 | MICL0.00925034/RNA
Build-In Floor | Mini Canal | MICL.00925034/RON | 9 | 250 | 34 | 34 | 821 | 821 | 821 | 0.019548 | 319 | 0.0075952 | 935 | 0.022262 | 1.362 | A04 | MICL0.00925034/RON
Build-In Floor | Mini Canal | MICL.00925034/ROV | 9 | 250 | 34 | 34 | 821 | 821 | 821 | 0.019548 | 319 | 0.0075952 | 935 | 0.022262 | 1.362 | A04 | MICL0.00925034/ROV
Build-In Floor | Mini Canal | MICL.00925034/RSS | 9 | 250 | 34 | 34 | 812 | 812 | 812 | 0.019333 | 316 | 0.0075238 | 925 | 0.022024 | 1.362 | A04 | MICL0.00925034/RSS
Build-In Floor | Mini Canal | MICL.00925034/SBL | 9 | 250 | 34 | 34 | 846 | 846 | 846 | 0.020143 | 329 | 0.0078333 | 964 | 0.022952 | 1.362 | A04 | MICL0.00925034/SBL
Build-In Floor | Mini Canal | MICL.00925034/SBR | 9 | 250 | 34 | 34 | 846 | 846 | 846 | 0.020143 | 329 | 0.0078333 | 964 | 0.022952 | 1.362 | A04 | MICL0.00925034/SBR
Build-In Floor | Mini Canal | MICL.00925034/SDB | 9 | 250 | 34 | 34 | 846 | 846 | 846 | 0.020143 | 329 | 0.0078333 | 964 | 0.022952 | 1.362 | A04 | MICL0.00925034/SDB
Build-In Floor | Mini Canal | MICL.00925034/SNA | 9 | 250 | 34 | 34 | 846 | 846 | 846 | 0.020143 | 329 | 0.0078333 | 964 | 0.022952 | 1.362 | A04 | MICL0.00925034/SNA
Build-In Floor | Mini Canal | MICL.00925034/SNC | 9 | 250 | 34 | 34 | 846 | 846 | 846 | 0.020143 | 329 | 0.0078333 | 964 | 0.022952 | 1.362 | A04 | MICL0.00925034/SNC
Build-In Floor | Mini Canal | MICL.00925042/ANA | 9 | 250 | 42 | 42 | 916 | 916 | 916 | 0.02181 | 356 | 0.0084762 | 1043 | 0.024833 | 1.362 | A04 | MICL0.00925042/ANA
Build-In Floor | Mini Canal | MICL.00925042/DBL | 9 | 250 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.00925042/DBL
Build-In Floor | Mini Canal | MICL.00925042/DBN | 9 | 250 | 42 | 42 | 1136 | 1136 | 1136 | 0.027048 | 442 | 0.010524 | 1294 | 0.03081 | 1.362 | A04 | MICL0.00925042/DBN
Build-In Floor | Mini Canal | MICL.00925042/DBR | 9 | 250 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.00925042/DBR
Build-In Floor | Mini Canal | MICL.00925042/DBV | 9 | 250 | 42 | 42 | 1136 | 1136 | 1136 | 0.027048 | 442 | 0.010524 | 1294 | 0.03081 | 1.362 | A04 | MICL0.00925042/DBV
Build-In Floor | Mini Canal | MICL.00925042/DDB | 9 | 250 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.00925042/DDB
Build-In Floor | Mini Canal | MICL.00925042/DMN | 9 | 250 | 42 | 42 | 1136 | 1136 | 1136 | 0.027048 | 442 | 0.010524 | 1294 | 0.03081 | 1.362 | A04 | MICL0.00925042/DMN
Build-In Floor | Mini Canal | MICL.00925042/DMV | 9 | 250 | 42 | 42 | 1136 | 1136 | 1136 | 0.027048 | 442 | 0.010524 | 1294 | 0.03081 | 1.362 | A04 | MICL0.00925042/DMV
Build-In Floor | Mini Canal | MICL.00925042/DNA | 9 | 250 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.00925042/DNA
Build-In Floor | Mini Canal | MICL.00925042/DNC | 9 | 250 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.00925042/DNC
Build-In Floor | Mini Canal | MICL.00925042/DON | 9 | 250 | 42 | 42 | 1136 | 1136 | 1136 | 0.027048 | 442 | 0.010524 | 1294 | 0.03081 | 1.362 | A04 | MICL0.00925042/DON
Build-In Floor | Mini Canal | MICL.00925042/DOV | 9 | 250 | 42 | 42 | 1136 | 1136 | 1136 | 0.027048 | 442 | 0.010524 | 1294 | 0.03081 | 1.362 | A04 | MICL0.00925042/DOV
Build-In Floor | Mini Canal | MICL.00925042/PNC | 9 | 250 | 42 | 42 | 1038 | 1038 | 1038 | 0.024714 | 404 | 0.009619 | 1182 | 0.028143 | 1.362 | A04 | MICL0.00925042/PNC
Build-In Floor | Mini Canal | MICL.00925042/RBL | 9 | 250 | 42 | 42 | 1221 | 1221 | 1221 | 0.029071 | 475 | 0.01131 | 1391 | 0.033119 | 1.362 | A04 | MICL0.00925042/RBL
Build-In Floor | Mini Canal | MICL.00925042/RBN | 9 | 250 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.00925042/RBN
Build-In Floor | Mini Canal | MICL.00925042/RBR | 9 | 250 | 42 | 42 | 1221 | 1221 | 1221 | 0.029071 | 475 | 0.01131 | 1391 | 0.033119 | 1.362 | A04 | MICL0.00925042/RBR
Build-In Floor | Mini Canal | MICL.00925042/RBV | 9 | 250 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.00925042/RBV
Build-In Floor | Mini Canal | MICL.00925042/RDB | 9 | 250 | 42 | 42 | 1221 | 1221 | 1221 | 0.029071 | 475 | 0.01131 | 1391 | 0.033119 | 1.362 | A04 | MICL0.00925042/RDB
Build-In Floor | Mini Canal | MICL.00925042/RMN | 9 | 250 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.00925042/RMN
Build-In Floor | Mini Canal | MICL.00925042/RMV | 9 | 250 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.00925042/RMV
Build-In Floor | Mini Canal | MICL.00925042/RNA | 9 | 250 | 42 | 42 | 1221 | 1221 | 1221 | 0.029071 | 475 | 0.01131 | 1391 | 0.033119 | 1.362 | A04 | MICL0.00925042/RNA
Build-In Floor | Mini Canal | MICL.00925042/RON | 9 | 250 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.00925042/RON
Build-In Floor | Mini Canal | MICL.00925042/ROV | 9 | 250 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.00925042/ROV
Build-In Floor | Mini Canal | MICL.00925042/RSS | 9 | 250 | 42 | 42 | 1172 | 1172 | 1172 | 0.027905 | 456 | 0.010857 | 1335 | 0.031786 | 1.362 | A04 | MICL0.00925042/RSS
Build-In Floor | Mini Canal | MICL.00925042/SBL | 9 | 250 | 42 | 42 | 1221 | 1221 | 1221 | 0.029071 | 475 | 0.01131 | 1391 | 0.033119 | 1.362 | A04 | MICL0.00925042/SBL
Build-In Floor | Mini Canal | MICL.00925042/SBR | 9 | 250 | 42 | 42 | 1221 | 1221 | 1221 | 0.029071 | 475 | 0.01131 | 1391 | 0.033119 | 1.362 | A04 | MICL0.00925042/SBR
Build-In Floor | Mini Canal | MICL.00925042/SDB | 9 | 250 | 42 | 42 | 1221 | 1221 | 1221 | 0.029071 | 475 | 0.01131 | 1391 | 0.033119 | 1.362 | A04 | MICL0.00925042/SDB
Build-In Floor | Mini Canal | MICL.00925042/SNA | 9 | 250 | 42 | 42 | 1221 | 1221 | 1221 | 0.029071 | 475 | 0.01131 | 1391 | 0.033119 | 1.362 | A04 | MICL0.00925042/SNA
Build-In Floor | Mini Canal | MICL.00925042/SNC | 9 | 250 | 42 | 42 | 1221 | 1221 | 1221 | 0.029071 | 475 | 0.01131 | 1391 | 0.033119 | 1.362 | A04 | MICL0.00925042/SNC
Build-In Floor | Mini Canal | MICL.00927014/ANA | 9 | 270 | 14 | 14 | 343 | 343 | 343 | 0.0081667 | 133 | 0.0031667 | 391 | 0.0093095 | 1.362 | A04 | MICL0.00927014/ANA
Build-In Floor | Mini Canal | MICL.00927014/DBL | 9 | 270 | 14 | 14 | 443 | 443 | 443 | 0.010548 | 172 | 0.0040952 | 505 | 0.012024 | 1.362 | A04 | MICL0.00927014/DBL
Build-In Floor | Mini Canal | MICL.00927014/DBN | 9 | 270 | 14 | 14 | 425 | 425 | 425 | 0.010119 | 165 | 0.0039286 | 484 | 0.011524 | 1.362 | A04 | MICL0.00927014/DBN
Build-In Floor | Mini Canal | MICL.00927014/DBR | 9 | 270 | 14 | 14 | 443 | 443 | 443 | 0.010548 | 172 | 0.0040952 | 505 | 0.012024 | 1.362 | A04 | MICL0.00927014/DBR
Build-In Floor | Mini Canal | MICL.00927014/DBV | 9 | 270 | 14 | 14 | 425 | 425 | 425 | 0.010119 | 165 | 0.0039286 | 484 | 0.011524 | 1.362 | A04 | MICL0.00927014/DBV
Build-In Floor | Mini Canal | MICL.00927014/DDB | 9 | 270 | 14 | 14 | 443 | 443 | 443 | 0.010548 | 172 | 0.0040952 | 505 | 0.012024 | 1.362 | A04 | MICL0.00927014/DDB
Build-In Floor | Mini Canal | MICL.00927014/DMN | 9 | 270 | 14 | 14 | 425 | 425 | 425 | 0.010119 | 165 | 0.0039286 | 484 | 0.011524 | 1.362 | A04 | MICL0.00927014/DMN
Build-In Floor | Mini Canal | MICL.00927014/DMV | 9 | 270 | 14 | 14 | 425 | 425 | 425 | 0.010119 | 165 | 0.0039286 | 484 | 0.011524 | 1.362 | A04 | MICL0.00927014/DMV
Build-In Floor | Mini Canal | MICL.00927014/DNA | 9 | 270 | 14 | 14 | 443 | 443 | 443 | 0.010548 | 172 | 0.0040952 | 505 | 0.012024 | 1.362 | A04 | MICL0.00927014/DNA
Build-In Floor | Mini Canal | MICL.00927014/DNC | 9 | 270 | 14 | 14 | 443 | 443 | 443 | 0.010548 | 172 | 0.0040952 | 505 | 0.012024 | 1.362 | A04 | MICL0.00927014/DNC
Build-In Floor | Mini Canal | MICL.00927014/DON | 9 | 270 | 14 | 14 | 425 | 425 | 425 | 0.010119 | 165 | 0.0039286 | 484 | 0.011524 | 1.362 | A04 | MICL0.00927014/DON
Build-In Floor | Mini Canal | MICL.00927014/DOV | 9 | 270 | 14 | 14 | 425 | 425 | 425 | 0.010119 | 165 | 0.0039286 | 484 | 0.011524 | 1.362 | A04 | MICL0.00927014/DOV
Build-In Floor | Mini Canal | MICL.00927014/RBL | 9 | 270 | 14 | 14 | 457 | 457 | 457 | 0.010881 | 178 | 0.0042381 | 521 | 0.012405 | 1.362 | A04 | MICL0.00927014/RBL
Build-In Floor | Mini Canal | MICL.00927014/RBN | 9 | 270 | 14 | 14 | 443 | 443 | 443 | 0.010548 | 172 | 0.0040952 | 505 | 0.012024 | 1.362 | A04 | MICL0.00927014/RBN
Build-In Floor | Mini Canal | MICL.00927014/RBR | 9 | 270 | 14 | 14 | 457 | 457 | 457 | 0.010881 | 178 | 0.0042381 | 521 | 0.012405 | 1.362 | A04 | MICL0.00927014/RBR
Build-In Floor | Mini Canal | MICL.00927014/RBV | 9 | 270 | 14 | 14 | 443 | 443 | 443 | 0.010548 | 172 | 0.0040952 | 505 | 0.012024 | 1.362 | A04 | MICL0.00927014/RBV
Build-In Floor | Mini Canal | MICL.00927014/RDB | 9 | 270 | 14 | 14 | 457 | 457 | 457 | 0.010881 | 178 | 0.0042381 | 521 | 0.012405 | 1.362 | A04 | MICL0.00927014/RDB
Build-In Floor | Mini Canal | MICL.00927014/RMN | 9 | 270 | 14 | 14 | 443 | 443 | 443 | 0.010548 | 172 | 0.0040952 | 505 | 0.012024 | 1.362 | A04 | MICL0.00927014/RMN
Build-In Floor | Mini Canal | MICL.00927014/RMV | 9 | 270 | 14 | 14 | 443 | 443 | 443 | 0.010548 | 172 | 0.0040952 | 505 | 0.012024 | 1.362 | A04 | MICL0.00927014/RMV
Build-In Floor | Mini Canal | MICL.00927014/RNA | 9 | 270 | 14 | 14 | 457 | 457 | 457 | 0.010881 | 178 | 0.0042381 | 521 | 0.012405 | 1.362 | A04 | MICL0.00927014/RNA
Build-In Floor | Mini Canal | MICL.00927014/RON | 9 | 270 | 14 | 14 | 443 | 443 | 443 | 0.010548 | 172 | 0.0040952 | 505 | 0.012024 | 1.362 | A04 | MICL0.00927014/RON
Build-In Floor | Mini Canal | MICL.00927014/ROV | 9 | 270 | 14 | 14 | 443 | 443 | 443 | 0.010548 | 172 | 0.0040952 | 505 | 0.012024 | 1.362 | A04 | MICL0.00927014/ROV
Build-In Floor | Mini Canal | MICL.00927014/RSS | 9 | 270 | 14 | 14 | 439 | 439 | 439 | 0.010452 | 171 | 0.0040714 | 500 | 0.011905 | 1.362 | A04 | MICL0.00927014/RSS
Build-In Floor | Mini Canal | MICL.00927014/SBL | 9 | 270 | 14 | 14 | 457 | 457 | 457 | 0.010881 | 178 | 0.0042381 | 521 | 0.012405 | 1.362 | A04 | MICL0.00927014/SBL
Build-In Floor | Mini Canal | MICL.00927014/SBR | 9 | 270 | 14 | 14 | 457 | 457 | 457 | 0.010881 | 178 | 0.0042381 | 521 | 0.012405 | 1.362 | A04 | MICL0.00927014/SBR
Build-In Floor | Mini Canal | MICL.00927014/SDB | 9 | 270 | 14 | 14 | 457 | 457 | 457 | 0.010881 | 178 | 0.0042381 | 521 | 0.012405 | 1.362 | A04 | MICL0.00927014/SDB
Build-In Floor | Mini Canal | MICL.00927014/SNA | 9 | 270 | 14 | 14 | 457 | 457 | 457 | 0.010881 | 178 | 0.0042381 | 521 | 0.012405 | 1.362 | A04 | MICL0.00927014/SNA
Build-In Floor | Mini Canal | MICL.00927014/SNC | 9 | 270 | 14 | 14 | 457 | 457 | 457 | 0.010881 | 178 | 0.0042381 | 521 | 0.012405 | 1.362 | A04 | MICL0.00927014/SNC
Build-In Floor | Mini Canal | MICL.00927018/ANA | 9 | 270 | 18 | 18 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.00927018/ANA
Build-In Floor | Mini Canal | MICL.00927018/DBL | 9 | 270 | 18 | 18 | 525 | 525 | 525 | 0.0125 | 204 | 0.0048571 | 598 | 0.014238 | 1.362 | A04 | MICL0.00927018/DBL
Build-In Floor | Mini Canal | MICL.00927018/DBN | 9 | 270 | 18 | 18 | 503 | 503 | 503 | 0.011976 | 196 | 0.0046667 | 573 | 0.013643 | 1.362 | A04 | MICL0.00927018/DBN
Build-In Floor | Mini Canal | MICL.00927018/DBR | 9 | 270 | 18 | 18 | 525 | 525 | 525 | 0.0125 | 204 | 0.0048571 | 598 | 0.014238 | 1.362 | A04 | MICL0.00927018/DBR
Build-In Floor | Mini Canal | MICL.00927018/DBV | 9 | 270 | 18 | 18 | 503 | 503 | 503 | 0.011976 | 196 | 0.0046667 | 573 | 0.013643 | 1.362 | A04 | MICL0.00927018/DBV
Build-In Floor | Mini Canal | MICL.00927018/DDB | 9 | 270 | 18 | 18 | 525 | 525 | 525 | 0.0125 | 204 | 0.0048571 | 598 | 0.014238 | 1.362 | A04 | MICL0.00927018/DDB
Build-In Floor | Mini Canal | MICL.00927018/DMN | 9 | 270 | 18 | 18 | 503 | 503 | 503 | 0.011976 | 196 | 0.0046667 | 573 | 0.013643 | 1.362 | A04 | MICL0.00927018/DMN
Build-In Floor | Mini Canal | MICL.00927018/DMV | 9 | 270 | 18 | 18 | 503 | 503 | 503 | 0.011976 | 196 | 0.0046667 | 573 | 0.013643 | 1.362 | A04 | MICL0.00927018/DMV
Build-In Floor | Mini Canal | MICL.00927018/DNA | 9 | 270 | 18 | 18 | 525 | 525 | 525 | 0.0125 | 204 | 0.0048571 | 598 | 0.014238 | 1.362 | A04 | MICL0.00927018/DNA
Build-In Floor | Mini Canal | MICL.00927018/DNC | 9 | 270 | 18 | 18 | 525 | 525 | 525 | 0.0125 | 204 | 0.0048571 | 598 | 0.014238 | 1.362 | A04 | MICL0.00927018/DNC
Build-In Floor | Mini Canal | MICL.00927018/DON | 9 | 270 | 18 | 18 | 503 | 503 | 503 | 0.011976 | 196 | 0.0046667 | 573 | 0.013643 | 1.362 | A04 | MICL0.00927018/DON
Build-In Floor | Mini Canal | MICL.00927018/DOV | 9 | 270 | 18 | 18 | 503 | 503 | 503 | 0.011976 | 196 | 0.0046667 | 573 | 0.013643 | 1.362 | A04 | MICL0.00927018/DOV
Build-In Floor | Mini Canal | MICL.00927018/RBL | 9 | 270 | 18 | 18 | 541 | 541 | 541 | 0.012881 | 210 | 0.005 | 616 | 0.014667 | 1.362 | A04 | MICL0.00927018/RBL
Build-In Floor | Mini Canal | MICL.00927018/RBN | 9 | 270 | 18 | 18 | 525 | 525 | 525 | 0.0125 | 204 | 0.0048571 | 598 | 0.014238 | 1.362 | A04 | MICL0.00927018/RBN
Build-In Floor | Mini Canal | MICL.00927018/RBR | 9 | 270 | 18 | 18 | 541 | 541 | 541 | 0.012881 | 210 | 0.005 | 616 | 0.014667 | 1.362 | A04 | MICL0.00927018/RBR
Build-In Floor | Mini Canal | MICL.00927018/RBV | 9 | 270 | 18 | 18 | 525 | 525 | 525 | 0.0125 | 204 | 0.0048571 | 598 | 0.014238 | 1.362 | A04 | MICL0.00927018/RBV
Build-In Floor | Mini Canal | MICL.00927018/RDB | 9 | 270 | 18 | 18 | 541 | 541 | 541 | 0.012881 | 210 | 0.005 | 616 | 0.014667 | 1.362 | A04 | MICL0.00927018/RDB
Build-In Floor | Mini Canal | MICL.00927018/RMN | 9 | 270 | 18 | 18 | 525 | 525 | 525 | 0.0125 | 204 | 0.0048571 | 598 | 0.014238 | 1.362 | A04 | MICL0.00927018/RMN
Build-In Floor | Mini Canal | MICL.00927018/RMV | 9 | 270 | 18 | 18 | 525 | 525 | 525 | 0.0125 | 204 | 0.0048571 | 598 | 0.014238 | 1.362 | A04 | MICL0.00927018/RMV
Build-In Floor | Mini Canal | MICL.00927018/RNA | 9 | 270 | 18 | 18 | 541 | 541 | 541 | 0.012881 | 210 | 0.005 | 616 | 0.014667 | 1.362 | A04 | MICL0.00927018/RNA
Build-In Floor | Mini Canal | MICL.00927018/RON | 9 | 270 | 18 | 18 | 525 | 525 | 525 | 0.0125 | 204 | 0.0048571 | 598 | 0.014238 | 1.362 | A04 | MICL0.00927018/RON
Build-In Floor | Mini Canal | MICL.00927018/ROV | 9 | 270 | 18 | 18 | 525 | 525 | 525 | 0.0125 | 204 | 0.0048571 | 598 | 0.014238 | 1.362 | A04 | MICL0.00927018/ROV
Build-In Floor | Mini Canal | MICL.00927018/RSS | 9 | 270 | 18 | 18 | 519 | 519 | 519 | 0.012357 | 202 | 0.0048095 | 591 | 0.014071 | 1.362 | A04 | MICL0.00927018/RSS
Build-In Floor | Mini Canal | MICL.00927018/SBL | 9 | 270 | 18 | 18 | 541 | 541 | 541 | 0.012881 | 210 | 0.005 | 616 | 0.014667 | 1.362 | A04 | MICL0.00927018/SBL
Build-In Floor | Mini Canal | MICL.00927018/SBR | 9 | 270 | 18 | 18 | 541 | 541 | 541 | 0.012881 | 210 | 0.005 | 616 | 0.014667 | 1.362 | A04 | MICL0.00927018/SBR
Build-In Floor | Mini Canal | MICL.00927018/SDB | 9 | 270 | 18 | 18 | 541 | 541 | 541 | 0.012881 | 210 | 0.005 | 616 | 0.014667 | 1.362 | A04 | MICL0.00927018/SDB
Build-In Floor | Mini Canal | MICL.00927018/SNA | 9 | 270 | 18 | 18 | 541 | 541 | 541 | 0.012881 | 210 | 0.005 | 616 | 0.014667 | 1.362 | A04 | MICL0.00927018/SNA
Build-In Floor | Mini Canal | MICL.00927018/SNC | 9 | 270 | 18 | 18 | 541 | 541 | 541 | 0.012881 | 210 | 0.005 | 616 | 0.014667 | 1.362 | A04 | MICL0.00927018/SNC
Build-In Floor | Mini Canal | MICL.00927026/ANA | 9 | 270 | 26 | 26 | 533 | 533 | 533 | 0.01269 | 207 | 0.0049286 | 607 | 0.014452 | 1.362 | A04 | MICL0.00927026/ANA
Build-In Floor | Mini Canal | MICL.00927026/DBL | 9 | 270 | 26 | 26 | 690 | 690 | 690 | 0.016429 | 268 | 0.006381 | 786 | 0.018714 | 1.362 | A04 | MICL0.00927026/DBL
Build-In Floor | Mini Canal | MICL.00927026/DBN | 9 | 270 | 26 | 26 | 661 | 661 | 661 | 0.015738 | 257 | 0.006119 | 753 | 0.017929 | 1.362 | A04 | MICL0.00927026/DBN
Build-In Floor | Mini Canal | MICL.00927026/DBR | 9 | 270 | 26 | 26 | 690 | 690 | 690 | 0.016429 | 268 | 0.006381 | 786 | 0.018714 | 1.362 | A04 | MICL0.00927026/DBR
Build-In Floor | Mini Canal | MICL.00927026/DBV | 9 | 270 | 26 | 26 | 661 | 661 | 661 | 0.015738 | 257 | 0.006119 | 753 | 0.017929 | 1.362 | A04 | MICL0.00927026/DBV
Build-In Floor | Mini Canal | MICL.00927026/DDB | 9 | 270 | 26 | 26 | 690 | 690 | 690 | 0.016429 | 268 | 0.006381 | 786 | 0.018714 | 1.362 | A04 | MICL0.00927026/DDB
Build-In Floor | Mini Canal | MICL.00927026/DMN | 9 | 270 | 26 | 26 | 661 | 661 | 661 | 0.015738 | 257 | 0.006119 | 753 | 0.017929 | 1.362 | A04 | MICL0.00927026/DMN
Build-In Floor | Mini Canal | MICL.00927026/DMV | 9 | 270 | 26 | 26 | 661 | 661 | 661 | 0.015738 | 257 | 0.006119 | 753 | 0.017929 | 1.362 | A04 | MICL0.00927026/DMV
Build-In Floor | Mini Canal | MICL.00927026/DNA | 9 | 270 | 26 | 26 | 690 | 690 | 690 | 0.016429 | 268 | 0.006381 | 786 | 0.018714 | 1.362 | A04 | MICL0.00927026/DNA
Build-In Floor | Mini Canal | MICL.00927026/DNC | 9 | 270 | 26 | 26 | 690 | 690 | 690 | 0.016429 | 268 | 0.006381 | 786 | 0.018714 | 1.362 | A04 | MICL0.00927026/DNC
Build-In Floor | Mini Canal | MICL.00927026/DON | 9 | 270 | 26 | 26 | 661 | 661 | 661 | 0.015738 | 257 | 0.006119 | 753 | 0.017929 | 1.362 | A04 | MICL0.00927026/DON
Build-In Floor | Mini Canal | MICL.00927026/DOV | 9 | 270 | 26 | 26 | 661 | 661 | 661 | 0.015738 | 257 | 0.006119 | 753 | 0.017929 | 1.362 | A04 | MICL0.00927026/DOV
Build-In Floor | Mini Canal | MICL.00927026/PNC | 9 | 270 | 26 | 26 | 604 | 604 | 604 | 0.014381 | 235 | 0.0055952 | 688 | 0.016381 | 1.362 | A04 | MICL0.00927026/PNC
Build-In Floor | Mini Canal | MICL.00927026/RBL | 9 | 270 | 26 | 26 | 711 | 711 | 711 | 0.016929 | 277 | 0.0065952 | 810 | 0.019286 | 1.362 | A04 | MICL0.00927026/RBL
Build-In Floor | Mini Canal | MICL.00927026/RBN | 9 | 270 | 26 | 26 | 690 | 690 | 690 | 0.016429 | 268 | 0.006381 | 786 | 0.018714 | 1.362 | A04 | MICL0.00927026/RBN
Build-In Floor | Mini Canal | MICL.00927026/RBR | 9 | 270 | 26 | 26 | 711 | 711 | 711 | 0.016929 | 277 | 0.0065952 | 810 | 0.019286 | 1.362 | A04 | MICL0.00927026/RBR
Build-In Floor | Mini Canal | MICL.00927026/RBV | 9 | 270 | 26 | 26 | 690 | 690 | 690 | 0.016429 | 268 | 0.006381 | 786 | 0.018714 | 1.362 | A04 | MICL0.00927026/RBV
Build-In Floor | Mini Canal | MICL.00927026/RDB | 9 | 270 | 26 | 26 | 711 | 711 | 711 | 0.016929 | 277 | 0.0065952 | 810 | 0.019286 | 1.362 | A04 | MICL0.00927026/RDB
Build-In Floor | Mini Canal | MICL.00927026/RMN | 9 | 270 | 26 | 26 | 690 | 690 | 690 | 0.016429 | 268 | 0.006381 | 786 | 0.018714 | 1.362 | A04 | MICL0.00927026/RMN
Build-In Floor | Mini Canal | MICL.00927026/RMV | 9 | 270 | 26 | 26 | 690 | 690 | 690 | 0.016429 | 268 | 0.006381 | 786 | 0.018714 | 1.362 | A04 | MICL0.00927026/RMV
Build-In Floor | Mini Canal | MICL.00927026/RNA | 9 | 270 | 26 | 26 | 711 | 711 | 711 | 0.016929 | 277 | 0.0065952 | 810 | 0.019286 | 1.362 | A04 | MICL0.00927026/RNA
Build-In Floor | Mini Canal | MICL.00927026/RON | 9 | 270 | 26 | 26 | 690 | 690 | 690 | 0.016429 | 268 | 0.006381 | 786 | 0.018714 | 1.362 | A04 | MICL0.00927026/RON
Build-In Floor | Mini Canal | MICL.00927026/ROV | 9 | 270 | 26 | 26 | 690 | 690 | 690 | 0.016429 | 268 | 0.006381 | 786 | 0.018714 | 1.362 | A04 | MICL0.00927026/ROV
Build-In Floor | Mini Canal | MICL.00927026/RSS | 9 | 270 | 26 | 26 | 683 | 683 | 683 | 0.016262 | 266 | 0.0063333 | 778 | 0.018524 | 1.362 | A04 | MICL0.00927026/RSS
Build-In Floor | Mini Canal | MICL.00927026/SBL | 9 | 270 | 26 | 26 | 711 | 711 | 711 | 0.016929 | 277 | 0.0065952 | 810 | 0.019286 | 1.362 | A04 | MICL0.00927026/SBL
Build-In Floor | Mini Canal | MICL.00927026/SBR | 9 | 270 | 26 | 26 | 711 | 711 | 711 | 0.016929 | 277 | 0.0065952 | 810 | 0.019286 | 1.362 | A04 | MICL0.00927026/SBR
Build-In Floor | Mini Canal | MICL.00927026/SDB | 9 | 270 | 26 | 26 | 711 | 711 | 711 | 0.016929 | 277 | 0.0065952 | 810 | 0.019286 | 1.362 | A04 | MICL0.00927026/SDB
Build-In Floor | Mini Canal | MICL.00927026/SNA | 9 | 270 | 26 | 26 | 711 | 711 | 711 | 0.016929 | 277 | 0.0065952 | 810 | 0.019286 | 1.362 | A04 | MICL0.00927026/SNA
Build-In Floor | Mini Canal | MICL.00927026/SNC | 9 | 270 | 26 | 26 | 711 | 711 | 711 | 0.016929 | 277 | 0.0065952 | 810 | 0.019286 | 1.362 | A04 | MICL0.00927026/SNC
Build-In Floor | Mini Canal | MICL.00927034/ANA | 9 | 270 | 34 | 34 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.00927034/ANA
Build-In Floor | Mini Canal | MICL.00927034/DBL | 9 | 270 | 34 | 34 | 895 | 895 | 895 | 0.02131 | 348 | 0.0082857 | 1019 | 0.024262 | 1.362 | A04 | MICL0.00927034/DBL
Build-In Floor | Mini Canal | MICL.00927034/DBN | 9 | 270 | 34 | 34 | 858 | 858 | 858 | 0.020429 | 334 | 0.0079524 | 977 | 0.023262 | 1.362 | A04 | MICL0.00927034/DBN
Build-In Floor | Mini Canal | MICL.00927034/DBR | 9 | 270 | 34 | 34 | 895 | 895 | 895 | 0.02131 | 348 | 0.0082857 | 1019 | 0.024262 | 1.362 | A04 | MICL0.00927034/DBR
Build-In Floor | Mini Canal | MICL.00927034/DBV | 9 | 270 | 34 | 34 | 858 | 858 | 858 | 0.020429 | 334 | 0.0079524 | 977 | 0.023262 | 1.362 | A04 | MICL0.00927034/DBV
Build-In Floor | Mini Canal | MICL.00927034/DDB | 9 | 270 | 34 | 34 | 895 | 895 | 895 | 0.02131 | 348 | 0.0082857 | 1019 | 0.024262 | 1.362 | A04 | MICL0.00927034/DDB
Build-In Floor | Mini Canal | MICL.00927034/DMN | 9 | 270 | 34 | 34 | 858 | 858 | 858 | 0.020429 | 334 | 0.0079524 | 977 | 0.023262 | 1.362 | A04 | MICL0.00927034/DMN
Build-In Floor | Mini Canal | MICL.00927034/DMV | 9 | 270 | 34 | 34 | 858 | 858 | 858 | 0.020429 | 334 | 0.0079524 | 977 | 0.023262 | 1.362 | A04 | MICL0.00927034/DMV
Build-In Floor | Mini Canal | MICL.00927034/DNA | 9 | 270 | 34 | 34 | 895 | 895 | 895 | 0.02131 | 348 | 0.0082857 | 1019 | 0.024262 | 1.362 | A04 | MICL0.00927034/DNA
Build-In Floor | Mini Canal | MICL.00927034/DNC | 9 | 270 | 34 | 34 | 895 | 895 | 895 | 0.02131 | 348 | 0.0082857 | 1019 | 0.024262 | 1.362 | A04 | MICL0.00927034/DNC
Build-In Floor | Mini Canal | MICL.00927034/DON | 9 | 270 | 34 | 34 | 858 | 858 | 858 | 0.020429 | 334 | 0.0079524 | 977 | 0.023262 | 1.362 | A04 | MICL0.00927034/DON
Build-In Floor | Mini Canal | MICL.00927034/DOV | 9 | 270 | 34 | 34 | 858 | 858 | 858 | 0.020429 | 334 | 0.0079524 | 977 | 0.023262 | 1.362 | A04 | MICL0.00927034/DOV
Build-In Floor | Mini Canal | MICL.00927034/PNC | 9 | 270 | 34 | 34 | 785 | 785 | 785 | 0.01869 | 305 | 0.0072619 | 894 | 0.021286 | 1.362 | A04 | MICL0.00927034/PNC
Build-In Floor | Mini Canal | MICL.00927034/RBL | 9 | 270 | 34 | 34 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00927034/RBL
Build-In Floor | Mini Canal | MICL.00927034/RBN | 9 | 270 | 34 | 34 | 895 | 895 | 895 | 0.02131 | 348 | 0.0082857 | 1019 | 0.024262 | 1.362 | A04 | MICL0.00927034/RBN
Build-In Floor | Mini Canal | MICL.00927034/RBR | 9 | 270 | 34 | 34 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00927034/RBR
Build-In Floor | Mini Canal | MICL.00927034/RBV | 9 | 270 | 34 | 34 | 895 | 895 | 895 | 0.02131 | 348 | 0.0082857 | 1019 | 0.024262 | 1.362 | A04 | MICL0.00927034/RBV
Build-In Floor | Mini Canal | MICL.00927034/RDB | 9 | 270 | 34 | 34 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00927034/RDB
Build-In Floor | Mini Canal | MICL.00927034/RMN | 9 | 270 | 34 | 34 | 895 | 895 | 895 | 0.02131 | 348 | 0.0082857 | 1019 | 0.024262 | 1.362 | A04 | MICL0.00927034/RMN
Build-In Floor | Mini Canal | MICL.00927034/RMV | 9 | 270 | 34 | 34 | 895 | 895 | 895 | 0.02131 | 348 | 0.0082857 | 1019 | 0.024262 | 1.362 | A04 | MICL0.00927034/RMV
Build-In Floor | Mini Canal | MICL.00927034/RNA | 9 | 270 | 34 | 34 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00927034/RNA
Build-In Floor | Mini Canal | MICL.00927034/RON | 9 | 270 | 34 | 34 | 895 | 895 | 895 | 0.02131 | 348 | 0.0082857 | 1019 | 0.024262 | 1.362 | A04 | MICL0.00927034/RON
Build-In Floor | Mini Canal | MICL.00927034/ROV | 9 | 270 | 34 | 34 | 895 | 895 | 895 | 0.02131 | 348 | 0.0082857 | 1019 | 0.024262 | 1.362 | A04 | MICL0.00927034/ROV
Build-In Floor | Mini Canal | MICL.00927034/RSS | 9 | 270 | 34 | 34 | 886 | 886 | 886 | 0.021095 | 345 | 0.0082143 | 1009 | 0.024024 | 1.362 | A04 | MICL0.00927034/RSS
Build-In Floor | Mini Canal | MICL.00927034/SBL | 9 | 270 | 34 | 34 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00927034/SBL
Build-In Floor | Mini Canal | MICL.00927034/SBR | 9 | 270 | 34 | 34 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00927034/SBR
Build-In Floor | Mini Canal | MICL.00927034/SDB | 9 | 270 | 34 | 34 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00927034/SDB
Build-In Floor | Mini Canal | MICL.00927034/SNA | 9 | 270 | 34 | 34 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00927034/SNA
Build-In Floor | Mini Canal | MICL.00927034/SNC | 9 | 270 | 34 | 34 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00927034/SNC
Build-In Floor | Mini Canal | MICL.00927042/ANA | 9 | 270 | 42 | 42 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00927042/ANA
Build-In Floor | Mini Canal | MICL.00927042/DBL | 9 | 270 | 42 | 42 | 1293 | 1293 | 1293 | 0.030786 | 503 | 0.011976 | 1473 | 0.035071 | 1.362 | A04 | MICL0.00927042/DBL
Build-In Floor | Mini Canal | MICL.00927042/DBN | 9 | 270 | 42 | 42 | 1240 | 1240 | 1240 | 0.029524 | 482 | 0.011476 | 1412 | 0.033619 | 1.362 | A04 | MICL0.00927042/DBN
Build-In Floor | Mini Canal | MICL.00927042/DBR | 9 | 270 | 42 | 42 | 1293 | 1293 | 1293 | 0.030786 | 503 | 0.011976 | 1473 | 0.035071 | 1.362 | A04 | MICL0.00927042/DBR
Build-In Floor | Mini Canal | MICL.00927042/DBV | 9 | 270 | 42 | 42 | 1240 | 1240 | 1240 | 0.029524 | 482 | 0.011476 | 1412 | 0.033619 | 1.362 | A04 | MICL0.00927042/DBV
Build-In Floor | Mini Canal | MICL.00927042/DDB | 9 | 270 | 42 | 42 | 1293 | 1293 | 1293 | 0.030786 | 503 | 0.011976 | 1473 | 0.035071 | 1.362 | A04 | MICL0.00927042/DDB
Build-In Floor | Mini Canal | MICL.00927042/DMN | 9 | 270 | 42 | 42 | 1240 | 1240 | 1240 | 0.029524 | 482 | 0.011476 | 1412 | 0.033619 | 1.362 | A04 | MICL0.00927042/DMN
Build-In Floor | Mini Canal | MICL.00927042/DMV | 9 | 270 | 42 | 42 | 1240 | 1240 | 1240 | 0.029524 | 482 | 0.011476 | 1412 | 0.033619 | 1.362 | A04 | MICL0.00927042/DMV
Build-In Floor | Mini Canal | MICL.00927042/DNA | 9 | 270 | 42 | 42 | 1293 | 1293 | 1293 | 0.030786 | 503 | 0.011976 | 1473 | 0.035071 | 1.362 | A04 | MICL0.00927042/DNA
Build-In Floor | Mini Canal | MICL.00927042/DNC | 9 | 270 | 42 | 42 | 1293 | 1293 | 1293 | 0.030786 | 503 | 0.011976 | 1473 | 0.035071 | 1.362 | A04 | MICL0.00927042/DNC
Build-In Floor | Mini Canal | MICL.00927042/DON | 9 | 270 | 42 | 42 | 1240 | 1240 | 1240 | 0.029524 | 482 | 0.011476 | 1412 | 0.033619 | 1.362 | A04 | MICL0.00927042/DON
Build-In Floor | Mini Canal | MICL.00927042/DOV | 9 | 270 | 42 | 42 | 1240 | 1240 | 1240 | 0.029524 | 482 | 0.011476 | 1412 | 0.033619 | 1.362 | A04 | MICL0.00927042/DOV
Build-In Floor | Mini Canal | MICL.00927042/PNC | 9 | 270 | 42 | 42 | 1133 | 1133 | 1133 | 0.026976 | 441 | 0.0105 | 1290 | 0.030714 | 1.362 | A04 | MICL0.00927042/PNC
Build-In Floor | Mini Canal | MICL.00927042/RBL | 9 | 270 | 42 | 42 | 1333 | 1333 | 1333 | 0.031738 | 519 | 0.012357 | 1518 | 0.036143 | 1.362 | A04 | MICL0.00927042/RBL
Build-In Floor | Mini Canal | MICL.00927042/RBN | 9 | 270 | 42 | 42 | 1293 | 1293 | 1293 | 0.030786 | 503 | 0.011976 | 1473 | 0.035071 | 1.362 | A04 | MICL0.00927042/RBN
Build-In Floor | Mini Canal | MICL.00927042/RBR | 9 | 270 | 42 | 42 | 1333 | 1333 | 1333 | 0.031738 | 519 | 0.012357 | 1518 | 0.036143 | 1.362 | A04 | MICL0.00927042/RBR
Build-In Floor | Mini Canal | MICL.00927042/RBV | 9 | 270 | 42 | 42 | 1293 | 1293 | 1293 | 0.030786 | 503 | 0.011976 | 1473 | 0.035071 | 1.362 | A04 | MICL0.00927042/RBV
Build-In Floor | Mini Canal | MICL.00927042/RDB | 9 | 270 | 42 | 42 | 1333 | 1333 | 1333 | 0.031738 | 519 | 0.012357 | 1518 | 0.036143 | 1.362 | A04 | MICL0.00927042/RDB
Build-In Floor | Mini Canal | MICL.00927042/RMN | 9 | 270 | 42 | 42 | 1293 | 1293 | 1293 | 0.030786 | 503 | 0.011976 | 1473 | 0.035071 | 1.362 | A04 | MICL0.00927042/RMN
Build-In Floor | Mini Canal | MICL.00927042/RMV | 9 | 270 | 42 | 42 | 1293 | 1293 | 1293 | 0.030786 | 503 | 0.011976 | 1473 | 0.035071 | 1.362 | A04 | MICL0.00927042/RMV
Build-In Floor | Mini Canal | MICL.00927042/RNA | 9 | 270 | 42 | 42 | 1333 | 1333 | 1333 | 0.031738 | 519 | 0.012357 | 1518 | 0.036143 | 1.362 | A04 | MICL0.00927042/RNA
Build-In Floor | Mini Canal | MICL.00927042/RON | 9 | 270 | 42 | 42 | 1293 | 1293 | 1293 | 0.030786 | 503 | 0.011976 | 1473 | 0.035071 | 1.362 | A04 | MICL0.00927042/RON
Build-In Floor | Mini Canal | MICL.00927042/ROV | 9 | 270 | 42 | 42 | 1293 | 1293 | 1293 | 0.030786 | 503 | 0.011976 | 1473 | 0.035071 | 1.362 | A04 | MICL0.00927042/ROV
Build-In Floor | Mini Canal | MICL.00927042/RSS | 9 | 270 | 42 | 42 | 1280 | 1280 | 1280 | 0.030476 | 498 | 0.011857 | 1458 | 0.034714 | 1.362 | A04 | MICL0.00927042/RSS
Build-In Floor | Mini Canal | MICL.00927042/SBL | 9 | 270 | 42 | 42 | 1333 | 1333 | 1333 | 0.031738 | 519 | 0.012357 | 1518 | 0.036143 | 1.362 | A04 | MICL0.00927042/SBL
Build-In Floor | Mini Canal | MICL.00927042/SBR | 9 | 270 | 42 | 42 | 1333 | 1333 | 1333 | 0.031738 | 519 | 0.012357 | 1518 | 0.036143 | 1.362 | A04 | MICL0.00927042/SBR
Build-In Floor | Mini Canal | MICL.00927042/SDB | 9 | 270 | 42 | 42 | 1333 | 1333 | 1333 | 0.031738 | 519 | 0.012357 | 1518 | 0.036143 | 1.362 | A04 | MICL0.00927042/SDB
Build-In Floor | Mini Canal | MICL.00927042/SNA | 9 | 270 | 42 | 42 | 1333 | 1333 | 1333 | 0.031738 | 519 | 0.012357 | 1518 | 0.036143 | 1.362 | A04 | MICL0.00927042/SNA
Build-In Floor | Mini Canal | MICL.00927042/SNC | 9 | 270 | 42 | 42 | 1333 | 1333 | 1333 | 0.031738 | 519 | 0.012357 | 1518 | 0.036143 | 1.362 | A04 | MICL0.00927042/SNC
Build-In Floor | Mini Canal | MICL.00929014/ANA | 9 | 290 | 14 | 14 | 371 | 371 | 371 | 0.0088333 | 144 | 0.0034286 | 423 | 0.010071 | 1.362 | A04 | MICL0.00929014/ANA
Build-In Floor | Mini Canal | MICL.00929014/DBL | 9 | 290 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.00929014/DBL
Build-In Floor | Mini Canal | MICL.00929014/DBN | 9 | 290 | 14 | 14 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00929014/DBN
Build-In Floor | Mini Canal | MICL.00929014/DBR | 9 | 290 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.00929014/DBR
Build-In Floor | Mini Canal | MICL.00929014/DBV | 9 | 290 | 14 | 14 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00929014/DBV
Build-In Floor | Mini Canal | MICL.00929014/DDB | 9 | 290 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.00929014/DDB
Build-In Floor | Mini Canal | MICL.00929014/DMN | 9 | 290 | 14 | 14 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00929014/DMN
Build-In Floor | Mini Canal | MICL.00929014/DMV | 9 | 290 | 14 | 14 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00929014/DMV
Build-In Floor | Mini Canal | MICL.00929014/DNA | 9 | 290 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.00929014/DNA
Build-In Floor | Mini Canal | MICL.00929014/DNC | 9 | 290 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.00929014/DNC
Build-In Floor | Mini Canal | MICL.00929014/DON | 9 | 290 | 14 | 14 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00929014/DON
Build-In Floor | Mini Canal | MICL.00929014/DOV | 9 | 290 | 14 | 14 | 460 | 460 | 460 | 0.010952 | 179 | 0.0042619 | 524 | 0.012476 | 1.362 | A04 | MICL0.00929014/DOV
Build-In Floor | Mini Canal | MICL.00929014/RBL | 9 | 290 | 14 | 14 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.00929014/RBL
Build-In Floor | Mini Canal | MICL.00929014/RBN | 9 | 290 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.00929014/RBN
Build-In Floor | Mini Canal | MICL.00929014/RBR | 9 | 290 | 14 | 14 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.00929014/RBR
Build-In Floor | Mini Canal | MICL.00929014/RBV | 9 | 290 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.00929014/RBV
Build-In Floor | Mini Canal | MICL.00929014/RDB | 9 | 290 | 14 | 14 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.00929014/RDB
Build-In Floor | Mini Canal | MICL.00929014/RMN | 9 | 290 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.00929014/RMN
Build-In Floor | Mini Canal | MICL.00929014/RMV | 9 | 290 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.00929014/RMV
Build-In Floor | Mini Canal | MICL.00929014/RNA | 9 | 290 | 14 | 14 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.00929014/RNA
Build-In Floor | Mini Canal | MICL.00929014/RON | 9 | 290 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.00929014/RON
Build-In Floor | Mini Canal | MICL.00929014/ROV | 9 | 290 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.00929014/ROV
Build-In Floor | Mini Canal | MICL.00929014/RSS | 9 | 290 | 14 | 14 | 475 | 475 | 475 | 0.01131 | 185 | 0.0044048 | 541 | 0.012881 | 1.362 | A04 | MICL0.00929014/RSS
Build-In Floor | Mini Canal | MICL.00929014/SBL | 9 | 290 | 14 | 14 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.00929014/SBL
Build-In Floor | Mini Canal | MICL.00929014/SBR | 9 | 290 | 14 | 14 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.00929014/SBR
Build-In Floor | Mini Canal | MICL.00929014/SDB | 9 | 290 | 14 | 14 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.00929014/SDB
Build-In Floor | Mini Canal | MICL.00929014/SNA | 9 | 290 | 14 | 14 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.00929014/SNA
Build-In Floor | Mini Canal | MICL.00929014/SNC | 9 | 290 | 14 | 14 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.00929014/SNC
Build-In Floor | Mini Canal | MICL.00929018/ANA | 9 | 290 | 18 | 18 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.00929018/ANA
Build-In Floor | Mini Canal | MICL.00929018/DBL | 9 | 290 | 18 | 18 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.00929018/DBL
Build-In Floor | Mini Canal | MICL.00929018/DBN | 9 | 290 | 18 | 18 | 545 | 545 | 545 | 0.012976 | 212 | 0.0050476 | 621 | 0.014786 | 1.362 | A04 | MICL0.00929018/DBN
Build-In Floor | Mini Canal | MICL.00929018/DBR | 9 | 290 | 18 | 18 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.00929018/DBR
Build-In Floor | Mini Canal | MICL.00929018/DBV | 9 | 290 | 18 | 18 | 545 | 545 | 545 | 0.012976 | 212 | 0.0050476 | 621 | 0.014786 | 1.362 | A04 | MICL0.00929018/DBV
Build-In Floor | Mini Canal | MICL.00929018/DDB | 9 | 290 | 18 | 18 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.00929018/DDB
Build-In Floor | Mini Canal | MICL.00929018/DMN | 9 | 290 | 18 | 18 | 545 | 545 | 545 | 0.012976 | 212 | 0.0050476 | 621 | 0.014786 | 1.362 | A04 | MICL0.00929018/DMN
Build-In Floor | Mini Canal | MICL.00929018/DMV | 9 | 290 | 18 | 18 | 545 | 545 | 545 | 0.012976 | 212 | 0.0050476 | 621 | 0.014786 | 1.362 | A04 | MICL0.00929018/DMV
Build-In Floor | Mini Canal | MICL.00929018/DNA | 9 | 290 | 18 | 18 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.00929018/DNA
Build-In Floor | Mini Canal | MICL.00929018/DNC | 9 | 290 | 18 | 18 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.00929018/DNC
Build-In Floor | Mini Canal | MICL.00929018/DON | 9 | 290 | 18 | 18 | 545 | 545 | 545 | 0.012976 | 212 | 0.0050476 | 621 | 0.014786 | 1.362 | A04 | MICL0.00929018/DON
Build-In Floor | Mini Canal | MICL.00929018/DOV | 9 | 290 | 18 | 18 | 545 | 545 | 545 | 0.012976 | 212 | 0.0050476 | 621 | 0.014786 | 1.362 | A04 | MICL0.00929018/DOV
Build-In Floor | Mini Canal | MICL.00929018/RBL | 9 | 290 | 18 | 18 | 586 | 586 | 586 | 0.013952 | 228 | 0.0054286 | 667 | 0.015881 | 1.362 | A04 | MICL0.00929018/RBL
Build-In Floor | Mini Canal | MICL.00929018/RBN | 9 | 290 | 18 | 18 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.00929018/RBN
Build-In Floor | Mini Canal | MICL.00929018/RBR | 9 | 290 | 18 | 18 | 586 | 586 | 586 | 0.013952 | 228 | 0.0054286 | 667 | 0.015881 | 1.362 | A04 | MICL0.00929018/RBR
Build-In Floor | Mini Canal | MICL.00929018/RBV | 9 | 290 | 18 | 18 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.00929018/RBV
Build-In Floor | Mini Canal | MICL.00929018/RDB | 9 | 290 | 18 | 18 | 586 | 586 | 586 | 0.013952 | 228 | 0.0054286 | 667 | 0.015881 | 1.362 | A04 | MICL0.00929018/RDB
Build-In Floor | Mini Canal | MICL.00929018/RMN | 9 | 290 | 18 | 18 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.00929018/RMN
Build-In Floor | Mini Canal | MICL.00929018/RMV | 9 | 290 | 18 | 18 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.00929018/RMV
Build-In Floor | Mini Canal | MICL.00929018/RNA | 9 | 290 | 18 | 18 | 586 | 586 | 586 | 0.013952 | 228 | 0.0054286 | 667 | 0.015881 | 1.362 | A04 | MICL0.00929018/RNA
Build-In Floor | Mini Canal | MICL.00929018/RON | 9 | 290 | 18 | 18 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.00929018/RON
Build-In Floor | Mini Canal | MICL.00929018/ROV | 9 | 290 | 18 | 18 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.00929018/ROV
Build-In Floor | Mini Canal | MICL.00929018/RSS | 9 | 290 | 18 | 18 | 563 | 563 | 563 | 0.013405 | 219 | 0.0052143 | 641 | 0.015262 | 1.362 | A04 | MICL0.00929018/RSS
Build-In Floor | Mini Canal | MICL.00929018/SBL | 9 | 290 | 18 | 18 | 586 | 586 | 586 | 0.013952 | 228 | 0.0054286 | 667 | 0.015881 | 1.362 | A04 | MICL0.00929018/SBL
Build-In Floor | Mini Canal | MICL.00929018/SBR | 9 | 290 | 18 | 18 | 586 | 586 | 586 | 0.013952 | 228 | 0.0054286 | 667 | 0.015881 | 1.362 | A04 | MICL0.00929018/SBR
Build-In Floor | Mini Canal | MICL.00929018/SDB | 9 | 290 | 18 | 18 | 586 | 586 | 586 | 0.013952 | 228 | 0.0054286 | 667 | 0.015881 | 1.362 | A04 | MICL0.00929018/SDB
Build-In Floor | Mini Canal | MICL.00929018/SNA | 9 | 290 | 18 | 18 | 586 | 586 | 586 | 0.013952 | 228 | 0.0054286 | 667 | 0.015881 | 1.362 | A04 | MICL0.00929018/SNA
Build-In Floor | Mini Canal | MICL.00929018/SNC | 9 | 290 | 18 | 18 | 586 | 586 | 586 | 0.013952 | 228 | 0.0054286 | 667 | 0.015881 | 1.362 | A04 | MICL0.00929018/SNC
Build-In Floor | Mini Canal | MICL.00929026/ANA | 9 | 290 | 26 | 26 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.00929026/ANA
Build-In Floor | Mini Canal | MICL.00929026/DBL | 9 | 290 | 26 | 26 | 748 | 748 | 748 | 0.01781 | 291 | 0.0069286 | 852 | 0.020286 | 1.362 | A04 | MICL0.00929026/DBL
Build-In Floor | Mini Canal | MICL.00929026/DBN | 9 | 290 | 26 | 26 | 717 | 717 | 717 | 0.017071 | 279 | 0.0066429 | 817 | 0.019452 | 1.362 | A04 | MICL0.00929026/DBN
Build-In Floor | Mini Canal | MICL.00929026/DBR | 9 | 290 | 26 | 26 | 748 | 748 | 748 | 0.01781 | 291 | 0.0069286 | 852 | 0.020286 | 1.362 | A04 | MICL0.00929026/DBR
Build-In Floor | Mini Canal | MICL.00929026/DBV | 9 | 290 | 26 | 26 | 717 | 717 | 717 | 0.017071 | 279 | 0.0066429 | 817 | 0.019452 | 1.362 | A04 | MICL0.00929026/DBV
Build-In Floor | Mini Canal | MICL.00929026/DDB | 9 | 290 | 26 | 26 | 748 | 748 | 748 | 0.01781 | 291 | 0.0069286 | 852 | 0.020286 | 1.362 | A04 | MICL0.00929026/DDB
Build-In Floor | Mini Canal | MICL.00929026/DMN | 9 | 290 | 26 | 26 | 717 | 717 | 717 | 0.017071 | 279 | 0.0066429 | 817 | 0.019452 | 1.362 | A04 | MICL0.00929026/DMN
Build-In Floor | Mini Canal | MICL.00929026/DMV | 9 | 290 | 26 | 26 | 717 | 717 | 717 | 0.017071 | 279 | 0.0066429 | 817 | 0.019452 | 1.362 | A04 | MICL0.00929026/DMV
Build-In Floor | Mini Canal | MICL.00929026/DNA | 9 | 290 | 26 | 26 | 748 | 748 | 748 | 0.01781 | 291 | 0.0069286 | 852 | 0.020286 | 1.362 | A04 | MICL0.00929026/DNA
Build-In Floor | Mini Canal | MICL.00929026/DNC | 9 | 290 | 26 | 26 | 748 | 748 | 748 | 0.01781 | 291 | 0.0069286 | 852 | 0.020286 | 1.362 | A04 | MICL0.00929026/DNC
Build-In Floor | Mini Canal | MICL.00929026/DON | 9 | 290 | 26 | 26 | 717 | 717 | 717 | 0.017071 | 279 | 0.0066429 | 817 | 0.019452 | 1.362 | A04 | MICL0.00929026/DON
Build-In Floor | Mini Canal | MICL.00929026/DOV | 9 | 290 | 26 | 26 | 717 | 717 | 717 | 0.017071 | 279 | 0.0066429 | 817 | 0.019452 | 1.362 | A04 | MICL0.00929026/DOV
Build-In Floor | Mini Canal | MICL.00929026/PNC | 9 | 290 | 26 | 26 | 655 | 655 | 655 | 0.015595 | 255 | 0.0060714 | 746 | 0.017762 | 1.362 | A04 | MICL0.00929026/PNC
Build-In Floor | Mini Canal | MICL.00929026/RBL | 9 | 290 | 26 | 26 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.00929026/RBL
Build-In Floor | Mini Canal | MICL.00929026/RBN | 9 | 290 | 26 | 26 | 748 | 748 | 748 | 0.01781 | 291 | 0.0069286 | 852 | 0.020286 | 1.362 | A04 | MICL0.00929026/RBN
Build-In Floor | Mini Canal | MICL.00929026/RBR | 9 | 290 | 26 | 26 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.00929026/RBR
Build-In Floor | Mini Canal | MICL.00929026/RBV | 9 | 290 | 26 | 26 | 748 | 748 | 748 | 0.01781 | 291 | 0.0069286 | 852 | 0.020286 | 1.362 | A04 | MICL0.00929026/RBV
Build-In Floor | Mini Canal | MICL.00929026/RDB | 9 | 290 | 26 | 26 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.00929026/RDB
Build-In Floor | Mini Canal | MICL.00929026/RMN | 9 | 290 | 26 | 26 | 748 | 748 | 748 | 0.01781 | 291 | 0.0069286 | 852 | 0.020286 | 1.362 | A04 | MICL0.00929026/RMN
Build-In Floor | Mini Canal | MICL.00929026/RMV | 9 | 290 | 26 | 26 | 748 | 748 | 748 | 0.01781 | 291 | 0.0069286 | 852 | 0.020286 | 1.362 | A04 | MICL0.00929026/RMV
Build-In Floor | Mini Canal | MICL.00929026/RNA | 9 | 290 | 26 | 26 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.00929026/RNA
Build-In Floor | Mini Canal | MICL.00929026/RON | 9 | 290 | 26 | 26 | 748 | 748 | 748 | 0.01781 | 291 | 0.0069286 | 852 | 0.020286 | 1.362 | A04 | MICL0.00929026/RON
Build-In Floor | Mini Canal | MICL.00929026/ROV | 9 | 290 | 26 | 26 | 748 | 748 | 748 | 0.01781 | 291 | 0.0069286 | 852 | 0.020286 | 1.362 | A04 | MICL0.00929026/ROV
Build-In Floor | Mini Canal | MICL.00929026/RSS | 9 | 290 | 26 | 26 | 740 | 740 | 740 | 0.017619 | 288 | 0.0068571 | 843 | 0.020071 | 1.362 | A04 | MICL0.00929026/RSS
Build-In Floor | Mini Canal | MICL.00929026/SBL | 9 | 290 | 26 | 26 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.00929026/SBL
Build-In Floor | Mini Canal | MICL.00929026/SBR | 9 | 290 | 26 | 26 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.00929026/SBR
Build-In Floor | Mini Canal | MICL.00929026/SDB | 9 | 290 | 26 | 26 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.00929026/SDB
Build-In Floor | Mini Canal | MICL.00929026/SNA | 9 | 290 | 26 | 26 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.00929026/SNA
Build-In Floor | Mini Canal | MICL.00929026/SNC | 9 | 290 | 26 | 26 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.00929026/SNC
Build-In Floor | Mini Canal | MICL.00929034/ANA | 9 | 290 | 34 | 34 | 750 | 750 | 750 | 0.017857 | 292 | 0.0069524 | 854 | 0.020333 | 1.362 | A04 | MICL0.00929034/ANA
Build-In Floor | Mini Canal | MICL.00929034/DBL | 9 | 290 | 34 | 34 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00929034/DBL
Build-In Floor | Mini Canal | MICL.00929034/DBN | 9 | 290 | 34 | 34 | 930 | 930 | 930 | 0.022143 | 362 | 0.008619 | 1059 | 0.025214 | 1.362 | A04 | MICL0.00929034/DBN
Build-In Floor | Mini Canal | MICL.00929034/DBR | 9 | 290 | 34 | 34 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00929034/DBR
Build-In Floor | Mini Canal | MICL.00929034/DBV | 9 | 290 | 34 | 34 | 930 | 930 | 930 | 0.022143 | 362 | 0.008619 | 1059 | 0.025214 | 1.362 | A04 | MICL0.00929034/DBV
Build-In Floor | Mini Canal | MICL.00929034/DDB | 9 | 290 | 34 | 34 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00929034/DDB
Build-In Floor | Mini Canal | MICL.00929034/DMN | 9 | 290 | 34 | 34 | 930 | 930 | 930 | 0.022143 | 362 | 0.008619 | 1059 | 0.025214 | 1.362 | A04 | MICL0.00929034/DMN
Build-In Floor | Mini Canal | MICL.00929034/DMV | 9 | 290 | 34 | 34 | 930 | 930 | 930 | 0.022143 | 362 | 0.008619 | 1059 | 0.025214 | 1.362 | A04 | MICL0.00929034/DMV
Build-In Floor | Mini Canal | MICL.00929034/DNA | 9 | 290 | 34 | 34 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00929034/DNA
Build-In Floor | Mini Canal | MICL.00929034/DNC | 9 | 290 | 34 | 34 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00929034/DNC
Build-In Floor | Mini Canal | MICL.00929034/DON | 9 | 290 | 34 | 34 | 930 | 930 | 930 | 0.022143 | 362 | 0.008619 | 1059 | 0.025214 | 1.362 | A04 | MICL0.00929034/DON
Build-In Floor | Mini Canal | MICL.00929034/DOV | 9 | 290 | 34 | 34 | 930 | 930 | 930 | 0.022143 | 362 | 0.008619 | 1059 | 0.025214 | 1.362 | A04 | MICL0.00929034/DOV
Build-In Floor | Mini Canal | MICL.00929034/PNC | 9 | 290 | 34 | 34 | 850 | 850 | 850 | 0.020238 | 331 | 0.007881 | 968 | 0.023048 | 1.362 | A04 | MICL0.00929034/PNC
Build-In Floor | Mini Canal | MICL.00929034/RBL | 9 | 290 | 34 | 34 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00929034/RBL
Build-In Floor | Mini Canal | MICL.00929034/RBN | 9 | 290 | 34 | 34 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00929034/RBN
Build-In Floor | Mini Canal | MICL.00929034/RBR | 9 | 290 | 34 | 34 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00929034/RBR
Build-In Floor | Mini Canal | MICL.00929034/RBV | 9 | 290 | 34 | 34 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00929034/RBV
Build-In Floor | Mini Canal | MICL.00929034/RDB | 9 | 290 | 34 | 34 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00929034/RDB
Build-In Floor | Mini Canal | MICL.00929034/RMN | 9 | 290 | 34 | 34 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00929034/RMN
Build-In Floor | Mini Canal | MICL.00929034/RMV | 9 | 290 | 34 | 34 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00929034/RMV
Build-In Floor | Mini Canal | MICL.00929034/RNA | 9 | 290 | 34 | 34 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00929034/RNA
Build-In Floor | Mini Canal | MICL.00929034/RON | 9 | 290 | 34 | 34 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00929034/RON
Build-In Floor | Mini Canal | MICL.00929034/ROV | 9 | 290 | 34 | 34 | 970 | 970 | 970 | 0.023095 | 377 | 0.0089762 | 1105 | 0.02631 | 1.362 | A04 | MICL0.00929034/ROV
Build-In Floor | Mini Canal | MICL.00929034/RSS | 9 | 290 | 34 | 34 | 960 | 960 | 960 | 0.022857 | 373 | 0.008881 | 1093 | 0.026024 | 1.362 | A04 | MICL0.00929034/RSS
Build-In Floor | Mini Canal | MICL.00929034/SBL | 9 | 290 | 34 | 34 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00929034/SBL
Build-In Floor | Mini Canal | MICL.00929034/SBR | 9 | 290 | 34 | 34 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00929034/SBR
Build-In Floor | Mini Canal | MICL.00929034/SDB | 9 | 290 | 34 | 34 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00929034/SDB
Build-In Floor | Mini Canal | MICL.00929034/SNA | 9 | 290 | 34 | 34 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00929034/SNA
Build-In Floor | Mini Canal | MICL.00929034/SNC | 9 | 290 | 34 | 34 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.00929034/SNC
Build-In Floor | Mini Canal | MICL.00929042/ANA | 9 | 290 | 42 | 42 | 1083 | 1083 | 1083 | 0.025786 | 421 | 0.010024 | 1234 | 0.029381 | 1.362 | A04 | MICL0.00929042/ANA
Build-In Floor | Mini Canal | MICL.00929042/DBL | 9 | 290 | 42 | 42 | 1401 | 1401 | 1401 | 0.033357 | 545 | 0.012976 | 1596 | 0.038 | 1.362 | A04 | MICL0.00929042/DBL
Build-In Floor | Mini Canal | MICL.00929042/DBN | 9 | 290 | 42 | 42 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00929042/DBN
Build-In Floor | Mini Canal | MICL.00929042/DBR | 9 | 290 | 42 | 42 | 1401 | 1401 | 1401 | 0.033357 | 545 | 0.012976 | 1596 | 0.038 | 1.362 | A04 | MICL0.00929042/DBR
Build-In Floor | Mini Canal | MICL.00929042/DBV | 9 | 290 | 42 | 42 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00929042/DBV
Build-In Floor | Mini Canal | MICL.00929042/DDB | 9 | 290 | 42 | 42 | 1401 | 1401 | 1401 | 0.033357 | 545 | 0.012976 | 1596 | 0.038 | 1.362 | A04 | MICL0.00929042/DDB
Build-In Floor | Mini Canal | MICL.00929042/DMN | 9 | 290 | 42 | 42 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00929042/DMN
Build-In Floor | Mini Canal | MICL.00929042/DMV | 9 | 290 | 42 | 42 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00929042/DMV
Build-In Floor | Mini Canal | MICL.00929042/DNA | 9 | 290 | 42 | 42 | 1401 | 1401 | 1401 | 0.033357 | 545 | 0.012976 | 1596 | 0.038 | 1.362 | A04 | MICL0.00929042/DNA
Build-In Floor | Mini Canal | MICL.00929042/DNC | 9 | 290 | 42 | 42 | 1401 | 1401 | 1401 | 0.033357 | 545 | 0.012976 | 1596 | 0.038 | 1.362 | A04 | MICL0.00929042/DNC
Build-In Floor | Mini Canal | MICL.00929042/DON | 9 | 290 | 42 | 42 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00929042/DON
Build-In Floor | Mini Canal | MICL.00929042/DOV | 9 | 290 | 42 | 42 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00929042/DOV
Build-In Floor | Mini Canal | MICL.00929042/PNC | 9 | 290 | 42 | 42 | 1227 | 1227 | 1227 | 0.029214 | 477 | 0.011357 | 1398 | 0.033286 | 1.362 | A04 | MICL0.00929042/PNC
Build-In Floor | Mini Canal | MICL.00929042/RBL | 9 | 290 | 42 | 42 | 1444 | 1444 | 1444 | 0.034381 | 562 | 0.013381 | 1645 | 0.039167 | 1.362 | A04 | MICL0.00929042/RBL
Build-In Floor | Mini Canal | MICL.00929042/RBN | 9 | 290 | 42 | 42 | 1401 | 1401 | 1401 | 0.033357 | 545 | 0.012976 | 1596 | 0.038 | 1.362 | A04 | MICL0.00929042/RBN
Build-In Floor | Mini Canal | MICL.00929042/RBR | 9 | 290 | 42 | 42 | 1444 | 1444 | 1444 | 0.034381 | 562 | 0.013381 | 1645 | 0.039167 | 1.362 | A04 | MICL0.00929042/RBR
Build-In Floor | Mini Canal | MICL.00929042/RBV | 9 | 290 | 42 | 42 | 1401 | 1401 | 1401 | 0.033357 | 545 | 0.012976 | 1596 | 0.038 | 1.362 | A04 | MICL0.00929042/RBV
Build-In Floor | Mini Canal | MICL.00929042/RDB | 9 | 290 | 42 | 42 | 1444 | 1444 | 1444 | 0.034381 | 562 | 0.013381 | 1645 | 0.039167 | 1.362 | A04 | MICL0.00929042/RDB
Build-In Floor | Mini Canal | MICL.00929042/RMN | 9 | 290 | 42 | 42 | 1401 | 1401 | 1401 | 0.033357 | 545 | 0.012976 | 1596 | 0.038 | 1.362 | A04 | MICL0.00929042/RMN
Build-In Floor | Mini Canal | MICL.00929042/RMV | 9 | 290 | 42 | 42 | 1401 | 1401 | 1401 | 0.033357 | 545 | 0.012976 | 1596 | 0.038 | 1.362 | A04 | MICL0.00929042/RMV
Build-In Floor | Mini Canal | MICL.00929042/RNA | 9 | 290 | 42 | 42 | 1444 | 1444 | 1444 | 0.034381 | 562 | 0.013381 | 1645 | 0.039167 | 1.362 | A04 | MICL0.00929042/RNA
Build-In Floor | Mini Canal | MICL.00929042/RON | 9 | 290 | 42 | 42 | 1401 | 1401 | 1401 | 0.033357 | 545 | 0.012976 | 1596 | 0.038 | 1.362 | A04 | MICL0.00929042/RON
Build-In Floor | Mini Canal | MICL.00929042/ROV | 9 | 290 | 42 | 42 | 1401 | 1401 | 1401 | 0.033357 | 545 | 0.012976 | 1596 | 0.038 | 1.362 | A04 | MICL0.00929042/ROV
Build-In Floor | Mini Canal | MICL.00929042/RSS | 9 | 290 | 42 | 42 | 1386 | 1386 | 1386 | 0.033 | 539 | 0.012833 | 1579 | 0.037595 | 1.362 | A04 | MICL0.00929042/RSS
Build-In Floor | Mini Canal | MICL.00929042/SBL | 9 | 290 | 42 | 42 | 1444 | 1444 | 1444 | 0.034381 | 562 | 0.013381 | 1645 | 0.039167 | 1.362 | A04 | MICL0.00929042/SBL
Build-In Floor | Mini Canal | MICL.00929042/SBR | 9 | 290 | 42 | 42 | 1444 | 1444 | 1444 | 0.034381 | 562 | 0.013381 | 1645 | 0.039167 | 1.362 | A04 | MICL0.00929042/SBR
Build-In Floor | Mini Canal | MICL.00929042/SDB | 9 | 290 | 42 | 42 | 1444 | 1444 | 1444 | 0.034381 | 562 | 0.013381 | 1645 | 0.039167 | 1.362 | A04 | MICL0.00929042/SDB
Build-In Floor | Mini Canal | MICL.00929042/SNA | 9 | 290 | 42 | 42 | 1444 | 1444 | 1444 | 0.034381 | 562 | 0.013381 | 1645 | 0.039167 | 1.362 | A04 | MICL0.00929042/SNA
Build-In Floor | Mini Canal | MICL.00929042/SNC | 9 | 290 | 42 | 42 | 1444 | 1444 | 1444 | 0.034381 | 562 | 0.013381 | 1645 | 0.039167 | 1.362 | A04 | MICL0.00929042/SNC
Build-In Floor | Mini Canal | MICL.00931014/ANA | 9 | 310 | 14 | 14 | 400 | 400 | 400 | 0.0095238 | 156 | 0.0037143 | 456 | 0.010857 | 1.362 | A04 | MICL0.00931014/ANA
Build-In Floor | Mini Canal | MICL.00931014/DBL | 9 | 310 | 14 | 14 | 517 | 517 | 517 | 0.01231 | 201 | 0.0047857 | 589 | 0.014024 | 1.362 | A04 | MICL0.00931014/DBL
Build-In Floor | Mini Canal | MICL.00931014/DBN | 9 | 310 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00931014/DBN
Build-In Floor | Mini Canal | MICL.00931014/DBR | 9 | 310 | 14 | 14 | 517 | 517 | 517 | 0.01231 | 201 | 0.0047857 | 589 | 0.014024 | 1.362 | A04 | MICL0.00931014/DBR
Build-In Floor | Mini Canal | MICL.00931014/DBV | 9 | 310 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00931014/DBV
Build-In Floor | Mini Canal | MICL.00931014/DDB | 9 | 310 | 14 | 14 | 517 | 517 | 517 | 0.01231 | 201 | 0.0047857 | 589 | 0.014024 | 1.362 | A04 | MICL0.00931014/DDB
Build-In Floor | Mini Canal | MICL.00931014/DMN | 9 | 310 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00931014/DMN
Build-In Floor | Mini Canal | MICL.00931014/DMV | 9 | 310 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00931014/DMV
Build-In Floor | Mini Canal | MICL.00931014/DNA | 9 | 310 | 14 | 14 | 517 | 517 | 517 | 0.01231 | 201 | 0.0047857 | 589 | 0.014024 | 1.362 | A04 | MICL0.00931014/DNA
Build-In Floor | Mini Canal | MICL.00931014/DNC | 9 | 310 | 14 | 14 | 517 | 517 | 517 | 0.01231 | 201 | 0.0047857 | 589 | 0.014024 | 1.362 | A04 | MICL0.00931014/DNC
Build-In Floor | Mini Canal | MICL.00931014/DON | 9 | 310 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00931014/DON
Build-In Floor | Mini Canal | MICL.00931014/DOV | 9 | 310 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.00931014/DOV
Build-In Floor | Mini Canal | MICL.00931014/RBL | 9 | 310 | 14 | 14 | 533 | 533 | 533 | 0.01269 | 207 | 0.0049286 | 607 | 0.014452 | 1.362 | A04 | MICL0.00931014/RBL
Build-In Floor | Mini Canal | MICL.00931014/RBN | 9 | 310 | 14 | 14 | 517 | 517 | 517 | 0.01231 | 201 | 0.0047857 | 589 | 0.014024 | 1.362 | A04 | MICL0.00931014/RBN
Build-In Floor | Mini Canal | MICL.00931014/RBR | 9 | 310 | 14 | 14 | 533 | 533 | 533 | 0.01269 | 207 | 0.0049286 | 607 | 0.014452 | 1.362 | A04 | MICL0.00931014/RBR
Build-In Floor | Mini Canal | MICL.00931014/RBV | 9 | 310 | 14 | 14 | 517 | 517 | 517 | 0.01231 | 201 | 0.0047857 | 589 | 0.014024 | 1.362 | A04 | MICL0.00931014/RBV
Build-In Floor | Mini Canal | MICL.00931014/RDB | 9 | 310 | 14 | 14 | 533 | 533 | 533 | 0.01269 | 207 | 0.0049286 | 607 | 0.014452 | 1.362 | A04 | MICL0.00931014/RDB
Build-In Floor | Mini Canal | MICL.00931014/RMN | 9 | 310 | 14 | 14 | 517 | 517 | 517 | 0.01231 | 201 | 0.0047857 | 589 | 0.014024 | 1.362 | A04 | MICL0.00931014/RMN
Build-In Floor | Mini Canal | MICL.00931014/RMV | 9 | 310 | 14 | 14 | 517 | 517 | 517 | 0.01231 | 201 | 0.0047857 | 589 | 0.014024 | 1.362 | A04 | MICL0.00931014/RMV
Build-In Floor | Mini Canal | MICL.00931014/RNA | 9 | 310 | 14 | 14 | 533 | 533 | 533 | 0.01269 | 207 | 0.0049286 | 607 | 0.014452 | 1.362 | A04 | MICL0.00931014/RNA
Build-In Floor | Mini Canal | MICL.00931014/RON | 9 | 310 | 14 | 14 | 517 | 517 | 517 | 0.01231 | 201 | 0.0047857 | 589 | 0.014024 | 1.362 | A04 | MICL0.00931014/RON
Build-In Floor | Mini Canal | MICL.00931014/ROV | 9 | 310 | 14 | 14 | 517 | 517 | 517 | 0.01231 | 201 | 0.0047857 | 589 | 0.014024 | 1.362 | A04 | MICL0.00931014/ROV
Build-In Floor | Mini Canal | MICL.00931014/RSS | 9 | 310 | 14 | 14 | 512 | 512 | 512 | 0.01219 | 199 | 0.0047381 | 583 | 0.013881 | 1.362 | A04 | MICL0.00931014/RSS
Build-In Floor | Mini Canal | MICL.00931014/SBL | 9 | 310 | 14 | 14 | 533 | 533 | 533 | 0.01269 | 207 | 0.0049286 | 607 | 0.014452 | 1.362 | A04 | MICL0.00931014/SBL
Build-In Floor | Mini Canal | MICL.00931014/SBR | 9 | 310 | 14 | 14 | 533 | 533 | 533 | 0.01269 | 207 | 0.0049286 | 607 | 0.014452 | 1.362 | A04 | MICL0.00931014/SBR
Build-In Floor | Mini Canal | MICL.00931014/SDB | 9 | 310 | 14 | 14 | 533 | 533 | 533 | 0.01269 | 207 | 0.0049286 | 607 | 0.014452 | 1.362 | A04 | MICL0.00931014/SDB
Build-In Floor | Mini Canal | MICL.00931014/SNA | 9 | 310 | 14 | 14 | 533 | 533 | 533 | 0.01269 | 207 | 0.0049286 | 607 | 0.014452 | 1.362 | A04 | MICL0.00931014/SNA
Build-In Floor | Mini Canal | MICL.00931014/SNC | 9 | 310 | 14 | 14 | 533 | 533 | 533 | 0.01269 | 207 | 0.0049286 | 607 | 0.014452 | 1.362 | A04 | MICL0.00931014/SNC
Build-In Floor | Mini Canal | MICL.00931018/ANA | 9 | 310 | 18 | 18 | 473 | 473 | 473 | 0.011262 | 184 | 0.004381 | 539 | 0.012833 | 1.362 | A04 | MICL0.00931018/ANA
Build-In Floor | Mini Canal | MICL.00931018/DBL | 9 | 310 | 18 | 18 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.00931018/DBL
Build-In Floor | Mini Canal | MICL.00931018/DBN | 9 | 310 | 18 | 18 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.00931018/DBN
Build-In Floor | Mini Canal | MICL.00931018/DBR | 9 | 310 | 18 | 18 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.00931018/DBR
Build-In Floor | Mini Canal | MICL.00931018/DBV | 9 | 310 | 18 | 18 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.00931018/DBV
Build-In Floor | Mini Canal | MICL.00931018/DDB | 9 | 310 | 18 | 18 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.00931018/DDB
Build-In Floor | Mini Canal | MICL.00931018/DMN | 9 | 310 | 18 | 18 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.00931018/DMN
Build-In Floor | Mini Canal | MICL.00931018/DMV | 9 | 310 | 18 | 18 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.00931018/DMV
Build-In Floor | Mini Canal | MICL.00931018/DNA | 9 | 310 | 18 | 18 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.00931018/DNA
Build-In Floor | Mini Canal | MICL.00931018/DNC | 9 | 310 | 18 | 18 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.00931018/DNC
Build-In Floor | Mini Canal | MICL.00931018/DON | 9 | 310 | 18 | 18 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.00931018/DON
Build-In Floor | Mini Canal | MICL.00931018/DOV | 9 | 310 | 18 | 18 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.00931018/DOV
Build-In Floor | Mini Canal | MICL.00931018/RBL | 9 | 310 | 18 | 18 | 631 | 631 | 631 | 0.015024 | 245 | 0.0058333 | 719 | 0.017119 | 1.362 | A04 | MICL0.00931018/RBL
Build-In Floor | Mini Canal | MICL.00931018/RBN | 9 | 310 | 18 | 18 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.00931018/RBN
Build-In Floor | Mini Canal | MICL.00931018/RBR | 9 | 310 | 18 | 18 | 631 | 631 | 631 | 0.015024 | 245 | 0.0058333 | 719 | 0.017119 | 1.362 | A04 | MICL0.00931018/RBR
Build-In Floor | Mini Canal | MICL.00931018/RBV | 9 | 310 | 18 | 18 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.00931018/RBV
Build-In Floor | Mini Canal | MICL.00931018/RDB | 9 | 310 | 18 | 18 | 631 | 631 | 631 | 0.015024 | 245 | 0.0058333 | 719 | 0.017119 | 1.362 | A04 | MICL0.00931018/RDB
Build-In Floor | Mini Canal | MICL.00931018/RMN | 9 | 310 | 18 | 18 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.00931018/RMN
Build-In Floor | Mini Canal | MICL.00931018/RMV | 9 | 310 | 18 | 18 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.00931018/RMV
Build-In Floor | Mini Canal | MICL.00931018/RNA | 9 | 310 | 18 | 18 | 631 | 631 | 631 | 0.015024 | 245 | 0.0058333 | 719 | 0.017119 | 1.362 | A04 | MICL0.00931018/RNA
Build-In Floor | Mini Canal | MICL.00931018/RON | 9 | 310 | 18 | 18 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.00931018/RON
Build-In Floor | Mini Canal | MICL.00931018/ROV | 9 | 310 | 18 | 18 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.00931018/ROV
Build-In Floor | Mini Canal | MICL.00931018/RSS | 9 | 310 | 18 | 18 | 606 | 606 | 606 | 0.014429 | 236 | 0.005619 | 690 | 0.016429 | 1.362 | A04 | MICL0.00931018/RSS
Build-In Floor | Mini Canal | MICL.00931018/SBL | 9 | 310 | 18 | 18 | 631 | 631 | 631 | 0.015024 | 245 | 0.0058333 | 719 | 0.017119 | 1.362 | A04 | MICL0.00931018/SBL
Build-In Floor | Mini Canal | MICL.00931018/SBR | 9 | 310 | 18 | 18 | 631 | 631 | 631 | 0.015024 | 245 | 0.0058333 | 719 | 0.017119 | 1.362 | A04 | MICL0.00931018/SBR
Build-In Floor | Mini Canal | MICL.00931018/SDB | 9 | 310 | 18 | 18 | 631 | 631 | 631 | 0.015024 | 245 | 0.0058333 | 719 | 0.017119 | 1.362 | A04 | MICL0.00931018/SDB
Build-In Floor | Mini Canal | MICL.00931018/SNA | 9 | 310 | 18 | 18 | 631 | 631 | 631 | 0.015024 | 245 | 0.0058333 | 719 | 0.017119 | 1.362 | A04 | MICL0.00931018/SNA
Build-In Floor | Mini Canal | MICL.00931018/SNC | 9 | 310 | 18 | 18 | 631 | 631 | 631 | 0.015024 | 245 | 0.0058333 | 719 | 0.017119 | 1.362 | A04 | MICL0.00931018/SNC
Build-In Floor | Mini Canal | MICL.00931026/ANA | 9 | 310 | 26 | 26 | 623 | 623 | 623 | 0.014833 | 242 | 0.0057619 | 710 | 0.016905 | 1.362 | A04 | MICL0.00931026/ANA
Build-In Floor | Mini Canal | MICL.00931026/DBL | 9 | 310 | 26 | 26 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.00931026/DBL
Build-In Floor | Mini Canal | MICL.00931026/DBN | 9 | 310 | 26 | 26 | 772 | 772 | 772 | 0.018381 | 300 | 0.0071429 | 879 | 0.020929 | 1.362 | A04 | MICL0.00931026/DBN
Build-In Floor | Mini Canal | MICL.00931026/DBR | 9 | 310 | 26 | 26 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.00931026/DBR
Build-In Floor | Mini Canal | MICL.00931026/DBV | 9 | 310 | 26 | 26 | 772 | 772 | 772 | 0.018381 | 300 | 0.0071429 | 879 | 0.020929 | 1.362 | A04 | MICL0.00931026/DBV
Build-In Floor | Mini Canal | MICL.00931026/DDB | 9 | 310 | 26 | 26 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.00931026/DDB
Build-In Floor | Mini Canal | MICL.00931026/DMN | 9 | 310 | 26 | 26 | 772 | 772 | 772 | 0.018381 | 300 | 0.0071429 | 879 | 0.020929 | 1.362 | A04 | MICL0.00931026/DMN
Build-In Floor | Mini Canal | MICL.00931026/DMV | 9 | 310 | 26 | 26 | 772 | 772 | 772 | 0.018381 | 300 | 0.0071429 | 879 | 0.020929 | 1.362 | A04 | MICL0.00931026/DMV
Build-In Floor | Mini Canal | MICL.00931026/DNA | 9 | 310 | 26 | 26 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.00931026/DNA
Build-In Floor | Mini Canal | MICL.00931026/DNC | 9 | 310 | 26 | 26 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.00931026/DNC
Build-In Floor | Mini Canal | MICL.00931026/DON | 9 | 310 | 26 | 26 | 772 | 772 | 772 | 0.018381 | 300 | 0.0071429 | 879 | 0.020929 | 1.362 | A04 | MICL0.00931026/DON
Build-In Floor | Mini Canal | MICL.00931026/DOV | 9 | 310 | 26 | 26 | 772 | 772 | 772 | 0.018381 | 300 | 0.0071429 | 879 | 0.020929 | 1.362 | A04 | MICL0.00931026/DOV
Build-In Floor | Mini Canal | MICL.00931026/PNC | 9 | 310 | 26 | 26 | 706 | 706 | 706 | 0.01681 | 275 | 0.0065476 | 804 | 0.019143 | 1.362 | A04 | MICL0.00931026/PNC
Build-In Floor | Mini Canal | MICL.00931026/RBL | 9 | 310 | 26 | 26 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00931026/RBL
Build-In Floor | Mini Canal | MICL.00931026/RBN | 9 | 310 | 26 | 26 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.00931026/RBN
Build-In Floor | Mini Canal | MICL.00931026/RBR | 9 | 310 | 26 | 26 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00931026/RBR
Build-In Floor | Mini Canal | MICL.00931026/RBV | 9 | 310 | 26 | 26 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.00931026/RBV
Build-In Floor | Mini Canal | MICL.00931026/RDB | 9 | 310 | 26 | 26 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00931026/RDB
Build-In Floor | Mini Canal | MICL.00931026/RMN | 9 | 310 | 26 | 26 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.00931026/RMN
Build-In Floor | Mini Canal | MICL.00931026/RMV | 9 | 310 | 26 | 26 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.00931026/RMV
Build-In Floor | Mini Canal | MICL.00931026/RNA | 9 | 310 | 26 | 26 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00931026/RNA
Build-In Floor | Mini Canal | MICL.00931026/RON | 9 | 310 | 26 | 26 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.00931026/RON
Build-In Floor | Mini Canal | MICL.00931026/ROV | 9 | 310 | 26 | 26 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.00931026/ROV
Build-In Floor | Mini Canal | MICL.00931026/RSS | 9 | 310 | 26 | 26 | 797 | 797 | 797 | 0.018976 | 310 | 0.007381 | 908 | 0.021619 | 1.362 | A04 | MICL0.00931026/RSS
Build-In Floor | Mini Canal | MICL.00931026/SBL | 9 | 310 | 26 | 26 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00931026/SBL
Build-In Floor | Mini Canal | MICL.00931026/SBR | 9 | 310 | 26 | 26 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00931026/SBR
Build-In Floor | Mini Canal | MICL.00931026/SDB | 9 | 310 | 26 | 26 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00931026/SDB
Build-In Floor | Mini Canal | MICL.00931026/SNA | 9 | 310 | 26 | 26 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00931026/SNA
Build-In Floor | Mini Canal | MICL.00931026/SNC | 9 | 310 | 26 | 26 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00931026/SNC
Build-In Floor | Mini Canal | MICL.00931034/ANA | 9 | 310 | 34 | 34 | 807 | 807 | 807 | 0.019214 | 314 | 0.0074762 | 919 | 0.021881 | 1.362 | A04 | MICL0.00931034/ANA
Build-In Floor | Mini Canal | MICL.00931034/DBL | 9 | 310 | 34 | 34 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.00931034/DBL
Build-In Floor | Mini Canal | MICL.00931034/DBN | 9 | 310 | 34 | 34 | 1001 | 1001 | 1001 | 0.023833 | 389 | 0.0092619 | 1140 | 0.027143 | 1.362 | A04 | MICL0.00931034/DBN
Build-In Floor | Mini Canal | MICL.00931034/DBR | 9 | 310 | 34 | 34 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.00931034/DBR
Build-In Floor | Mini Canal | MICL.00931034/DBV | 9 | 310 | 34 | 34 | 1001 | 1001 | 1001 | 0.023833 | 389 | 0.0092619 | 1140 | 0.027143 | 1.362 | A04 | MICL0.00931034/DBV
Build-In Floor | Mini Canal | MICL.00931034/DDB | 9 | 310 | 34 | 34 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.00931034/DDB
Build-In Floor | Mini Canal | MICL.00931034/DMN | 9 | 310 | 34 | 34 | 1001 | 1001 | 1001 | 0.023833 | 389 | 0.0092619 | 1140 | 0.027143 | 1.362 | A04 | MICL0.00931034/DMN
Build-In Floor | Mini Canal | MICL.00931034/DMV | 9 | 310 | 34 | 34 | 1001 | 1001 | 1001 | 0.023833 | 389 | 0.0092619 | 1140 | 0.027143 | 1.362 | A04 | MICL0.00931034/DMV
Build-In Floor | Mini Canal | MICL.00931034/DNA | 9 | 310 | 34 | 34 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.00931034/DNA
Build-In Floor | Mini Canal | MICL.00931034/DNC | 9 | 310 | 34 | 34 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.00931034/DNC
Build-In Floor | Mini Canal | MICL.00931034/DON | 9 | 310 | 34 | 34 | 1001 | 1001 | 1001 | 0.023833 | 389 | 0.0092619 | 1140 | 0.027143 | 1.362 | A04 | MICL0.00931034/DON
Build-In Floor | Mini Canal | MICL.00931034/DOV | 9 | 310 | 34 | 34 | 1001 | 1001 | 1001 | 0.023833 | 389 | 0.0092619 | 1140 | 0.027143 | 1.362 | A04 | MICL0.00931034/DOV
Build-In Floor | Mini Canal | MICL.00931034/PNC | 9 | 310 | 34 | 34 | 915 | 915 | 915 | 0.021786 | 356 | 0.0084762 | 1042 | 0.02481 | 1.362 | A04 | MICL0.00931034/PNC
Build-In Floor | Mini Canal | MICL.00931034/RBL | 9 | 310 | 34 | 34 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.00931034/RBL
Build-In Floor | Mini Canal | MICL.00931034/RBN | 9 | 310 | 34 | 34 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.00931034/RBN
Build-In Floor | Mini Canal | MICL.00931034/RBR | 9 | 310 | 34 | 34 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.00931034/RBR
Build-In Floor | Mini Canal | MICL.00931034/RBV | 9 | 310 | 34 | 34 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.00931034/RBV
Build-In Floor | Mini Canal | MICL.00931034/RDB | 9 | 310 | 34 | 34 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.00931034/RDB
Build-In Floor | Mini Canal | MICL.00931034/RMN | 9 | 310 | 34 | 34 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.00931034/RMN
Build-In Floor | Mini Canal | MICL.00931034/RMV | 9 | 310 | 34 | 34 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.00931034/RMV
Build-In Floor | Mini Canal | MICL.00931034/RNA | 9 | 310 | 34 | 34 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.00931034/RNA
Build-In Floor | Mini Canal | MICL.00931034/RON | 9 | 310 | 34 | 34 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.00931034/RON
Build-In Floor | Mini Canal | MICL.00931034/ROV | 9 | 310 | 34 | 34 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.00931034/ROV
Build-In Floor | Mini Canal | MICL.00931034/RSS | 9 | 310 | 34 | 34 | 1033 | 1033 | 1033 | 0.024595 | 402 | 0.0095714 | 1177 | 0.028024 | 1.362 | A04 | MICL0.00931034/RSS
Build-In Floor | Mini Canal | MICL.00931034/SBL | 9 | 310 | 34 | 34 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.00931034/SBL
Build-In Floor | Mini Canal | MICL.00931034/SBR | 9 | 310 | 34 | 34 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.00931034/SBR
Build-In Floor | Mini Canal | MICL.00931034/SDB | 9 | 310 | 34 | 34 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.00931034/SDB
Build-In Floor | Mini Canal | MICL.00931034/SNA | 9 | 310 | 34 | 34 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.00931034/SNA
Build-In Floor | Mini Canal | MICL.00931034/SNC | 9 | 310 | 34 | 34 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.00931034/SNC
Build-In Floor | Mini Canal | MICL.00931042/ANA | 9 | 310 | 42 | 42 | 1166 | 1166 | 1166 | 0.027762 | 454 | 0.01081 | 1328 | 0.031619 | 1.362 | A04 | MICL0.00931042/ANA
Build-In Floor | Mini Canal | MICL.00931042/DBL | 9 | 310 | 42 | 42 | 1508 | 1508 | 1508 | 0.035905 | 587 | 0.013976 | 1718 | 0.040905 | 1.362 | A04 | MICL0.00931042/DBL
Build-In Floor | Mini Canal | MICL.00931042/DBN | 9 | 310 | 42 | 42 | 1446 | 1446 | 1446 | 0.034429 | 562 | 0.013381 | 1647 | 0.039214 | 1.362 | A04 | MICL0.00931042/DBN
Build-In Floor | Mini Canal | MICL.00931042/DBR | 9 | 310 | 42 | 42 | 1508 | 1508 | 1508 | 0.035905 | 587 | 0.013976 | 1718 | 0.040905 | 1.362 | A04 | MICL0.00931042/DBR
Build-In Floor | Mini Canal | MICL.00931042/DBV | 9 | 310 | 42 | 42 | 1446 | 1446 | 1446 | 0.034429 | 562 | 0.013381 | 1647 | 0.039214 | 1.362 | A04 | MICL0.00931042/DBV
Build-In Floor | Mini Canal | MICL.00931042/DDB | 9 | 310 | 42 | 42 | 1508 | 1508 | 1508 | 0.035905 | 587 | 0.013976 | 1718 | 0.040905 | 1.362 | A04 | MICL0.00931042/DDB
Build-In Floor | Mini Canal | MICL.00931042/DMN | 9 | 310 | 42 | 42 | 1446 | 1446 | 1446 | 0.034429 | 562 | 0.013381 | 1647 | 0.039214 | 1.362 | A04 | MICL0.00931042/DMN
Build-In Floor | Mini Canal | MICL.00931042/DMV | 9 | 310 | 42 | 42 | 1446 | 1446 | 1446 | 0.034429 | 562 | 0.013381 | 1647 | 0.039214 | 1.362 | A04 | MICL0.00931042/DMV
Build-In Floor | Mini Canal | MICL.00931042/DNA | 9 | 310 | 42 | 42 | 1508 | 1508 | 1508 | 0.035905 | 587 | 0.013976 | 1718 | 0.040905 | 1.362 | A04 | MICL0.00931042/DNA
Build-In Floor | Mini Canal | MICL.00931042/DNC | 9 | 310 | 42 | 42 | 1508 | 1508 | 1508 | 0.035905 | 587 | 0.013976 | 1718 | 0.040905 | 1.362 | A04 | MICL0.00931042/DNC
Build-In Floor | Mini Canal | MICL.00931042/DON | 9 | 310 | 42 | 42 | 1446 | 1446 | 1446 | 0.034429 | 562 | 0.013381 | 1647 | 0.039214 | 1.362 | A04 | MICL0.00931042/DON
Build-In Floor | Mini Canal | MICL.00931042/DOV | 9 | 310 | 42 | 42 | 1446 | 1446 | 1446 | 0.034429 | 562 | 0.013381 | 1647 | 0.039214 | 1.362 | A04 | MICL0.00931042/DOV
Build-In Floor | Mini Canal | MICL.00931042/PNC | 9 | 310 | 42 | 42 | 1322 | 1322 | 1322 | 0.031476 | 514 | 0.012238 | 1506 | 0.035857 | 1.362 | A04 | MICL0.00931042/PNC
Build-In Floor | Mini Canal | MICL.00931042/RBL | 9 | 310 | 42 | 42 | 1555 | 1555 | 1555 | 0.037024 | 605 | 0.014405 | 1771 | 0.042167 | 1.362 | A04 | MICL0.00931042/RBL
Build-In Floor | Mini Canal | MICL.00931042/RBN | 9 | 310 | 42 | 42 | 1508 | 1508 | 1508 | 0.035905 | 587 | 0.013976 | 1718 | 0.040905 | 1.362 | A04 | MICL0.00931042/RBN
Build-In Floor | Mini Canal | MICL.00931042/RBR | 9 | 310 | 42 | 42 | 1555 | 1555 | 1555 | 0.037024 | 605 | 0.014405 | 1771 | 0.042167 | 1.362 | A04 | MICL0.00931042/RBR
Build-In Floor | Mini Canal | MICL.00931042/RBV | 9 | 310 | 42 | 42 | 1508 | 1508 | 1508 | 0.035905 | 587 | 0.013976 | 1718 | 0.040905 | 1.362 | A04 | MICL0.00931042/RBV
Build-In Floor | Mini Canal | MICL.00931042/RDB | 9 | 310 | 42 | 42 | 1555 | 1555 | 1555 | 0.037024 | 605 | 0.014405 | 1771 | 0.042167 | 1.362 | A04 | MICL0.00931042/RDB
Build-In Floor | Mini Canal | MICL.00931042/RMN | 9 | 310 | 42 | 42 | 1508 | 1508 | 1508 | 0.035905 | 587 | 0.013976 | 1718 | 0.040905 | 1.362 | A04 | MICL0.00931042/RMN
Build-In Floor | Mini Canal | MICL.00931042/RMV | 9 | 310 | 42 | 42 | 1508 | 1508 | 1508 | 0.035905 | 587 | 0.013976 | 1718 | 0.040905 | 1.362 | A04 | MICL0.00931042/RMV
Build-In Floor | Mini Canal | MICL.00931042/RNA | 9 | 310 | 42 | 42 | 1555 | 1555 | 1555 | 0.037024 | 605 | 0.014405 | 1771 | 0.042167 | 1.362 | A04 | MICL0.00931042/RNA
Build-In Floor | Mini Canal | MICL.00931042/RON | 9 | 310 | 42 | 42 | 1508 | 1508 | 1508 | 0.035905 | 587 | 0.013976 | 1718 | 0.040905 | 1.362 | A04 | MICL0.00931042/RON
Build-In Floor | Mini Canal | MICL.00931042/ROV | 9 | 310 | 42 | 42 | 1508 | 1508 | 1508 | 0.035905 | 587 | 0.013976 | 1718 | 0.040905 | 1.362 | A04 | MICL0.00931042/ROV
Build-In Floor | Mini Canal | MICL.00931042/RSS | 9 | 310 | 42 | 42 | 1493 | 1493 | 1493 | 0.035548 | 581 | 0.013833 | 1701 | 0.0405 | 1.362 | A04 | MICL0.00931042/RSS
Build-In Floor | Mini Canal | MICL.00931042/SBL | 9 | 310 | 42 | 42 | 1555 | 1555 | 1555 | 0.037024 | 605 | 0.014405 | 1771 | 0.042167 | 1.362 | A04 | MICL0.00931042/SBL
Build-In Floor | Mini Canal | MICL.00931042/SBR | 9 | 310 | 42 | 42 | 1555 | 1555 | 1555 | 0.037024 | 605 | 0.014405 | 1771 | 0.042167 | 1.362 | A04 | MICL0.00931042/SBR
Build-In Floor | Mini Canal | MICL.00931042/SDB | 9 | 310 | 42 | 42 | 1555 | 1555 | 1555 | 0.037024 | 605 | 0.014405 | 1771 | 0.042167 | 1.362 | A04 | MICL0.00931042/SDB
Build-In Floor | Mini Canal | MICL.00931042/SNA | 9 | 310 | 42 | 42 | 1555 | 1555 | 1555 | 0.037024 | 605 | 0.014405 | 1771 | 0.042167 | 1.362 | A04 | MICL0.00931042/SNA
Build-In Floor | Mini Canal | MICL.00931042/SNC | 9 | 310 | 42 | 42 | 1555 | 1555 | 1555 | 0.037024 | 605 | 0.014405 | 1771 | 0.042167 | 1.362 | A04 | MICL0.00931042/SNC
Build-In Floor | Mini Canal | MICL.00933014/ANA | 9 | 330 | 14 | 14 | 428 | 428 | 428 | 0.01019 | 166 | 0.0039524 | 487 | 0.011595 | 1.362 | A04 | MICL0.00933014/ANA
Build-In Floor | Mini Canal | MICL.00933014/DBL | 9 | 330 | 14 | 14 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.00933014/DBL
Build-In Floor | Mini Canal | MICL.00933014/DBN | 9 | 330 | 14 | 14 | 531 | 531 | 531 | 0.012643 | 207 | 0.0049286 | 605 | 0.014405 | 1.362 | A04 | MICL0.00933014/DBN
Build-In Floor | Mini Canal | MICL.00933014/DBR | 9 | 330 | 14 | 14 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.00933014/DBR
Build-In Floor | Mini Canal | MICL.00933014/DBV | 9 | 330 | 14 | 14 | 531 | 531 | 531 | 0.012643 | 207 | 0.0049286 | 605 | 0.014405 | 1.362 | A04 | MICL0.00933014/DBV
Build-In Floor | Mini Canal | MICL.00933014/DDB | 9 | 330 | 14 | 14 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.00933014/DDB
Build-In Floor | Mini Canal | MICL.00933014/DMN | 9 | 330 | 14 | 14 | 531 | 531 | 531 | 0.012643 | 207 | 0.0049286 | 605 | 0.014405 | 1.362 | A04 | MICL0.00933014/DMN
Build-In Floor | Mini Canal | MICL.00933014/DMV | 9 | 330 | 14 | 14 | 531 | 531 | 531 | 0.012643 | 207 | 0.0049286 | 605 | 0.014405 | 1.362 | A04 | MICL0.00933014/DMV
Build-In Floor | Mini Canal | MICL.00933014/DNA | 9 | 330 | 14 | 14 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.00933014/DNA
Build-In Floor | Mini Canal | MICL.00933014/DNC | 9 | 330 | 14 | 14 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.00933014/DNC
Build-In Floor | Mini Canal | MICL.00933014/DON | 9 | 330 | 14 | 14 | 531 | 531 | 531 | 0.012643 | 207 | 0.0049286 | 605 | 0.014405 | 1.362 | A04 | MICL0.00933014/DON
Build-In Floor | Mini Canal | MICL.00933014/DOV | 9 | 330 | 14 | 14 | 531 | 531 | 531 | 0.012643 | 207 | 0.0049286 | 605 | 0.014405 | 1.362 | A04 | MICL0.00933014/DOV
Build-In Floor | Mini Canal | MICL.00933014/RBL | 9 | 330 | 14 | 14 | 571 | 571 | 571 | 0.013595 | 222 | 0.0052857 | 650 | 0.015476 | 1.362 | A04 | MICL0.00933014/RBL
Build-In Floor | Mini Canal | MICL.00933014/RBN | 9 | 330 | 14 | 14 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.00933014/RBN
Build-In Floor | Mini Canal | MICL.00933014/RBR | 9 | 330 | 14 | 14 | 571 | 571 | 571 | 0.013595 | 222 | 0.0052857 | 650 | 0.015476 | 1.362 | A04 | MICL0.00933014/RBR
Build-In Floor | Mini Canal | MICL.00933014/RBV | 9 | 330 | 14 | 14 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.00933014/RBV
Build-In Floor | Mini Canal | MICL.00933014/RDB | 9 | 330 | 14 | 14 | 571 | 571 | 571 | 0.013595 | 222 | 0.0052857 | 650 | 0.015476 | 1.362 | A04 | MICL0.00933014/RDB
Build-In Floor | Mini Canal | MICL.00933014/RMN | 9 | 330 | 14 | 14 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.00933014/RMN
Build-In Floor | Mini Canal | MICL.00933014/RMV | 9 | 330 | 14 | 14 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.00933014/RMV
Build-In Floor | Mini Canal | MICL.00933014/RNA | 9 | 330 | 14 | 14 | 571 | 571 | 571 | 0.013595 | 222 | 0.0052857 | 650 | 0.015476 | 1.362 | A04 | MICL0.00933014/RNA
Build-In Floor | Mini Canal | MICL.00933014/RON | 9 | 330 | 14 | 14 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.00933014/RON
Build-In Floor | Mini Canal | MICL.00933014/ROV | 9 | 330 | 14 | 14 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.00933014/ROV
Build-In Floor | Mini Canal | MICL.00933014/RSS | 9 | 330 | 14 | 14 | 548 | 548 | 548 | 0.013048 | 213 | 0.0050714 | 624 | 0.014857 | 1.362 | A04 | MICL0.00933014/RSS
Build-In Floor | Mini Canal | MICL.00933014/SBL | 9 | 330 | 14 | 14 | 571 | 571 | 571 | 0.013595 | 222 | 0.0052857 | 650 | 0.015476 | 1.362 | A04 | MICL0.00933014/SBL
Build-In Floor | Mini Canal | MICL.00933014/SBR | 9 | 330 | 14 | 14 | 571 | 571 | 571 | 0.013595 | 222 | 0.0052857 | 650 | 0.015476 | 1.362 | A04 | MICL0.00933014/SBR
Build-In Floor | Mini Canal | MICL.00933014/SDB | 9 | 330 | 14 | 14 | 571 | 571 | 571 | 0.013595 | 222 | 0.0052857 | 650 | 0.015476 | 1.362 | A04 | MICL0.00933014/SDB
Build-In Floor | Mini Canal | MICL.00933014/SNA | 9 | 330 | 14 | 14 | 571 | 571 | 571 | 0.013595 | 222 | 0.0052857 | 650 | 0.015476 | 1.362 | A04 | MICL0.00933014/SNA
Build-In Floor | Mini Canal | MICL.00933014/SNC | 9 | 330 | 14 | 14 | 571 | 571 | 571 | 0.013595 | 222 | 0.0052857 | 650 | 0.015476 | 1.362 | A04 | MICL0.00933014/SNC
Build-In Floor | Mini Canal | MICL.00933018/ANA | 9 | 330 | 18 | 18 | 507 | 507 | 507 | 0.012071 | 197 | 0.0046905 | 577 | 0.013738 | 1.362 | A04 | MICL0.00933018/ANA
Build-In Floor | Mini Canal | MICL.00933018/DBL | 9 | 330 | 18 | 18 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.00933018/DBL
Build-In Floor | Mini Canal | MICL.00933018/DBN | 9 | 330 | 18 | 18 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.00933018/DBN
Build-In Floor | Mini Canal | MICL.00933018/DBR | 9 | 330 | 18 | 18 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.00933018/DBR
Build-In Floor | Mini Canal | MICL.00933018/DBV | 9 | 330 | 18 | 18 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.00933018/DBV
Build-In Floor | Mini Canal | MICL.00933018/DDB | 9 | 330 | 18 | 18 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.00933018/DDB
Build-In Floor | Mini Canal | MICL.00933018/DMN | 9 | 330 | 18 | 18 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.00933018/DMN
Build-In Floor | Mini Canal | MICL.00933018/DMV | 9 | 330 | 18 | 18 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.00933018/DMV
Build-In Floor | Mini Canal | MICL.00933018/DNA | 9 | 330 | 18 | 18 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.00933018/DNA
Build-In Floor | Mini Canal | MICL.00933018/DNC | 9 | 330 | 18 | 18 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.00933018/DNC
Build-In Floor | Mini Canal | MICL.00933018/DON | 9 | 330 | 18 | 18 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.00933018/DON
Build-In Floor | Mini Canal | MICL.00933018/DOV | 9 | 330 | 18 | 18 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.00933018/DOV
Build-In Floor | Mini Canal | MICL.00933018/RBL | 9 | 330 | 18 | 18 | 676 | 676 | 676 | 0.016095 | 263 | 0.0062619 | 770 | 0.018333 | 1.362 | A04 | MICL0.00933018/RBL
Build-In Floor | Mini Canal | MICL.00933018/RBN | 9 | 330 | 18 | 18 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.00933018/RBN
Build-In Floor | Mini Canal | MICL.00933018/RBR | 9 | 330 | 18 | 18 | 676 | 676 | 676 | 0.016095 | 263 | 0.0062619 | 770 | 0.018333 | 1.362 | A04 | MICL0.00933018/RBR
Build-In Floor | Mini Canal | MICL.00933018/RBV | 9 | 330 | 18 | 18 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.00933018/RBV
Build-In Floor | Mini Canal | MICL.00933018/RDB | 9 | 330 | 18 | 18 | 676 | 676 | 676 | 0.016095 | 263 | 0.0062619 | 770 | 0.018333 | 1.362 | A04 | MICL0.00933018/RDB
Build-In Floor | Mini Canal | MICL.00933018/RMN | 9 | 330 | 18 | 18 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.00933018/RMN
Build-In Floor | Mini Canal | MICL.00933018/RMV | 9 | 330 | 18 | 18 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.00933018/RMV
Build-In Floor | Mini Canal | MICL.00933018/RNA | 9 | 330 | 18 | 18 | 676 | 676 | 676 | 0.016095 | 263 | 0.0062619 | 770 | 0.018333 | 1.362 | A04 | MICL0.00933018/RNA
Build-In Floor | Mini Canal | MICL.00933018/RON | 9 | 330 | 18 | 18 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.00933018/RON
Build-In Floor | Mini Canal | MICL.00933018/ROV | 9 | 330 | 18 | 18 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.00933018/ROV
Build-In Floor | Mini Canal | MICL.00933018/RSS | 9 | 330 | 18 | 18 | 649 | 649 | 649 | 0.015452 | 252 | 0.006 | 739 | 0.017595 | 1.362 | A04 | MICL0.00933018/RSS
Build-In Floor | Mini Canal | MICL.00933018/SBL | 9 | 330 | 18 | 18 | 676 | 676 | 676 | 0.016095 | 263 | 0.0062619 | 770 | 0.018333 | 1.362 | A04 | MICL0.00933018/SBL
Build-In Floor | Mini Canal | MICL.00933018/SBR | 9 | 330 | 18 | 18 | 676 | 676 | 676 | 0.016095 | 263 | 0.0062619 | 770 | 0.018333 | 1.362 | A04 | MICL0.00933018/SBR
Build-In Floor | Mini Canal | MICL.00933018/SDB | 9 | 330 | 18 | 18 | 676 | 676 | 676 | 0.016095 | 263 | 0.0062619 | 770 | 0.018333 | 1.362 | A04 | MICL0.00933018/SDB
Build-In Floor | Mini Canal | MICL.00933018/SNA | 9 | 330 | 18 | 18 | 676 | 676 | 676 | 0.016095 | 263 | 0.0062619 | 770 | 0.018333 | 1.362 | A04 | MICL0.00933018/SNA
Build-In Floor | Mini Canal | MICL.00933018/SNC | 9 | 330 | 18 | 18 | 676 | 676 | 676 | 0.016095 | 263 | 0.0062619 | 770 | 0.018333 | 1.362 | A04 | MICL0.00933018/SNC
Build-In Floor | Mini Canal | MICL.00933026/ANA | 9 | 330 | 26 | 26 | 667 | 667 | 667 | 0.015881 | 259 | 0.0061667 | 760 | 0.018095 | 1.362 | A04 | MICL0.00933026/ANA
Build-In Floor | Mini Canal | MICL.00933026/DBL | 9 | 330 | 26 | 26 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.00933026/DBL
Build-In Floor | Mini Canal | MICL.00933026/DBN | 9 | 330 | 26 | 26 | 827 | 827 | 827 | 0.01969 | 322 | 0.0076667 | 942 | 0.022429 | 1.362 | A04 | MICL0.00933026/DBN
Build-In Floor | Mini Canal | MICL.00933026/DBR | 9 | 330 | 26 | 26 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.00933026/DBR
Build-In Floor | Mini Canal | MICL.00933026/DBV | 9 | 330 | 26 | 26 | 827 | 827 | 827 | 0.01969 | 322 | 0.0076667 | 942 | 0.022429 | 1.362 | A04 | MICL0.00933026/DBV
Build-In Floor | Mini Canal | MICL.00933026/DDB | 9 | 330 | 26 | 26 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.00933026/DDB
Build-In Floor | Mini Canal | MICL.00933026/DMN | 9 | 330 | 26 | 26 | 827 | 827 | 827 | 0.01969 | 322 | 0.0076667 | 942 | 0.022429 | 1.362 | A04 | MICL0.00933026/DMN
Build-In Floor | Mini Canal | MICL.00933026/DMV | 9 | 330 | 26 | 26 | 827 | 827 | 827 | 0.01969 | 322 | 0.0076667 | 942 | 0.022429 | 1.362 | A04 | MICL0.00933026/DMV
Build-In Floor | Mini Canal | MICL.00933026/DNA | 9 | 330 | 26 | 26 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.00933026/DNA
Build-In Floor | Mini Canal | MICL.00933026/DNC | 9 | 330 | 26 | 26 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.00933026/DNC
Build-In Floor | Mini Canal | MICL.00933026/DON | 9 | 330 | 26 | 26 | 827 | 827 | 827 | 0.01969 | 322 | 0.0076667 | 942 | 0.022429 | 1.362 | A04 | MICL0.00933026/DON
Build-In Floor | Mini Canal | MICL.00933026/DOV | 9 | 330 | 26 | 26 | 827 | 827 | 827 | 0.01969 | 322 | 0.0076667 | 942 | 0.022429 | 1.362 | A04 | MICL0.00933026/DOV
Build-In Floor | Mini Canal | MICL.00933026/PNC | 9 | 330 | 26 | 26 | 756 | 756 | 756 | 0.018 | 294 | 0.007 | 861 | 0.0205 | 1.362 | A04 | MICL0.00933026/PNC
Build-In Floor | Mini Canal | MICL.00933026/RBL | 9 | 330 | 26 | 26 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.00933026/RBL
Build-In Floor | Mini Canal | MICL.00933026/RBN | 9 | 330 | 26 | 26 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.00933026/RBN
Build-In Floor | Mini Canal | MICL.00933026/RBR | 9 | 330 | 26 | 26 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.00933026/RBR
Build-In Floor | Mini Canal | MICL.00933026/RBV | 9 | 330 | 26 | 26 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.00933026/RBV
Build-In Floor | Mini Canal | MICL.00933026/RDB | 9 | 330 | 26 | 26 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.00933026/RDB
Build-In Floor | Mini Canal | MICL.00933026/RMN | 9 | 330 | 26 | 26 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.00933026/RMN
Build-In Floor | Mini Canal | MICL.00933026/RMV | 9 | 330 | 26 | 26 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.00933026/RMV
Build-In Floor | Mini Canal | MICL.00933026/RNA | 9 | 330 | 26 | 26 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.00933026/RNA
Build-In Floor | Mini Canal | MICL.00933026/RON | 9 | 330 | 26 | 26 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.00933026/RON
Build-In Floor | Mini Canal | MICL.00933026/ROV | 9 | 330 | 26 | 26 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.00933026/ROV
Build-In Floor | Mini Canal | MICL.00933026/RSS | 9 | 330 | 26 | 26 | 853 | 853 | 853 | 0.02031 | 332 | 0.0079048 | 972 | 0.023143 | 1.362 | A04 | MICL0.00933026/RSS
Build-In Floor | Mini Canal | MICL.00933026/SBL | 9 | 330 | 26 | 26 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.00933026/SBL
Build-In Floor | Mini Canal | MICL.00933026/SBR | 9 | 330 | 26 | 26 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.00933026/SBR
Build-In Floor | Mini Canal | MICL.00933026/SDB | 9 | 330 | 26 | 26 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.00933026/SDB
Build-In Floor | Mini Canal | MICL.00933026/SNA | 9 | 330 | 26 | 26 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.00933026/SNA
Build-In Floor | Mini Canal | MICL.00933026/SNC | 9 | 330 | 26 | 26 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.00933026/SNC
Build-In Floor | Mini Canal | MICL.00933034/ANA | 9 | 330 | 34 | 34 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.00933034/ANA
Build-In Floor | Mini Canal | MICL.00933034/DBL | 9 | 330 | 34 | 34 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.00933034/DBL
Build-In Floor | Mini Canal | MICL.00933034/DBN | 9 | 330 | 34 | 34 | 1073 | 1073 | 1073 | 0.025548 | 417 | 0.0099286 | 1222 | 0.029095 | 1.362 | A04 | MICL0.00933034/DBN
Build-In Floor | Mini Canal | MICL.00933034/DBR | 9 | 330 | 34 | 34 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.00933034/DBR
Build-In Floor | Mini Canal | MICL.00933034/DBV | 9 | 330 | 34 | 34 | 1073 | 1073 | 1073 | 0.025548 | 417 | 0.0099286 | 1222 | 0.029095 | 1.362 | A04 | MICL0.00933034/DBV
Build-In Floor | Mini Canal | MICL.00933034/DDB | 9 | 330 | 34 | 34 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.00933034/DDB
Build-In Floor | Mini Canal | MICL.00933034/DMN | 9 | 330 | 34 | 34 | 1073 | 1073 | 1073 | 0.025548 | 417 | 0.0099286 | 1222 | 0.029095 | 1.362 | A04 | MICL0.00933034/DMN
Build-In Floor | Mini Canal | MICL.00933034/DMV | 9 | 330 | 34 | 34 | 1073 | 1073 | 1073 | 0.025548 | 417 | 0.0099286 | 1222 | 0.029095 | 1.362 | A04 | MICL0.00933034/DMV
Build-In Floor | Mini Canal | MICL.00933034/DNA | 9 | 330 | 34 | 34 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.00933034/DNA
Build-In Floor | Mini Canal | MICL.00933034/DNC | 9 | 330 | 34 | 34 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.00933034/DNC
Build-In Floor | Mini Canal | MICL.00933034/DON | 9 | 330 | 34 | 34 | 1073 | 1073 | 1073 | 0.025548 | 417 | 0.0099286 | 1222 | 0.029095 | 1.362 | A04 | MICL0.00933034/DON
Build-In Floor | Mini Canal | MICL.00933034/DOV | 9 | 330 | 34 | 34 | 1073 | 1073 | 1073 | 0.025548 | 417 | 0.0099286 | 1222 | 0.029095 | 1.362 | A04 | MICL0.00933034/DOV
Build-In Floor | Mini Canal | MICL.00933034/PNC | 9 | 330 | 34 | 34 | 981 | 981 | 981 | 0.023357 | 382 | 0.0090952 | 1117 | 0.026595 | 1.362 | A04 | MICL0.00933034/PNC
Build-In Floor | Mini Canal | MICL.00933034/RBL | 9 | 330 | 34 | 34 | 1154 | 1154 | 1154 | 0.027476 | 449 | 0.01069 | 1314 | 0.031286 | 1.362 | A04 | MICL0.00933034/RBL
Build-In Floor | Mini Canal | MICL.00933034/RBN | 9 | 330 | 34 | 34 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.00933034/RBN
Build-In Floor | Mini Canal | MICL.00933034/RBR | 9 | 330 | 34 | 34 | 1154 | 1154 | 1154 | 0.027476 | 449 | 0.01069 | 1314 | 0.031286 | 1.362 | A04 | MICL0.00933034/RBR
Build-In Floor | Mini Canal | MICL.00933034/RBV | 9 | 330 | 34 | 34 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.00933034/RBV
Build-In Floor | Mini Canal | MICL.00933034/RDB | 9 | 330 | 34 | 34 | 1154 | 1154 | 1154 | 0.027476 | 449 | 0.01069 | 1314 | 0.031286 | 1.362 | A04 | MICL0.00933034/RDB
Build-In Floor | Mini Canal | MICL.00933034/RMN | 9 | 330 | 34 | 34 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.00933034/RMN
Build-In Floor | Mini Canal | MICL.00933034/RMV | 9 | 330 | 34 | 34 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.00933034/RMV
Build-In Floor | Mini Canal | MICL.00933034/RNA | 9 | 330 | 34 | 34 | 1154 | 1154 | 1154 | 0.027476 | 449 | 0.01069 | 1314 | 0.031286 | 1.362 | A04 | MICL0.00933034/RNA
Build-In Floor | Mini Canal | MICL.00933034/RON | 9 | 330 | 34 | 34 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.00933034/RON
Build-In Floor | Mini Canal | MICL.00933034/ROV | 9 | 330 | 34 | 34 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.00933034/ROV
Build-In Floor | Mini Canal | MICL.00933034/RSS | 9 | 330 | 34 | 34 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.00933034/RSS
Build-In Floor | Mini Canal | MICL.00933034/SBL | 9 | 330 | 34 | 34 | 1154 | 1154 | 1154 | 0.027476 | 449 | 0.01069 | 1314 | 0.031286 | 1.362 | A04 | MICL0.00933034/SBL
Build-In Floor | Mini Canal | MICL.00933034/SBR | 9 | 330 | 34 | 34 | 1154 | 1154 | 1154 | 0.027476 | 449 | 0.01069 | 1314 | 0.031286 | 1.362 | A04 | MICL0.00933034/SBR
Build-In Floor | Mini Canal | MICL.00933034/SDB | 9 | 330 | 34 | 34 | 1154 | 1154 | 1154 | 0.027476 | 449 | 0.01069 | 1314 | 0.031286 | 1.362 | A04 | MICL0.00933034/SDB
Build-In Floor | Mini Canal | MICL.00933034/SNA | 9 | 330 | 34 | 34 | 1154 | 1154 | 1154 | 0.027476 | 449 | 0.01069 | 1314 | 0.031286 | 1.362 | A04 | MICL0.00933034/SNA
Build-In Floor | Mini Canal | MICL.00933034/SNC | 9 | 330 | 34 | 34 | 1154 | 1154 | 1154 | 0.027476 | 449 | 0.01069 | 1314 | 0.031286 | 1.362 | A04 | MICL0.00933034/SNC
Build-In Floor | Mini Canal | MICL.00933042/ANA | 9 | 330 | 42 | 42 | 1250 | 1250 | 1250 | 0.029762 | 486 | 0.011571 | 1424 | 0.033905 | 1.362 | A04 | MICL0.00933042/ANA
Build-In Floor | Mini Canal | MICL.00933042/DBL | 9 | 330 | 42 | 42 | 1616 | 1616 | 1616 | 0.038476 | 629 | 0.014976 | 1841 | 0.043833 | 1.362 | A04 | MICL0.00933042/DBL
Build-In Floor | Mini Canal | MICL.00933042/DBN | 9 | 330 | 42 | 42 | 1549 | 1549 | 1549 | 0.036881 | 603 | 0.014357 | 1764 | 0.042 | 1.362 | A04 | MICL0.00933042/DBN
Build-In Floor | Mini Canal | MICL.00933042/DBR | 9 | 330 | 42 | 42 | 1616 | 1616 | 1616 | 0.038476 | 629 | 0.014976 | 1841 | 0.043833 | 1.362 | A04 | MICL0.00933042/DBR
Build-In Floor | Mini Canal | MICL.00933042/DBV | 9 | 330 | 42 | 42 | 1549 | 1549 | 1549 | 0.036881 | 603 | 0.014357 | 1764 | 0.042 | 1.362 | A04 | MICL0.00933042/DBV
Build-In Floor | Mini Canal | MICL.00933042/DDB | 9 | 330 | 42 | 42 | 1616 | 1616 | 1616 | 0.038476 | 629 | 0.014976 | 1841 | 0.043833 | 1.362 | A04 | MICL0.00933042/DDB
Build-In Floor | Mini Canal | MICL.00933042/DMN | 9 | 330 | 42 | 42 | 1549 | 1549 | 1549 | 0.036881 | 603 | 0.014357 | 1764 | 0.042 | 1.362 | A04 | MICL0.00933042/DMN
Build-In Floor | Mini Canal | MICL.00933042/DMV | 9 | 330 | 42 | 42 | 1549 | 1549 | 1549 | 0.036881 | 603 | 0.014357 | 1764 | 0.042 | 1.362 | A04 | MICL0.00933042/DMV
Build-In Floor | Mini Canal | MICL.00933042/DNA | 9 | 330 | 42 | 42 | 1616 | 1616 | 1616 | 0.038476 | 629 | 0.014976 | 1841 | 0.043833 | 1.362 | A04 | MICL0.00933042/DNA
Build-In Floor | Mini Canal | MICL.00933042/DNC | 9 | 330 | 42 | 42 | 1616 | 1616 | 1616 | 0.038476 | 629 | 0.014976 | 1841 | 0.043833 | 1.362 | A04 | MICL0.00933042/DNC
Build-In Floor | Mini Canal | MICL.00933042/DON | 9 | 330 | 42 | 42 | 1549 | 1549 | 1549 | 0.036881 | 603 | 0.014357 | 1764 | 0.042 | 1.362 | A04 | MICL0.00933042/DON
Build-In Floor | Mini Canal | MICL.00933042/DOV | 9 | 330 | 42 | 42 | 1549 | 1549 | 1549 | 0.036881 | 603 | 0.014357 | 1764 | 0.042 | 1.362 | A04 | MICL0.00933042/DOV
Build-In Floor | Mini Canal | MICL.00933042/PNC | 9 | 330 | 42 | 42 | 1416 | 1416 | 1416 | 0.033714 | 551 | 0.013119 | 1613 | 0.038405 | 1.362 | A04 | MICL0.00933042/PNC
Build-In Floor | Mini Canal | MICL.00933042/RBL | 9 | 330 | 42 | 42 | 1666 | 1666 | 1666 | 0.039667 | 648 | 0.015429 | 1898 | 0.04519 | 1.362 | A04 | MICL0.00933042/RBL
Build-In Floor | Mini Canal | MICL.00933042/RBN | 9 | 330 | 42 | 42 | 1616 | 1616 | 1616 | 0.038476 | 629 | 0.014976 | 1841 | 0.043833 | 1.362 | A04 | MICL0.00933042/RBN
Build-In Floor | Mini Canal | MICL.00933042/RBR | 9 | 330 | 42 | 42 | 1666 | 1666 | 1666 | 0.039667 | 648 | 0.015429 | 1898 | 0.04519 | 1.362 | A04 | MICL0.00933042/RBR
Build-In Floor | Mini Canal | MICL.00933042/RBV | 9 | 330 | 42 | 42 | 1616 | 1616 | 1616 | 0.038476 | 629 | 0.014976 | 1841 | 0.043833 | 1.362 | A04 | MICL0.00933042/RBV
Build-In Floor | Mini Canal | MICL.00933042/RDB | 9 | 330 | 42 | 42 | 1666 | 1666 | 1666 | 0.039667 | 648 | 0.015429 | 1898 | 0.04519 | 1.362 | A04 | MICL0.00933042/RDB
Build-In Floor | Mini Canal | MICL.00933042/RMN | 9 | 330 | 42 | 42 | 1616 | 1616 | 1616 | 0.038476 | 629 | 0.014976 | 1841 | 0.043833 | 1.362 | A04 | MICL0.00933042/RMN
Build-In Floor | Mini Canal | MICL.00933042/RMV | 9 | 330 | 42 | 42 | 1616 | 1616 | 1616 | 0.038476 | 629 | 0.014976 | 1841 | 0.043833 | 1.362 | A04 | MICL0.00933042/RMV
Build-In Floor | Mini Canal | MICL.00933042/RNA | 9 | 330 | 42 | 42 | 1666 | 1666 | 1666 | 0.039667 | 648 | 0.015429 | 1898 | 0.04519 | 1.362 | A04 | MICL0.00933042/RNA
Build-In Floor | Mini Canal | MICL.00933042/RON | 9 | 330 | 42 | 42 | 1616 | 1616 | 1616 | 0.038476 | 629 | 0.014976 | 1841 | 0.043833 | 1.362 | A04 | MICL0.00933042/RON
Build-In Floor | Mini Canal | MICL.00933042/ROV | 9 | 330 | 42 | 42 | 1616 | 1616 | 1616 | 0.038476 | 629 | 0.014976 | 1841 | 0.043833 | 1.362 | A04 | MICL0.00933042/ROV
Build-In Floor | Mini Canal | MICL.00933042/RSS | 9 | 330 | 42 | 42 | 1599 | 1599 | 1599 | 0.038071 | 622 | 0.01481 | 1821 | 0.043357 | 1.362 | A04 | MICL0.00933042/RSS
Build-In Floor | Mini Canal | MICL.00933042/SBL | 9 | 330 | 42 | 42 | 1666 | 1666 | 1666 | 0.039667 | 648 | 0.015429 | 1898 | 0.04519 | 1.362 | A04 | MICL0.00933042/SBL
Build-In Floor | Mini Canal | MICL.00933042/SBR | 9 | 330 | 42 | 42 | 1666 | 1666 | 1666 | 0.039667 | 648 | 0.015429 | 1898 | 0.04519 | 1.362 | A04 | MICL0.00933042/SBR
Build-In Floor | Mini Canal | MICL.00933042/SDB | 9 | 330 | 42 | 42 | 1666 | 1666 | 1666 | 0.039667 | 648 | 0.015429 | 1898 | 0.04519 | 1.362 | A04 | MICL0.00933042/SDB
Build-In Floor | Mini Canal | MICL.00933042/SNA | 9 | 330 | 42 | 42 | 1666 | 1666 | 1666 | 0.039667 | 648 | 0.015429 | 1898 | 0.04519 | 1.362 | A04 | MICL0.00933042/SNA
Build-In Floor | Mini Canal | MICL.00933042/SNC | 9 | 330 | 42 | 42 | 1666 | 1666 | 1666 | 0.039667 | 648 | 0.015429 | 1898 | 0.04519 | 1.362 | A04 | MICL0.00933042/SNC
Build-In Floor | Mini Canal | MICL.00935014/ANA | 9 | 350 | 14 | 14 | 457 | 457 | 457 | 0.010881 | 178 | 0.0042381 | 521 | 0.012405 | 1.362 | A04 | MICL0.00935014/ANA
Build-In Floor | Mini Canal | MICL.00935014/DBL | 9 | 350 | 14 | 14 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.00935014/DBL
Build-In Floor | Mini Canal | MICL.00935014/DBN | 9 | 350 | 14 | 14 | 566 | 566 | 566 | 0.013476 | 220 | 0.0052381 | 645 | 0.015357 | 1.362 | A04 | MICL0.00935014/DBN
Build-In Floor | Mini Canal | MICL.00935014/DBR | 9 | 350 | 14 | 14 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.00935014/DBR
Build-In Floor | Mini Canal | MICL.00935014/DBV | 9 | 350 | 14 | 14 | 566 | 566 | 566 | 0.013476 | 220 | 0.0052381 | 645 | 0.015357 | 1.362 | A04 | MICL0.00935014/DBV
Build-In Floor | Mini Canal | MICL.00935014/DDB | 9 | 350 | 14 | 14 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.00935014/DDB
Build-In Floor | Mini Canal | MICL.00935014/DMN | 9 | 350 | 14 | 14 | 566 | 566 | 566 | 0.013476 | 220 | 0.0052381 | 645 | 0.015357 | 1.362 | A04 | MICL0.00935014/DMN
Build-In Floor | Mini Canal | MICL.00935014/DMV | 9 | 350 | 14 | 14 | 566 | 566 | 566 | 0.013476 | 220 | 0.0052381 | 645 | 0.015357 | 1.362 | A04 | MICL0.00935014/DMV
Build-In Floor | Mini Canal | MICL.00935014/DNA | 9 | 350 | 14 | 14 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.00935014/DNA
Build-In Floor | Mini Canal | MICL.00935014/DNC | 9 | 350 | 14 | 14 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.00935014/DNC
Build-In Floor | Mini Canal | MICL.00935014/DON | 9 | 350 | 14 | 14 | 566 | 566 | 566 | 0.013476 | 220 | 0.0052381 | 645 | 0.015357 | 1.362 | A04 | MICL0.00935014/DON
Build-In Floor | Mini Canal | MICL.00935014/DOV | 9 | 350 | 14 | 14 | 566 | 566 | 566 | 0.013476 | 220 | 0.0052381 | 645 | 0.015357 | 1.362 | A04 | MICL0.00935014/DOV
Build-In Floor | Mini Canal | MICL.00935014/RBL | 9 | 350 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.00935014/RBL
Build-In Floor | Mini Canal | MICL.00935014/RBN | 9 | 350 | 14 | 14 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.00935014/RBN
Build-In Floor | Mini Canal | MICL.00935014/RBR | 9 | 350 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.00935014/RBR
Build-In Floor | Mini Canal | MICL.00935014/RBV | 9 | 350 | 14 | 14 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.00935014/RBV
Build-In Floor | Mini Canal | MICL.00935014/RDB | 9 | 350 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.00935014/RDB
Build-In Floor | Mini Canal | MICL.00935014/RMN | 9 | 350 | 14 | 14 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.00935014/RMN
Build-In Floor | Mini Canal | MICL.00935014/RMV | 9 | 350 | 14 | 14 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.00935014/RMV
Build-In Floor | Mini Canal | MICL.00935014/RNA | 9 | 350 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.00935014/RNA
Build-In Floor | Mini Canal | MICL.00935014/RON | 9 | 350 | 14 | 14 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.00935014/RON
Build-In Floor | Mini Canal | MICL.00935014/ROV | 9 | 350 | 14 | 14 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.00935014/ROV
Build-In Floor | Mini Canal | MICL.00935014/RSS | 9 | 350 | 14 | 14 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.00935014/RSS
Build-In Floor | Mini Canal | MICL.00935014/SBL | 9 | 350 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.00935014/SBL
Build-In Floor | Mini Canal | MICL.00935014/SBR | 9 | 350 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.00935014/SBR
Build-In Floor | Mini Canal | MICL.00935014/SDB | 9 | 350 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.00935014/SDB
Build-In Floor | Mini Canal | MICL.00935014/SNA | 9 | 350 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.00935014/SNA
Build-In Floor | Mini Canal | MICL.00935014/SNC | 9 | 350 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.00935014/SNC
Build-In Floor | Mini Canal | MICL.00935018/ANA | 9 | 350 | 18 | 18 | 542 | 542 | 542 | 0.012905 | 211 | 0.0050238 | 617 | 0.01469 | 1.362 | A04 | MICL0.00935018/ANA
Build-In Floor | Mini Canal | MICL.00935018/DBL | 9 | 350 | 18 | 18 | 700 | 700 | 700 | 0.016667 | 272 | 0.0064762 | 797 | 0.018976 | 1.362 | A04 | MICL0.00935018/DBL
Build-In Floor | Mini Canal | MICL.00935018/DBN | 9 | 350 | 18 | 18 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00935018/DBN
Build-In Floor | Mini Canal | MICL.00935018/DBR | 9 | 350 | 18 | 18 | 700 | 700 | 700 | 0.016667 | 272 | 0.0064762 | 797 | 0.018976 | 1.362 | A04 | MICL0.00935018/DBR
Build-In Floor | Mini Canal | MICL.00935018/DBV | 9 | 350 | 18 | 18 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00935018/DBV
Build-In Floor | Mini Canal | MICL.00935018/DDB | 9 | 350 | 18 | 18 | 700 | 700 | 700 | 0.016667 | 272 | 0.0064762 | 797 | 0.018976 | 1.362 | A04 | MICL0.00935018/DDB
Build-In Floor | Mini Canal | MICL.00935018/DMN | 9 | 350 | 18 | 18 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00935018/DMN
Build-In Floor | Mini Canal | MICL.00935018/DMV | 9 | 350 | 18 | 18 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00935018/DMV
Build-In Floor | Mini Canal | MICL.00935018/DNA | 9 | 350 | 18 | 18 | 700 | 700 | 700 | 0.016667 | 272 | 0.0064762 | 797 | 0.018976 | 1.362 | A04 | MICL0.00935018/DNA
Build-In Floor | Mini Canal | MICL.00935018/DNC | 9 | 350 | 18 | 18 | 700 | 700 | 700 | 0.016667 | 272 | 0.0064762 | 797 | 0.018976 | 1.362 | A04 | MICL0.00935018/DNC
Build-In Floor | Mini Canal | MICL.00935018/DON | 9 | 350 | 18 | 18 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00935018/DON
Build-In Floor | Mini Canal | MICL.00935018/DOV | 9 | 350 | 18 | 18 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.00935018/DOV
Build-In Floor | Mini Canal | MICL.00935018/RBL | 9 | 350 | 18 | 18 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.00935018/RBL
Build-In Floor | Mini Canal | MICL.00935018/RBN | 9 | 350 | 18 | 18 | 700 | 700 | 700 | 0.016667 | 272 | 0.0064762 | 797 | 0.018976 | 1.362 | A04 | MICL0.00935018/RBN
Build-In Floor | Mini Canal | MICL.00935018/RBR | 9 | 350 | 18 | 18 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.00935018/RBR
Build-In Floor | Mini Canal | MICL.00935018/RBV | 9 | 350 | 18 | 18 | 700 | 700 | 700 | 0.016667 | 272 | 0.0064762 | 797 | 0.018976 | 1.362 | A04 | MICL0.00935018/RBV
Build-In Floor | Mini Canal | MICL.00935018/RDB | 9 | 350 | 18 | 18 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.00935018/RDB
Build-In Floor | Mini Canal | MICL.00935018/RMN | 9 | 350 | 18 | 18 | 700 | 700 | 700 | 0.016667 | 272 | 0.0064762 | 797 | 0.018976 | 1.362 | A04 | MICL0.00935018/RMN
Build-In Floor | Mini Canal | MICL.00935018/RMV | 9 | 350 | 18 | 18 | 700 | 700 | 700 | 0.016667 | 272 | 0.0064762 | 797 | 0.018976 | 1.362 | A04 | MICL0.00935018/RMV
Build-In Floor | Mini Canal | MICL.00935018/RNA | 9 | 350 | 18 | 18 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.00935018/RNA
Build-In Floor | Mini Canal | MICL.00935018/RON | 9 | 350 | 18 | 18 | 700 | 700 | 700 | 0.016667 | 272 | 0.0064762 | 797 | 0.018976 | 1.362 | A04 | MICL0.00935018/RON
Build-In Floor | Mini Canal | MICL.00935018/ROV | 9 | 350 | 18 | 18 | 700 | 700 | 700 | 0.016667 | 272 | 0.0064762 | 797 | 0.018976 | 1.362 | A04 | MICL0.00935018/ROV
Build-In Floor | Mini Canal | MICL.00935018/RSS | 9 | 350 | 18 | 18 | 693 | 693 | 693 | 0.0165 | 270 | 0.0064286 | 789 | 0.018786 | 1.362 | A04 | MICL0.00935018/RSS
Build-In Floor | Mini Canal | MICL.00935018/SBL | 9 | 350 | 18 | 18 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.00935018/SBL
Build-In Floor | Mini Canal | MICL.00935018/SBR | 9 | 350 | 18 | 18 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.00935018/SBR
Build-In Floor | Mini Canal | MICL.00935018/SDB | 9 | 350 | 18 | 18 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.00935018/SDB
Build-In Floor | Mini Canal | MICL.00935018/SNA | 9 | 350 | 18 | 18 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.00935018/SNA
Build-In Floor | Mini Canal | MICL.00935018/SNC | 9 | 350 | 18 | 18 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.00935018/SNC
Build-In Floor | Mini Canal | MICL.00935026/ANA | 9 | 350 | 26 | 26 | 711 | 711 | 711 | 0.016929 | 277 | 0.0065952 | 810 | 0.019286 | 1.362 | A04 | MICL0.00935026/ANA
Build-In Floor | Mini Canal | MICL.00935026/DBL | 9 | 350 | 26 | 26 | 920 | 920 | 920 | 0.021905 | 358 | 0.0085238 | 1048 | 0.024952 | 1.362 | A04 | MICL0.00935026/DBL
Build-In Floor | Mini Canal | MICL.00935026/DBN | 9 | 350 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.00935026/DBN
Build-In Floor | Mini Canal | MICL.00935026/DBR | 9 | 350 | 26 | 26 | 920 | 920 | 920 | 0.021905 | 358 | 0.0085238 | 1048 | 0.024952 | 1.362 | A04 | MICL0.00935026/DBR
Build-In Floor | Mini Canal | MICL.00935026/DBV | 9 | 350 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.00935026/DBV
Build-In Floor | Mini Canal | MICL.00935026/DDB | 9 | 350 | 26 | 26 | 920 | 920 | 920 | 0.021905 | 358 | 0.0085238 | 1048 | 0.024952 | 1.362 | A04 | MICL0.00935026/DDB
Build-In Floor | Mini Canal | MICL.00935026/DMN | 9 | 350 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.00935026/DMN
Build-In Floor | Mini Canal | MICL.00935026/DMV | 9 | 350 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.00935026/DMV
Build-In Floor | Mini Canal | MICL.00935026/DNA | 9 | 350 | 26 | 26 | 920 | 920 | 920 | 0.021905 | 358 | 0.0085238 | 1048 | 0.024952 | 1.362 | A04 | MICL0.00935026/DNA
Build-In Floor | Mini Canal | MICL.00935026/DNC | 9 | 350 | 26 | 26 | 920 | 920 | 920 | 0.021905 | 358 | 0.0085238 | 1048 | 0.024952 | 1.362 | A04 | MICL0.00935026/DNC
Build-In Floor | Mini Canal | MICL.00935026/DON | 9 | 350 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.00935026/DON
Build-In Floor | Mini Canal | MICL.00935026/DOV | 9 | 350 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.00935026/DOV
Build-In Floor | Mini Canal | MICL.00935026/PNC | 9 | 350 | 26 | 26 | 806 | 806 | 806 | 0.01919 | 314 | 0.0074762 | 918 | 0.021857 | 1.362 | A04 | MICL0.00935026/PNC
Build-In Floor | Mini Canal | MICL.00935026/RBL | 9 | 350 | 26 | 26 | 948 | 948 | 948 | 0.022571 | 369 | 0.0087857 | 1080 | 0.025714 | 1.362 | A04 | MICL0.00935026/RBL
Build-In Floor | Mini Canal | MICL.00935026/RBN | 9 | 350 | 26 | 26 | 920 | 920 | 920 | 0.021905 | 358 | 0.0085238 | 1048 | 0.024952 | 1.362 | A04 | MICL0.00935026/RBN
Build-In Floor | Mini Canal | MICL.00935026/RBR | 9 | 350 | 26 | 26 | 948 | 948 | 948 | 0.022571 | 369 | 0.0087857 | 1080 | 0.025714 | 1.362 | A04 | MICL0.00935026/RBR
Build-In Floor | Mini Canal | MICL.00935026/RBV | 9 | 350 | 26 | 26 | 920 | 920 | 920 | 0.021905 | 358 | 0.0085238 | 1048 | 0.024952 | 1.362 | A04 | MICL0.00935026/RBV
Build-In Floor | Mini Canal | MICL.00935026/RDB | 9 | 350 | 26 | 26 | 948 | 948 | 948 | 0.022571 | 369 | 0.0087857 | 1080 | 0.025714 | 1.362 | A04 | MICL0.00935026/RDB
Build-In Floor | Mini Canal | MICL.00935026/RMN | 9 | 350 | 26 | 26 | 920 | 920 | 920 | 0.021905 | 358 | 0.0085238 | 1048 | 0.024952 | 1.362 | A04 | MICL0.00935026/RMN
Build-In Floor | Mini Canal | MICL.00935026/RMV | 9 | 350 | 26 | 26 | 920 | 920 | 920 | 0.021905 | 358 | 0.0085238 | 1048 | 0.024952 | 1.362 | A04 | MICL0.00935026/RMV
Build-In Floor | Mini Canal | MICL.00935026/RNA | 9 | 350 | 26 | 26 | 948 | 948 | 948 | 0.022571 | 369 | 0.0087857 | 1080 | 0.025714 | 1.362 | A04 | MICL0.00935026/RNA
Build-In Floor | Mini Canal | MICL.00935026/RON | 9 | 350 | 26 | 26 | 920 | 920 | 920 | 0.021905 | 358 | 0.0085238 | 1048 | 0.024952 | 1.362 | A04 | MICL0.00935026/RON
Build-In Floor | Mini Canal | MICL.00935026/ROV | 9 | 350 | 26 | 26 | 920 | 920 | 920 | 0.021905 | 358 | 0.0085238 | 1048 | 0.024952 | 1.362 | A04 | MICL0.00935026/ROV
Build-In Floor | Mini Canal | MICL.00935026/RSS | 9 | 350 | 26 | 26 | 910 | 910 | 910 | 0.021667 | 354 | 0.0084286 | 1036 | 0.024667 | 1.362 | A04 | MICL0.00935026/RSS
Build-In Floor | Mini Canal | MICL.00935026/SBL | 9 | 350 | 26 | 26 | 948 | 948 | 948 | 0.022571 | 369 | 0.0087857 | 1080 | 0.025714 | 1.362 | A04 | MICL0.00935026/SBL
Build-In Floor | Mini Canal | MICL.00935026/SBR | 9 | 350 | 26 | 26 | 948 | 948 | 948 | 0.022571 | 369 | 0.0087857 | 1080 | 0.025714 | 1.362 | A04 | MICL0.00935026/SBR
Build-In Floor | Mini Canal | MICL.00935026/SDB | 9 | 350 | 26 | 26 | 948 | 948 | 948 | 0.022571 | 369 | 0.0087857 | 1080 | 0.025714 | 1.362 | A04 | MICL0.00935026/SDB
Build-In Floor | Mini Canal | MICL.00935026/SNA | 9 | 350 | 26 | 26 | 948 | 948 | 948 | 0.022571 | 369 | 0.0087857 | 1080 | 0.025714 | 1.362 | A04 | MICL0.00935026/SNA
Build-In Floor | Mini Canal | MICL.00935026/SNC | 9 | 350 | 26 | 26 | 948 | 948 | 948 | 0.022571 | 369 | 0.0087857 | 1080 | 0.025714 | 1.362 | A04 | MICL0.00935026/SNC
Build-In Floor | Mini Canal | MICL.00935034/ANA | 9 | 350 | 34 | 34 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00935034/ANA
Build-In Floor | Mini Canal | MICL.00935034/DBL | 9 | 350 | 34 | 34 | 1194 | 1194 | 1194 | 0.028429 | 464 | 0.011048 | 1360 | 0.032381 | 1.362 | A04 | MICL0.00935034/DBL
Build-In Floor | Mini Canal | MICL.00935034/DBN | 9 | 350 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.00935034/DBN
Build-In Floor | Mini Canal | MICL.00935034/DBR | 9 | 350 | 34 | 34 | 1194 | 1194 | 1194 | 0.028429 | 464 | 0.011048 | 1360 | 0.032381 | 1.362 | A04 | MICL0.00935034/DBR
Build-In Floor | Mini Canal | MICL.00935034/DBV | 9 | 350 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.00935034/DBV
Build-In Floor | Mini Canal | MICL.00935034/DDB | 9 | 350 | 34 | 34 | 1194 | 1194 | 1194 | 0.028429 | 464 | 0.011048 | 1360 | 0.032381 | 1.362 | A04 | MICL0.00935034/DDB
Build-In Floor | Mini Canal | MICL.00935034/DMN | 9 | 350 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.00935034/DMN
Build-In Floor | Mini Canal | MICL.00935034/DMV | 9 | 350 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.00935034/DMV
Build-In Floor | Mini Canal | MICL.00935034/DNA | 9 | 350 | 34 | 34 | 1194 | 1194 | 1194 | 0.028429 | 464 | 0.011048 | 1360 | 0.032381 | 1.362 | A04 | MICL0.00935034/DNA
Build-In Floor | Mini Canal | MICL.00935034/DNC | 9 | 350 | 34 | 34 | 1194 | 1194 | 1194 | 0.028429 | 464 | 0.011048 | 1360 | 0.032381 | 1.362 | A04 | MICL0.00935034/DNC
Build-In Floor | Mini Canal | MICL.00935034/DON | 9 | 350 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.00935034/DON
Build-In Floor | Mini Canal | MICL.00935034/DOV | 9 | 350 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.00935034/DOV
Build-In Floor | Mini Canal | MICL.00935034/PNC | 9 | 350 | 34 | 34 | 1046 | 1046 | 1046 | 0.024905 | 407 | 0.0096905 | 1191 | 0.028357 | 1.362 | A04 | MICL0.00935034/PNC
Build-In Floor | Mini Canal | MICL.00935034/RBL | 9 | 350 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.00935034/RBL
Build-In Floor | Mini Canal | MICL.00935034/RBN | 9 | 350 | 34 | 34 | 1194 | 1194 | 1194 | 0.028429 | 464 | 0.011048 | 1360 | 0.032381 | 1.362 | A04 | MICL0.00935034/RBN
Build-In Floor | Mini Canal | MICL.00935034/RBR | 9 | 350 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.00935034/RBR
Build-In Floor | Mini Canal | MICL.00935034/RBV | 9 | 350 | 34 | 34 | 1194 | 1194 | 1194 | 0.028429 | 464 | 0.011048 | 1360 | 0.032381 | 1.362 | A04 | MICL0.00935034/RBV
Build-In Floor | Mini Canal | MICL.00935034/RDB | 9 | 350 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.00935034/RDB
Build-In Floor | Mini Canal | MICL.00935034/RMN | 9 | 350 | 34 | 34 | 1194 | 1194 | 1194 | 0.028429 | 464 | 0.011048 | 1360 | 0.032381 | 1.362 | A04 | MICL0.00935034/RMN
Build-In Floor | Mini Canal | MICL.00935034/RMV | 9 | 350 | 34 | 34 | 1194 | 1194 | 1194 | 0.028429 | 464 | 0.011048 | 1360 | 0.032381 | 1.362 | A04 | MICL0.00935034/RMV
Build-In Floor | Mini Canal | MICL.00935034/RNA | 9 | 350 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.00935034/RNA
Build-In Floor | Mini Canal | MICL.00935034/RON | 9 | 350 | 34 | 34 | 1194 | 1194 | 1194 | 0.028429 | 464 | 0.011048 | 1360 | 0.032381 | 1.362 | A04 | MICL0.00935034/RON
Build-In Floor | Mini Canal | MICL.00935034/ROV | 9 | 350 | 34 | 34 | 1194 | 1194 | 1194 | 0.028429 | 464 | 0.011048 | 1360 | 0.032381 | 1.362 | A04 | MICL0.00935034/ROV
Build-In Floor | Mini Canal | MICL.00935034/RSS | 9 | 350 | 34 | 34 | 1182 | 1182 | 1182 | 0.028143 | 460 | 0.010952 | 1346 | 0.032048 | 1.362 | A04 | MICL0.00935034/RSS
Build-In Floor | Mini Canal | MICL.00935034/SBL | 9 | 350 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.00935034/SBL
Build-In Floor | Mini Canal | MICL.00935034/SBR | 9 | 350 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.00935034/SBR
Build-In Floor | Mini Canal | MICL.00935034/SDB | 9 | 350 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.00935034/SDB
Build-In Floor | Mini Canal | MICL.00935034/SNA | 9 | 350 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.00935034/SNA
Build-In Floor | Mini Canal | MICL.00935034/SNC | 9 | 350 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.00935034/SNC
Build-In Floor | Mini Canal | MICL.00935042/ANA | 9 | 350 | 42 | 42 | 1333 | 1333 | 1333 | 0.031738 | 519 | 0.012357 | 1518 | 0.036143 | 1.362 | A04 | MICL0.00935042/ANA
Build-In Floor | Mini Canal | MICL.00935042/DBL | 9 | 350 | 42 | 42 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.00935042/DBL
Build-In Floor | Mini Canal | MICL.00935042/DBN | 9 | 350 | 42 | 42 | 1653 | 1653 | 1653 | 0.039357 | 643 | 0.01531 | 1883 | 0.044833 | 1.362 | A04 | MICL0.00935042/DBN
Build-In Floor | Mini Canal | MICL.00935042/DBR | 9 | 350 | 42 | 42 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.00935042/DBR
Build-In Floor | Mini Canal | MICL.00935042/DBV | 9 | 350 | 42 | 42 | 1653 | 1653 | 1653 | 0.039357 | 643 | 0.01531 | 1883 | 0.044833 | 1.362 | A04 | MICL0.00935042/DBV
Build-In Floor | Mini Canal | MICL.00935042/DDB | 9 | 350 | 42 | 42 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.00935042/DDB
Build-In Floor | Mini Canal | MICL.00935042/DMN | 9 | 350 | 42 | 42 | 1653 | 1653 | 1653 | 0.039357 | 643 | 0.01531 | 1883 | 0.044833 | 1.362 | A04 | MICL0.00935042/DMN
Build-In Floor | Mini Canal | MICL.00935042/DMV | 9 | 350 | 42 | 42 | 1653 | 1653 | 1653 | 0.039357 | 643 | 0.01531 | 1883 | 0.044833 | 1.362 | A04 | MICL0.00935042/DMV
Build-In Floor | Mini Canal | MICL.00935042/DNA | 9 | 350 | 42 | 42 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.00935042/DNA
Build-In Floor | Mini Canal | MICL.00935042/DNC | 9 | 350 | 42 | 42 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.00935042/DNC
Build-In Floor | Mini Canal | MICL.00935042/DON | 9 | 350 | 42 | 42 | 1653 | 1653 | 1653 | 0.039357 | 643 | 0.01531 | 1883 | 0.044833 | 1.362 | A04 | MICL0.00935042/DON
Build-In Floor | Mini Canal | MICL.00935042/DOV | 9 | 350 | 42 | 42 | 1653 | 1653 | 1653 | 0.039357 | 643 | 0.01531 | 1883 | 0.044833 | 1.362 | A04 | MICL0.00935042/DOV
Build-In Floor | Mini Canal | MICL.00935042/PNC | 9 | 350 | 42 | 42 | 1510 | 1510 | 1510 | 0.035952 | 587 | 0.013976 | 1720 | 0.040952 | 1.362 | A04 | MICL0.00935042/PNC
Build-In Floor | Mini Canal | MICL.00935042/RBL | 9 | 350 | 42 | 42 | 1777 | 1777 | 1777 | 0.04231 | 691 | 0.016452 | 2024 | 0.04819 | 1.362 | A04 | MICL0.00935042/RBL
Build-In Floor | Mini Canal | MICL.00935042/RBN | 9 | 350 | 42 | 42 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.00935042/RBN
Build-In Floor | Mini Canal | MICL.00935042/RBR | 9 | 350 | 42 | 42 | 1777 | 1777 | 1777 | 0.04231 | 691 | 0.016452 | 2024 | 0.04819 | 1.362 | A04 | MICL0.00935042/RBR
Build-In Floor | Mini Canal | MICL.00935042/RBV | 9 | 350 | 42 | 42 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.00935042/RBV
Build-In Floor | Mini Canal | MICL.00935042/RDB | 9 | 350 | 42 | 42 | 1777 | 1777 | 1777 | 0.04231 | 691 | 0.016452 | 2024 | 0.04819 | 1.362 | A04 | MICL0.00935042/RDB
Build-In Floor | Mini Canal | MICL.00935042/RMN | 9 | 350 | 42 | 42 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.00935042/RMN
Build-In Floor | Mini Canal | MICL.00935042/RMV | 9 | 350 | 42 | 42 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.00935042/RMV
Build-In Floor | Mini Canal | MICL.00935042/RNA | 9 | 350 | 42 | 42 | 1777 | 1777 | 1777 | 0.04231 | 691 | 0.016452 | 2024 | 0.04819 | 1.362 | A04 | MICL0.00935042/RNA
Build-In Floor | Mini Canal | MICL.00935042/RON | 9 | 350 | 42 | 42 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.00935042/RON
Build-In Floor | Mini Canal | MICL.00935042/ROV | 9 | 350 | 42 | 42 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.00935042/ROV
Build-In Floor | Mini Canal | MICL.00935042/RSS | 9 | 350 | 42 | 42 | 1706 | 1706 | 1706 | 0.040619 | 664 | 0.01581 | 1943 | 0.046262 | 1.362 | A04 | MICL0.00935042/RSS
Build-In Floor | Mini Canal | MICL.00935042/SBL | 9 | 350 | 42 | 42 | 1777 | 1777 | 1777 | 0.04231 | 691 | 0.016452 | 2024 | 0.04819 | 1.362 | A04 | MICL0.00935042/SBL
Build-In Floor | Mini Canal | MICL.00935042/SBR | 9 | 350 | 42 | 42 | 1777 | 1777 | 1777 | 0.04231 | 691 | 0.016452 | 2024 | 0.04819 | 1.362 | A04 | MICL0.00935042/SBR
Build-In Floor | Mini Canal | MICL.00935042/SDB | 9 | 350 | 42 | 42 | 1777 | 1777 | 1777 | 0.04231 | 691 | 0.016452 | 2024 | 0.04819 | 1.362 | A04 | MICL0.00935042/SDB
Build-In Floor | Mini Canal | MICL.00935042/SNA | 9 | 350 | 42 | 42 | 1777 | 1777 | 1777 | 0.04231 | 691 | 0.016452 | 2024 | 0.04819 | 1.362 | A04 | MICL0.00935042/SNA
Build-In Floor | Mini Canal | MICL.00935042/SNC | 9 | 350 | 42 | 42 | 1777 | 1777 | 1777 | 0.04231 | 691 | 0.016452 | 2024 | 0.04819 | 1.362 | A04 | MICL0.00935042/SNC
Build-In Floor | Mini Canal | MICL.00937014/ANA | 9 | 370 | 14 | 14 | 485 | 485 | 485 | 0.011548 | 189 | 0.0045 | 552 | 0.013143 | 1.362 | A04 | MICL0.00937014/ANA
Build-In Floor | Mini Canal | MICL.00937014/DBL | 9 | 370 | 14 | 14 | 628 | 628 | 628 | 0.014952 | 244 | 0.0058095 | 715 | 0.017024 | 1.362 | A04 | MICL0.00937014/DBL
Build-In Floor | Mini Canal | MICL.00937014/DBN | 9 | 370 | 14 | 14 | 602 | 602 | 602 | 0.014333 | 234 | 0.0055714 | 686 | 0.016333 | 1.362 | A04 | MICL0.00937014/DBN
Build-In Floor | Mini Canal | MICL.00937014/DBR | 9 | 370 | 14 | 14 | 628 | 628 | 628 | 0.014952 | 244 | 0.0058095 | 715 | 0.017024 | 1.362 | A04 | MICL0.00937014/DBR
Build-In Floor | Mini Canal | MICL.00937014/DBV | 9 | 370 | 14 | 14 | 602 | 602 | 602 | 0.014333 | 234 | 0.0055714 | 686 | 0.016333 | 1.362 | A04 | MICL0.00937014/DBV
Build-In Floor | Mini Canal | MICL.00937014/DDB | 9 | 370 | 14 | 14 | 628 | 628 | 628 | 0.014952 | 244 | 0.0058095 | 715 | 0.017024 | 1.362 | A04 | MICL0.00937014/DDB
Build-In Floor | Mini Canal | MICL.00937014/DMN | 9 | 370 | 14 | 14 | 602 | 602 | 602 | 0.014333 | 234 | 0.0055714 | 686 | 0.016333 | 1.362 | A04 | MICL0.00937014/DMN
Build-In Floor | Mini Canal | MICL.00937014/DMV | 9 | 370 | 14 | 14 | 602 | 602 | 602 | 0.014333 | 234 | 0.0055714 | 686 | 0.016333 | 1.362 | A04 | MICL0.00937014/DMV
Build-In Floor | Mini Canal | MICL.00937014/DNA | 9 | 370 | 14 | 14 | 628 | 628 | 628 | 0.014952 | 244 | 0.0058095 | 715 | 0.017024 | 1.362 | A04 | MICL0.00937014/DNA
Build-In Floor | Mini Canal | MICL.00937014/DNC | 9 | 370 | 14 | 14 | 628 | 628 | 628 | 0.014952 | 244 | 0.0058095 | 715 | 0.017024 | 1.362 | A04 | MICL0.00937014/DNC
Build-In Floor | Mini Canal | MICL.00937014/DON | 9 | 370 | 14 | 14 | 602 | 602 | 602 | 0.014333 | 234 | 0.0055714 | 686 | 0.016333 | 1.362 | A04 | MICL0.00937014/DON
Build-In Floor | Mini Canal | MICL.00937014/DOV | 9 | 370 | 14 | 14 | 602 | 602 | 602 | 0.014333 | 234 | 0.0055714 | 686 | 0.016333 | 1.362 | A04 | MICL0.00937014/DOV
Build-In Floor | Mini Canal | MICL.00937014/RBL | 9 | 370 | 14 | 14 | 647 | 647 | 647 | 0.015405 | 252 | 0.006 | 737 | 0.017548 | 1.362 | A04 | MICL0.00937014/RBL
Build-In Floor | Mini Canal | MICL.00937014/RBN | 9 | 370 | 14 | 14 | 628 | 628 | 628 | 0.014952 | 244 | 0.0058095 | 715 | 0.017024 | 1.362 | A04 | MICL0.00937014/RBN
Build-In Floor | Mini Canal | MICL.00937014/RBR | 9 | 370 | 14 | 14 | 647 | 647 | 647 | 0.015405 | 252 | 0.006 | 737 | 0.017548 | 1.362 | A04 | MICL0.00937014/RBR
Build-In Floor | Mini Canal | MICL.00937014/RBV | 9 | 370 | 14 | 14 | 628 | 628 | 628 | 0.014952 | 244 | 0.0058095 | 715 | 0.017024 | 1.362 | A04 | MICL0.00937014/RBV
Build-In Floor | Mini Canal | MICL.00937014/RDB | 9 | 370 | 14 | 14 | 647 | 647 | 647 | 0.015405 | 252 | 0.006 | 737 | 0.017548 | 1.362 | A04 | MICL0.00937014/RDB
Build-In Floor | Mini Canal | MICL.00937014/RMN | 9 | 370 | 14 | 14 | 628 | 628 | 628 | 0.014952 | 244 | 0.0058095 | 715 | 0.017024 | 1.362 | A04 | MICL0.00937014/RMN
Build-In Floor | Mini Canal | MICL.00937014/RMV | 9 | 370 | 14 | 14 | 628 | 628 | 628 | 0.014952 | 244 | 0.0058095 | 715 | 0.017024 | 1.362 | A04 | MICL0.00937014/RMV
Build-In Floor | Mini Canal | MICL.00937014/RNA | 9 | 370 | 14 | 14 | 647 | 647 | 647 | 0.015405 | 252 | 0.006 | 737 | 0.017548 | 1.362 | A04 | MICL0.00937014/RNA
Build-In Floor | Mini Canal | MICL.00937014/RON | 9 | 370 | 14 | 14 | 628 | 628 | 628 | 0.014952 | 244 | 0.0058095 | 715 | 0.017024 | 1.362 | A04 | MICL0.00937014/RON
Build-In Floor | Mini Canal | MICL.00937014/ROV | 9 | 370 | 14 | 14 | 628 | 628 | 628 | 0.014952 | 244 | 0.0058095 | 715 | 0.017024 | 1.362 | A04 | MICL0.00937014/ROV
Build-In Floor | Mini Canal | MICL.00937014/RSS | 9 | 370 | 14 | 14 | 621 | 621 | 621 | 0.014786 | 242 | 0.0057619 | 707 | 0.016833 | 1.362 | A04 | MICL0.00937014/RSS
Build-In Floor | Mini Canal | MICL.00937014/SBL | 9 | 370 | 14 | 14 | 647 | 647 | 647 | 0.015405 | 252 | 0.006 | 737 | 0.017548 | 1.362 | A04 | MICL0.00937014/SBL
Build-In Floor | Mini Canal | MICL.00937014/SBR | 9 | 370 | 14 | 14 | 647 | 647 | 647 | 0.015405 | 252 | 0.006 | 737 | 0.017548 | 1.362 | A04 | MICL0.00937014/SBR
Build-In Floor | Mini Canal | MICL.00937014/SDB | 9 | 370 | 14 | 14 | 647 | 647 | 647 | 0.015405 | 252 | 0.006 | 737 | 0.017548 | 1.362 | A04 | MICL0.00937014/SDB
Build-In Floor | Mini Canal | MICL.00937014/SNA | 9 | 370 | 14 | 14 | 647 | 647 | 647 | 0.015405 | 252 | 0.006 | 737 | 0.017548 | 1.362 | A04 | MICL0.00937014/SNA
Build-In Floor | Mini Canal | MICL.00937014/SNC | 9 | 370 | 14 | 14 | 647 | 647 | 647 | 0.015405 | 252 | 0.006 | 737 | 0.017548 | 1.362 | A04 | MICL0.00937014/SNC
Build-In Floor | Mini Canal | MICL.00937018/ANA | 9 | 370 | 18 | 18 | 575 | 575 | 575 | 0.01369 | 224 | 0.0053333 | 655 | 0.015595 | 1.362 | A04 | MICL0.00937018/ANA
Build-In Floor | Mini Canal | MICL.00937018/DBL | 9 | 370 | 18 | 18 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00937018/DBL
Build-In Floor | Mini Canal | MICL.00937018/DBN | 9 | 370 | 18 | 18 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.00937018/DBN
Build-In Floor | Mini Canal | MICL.00937018/DBR | 9 | 370 | 18 | 18 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00937018/DBR
Build-In Floor | Mini Canal | MICL.00937018/DBV | 9 | 370 | 18 | 18 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.00937018/DBV
Build-In Floor | Mini Canal | MICL.00937018/DDB | 9 | 370 | 18 | 18 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00937018/DDB
Build-In Floor | Mini Canal | MICL.00937018/DMN | 9 | 370 | 18 | 18 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.00937018/DMN
Build-In Floor | Mini Canal | MICL.00937018/DMV | 9 | 370 | 18 | 18 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.00937018/DMV
Build-In Floor | Mini Canal | MICL.00937018/DNA | 9 | 370 | 18 | 18 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00937018/DNA
Build-In Floor | Mini Canal | MICL.00937018/DNC | 9 | 370 | 18 | 18 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00937018/DNC
Build-In Floor | Mini Canal | MICL.00937018/DON | 9 | 370 | 18 | 18 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.00937018/DON
Build-In Floor | Mini Canal | MICL.00937018/DOV | 9 | 370 | 18 | 18 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.00937018/DOV
Build-In Floor | Mini Canal | MICL.00937018/RBL | 9 | 370 | 18 | 18 | 767 | 767 | 767 | 0.018262 | 298 | 0.0070952 | 874 | 0.02081 | 1.362 | A04 | MICL0.00937018/RBL
Build-In Floor | Mini Canal | MICL.00937018/RBN | 9 | 370 | 18 | 18 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00937018/RBN
Build-In Floor | Mini Canal | MICL.00937018/RBR | 9 | 370 | 18 | 18 | 767 | 767 | 767 | 0.018262 | 298 | 0.0070952 | 874 | 0.02081 | 1.362 | A04 | MICL0.00937018/RBR
Build-In Floor | Mini Canal | MICL.00937018/RBV | 9 | 370 | 18 | 18 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00937018/RBV
Build-In Floor | Mini Canal | MICL.00937018/RDB | 9 | 370 | 18 | 18 | 767 | 767 | 767 | 0.018262 | 298 | 0.0070952 | 874 | 0.02081 | 1.362 | A04 | MICL0.00937018/RDB
Build-In Floor | Mini Canal | MICL.00937018/RMN | 9 | 370 | 18 | 18 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00937018/RMN
Build-In Floor | Mini Canal | MICL.00937018/RMV | 9 | 370 | 18 | 18 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00937018/RMV
Build-In Floor | Mini Canal | MICL.00937018/RNA | 9 | 370 | 18 | 18 | 767 | 767 | 767 | 0.018262 | 298 | 0.0070952 | 874 | 0.02081 | 1.362 | A04 | MICL0.00937018/RNA
Build-In Floor | Mini Canal | MICL.00937018/RON | 9 | 370 | 18 | 18 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00937018/RON
Build-In Floor | Mini Canal | MICL.00937018/ROV | 9 | 370 | 18 | 18 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00937018/ROV
Build-In Floor | Mini Canal | MICL.00937018/RSS | 9 | 370 | 18 | 18 | 736 | 736 | 736 | 0.017524 | 286 | 0.0068095 | 838 | 0.019952 | 1.362 | A04 | MICL0.00937018/RSS
Build-In Floor | Mini Canal | MICL.00937018/SBL | 9 | 370 | 18 | 18 | 767 | 767 | 767 | 0.018262 | 298 | 0.0070952 | 874 | 0.02081 | 1.362 | A04 | MICL0.00937018/SBL
Build-In Floor | Mini Canal | MICL.00937018/SBR | 9 | 370 | 18 | 18 | 767 | 767 | 767 | 0.018262 | 298 | 0.0070952 | 874 | 0.02081 | 1.362 | A04 | MICL0.00937018/SBR
Build-In Floor | Mini Canal | MICL.00937018/SDB | 9 | 370 | 18 | 18 | 767 | 767 | 767 | 0.018262 | 298 | 0.0070952 | 874 | 0.02081 | 1.362 | A04 | MICL0.00937018/SDB
Build-In Floor | Mini Canal | MICL.00937018/SNA | 9 | 370 | 18 | 18 | 767 | 767 | 767 | 0.018262 | 298 | 0.0070952 | 874 | 0.02081 | 1.362 | A04 | MICL0.00937018/SNA
Build-In Floor | Mini Canal | MICL.00937018/SNC | 9 | 370 | 18 | 18 | 767 | 767 | 767 | 0.018262 | 298 | 0.0070952 | 874 | 0.02081 | 1.362 | A04 | MICL0.00937018/SNC
Build-In Floor | Mini Canal | MICL.00937026/ANA | 9 | 370 | 26 | 26 | 756 | 756 | 756 | 0.018 | 294 | 0.007 | 861 | 0.0205 | 1.362 | A04 | MICL0.00937026/ANA
Build-In Floor | Mini Canal | MICL.00937026/DBL | 9 | 370 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.00937026/DBL
Build-In Floor | Mini Canal | MICL.00937026/DBN | 9 | 370 | 26 | 26 | 937 | 937 | 937 | 0.02231 | 364 | 0.0086667 | 1067 | 0.025405 | 1.362 | A04 | MICL0.00937026/DBN
Build-In Floor | Mini Canal | MICL.00937026/DBR | 9 | 370 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.00937026/DBR
Build-In Floor | Mini Canal | MICL.00937026/DBV | 9 | 370 | 26 | 26 | 937 | 937 | 937 | 0.02231 | 364 | 0.0086667 | 1067 | 0.025405 | 1.362 | A04 | MICL0.00937026/DBV
Build-In Floor | Mini Canal | MICL.00937026/DDB | 9 | 370 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.00937026/DDB
Build-In Floor | Mini Canal | MICL.00937026/DMN | 9 | 370 | 26 | 26 | 937 | 937 | 937 | 0.02231 | 364 | 0.0086667 | 1067 | 0.025405 | 1.362 | A04 | MICL0.00937026/DMN
Build-In Floor | Mini Canal | MICL.00937026/DMV | 9 | 370 | 26 | 26 | 937 | 937 | 937 | 0.02231 | 364 | 0.0086667 | 1067 | 0.025405 | 1.362 | A04 | MICL0.00937026/DMV
Build-In Floor | Mini Canal | MICL.00937026/DNA | 9 | 370 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.00937026/DNA
Build-In Floor | Mini Canal | MICL.00937026/DNC | 9 | 370 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.00937026/DNC
Build-In Floor | Mini Canal | MICL.00937026/DON | 9 | 370 | 26 | 26 | 937 | 937 | 937 | 0.02231 | 364 | 0.0086667 | 1067 | 0.025405 | 1.362 | A04 | MICL0.00937026/DON
Build-In Floor | Mini Canal | MICL.00937026/DOV | 9 | 370 | 26 | 26 | 937 | 937 | 937 | 0.02231 | 364 | 0.0086667 | 1067 | 0.025405 | 1.362 | A04 | MICL0.00937026/DOV
Build-In Floor | Mini Canal | MICL.00937026/PNC | 9 | 370 | 26 | 26 | 857 | 857 | 857 | 0.020405 | 333 | 0.0079286 | 976 | 0.023238 | 1.362 | A04 | MICL0.00937026/PNC
Build-In Floor | Mini Canal | MICL.00937026/RBL | 9 | 370 | 26 | 26 | 1008 | 1008 | 1008 | 0.024 | 392 | 0.0093333 | 1148 | 0.027333 | 1.362 | A04 | MICL0.00937026/RBL
Build-In Floor | Mini Canal | MICL.00937026/RBN | 9 | 370 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.00937026/RBN
Build-In Floor | Mini Canal | MICL.00937026/RBR | 9 | 370 | 26 | 26 | 1008 | 1008 | 1008 | 0.024 | 392 | 0.0093333 | 1148 | 0.027333 | 1.362 | A04 | MICL0.00937026/RBR
Build-In Floor | Mini Canal | MICL.00937026/RBV | 9 | 370 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.00937026/RBV
Build-In Floor | Mini Canal | MICL.00937026/RDB | 9 | 370 | 26 | 26 | 1008 | 1008 | 1008 | 0.024 | 392 | 0.0093333 | 1148 | 0.027333 | 1.362 | A04 | MICL0.00937026/RDB
Build-In Floor | Mini Canal | MICL.00937026/RMN | 9 | 370 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.00937026/RMN
Build-In Floor | Mini Canal | MICL.00937026/RMV | 9 | 370 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.00937026/RMV
Build-In Floor | Mini Canal | MICL.00937026/RNA | 9 | 370 | 26 | 26 | 1008 | 1008 | 1008 | 0.024 | 392 | 0.0093333 | 1148 | 0.027333 | 1.362 | A04 | MICL0.00937026/RNA
Build-In Floor | Mini Canal | MICL.00937026/RON | 9 | 370 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.00937026/RON
Build-In Floor | Mini Canal | MICL.00937026/ROV | 9 | 370 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.00937026/ROV
Build-In Floor | Mini Canal | MICL.00937026/RSS | 9 | 370 | 26 | 26 | 968 | 968 | 968 | 0.023048 | 377 | 0.0089762 | 1103 | 0.026262 | 1.362 | A04 | MICL0.00937026/RSS
Build-In Floor | Mini Canal | MICL.00937026/SBL | 9 | 370 | 26 | 26 | 1008 | 1008 | 1008 | 0.024 | 392 | 0.0093333 | 1148 | 0.027333 | 1.362 | A04 | MICL0.00937026/SBL
Build-In Floor | Mini Canal | MICL.00937026/SBR | 9 | 370 | 26 | 26 | 1008 | 1008 | 1008 | 0.024 | 392 | 0.0093333 | 1148 | 0.027333 | 1.362 | A04 | MICL0.00937026/SBR
Build-In Floor | Mini Canal | MICL.00937026/SDB | 9 | 370 | 26 | 26 | 1008 | 1008 | 1008 | 0.024 | 392 | 0.0093333 | 1148 | 0.027333 | 1.362 | A04 | MICL0.00937026/SDB
Build-In Floor | Mini Canal | MICL.00937026/SNA | 9 | 370 | 26 | 26 | 1008 | 1008 | 1008 | 0.024 | 392 | 0.0093333 | 1148 | 0.027333 | 1.362 | A04 | MICL0.00937026/SNA
Build-In Floor | Mini Canal | MICL.00937026/SNC | 9 | 370 | 26 | 26 | 1008 | 1008 | 1008 | 0.024 | 392 | 0.0093333 | 1148 | 0.027333 | 1.362 | A04 | MICL0.00937026/SNC
Build-In Floor | Mini Canal | MICL.00937034/ANA | 9 | 370 | 34 | 34 | 980 | 980 | 980 | 0.023333 | 381 | 0.0090714 | 1116 | 0.026571 | 1.362 | A04 | MICL0.00937034/ANA
Build-In Floor | Mini Canal | MICL.00937034/DBL | 9 | 370 | 34 | 34 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00937034/DBL
Build-In Floor | Mini Canal | MICL.00937034/DBN | 9 | 370 | 34 | 34 | 1216 | 1216 | 1216 | 0.028952 | 473 | 0.011262 | 1385 | 0.032976 | 1.362 | A04 | MICL0.00937034/DBN
Build-In Floor | Mini Canal | MICL.00937034/DBR | 9 | 370 | 34 | 34 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00937034/DBR
Build-In Floor | Mini Canal | MICL.00937034/DBV | 9 | 370 | 34 | 34 | 1216 | 1216 | 1216 | 0.028952 | 473 | 0.011262 | 1385 | 0.032976 | 1.362 | A04 | MICL0.00937034/DBV
Build-In Floor | Mini Canal | MICL.00937034/DDB | 9 | 370 | 34 | 34 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00937034/DDB
Build-In Floor | Mini Canal | MICL.00937034/DMN | 9 | 370 | 34 | 34 | 1216 | 1216 | 1216 | 0.028952 | 473 | 0.011262 | 1385 | 0.032976 | 1.362 | A04 | MICL0.00937034/DMN
Build-In Floor | Mini Canal | MICL.00937034/DMV | 9 | 370 | 34 | 34 | 1216 | 1216 | 1216 | 0.028952 | 473 | 0.011262 | 1385 | 0.032976 | 1.362 | A04 | MICL0.00937034/DMV
Build-In Floor | Mini Canal | MICL.00937034/DNA | 9 | 370 | 34 | 34 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00937034/DNA
Build-In Floor | Mini Canal | MICL.00937034/DNC | 9 | 370 | 34 | 34 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00937034/DNC
Build-In Floor | Mini Canal | MICL.00937034/DON | 9 | 370 | 34 | 34 | 1216 | 1216 | 1216 | 0.028952 | 473 | 0.011262 | 1385 | 0.032976 | 1.362 | A04 | MICL0.00937034/DON
Build-In Floor | Mini Canal | MICL.00937034/DOV | 9 | 370 | 34 | 34 | 1216 | 1216 | 1216 | 0.028952 | 473 | 0.011262 | 1385 | 0.032976 | 1.362 | A04 | MICL0.00937034/DOV
Build-In Floor | Mini Canal | MICL.00937034/PNC | 9 | 370 | 34 | 34 | 1111 | 1111 | 1111 | 0.026452 | 432 | 0.010286 | 1265 | 0.030119 | 1.362 | A04 | MICL0.00937034/PNC
Build-In Floor | Mini Canal | MICL.00937034/RBL | 9 | 370 | 34 | 34 | 1307 | 1307 | 1307 | 0.031119 | 508 | 0.012095 | 1489 | 0.035452 | 1.362 | A04 | MICL0.00937034/RBL
Build-In Floor | Mini Canal | MICL.00937034/RBN | 9 | 370 | 34 | 34 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00937034/RBN
Build-In Floor | Mini Canal | MICL.00937034/RBR | 9 | 370 | 34 | 34 | 1307 | 1307 | 1307 | 0.031119 | 508 | 0.012095 | 1489 | 0.035452 | 1.362 | A04 | MICL0.00937034/RBR
Build-In Floor | Mini Canal | MICL.00937034/RBV | 9 | 370 | 34 | 34 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00937034/RBV
Build-In Floor | Mini Canal | MICL.00937034/RDB | 9 | 370 | 34 | 34 | 1307 | 1307 | 1307 | 0.031119 | 508 | 0.012095 | 1489 | 0.035452 | 1.362 | A04 | MICL0.00937034/RDB
Build-In Floor | Mini Canal | MICL.00937034/RMN | 9 | 370 | 34 | 34 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00937034/RMN
Build-In Floor | Mini Canal | MICL.00937034/RMV | 9 | 370 | 34 | 34 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00937034/RMV
Build-In Floor | Mini Canal | MICL.00937034/RNA | 9 | 370 | 34 | 34 | 1307 | 1307 | 1307 | 0.031119 | 508 | 0.012095 | 1489 | 0.035452 | 1.362 | A04 | MICL0.00937034/RNA
Build-In Floor | Mini Canal | MICL.00937034/RON | 9 | 370 | 34 | 34 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00937034/RON
Build-In Floor | Mini Canal | MICL.00937034/ROV | 9 | 370 | 34 | 34 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00937034/ROV
Build-In Floor | Mini Canal | MICL.00937034/RSS | 9 | 370 | 34 | 34 | 1255 | 1255 | 1255 | 0.029881 | 488 | 0.011619 | 1429 | 0.034024 | 1.362 | A04 | MICL0.00937034/RSS
Build-In Floor | Mini Canal | MICL.00937034/SBL | 9 | 370 | 34 | 34 | 1307 | 1307 | 1307 | 0.031119 | 508 | 0.012095 | 1489 | 0.035452 | 1.362 | A04 | MICL0.00937034/SBL
Build-In Floor | Mini Canal | MICL.00937034/SBR | 9 | 370 | 34 | 34 | 1307 | 1307 | 1307 | 0.031119 | 508 | 0.012095 | 1489 | 0.035452 | 1.362 | A04 | MICL0.00937034/SBR
Build-In Floor | Mini Canal | MICL.00937034/SDB | 9 | 370 | 34 | 34 | 1307 | 1307 | 1307 | 0.031119 | 508 | 0.012095 | 1489 | 0.035452 | 1.362 | A04 | MICL0.00937034/SDB
Build-In Floor | Mini Canal | MICL.00937034/SNA | 9 | 370 | 34 | 34 | 1307 | 1307 | 1307 | 0.031119 | 508 | 0.012095 | 1489 | 0.035452 | 1.362 | A04 | MICL0.00937034/SNA
Build-In Floor | Mini Canal | MICL.00937034/SNC | 9 | 370 | 34 | 34 | 1307 | 1307 | 1307 | 0.031119 | 508 | 0.012095 | 1489 | 0.035452 | 1.362 | A04 | MICL0.00937034/SNC
Build-In Floor | Mini Canal | MICL.00937042/ANA | 9 | 370 | 42 | 42 | 1416 | 1416 | 1416 | 0.033714 | 551 | 0.013119 | 1613 | 0.038405 | 1.362 | A04 | MICL0.00937042/ANA
Build-In Floor | Mini Canal | MICL.00937042/DBL | 9 | 370 | 42 | 42 | 1831 | 1831 | 1831 | 0.043595 | 712 | 0.016952 | 2086 | 0.049667 | 1.362 | A04 | MICL0.00937042/DBL
Build-In Floor | Mini Canal | MICL.00937042/DBN | 9 | 370 | 42 | 42 | 1756 | 1756 | 1756 | 0.04181 | 683 | 0.016262 | 2000 | 0.047619 | 1.362 | A04 | MICL0.00937042/DBN
Build-In Floor | Mini Canal | MICL.00937042/DBR | 9 | 370 | 42 | 42 | 1831 | 1831 | 1831 | 0.043595 | 712 | 0.016952 | 2086 | 0.049667 | 1.362 | A04 | MICL0.00937042/DBR
Build-In Floor | Mini Canal | MICL.00937042/DBV | 9 | 370 | 42 | 42 | 1756 | 1756 | 1756 | 0.04181 | 683 | 0.016262 | 2000 | 0.047619 | 1.362 | A04 | MICL0.00937042/DBV
Build-In Floor | Mini Canal | MICL.00937042/DDB | 9 | 370 | 42 | 42 | 1831 | 1831 | 1831 | 0.043595 | 712 | 0.016952 | 2086 | 0.049667 | 1.362 | A04 | MICL0.00937042/DDB
Build-In Floor | Mini Canal | MICL.00937042/DMN | 9 | 370 | 42 | 42 | 1756 | 1756 | 1756 | 0.04181 | 683 | 0.016262 | 2000 | 0.047619 | 1.362 | A04 | MICL0.00937042/DMN
Build-In Floor | Mini Canal | MICL.00937042/DMV | 9 | 370 | 42 | 42 | 1756 | 1756 | 1756 | 0.04181 | 683 | 0.016262 | 2000 | 0.047619 | 1.362 | A04 | MICL0.00937042/DMV
Build-In Floor | Mini Canal | MICL.00937042/DNA | 9 | 370 | 42 | 42 | 1831 | 1831 | 1831 | 0.043595 | 712 | 0.016952 | 2086 | 0.049667 | 1.362 | A04 | MICL0.00937042/DNA
Build-In Floor | Mini Canal | MICL.00937042/DNC | 9 | 370 | 42 | 42 | 1831 | 1831 | 1831 | 0.043595 | 712 | 0.016952 | 2086 | 0.049667 | 1.362 | A04 | MICL0.00937042/DNC
Build-In Floor | Mini Canal | MICL.00937042/DON | 9 | 370 | 42 | 42 | 1756 | 1756 | 1756 | 0.04181 | 683 | 0.016262 | 2000 | 0.047619 | 1.362 | A04 | MICL0.00937042/DON
Build-In Floor | Mini Canal | MICL.00937042/DOV | 9 | 370 | 42 | 42 | 1756 | 1756 | 1756 | 0.04181 | 683 | 0.016262 | 2000 | 0.047619 | 1.362 | A04 | MICL0.00937042/DOV
Build-In Floor | Mini Canal | MICL.00937042/PNC | 9 | 370 | 42 | 42 | 1605 | 1605 | 1605 | 0.038214 | 624 | 0.014857 | 1828 | 0.043524 | 1.362 | A04 | MICL0.00937042/PNC
Build-In Floor | Mini Canal | MICL.00937042/RBL | 9 | 370 | 42 | 42 | 1888 | 1888 | 1888 | 0.044952 | 734 | 0.017476 | 2150 | 0.05119 | 1.362 | A04 | MICL0.00937042/RBL
Build-In Floor | Mini Canal | MICL.00937042/RBN | 9 | 370 | 42 | 42 | 1831 | 1831 | 1831 | 0.043595 | 712 | 0.016952 | 2086 | 0.049667 | 1.362 | A04 | MICL0.00937042/RBN
Build-In Floor | Mini Canal | MICL.00937042/RBR | 9 | 370 | 42 | 42 | 1888 | 1888 | 1888 | 0.044952 | 734 | 0.017476 | 2150 | 0.05119 | 1.362 | A04 | MICL0.00937042/RBR
Build-In Floor | Mini Canal | MICL.00937042/RBV | 9 | 370 | 42 | 42 | 1831 | 1831 | 1831 | 0.043595 | 712 | 0.016952 | 2086 | 0.049667 | 1.362 | A04 | MICL0.00937042/RBV
Build-In Floor | Mini Canal | MICL.00937042/RDB | 9 | 370 | 42 | 42 | 1888 | 1888 | 1888 | 0.044952 | 734 | 0.017476 | 2150 | 0.05119 | 1.362 | A04 | MICL0.00937042/RDB
Build-In Floor | Mini Canal | MICL.00937042/RMN | 9 | 370 | 42 | 42 | 1831 | 1831 | 1831 | 0.043595 | 712 | 0.016952 | 2086 | 0.049667 | 1.362 | A04 | MICL0.00937042/RMN
Build-In Floor | Mini Canal | MICL.00937042/RMV | 9 | 370 | 42 | 42 | 1831 | 1831 | 1831 | 0.043595 | 712 | 0.016952 | 2086 | 0.049667 | 1.362 | A04 | MICL0.00937042/RMV
Build-In Floor | Mini Canal | MICL.00937042/RNA | 9 | 370 | 42 | 42 | 1888 | 1888 | 1888 | 0.044952 | 734 | 0.017476 | 2150 | 0.05119 | 1.362 | A04 | MICL0.00937042/RNA
Build-In Floor | Mini Canal | MICL.00937042/RON | 9 | 370 | 42 | 42 | 1831 | 1831 | 1831 | 0.043595 | 712 | 0.016952 | 2086 | 0.049667 | 1.362 | A04 | MICL0.00937042/RON
Build-In Floor | Mini Canal | MICL.00937042/ROV | 9 | 370 | 42 | 42 | 1831 | 1831 | 1831 | 0.043595 | 712 | 0.016952 | 2086 | 0.049667 | 1.362 | A04 | MICL0.00937042/ROV
Build-In Floor | Mini Canal | MICL.00937042/RSS | 9 | 370 | 42 | 42 | 1812 | 1812 | 1812 | 0.043143 | 705 | 0.016786 | 2064 | 0.049143 | 1.362 | A04 | MICL0.00937042/RSS
Build-In Floor | Mini Canal | MICL.00937042/SBL | 9 | 370 | 42 | 42 | 1888 | 1888 | 1888 | 0.044952 | 734 | 0.017476 | 2150 | 0.05119 | 1.362 | A04 | MICL0.00937042/SBL
Build-In Floor | Mini Canal | MICL.00937042/SBR | 9 | 370 | 42 | 42 | 1888 | 1888 | 1888 | 0.044952 | 734 | 0.017476 | 2150 | 0.05119 | 1.362 | A04 | MICL0.00937042/SBR
Build-In Floor | Mini Canal | MICL.00937042/SDB | 9 | 370 | 42 | 42 | 1888 | 1888 | 1888 | 0.044952 | 734 | 0.017476 | 2150 | 0.05119 | 1.362 | A04 | MICL0.00937042/SDB
Build-In Floor | Mini Canal | MICL.00937042/SNA | 9 | 370 | 42 | 42 | 1888 | 1888 | 1888 | 0.044952 | 734 | 0.017476 | 2150 | 0.05119 | 1.362 | A04 | MICL0.00937042/SNA
Build-In Floor | Mini Canal | MICL.00937042/SNC | 9 | 370 | 42 | 42 | 1888 | 1888 | 1888 | 0.044952 | 734 | 0.017476 | 2150 | 0.05119 | 1.362 | A04 | MICL0.00937042/SNC
Build-In Floor | Mini Canal | MICL.00939014/ANA | 9 | 390 | 14 | 14 | 514 | 514 | 514 | 0.012238 | 200 | 0.0047619 | 585 | 0.013929 | 1.362 | A04 | MICL0.00939014/ANA
Build-In Floor | Mini Canal | MICL.00939014/DBL | 9 | 390 | 14 | 14 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.00939014/DBL
Build-In Floor | Mini Canal | MICL.00939014/DBN | 9 | 390 | 14 | 14 | 637 | 637 | 637 | 0.015167 | 248 | 0.0059048 | 726 | 0.017286 | 1.362 | A04 | MICL0.00939014/DBN
Build-In Floor | Mini Canal | MICL.00939014/DBR | 9 | 390 | 14 | 14 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.00939014/DBR
Build-In Floor | Mini Canal | MICL.00939014/DBV | 9 | 390 | 14 | 14 | 637 | 637 | 637 | 0.015167 | 248 | 0.0059048 | 726 | 0.017286 | 1.362 | A04 | MICL0.00939014/DBV
Build-In Floor | Mini Canal | MICL.00939014/DDB | 9 | 390 | 14 | 14 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.00939014/DDB
Build-In Floor | Mini Canal | MICL.00939014/DMN | 9 | 390 | 14 | 14 | 637 | 637 | 637 | 0.015167 | 248 | 0.0059048 | 726 | 0.017286 | 1.362 | A04 | MICL0.00939014/DMN
Build-In Floor | Mini Canal | MICL.00939014/DMV | 9 | 390 | 14 | 14 | 637 | 637 | 637 | 0.015167 | 248 | 0.0059048 | 726 | 0.017286 | 1.362 | A04 | MICL0.00939014/DMV
Build-In Floor | Mini Canal | MICL.00939014/DNA | 9 | 390 | 14 | 14 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.00939014/DNA
Build-In Floor | Mini Canal | MICL.00939014/DNC | 9 | 390 | 14 | 14 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.00939014/DNC
Build-In Floor | Mini Canal | MICL.00939014/DON | 9 | 390 | 14 | 14 | 637 | 637 | 637 | 0.015167 | 248 | 0.0059048 | 726 | 0.017286 | 1.362 | A04 | MICL0.00939014/DON
Build-In Floor | Mini Canal | MICL.00939014/DOV | 9 | 390 | 14 | 14 | 637 | 637 | 637 | 0.015167 | 248 | 0.0059048 | 726 | 0.017286 | 1.362 | A04 | MICL0.00939014/DOV
Build-In Floor | Mini Canal | MICL.00939014/RBL | 9 | 390 | 14 | 14 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.00939014/RBL
Build-In Floor | Mini Canal | MICL.00939014/RBN | 9 | 390 | 14 | 14 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.00939014/RBN
Build-In Floor | Mini Canal | MICL.00939014/RBR | 9 | 390 | 14 | 14 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.00939014/RBR
Build-In Floor | Mini Canal | MICL.00939014/RBV | 9 | 390 | 14 | 14 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.00939014/RBV
Build-In Floor | Mini Canal | MICL.00939014/RDB | 9 | 390 | 14 | 14 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.00939014/RDB
Build-In Floor | Mini Canal | MICL.00939014/RMN | 9 | 390 | 14 | 14 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.00939014/RMN
Build-In Floor | Mini Canal | MICL.00939014/RMV | 9 | 390 | 14 | 14 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.00939014/RMV
Build-In Floor | Mini Canal | MICL.00939014/RNA | 9 | 390 | 14 | 14 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.00939014/RNA
Build-In Floor | Mini Canal | MICL.00939014/RON | 9 | 390 | 14 | 14 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.00939014/RON
Build-In Floor | Mini Canal | MICL.00939014/ROV | 9 | 390 | 14 | 14 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.00939014/ROV
Build-In Floor | Mini Canal | MICL.00939014/RSS | 9 | 390 | 14 | 14 | 658 | 658 | 658 | 0.015667 | 256 | 0.0060952 | 749 | 0.017833 | 1.362 | A04 | MICL0.00939014/RSS
Build-In Floor | Mini Canal | MICL.00939014/SBL | 9 | 390 | 14 | 14 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.00939014/SBL
Build-In Floor | Mini Canal | MICL.00939014/SBR | 9 | 390 | 14 | 14 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.00939014/SBR
Build-In Floor | Mini Canal | MICL.00939014/SDB | 9 | 390 | 14 | 14 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.00939014/SDB
Build-In Floor | Mini Canal | MICL.00939014/SNA | 9 | 390 | 14 | 14 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.00939014/SNA
Build-In Floor | Mini Canal | MICL.00939014/SNC | 9 | 390 | 14 | 14 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.00939014/SNC
Build-In Floor | Mini Canal | MICL.00939018/ANA | 9 | 390 | 18 | 18 | 608 | 608 | 608 | 0.014476 | 237 | 0.0056429 | 693 | 0.0165 | 1.362 | A04 | MICL0.00939018/ANA
Build-In Floor | Mini Canal | MICL.00939018/DBL | 9 | 390 | 18 | 18 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00939018/DBL
Build-In Floor | Mini Canal | MICL.00939018/DBN | 9 | 390 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.00939018/DBN
Build-In Floor | Mini Canal | MICL.00939018/DBR | 9 | 390 | 18 | 18 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00939018/DBR
Build-In Floor | Mini Canal | MICL.00939018/DBV | 9 | 390 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.00939018/DBV
Build-In Floor | Mini Canal | MICL.00939018/DDB | 9 | 390 | 18 | 18 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00939018/DDB
Build-In Floor | Mini Canal | MICL.00939018/DMN | 9 | 390 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.00939018/DMN
Build-In Floor | Mini Canal | MICL.00939018/DMV | 9 | 390 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.00939018/DMV
Build-In Floor | Mini Canal | MICL.00939018/DNA | 9 | 390 | 18 | 18 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00939018/DNA
Build-In Floor | Mini Canal | MICL.00939018/DNC | 9 | 390 | 18 | 18 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00939018/DNC
Build-In Floor | Mini Canal | MICL.00939018/DON | 9 | 390 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.00939018/DON
Build-In Floor | Mini Canal | MICL.00939018/DOV | 9 | 390 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.00939018/DOV
Build-In Floor | Mini Canal | MICL.00939018/RBL | 9 | 390 | 18 | 18 | 811 | 811 | 811 | 0.01931 | 315 | 0.0075 | 924 | 0.022 | 1.362 | A04 | MICL0.00939018/RBL
Build-In Floor | Mini Canal | MICL.00939018/RBN | 9 | 390 | 18 | 18 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00939018/RBN
Build-In Floor | Mini Canal | MICL.00939018/RBR | 9 | 390 | 18 | 18 | 811 | 811 | 811 | 0.01931 | 315 | 0.0075 | 924 | 0.022 | 1.362 | A04 | MICL0.00939018/RBR
Build-In Floor | Mini Canal | MICL.00939018/RBV | 9 | 390 | 18 | 18 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00939018/RBV
Build-In Floor | Mini Canal | MICL.00939018/RDB | 9 | 390 | 18 | 18 | 811 | 811 | 811 | 0.01931 | 315 | 0.0075 | 924 | 0.022 | 1.362 | A04 | MICL0.00939018/RDB
Build-In Floor | Mini Canal | MICL.00939018/RMN | 9 | 390 | 18 | 18 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00939018/RMN
Build-In Floor | Mini Canal | MICL.00939018/RMV | 9 | 390 | 18 | 18 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00939018/RMV
Build-In Floor | Mini Canal | MICL.00939018/RNA | 9 | 390 | 18 | 18 | 811 | 811 | 811 | 0.01931 | 315 | 0.0075 | 924 | 0.022 | 1.362 | A04 | MICL0.00939018/RNA
Build-In Floor | Mini Canal | MICL.00939018/RON | 9 | 390 | 18 | 18 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00939018/RON
Build-In Floor | Mini Canal | MICL.00939018/ROV | 9 | 390 | 18 | 18 | 787 | 787 | 787 | 0.018738 | 306 | 0.0072857 | 896 | 0.021333 | 1.362 | A04 | MICL0.00939018/ROV
Build-In Floor | Mini Canal | MICL.00939018/RSS | 9 | 390 | 18 | 18 | 779 | 779 | 779 | 0.018548 | 303 | 0.0072143 | 887 | 0.021119 | 1.362 | A04 | MICL0.00939018/RSS
Build-In Floor | Mini Canal | MICL.00939018/SBL | 9 | 390 | 18 | 18 | 811 | 811 | 811 | 0.01931 | 315 | 0.0075 | 924 | 0.022 | 1.362 | A04 | MICL0.00939018/SBL
Build-In Floor | Mini Canal | MICL.00939018/SBR | 9 | 390 | 18 | 18 | 811 | 811 | 811 | 0.01931 | 315 | 0.0075 | 924 | 0.022 | 1.362 | A04 | MICL0.00939018/SBR
Build-In Floor | Mini Canal | MICL.00939018/SDB | 9 | 390 | 18 | 18 | 811 | 811 | 811 | 0.01931 | 315 | 0.0075 | 924 | 0.022 | 1.362 | A04 | MICL0.00939018/SDB
Build-In Floor | Mini Canal | MICL.00939018/SNA | 9 | 390 | 18 | 18 | 811 | 811 | 811 | 0.01931 | 315 | 0.0075 | 924 | 0.022 | 1.362 | A04 | MICL0.00939018/SNA
Build-In Floor | Mini Canal | MICL.00939018/SNC | 9 | 390 | 18 | 18 | 811 | 811 | 811 | 0.01931 | 315 | 0.0075 | 924 | 0.022 | 1.362 | A04 | MICL0.00939018/SNC
Build-In Floor | Mini Canal | MICL.00939026/ANA | 9 | 390 | 26 | 26 | 800 | 800 | 800 | 0.019048 | 311 | 0.0074048 | 911 | 0.02169 | 1.362 | A04 | MICL0.00939026/ANA
Build-In Floor | Mini Canal | MICL.00939026/DBL | 9 | 390 | 26 | 26 | 1035 | 1035 | 1035 | 0.024643 | 403 | 0.0095952 | 1179 | 0.028071 | 1.362 | A04 | MICL0.00939026/DBL
Build-In Floor | Mini Canal | MICL.00939026/DBN | 9 | 390 | 26 | 26 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00939026/DBN
Build-In Floor | Mini Canal | MICL.00939026/DBR | 9 | 390 | 26 | 26 | 1035 | 1035 | 1035 | 0.024643 | 403 | 0.0095952 | 1179 | 0.028071 | 1.362 | A04 | MICL0.00939026/DBR
Build-In Floor | Mini Canal | MICL.00939026/DBV | 9 | 390 | 26 | 26 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00939026/DBV
Build-In Floor | Mini Canal | MICL.00939026/DDB | 9 | 390 | 26 | 26 | 1035 | 1035 | 1035 | 0.024643 | 403 | 0.0095952 | 1179 | 0.028071 | 1.362 | A04 | MICL0.00939026/DDB
Build-In Floor | Mini Canal | MICL.00939026/DMN | 9 | 390 | 26 | 26 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00939026/DMN
Build-In Floor | Mini Canal | MICL.00939026/DMV | 9 | 390 | 26 | 26 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00939026/DMV
Build-In Floor | Mini Canal | MICL.00939026/DNA | 9 | 390 | 26 | 26 | 1035 | 1035 | 1035 | 0.024643 | 403 | 0.0095952 | 1179 | 0.028071 | 1.362 | A04 | MICL0.00939026/DNA
Build-In Floor | Mini Canal | MICL.00939026/DNC | 9 | 390 | 26 | 26 | 1035 | 1035 | 1035 | 0.024643 | 403 | 0.0095952 | 1179 | 0.028071 | 1.362 | A04 | MICL0.00939026/DNC
Build-In Floor | Mini Canal | MICL.00939026/DON | 9 | 390 | 26 | 26 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00939026/DON
Build-In Floor | Mini Canal | MICL.00939026/DOV | 9 | 390 | 26 | 26 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00939026/DOV
Build-In Floor | Mini Canal | MICL.00939026/PNC | 9 | 390 | 26 | 26 | 907 | 907 | 907 | 0.021595 | 353 | 0.0084048 | 1033 | 0.024595 | 1.362 | A04 | MICL0.00939026/PNC
Build-In Floor | Mini Canal | MICL.00939026/RBL | 9 | 390 | 26 | 26 | 1067 | 1067 | 1067 | 0.025405 | 415 | 0.009881 | 1215 | 0.028929 | 1.362 | A04 | MICL0.00939026/RBL
Build-In Floor | Mini Canal | MICL.00939026/RBN | 9 | 390 | 26 | 26 | 1035 | 1035 | 1035 | 0.024643 | 403 | 0.0095952 | 1179 | 0.028071 | 1.362 | A04 | MICL0.00939026/RBN
Build-In Floor | Mini Canal | MICL.00939026/RBR | 9 | 390 | 26 | 26 | 1067 | 1067 | 1067 | 0.025405 | 415 | 0.009881 | 1215 | 0.028929 | 1.362 | A04 | MICL0.00939026/RBR
Build-In Floor | Mini Canal | MICL.00939026/RBV | 9 | 390 | 26 | 26 | 1035 | 1035 | 1035 | 0.024643 | 403 | 0.0095952 | 1179 | 0.028071 | 1.362 | A04 | MICL0.00939026/RBV
Build-In Floor | Mini Canal | MICL.00939026/RDB | 9 | 390 | 26 | 26 | 1067 | 1067 | 1067 | 0.025405 | 415 | 0.009881 | 1215 | 0.028929 | 1.362 | A04 | MICL0.00939026/RDB
Build-In Floor | Mini Canal | MICL.00939026/RMN | 9 | 390 | 26 | 26 | 1035 | 1035 | 1035 | 0.024643 | 403 | 0.0095952 | 1179 | 0.028071 | 1.362 | A04 | MICL0.00939026/RMN
Build-In Floor | Mini Canal | MICL.00939026/RMV | 9 | 390 | 26 | 26 | 1035 | 1035 | 1035 | 0.024643 | 403 | 0.0095952 | 1179 | 0.028071 | 1.362 | A04 | MICL0.00939026/RMV
Build-In Floor | Mini Canal | MICL.00939026/RNA | 9 | 390 | 26 | 26 | 1067 | 1067 | 1067 | 0.025405 | 415 | 0.009881 | 1215 | 0.028929 | 1.362 | A04 | MICL0.00939026/RNA
Build-In Floor | Mini Canal | MICL.00939026/RON | 9 | 390 | 26 | 26 | 1035 | 1035 | 1035 | 0.024643 | 403 | 0.0095952 | 1179 | 0.028071 | 1.362 | A04 | MICL0.00939026/RON
Build-In Floor | Mini Canal | MICL.00939026/ROV | 9 | 390 | 26 | 26 | 1035 | 1035 | 1035 | 0.024643 | 403 | 0.0095952 | 1179 | 0.028071 | 1.362 | A04 | MICL0.00939026/ROV
Build-In Floor | Mini Canal | MICL.00939026/RSS | 9 | 390 | 26 | 26 | 1024 | 1024 | 1024 | 0.024381 | 398 | 0.0094762 | 1166 | 0.027762 | 1.362 | A04 | MICL0.00939026/RSS
Build-In Floor | Mini Canal | MICL.00939026/SBL | 9 | 390 | 26 | 26 | 1067 | 1067 | 1067 | 0.025405 | 415 | 0.009881 | 1215 | 0.028929 | 1.362 | A04 | MICL0.00939026/SBL
Build-In Floor | Mini Canal | MICL.00939026/SBR | 9 | 390 | 26 | 26 | 1067 | 1067 | 1067 | 0.025405 | 415 | 0.009881 | 1215 | 0.028929 | 1.362 | A04 | MICL0.00939026/SBR
Build-In Floor | Mini Canal | MICL.00939026/SDB | 9 | 390 | 26 | 26 | 1067 | 1067 | 1067 | 0.025405 | 415 | 0.009881 | 1215 | 0.028929 | 1.362 | A04 | MICL0.00939026/SDB
Build-In Floor | Mini Canal | MICL.00939026/SNA | 9 | 390 | 26 | 26 | 1067 | 1067 | 1067 | 0.025405 | 415 | 0.009881 | 1215 | 0.028929 | 1.362 | A04 | MICL0.00939026/SNA
Build-In Floor | Mini Canal | MICL.00939026/SNC | 9 | 390 | 26 | 26 | 1067 | 1067 | 1067 | 0.025405 | 415 | 0.009881 | 1215 | 0.028929 | 1.362 | A04 | MICL0.00939026/SNC
Build-In Floor | Mini Canal | MICL.00939034/ANA | 9 | 390 | 34 | 34 | 1039 | 1039 | 1039 | 0.024738 | 404 | 0.009619 | 1183 | 0.028167 | 1.362 | A04 | MICL0.00939034/ANA
Build-In Floor | Mini Canal | MICL.00939034/DBL | 9 | 390 | 34 | 34 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00939034/DBL
Build-In Floor | Mini Canal | MICL.00939034/DBN | 9 | 390 | 34 | 34 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.00939034/DBN
Build-In Floor | Mini Canal | MICL.00939034/DBR | 9 | 390 | 34 | 34 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00939034/DBR
Build-In Floor | Mini Canal | MICL.00939034/DBV | 9 | 390 | 34 | 34 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.00939034/DBV
Build-In Floor | Mini Canal | MICL.00939034/DDB | 9 | 390 | 34 | 34 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00939034/DDB
Build-In Floor | Mini Canal | MICL.00939034/DMN | 9 | 390 | 34 | 34 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.00939034/DMN
Build-In Floor | Mini Canal | MICL.00939034/DMV | 9 | 390 | 34 | 34 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.00939034/DMV
Build-In Floor | Mini Canal | MICL.00939034/DNA | 9 | 390 | 34 | 34 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00939034/DNA
Build-In Floor | Mini Canal | MICL.00939034/DNC | 9 | 390 | 34 | 34 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00939034/DNC
Build-In Floor | Mini Canal | MICL.00939034/DON | 9 | 390 | 34 | 34 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.00939034/DON
Build-In Floor | Mini Canal | MICL.00939034/DOV | 9 | 390 | 34 | 34 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.00939034/DOV
Build-In Floor | Mini Canal | MICL.00939034/PNC | 9 | 390 | 34 | 34 | 1177 | 1177 | 1177 | 0.028024 | 458 | 0.010905 | 1341 | 0.031929 | 1.362 | A04 | MICL0.00939034/PNC
Build-In Floor | Mini Canal | MICL.00939034/RBL | 9 | 390 | 34 | 34 | 1385 | 1385 | 1385 | 0.032976 | 539 | 0.012833 | 1578 | 0.037571 | 1.362 | A04 | MICL0.00939034/RBL
Build-In Floor | Mini Canal | MICL.00939034/RBN | 9 | 390 | 34 | 34 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00939034/RBN
Build-In Floor | Mini Canal | MICL.00939034/RBR | 9 | 390 | 34 | 34 | 1385 | 1385 | 1385 | 0.032976 | 539 | 0.012833 | 1578 | 0.037571 | 1.362 | A04 | MICL0.00939034/RBR
Build-In Floor | Mini Canal | MICL.00939034/RBV | 9 | 390 | 34 | 34 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00939034/RBV
Build-In Floor | Mini Canal | MICL.00939034/RDB | 9 | 390 | 34 | 34 | 1385 | 1385 | 1385 | 0.032976 | 539 | 0.012833 | 1578 | 0.037571 | 1.362 | A04 | MICL0.00939034/RDB
Build-In Floor | Mini Canal | MICL.00939034/RMN | 9 | 390 | 34 | 34 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00939034/RMN
Build-In Floor | Mini Canal | MICL.00939034/RMV | 9 | 390 | 34 | 34 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00939034/RMV
Build-In Floor | Mini Canal | MICL.00939034/RNA | 9 | 390 | 34 | 34 | 1385 | 1385 | 1385 | 0.032976 | 539 | 0.012833 | 1578 | 0.037571 | 1.362 | A04 | MICL0.00939034/RNA
Build-In Floor | Mini Canal | MICL.00939034/RON | 9 | 390 | 34 | 34 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00939034/RON
Build-In Floor | Mini Canal | MICL.00939034/ROV | 9 | 390 | 34 | 34 | 1343 | 1343 | 1343 | 0.031976 | 522 | 0.012429 | 1530 | 0.036429 | 1.362 | A04 | MICL0.00939034/ROV
Build-In Floor | Mini Canal | MICL.00939034/RSS | 9 | 390 | 34 | 34 | 1330 | 1330 | 1330 | 0.031667 | 517 | 0.01231 | 1515 | 0.036071 | 1.362 | A04 | MICL0.00939034/RSS
Build-In Floor | Mini Canal | MICL.00939034/SBL | 9 | 390 | 34 | 34 | 1385 | 1385 | 1385 | 0.032976 | 539 | 0.012833 | 1578 | 0.037571 | 1.362 | A04 | MICL0.00939034/SBL
Build-In Floor | Mini Canal | MICL.00939034/SBR | 9 | 390 | 34 | 34 | 1385 | 1385 | 1385 | 0.032976 | 539 | 0.012833 | 1578 | 0.037571 | 1.362 | A04 | MICL0.00939034/SBR
Build-In Floor | Mini Canal | MICL.00939034/SDB | 9 | 390 | 34 | 34 | 1385 | 1385 | 1385 | 0.032976 | 539 | 0.012833 | 1578 | 0.037571 | 1.362 | A04 | MICL0.00939034/SDB
Build-In Floor | Mini Canal | MICL.00939034/SNA | 9 | 390 | 34 | 34 | 1385 | 1385 | 1385 | 0.032976 | 539 | 0.012833 | 1578 | 0.037571 | 1.362 | A04 | MICL0.00939034/SNA
Build-In Floor | Mini Canal | MICL.00939034/SNC | 9 | 390 | 34 | 34 | 1385 | 1385 | 1385 | 0.032976 | 539 | 0.012833 | 1578 | 0.037571 | 1.362 | A04 | MICL0.00939034/SNC
Build-In Floor | Mini Canal | MICL.00939042/ANA | 9 | 390 | 42 | 42 | 1499 | 1499 | 1499 | 0.03569 | 583 | 0.013881 | 1707 | 0.040643 | 1.362 | A04 | MICL0.00939042/ANA
Build-In Floor | Mini Canal | MICL.00939042/DBL | 9 | 390 | 42 | 42 | 1939 | 1939 | 1939 | 0.046167 | 754 | 0.017952 | 2209 | 0.052595 | 1.362 | A04 | MICL0.00939042/DBL
Build-In Floor | Mini Canal | MICL.00939042/DBN | 9 | 390 | 42 | 42 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.00939042/DBN
Build-In Floor | Mini Canal | MICL.00939042/DBR | 9 | 390 | 42 | 42 | 1939 | 1939 | 1939 | 0.046167 | 754 | 0.017952 | 2209 | 0.052595 | 1.362 | A04 | MICL0.00939042/DBR
Build-In Floor | Mini Canal | MICL.00939042/DBV | 9 | 390 | 42 | 42 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.00939042/DBV
Build-In Floor | Mini Canal | MICL.00939042/DDB | 9 | 390 | 42 | 42 | 1939 | 1939 | 1939 | 0.046167 | 754 | 0.017952 | 2209 | 0.052595 | 1.362 | A04 | MICL0.00939042/DDB
Build-In Floor | Mini Canal | MICL.00939042/DMN | 9 | 390 | 42 | 42 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.00939042/DMN
Build-In Floor | Mini Canal | MICL.00939042/DMV | 9 | 390 | 42 | 42 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.00939042/DMV
Build-In Floor | Mini Canal | MICL.00939042/DNA | 9 | 390 | 42 | 42 | 1939 | 1939 | 1939 | 0.046167 | 754 | 0.017952 | 2209 | 0.052595 | 1.362 | A04 | MICL0.00939042/DNA
Build-In Floor | Mini Canal | MICL.00939042/DNC | 9 | 390 | 42 | 42 | 1939 | 1939 | 1939 | 0.046167 | 754 | 0.017952 | 2209 | 0.052595 | 1.362 | A04 | MICL0.00939042/DNC
Build-In Floor | Mini Canal | MICL.00939042/DON | 9 | 390 | 42 | 42 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.00939042/DON
Build-In Floor | Mini Canal | MICL.00939042/DOV | 9 | 390 | 42 | 42 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.00939042/DOV
Build-In Floor | Mini Canal | MICL.00939042/PNC | 9 | 390 | 42 | 42 | 1699 | 1699 | 1699 | 0.040452 | 661 | 0.015738 | 1935 | 0.046071 | 1.362 | A04 | MICL0.00939042/PNC
Build-In Floor | Mini Canal | MICL.00939042/RBL | 9 | 390 | 42 | 42 | 1999 | 1999 | 1999 | 0.047595 | 778 | 0.018524 | 2277 | 0.054214 | 1.362 | A04 | MICL0.00939042/RBL
Build-In Floor | Mini Canal | MICL.00939042/RBN | 9 | 390 | 42 | 42 | 1939 | 1939 | 1939 | 0.046167 | 754 | 0.017952 | 2209 | 0.052595 | 1.362 | A04 | MICL0.00939042/RBN
Build-In Floor | Mini Canal | MICL.00939042/RBR | 9 | 390 | 42 | 42 | 1999 | 1999 | 1999 | 0.047595 | 778 | 0.018524 | 2277 | 0.054214 | 1.362 | A04 | MICL0.00939042/RBR
Build-In Floor | Mini Canal | MICL.00939042/RBV | 9 | 390 | 42 | 42 | 1939 | 1939 | 1939 | 0.046167 | 754 | 0.017952 | 2209 | 0.052595 | 1.362 | A04 | MICL0.00939042/RBV
Build-In Floor | Mini Canal | MICL.00939042/RDB | 9 | 390 | 42 | 42 | 1999 | 1999 | 1999 | 0.047595 | 778 | 0.018524 | 2277 | 0.054214 | 1.362 | A04 | MICL0.00939042/RDB
Build-In Floor | Mini Canal | MICL.00939042/RMN | 9 | 390 | 42 | 42 | 1939 | 1939 | 1939 | 0.046167 | 754 | 0.017952 | 2209 | 0.052595 | 1.362 | A04 | MICL0.00939042/RMN
Build-In Floor | Mini Canal | MICL.00939042/RMV | 9 | 390 | 42 | 42 | 1939 | 1939 | 1939 | 0.046167 | 754 | 0.017952 | 2209 | 0.052595 | 1.362 | A04 | MICL0.00939042/RMV
Build-In Floor | Mini Canal | MICL.00939042/RNA | 9 | 390 | 42 | 42 | 1999 | 1999 | 1999 | 0.047595 | 778 | 0.018524 | 2277 | 0.054214 | 1.362 | A04 | MICL0.00939042/RNA
Build-In Floor | Mini Canal | MICL.00939042/RON | 9 | 390 | 42 | 42 | 1939 | 1939 | 1939 | 0.046167 | 754 | 0.017952 | 2209 | 0.052595 | 1.362 | A04 | MICL0.00939042/RON
Build-In Floor | Mini Canal | MICL.00939042/ROV | 9 | 390 | 42 | 42 | 1939 | 1939 | 1939 | 0.046167 | 754 | 0.017952 | 2209 | 0.052595 | 1.362 | A04 | MICL0.00939042/ROV
Build-In Floor | Mini Canal | MICL.00939042/RSS | 9 | 390 | 42 | 42 | 1919 | 1919 | 1919 | 0.04569 | 746 | 0.017762 | 2186 | 0.052048 | 1.362 | A04 | MICL0.00939042/RSS
Build-In Floor | Mini Canal | MICL.00939042/SBL | 9 | 390 | 42 | 42 | 1999 | 1999 | 1999 | 0.047595 | 778 | 0.018524 | 2277 | 0.054214 | 1.362 | A04 | MICL0.00939042/SBL
Build-In Floor | Mini Canal | MICL.00939042/SBR | 9 | 390 | 42 | 42 | 1999 | 1999 | 1999 | 0.047595 | 778 | 0.018524 | 2277 | 0.054214 | 1.362 | A04 | MICL0.00939042/SBR
Build-In Floor | Mini Canal | MICL.00939042/SDB | 9 | 390 | 42 | 42 | 1999 | 1999 | 1999 | 0.047595 | 778 | 0.018524 | 2277 | 0.054214 | 1.362 | A04 | MICL0.00939042/SDB
Build-In Floor | Mini Canal | MICL.00939042/SNA | 9 | 390 | 42 | 42 | 1999 | 1999 | 1999 | 0.047595 | 778 | 0.018524 | 2277 | 0.054214 | 1.362 | A04 | MICL0.00939042/SNA
Build-In Floor | Mini Canal | MICL.00939042/SNC | 9 | 390 | 42 | 42 | 1999 | 1999 | 1999 | 0.047595 | 778 | 0.018524 | 2277 | 0.054214 | 1.362 | A04 | MICL0.00939042/SNC
Build-In Floor | Mini Canal | MICL.00941014/ANA | 9 | 410 | 14 | 14 | 542 | 542 | 542 | 0.012905 | 211 | 0.0050238 | 617 | 0.01469 | 1.362 | A04 | MICL0.00941014/ANA
Build-In Floor | Mini Canal | MICL.00941014/DBL | 9 | 410 | 14 | 14 | 701 | 701 | 701 | 0.01669 | 273 | 0.0065 | 798 | 0.019 | 1.362 | A04 | MICL0.00941014/DBL
Build-In Floor | Mini Canal | MICL.00941014/DBN | 9 | 410 | 14 | 14 | 672 | 672 | 672 | 0.016 | 261 | 0.0062143 | 765 | 0.018214 | 1.362 | A04 | MICL0.00941014/DBN
Build-In Floor | Mini Canal | MICL.00941014/DBR | 9 | 410 | 14 | 14 | 701 | 701 | 701 | 0.01669 | 273 | 0.0065 | 798 | 0.019 | 1.362 | A04 | MICL0.00941014/DBR
Build-In Floor | Mini Canal | MICL.00941014/DBV | 9 | 410 | 14 | 14 | 672 | 672 | 672 | 0.016 | 261 | 0.0062143 | 765 | 0.018214 | 1.362 | A04 | MICL0.00941014/DBV
Build-In Floor | Mini Canal | MICL.00941014/DDB | 9 | 410 | 14 | 14 | 701 | 701 | 701 | 0.01669 | 273 | 0.0065 | 798 | 0.019 | 1.362 | A04 | MICL0.00941014/DDB
Build-In Floor | Mini Canal | MICL.00941014/DMN | 9 | 410 | 14 | 14 | 672 | 672 | 672 | 0.016 | 261 | 0.0062143 | 765 | 0.018214 | 1.362 | A04 | MICL0.00941014/DMN
Build-In Floor | Mini Canal | MICL.00941014/DMV | 9 | 410 | 14 | 14 | 672 | 672 | 672 | 0.016 | 261 | 0.0062143 | 765 | 0.018214 | 1.362 | A04 | MICL0.00941014/DMV
Build-In Floor | Mini Canal | MICL.00941014/DNA | 9 | 410 | 14 | 14 | 701 | 701 | 701 | 0.01669 | 273 | 0.0065 | 798 | 0.019 | 1.362 | A04 | MICL0.00941014/DNA
Build-In Floor | Mini Canal | MICL.00941014/DNC | 9 | 410 | 14 | 14 | 701 | 701 | 701 | 0.01669 | 273 | 0.0065 | 798 | 0.019 | 1.362 | A04 | MICL0.00941014/DNC
Build-In Floor | Mini Canal | MICL.00941014/DON | 9 | 410 | 14 | 14 | 672 | 672 | 672 | 0.016 | 261 | 0.0062143 | 765 | 0.018214 | 1.362 | A04 | MICL0.00941014/DON
Build-In Floor | Mini Canal | MICL.00941014/DOV | 9 | 410 | 14 | 14 | 672 | 672 | 672 | 0.016 | 261 | 0.0062143 | 765 | 0.018214 | 1.362 | A04 | MICL0.00941014/DOV
Build-In Floor | Mini Canal | MICL.00941014/RBL | 9 | 410 | 14 | 14 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.00941014/RBL
Build-In Floor | Mini Canal | MICL.00941014/RBN | 9 | 410 | 14 | 14 | 701 | 701 | 701 | 0.01669 | 273 | 0.0065 | 798 | 0.019 | 1.362 | A04 | MICL0.00941014/RBN
Build-In Floor | Mini Canal | MICL.00941014/RBR | 9 | 410 | 14 | 14 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.00941014/RBR
Build-In Floor | Mini Canal | MICL.00941014/RBV | 9 | 410 | 14 | 14 | 701 | 701 | 701 | 0.01669 | 273 | 0.0065 | 798 | 0.019 | 1.362 | A04 | MICL0.00941014/RBV
Build-In Floor | Mini Canal | MICL.00941014/RDB | 9 | 410 | 14 | 14 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.00941014/RDB
Build-In Floor | Mini Canal | MICL.00941014/RMN | 9 | 410 | 14 | 14 | 701 | 701 | 701 | 0.01669 | 273 | 0.0065 | 798 | 0.019 | 1.362 | A04 | MICL0.00941014/RMN
Build-In Floor | Mini Canal | MICL.00941014/RMV | 9 | 410 | 14 | 14 | 701 | 701 | 701 | 0.01669 | 273 | 0.0065 | 798 | 0.019 | 1.362 | A04 | MICL0.00941014/RMV
Build-In Floor | Mini Canal | MICL.00941014/RNA | 9 | 410 | 14 | 14 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.00941014/RNA
Build-In Floor | Mini Canal | MICL.00941014/RON | 9 | 410 | 14 | 14 | 701 | 701 | 701 | 0.01669 | 273 | 0.0065 | 798 | 0.019 | 1.362 | A04 | MICL0.00941014/RON
Build-In Floor | Mini Canal | MICL.00941014/ROV | 9 | 410 | 14 | 14 | 701 | 701 | 701 | 0.01669 | 273 | 0.0065 | 798 | 0.019 | 1.362 | A04 | MICL0.00941014/ROV
Build-In Floor | Mini Canal | MICL.00941014/RSS | 9 | 410 | 14 | 14 | 694 | 694 | 694 | 0.016524 | 270 | 0.0064286 | 790 | 0.01881 | 1.362 | A04 | MICL0.00941014/RSS
Build-In Floor | Mini Canal | MICL.00941014/SBL | 9 | 410 | 14 | 14 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.00941014/SBL
Build-In Floor | Mini Canal | MICL.00941014/SBR | 9 | 410 | 14 | 14 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.00941014/SBR
Build-In Floor | Mini Canal | MICL.00941014/SDB | 9 | 410 | 14 | 14 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.00941014/SDB
Build-In Floor | Mini Canal | MICL.00941014/SNA | 9 | 410 | 14 | 14 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.00941014/SNA
Build-In Floor | Mini Canal | MICL.00941014/SNC | 9 | 410 | 14 | 14 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.00941014/SNC
Build-In Floor | Mini Canal | MICL.00941018/ANA | 9 | 410 | 18 | 18 | 642 | 642 | 642 | 0.015286 | 250 | 0.0059524 | 731 | 0.017405 | 1.362 | A04 | MICL0.00941018/ANA
Build-In Floor | Mini Canal | MICL.00941018/DBL | 9 | 410 | 18 | 18 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00941018/DBL
Build-In Floor | Mini Canal | MICL.00941018/DBN | 9 | 410 | 18 | 18 | 796 | 796 | 796 | 0.018952 | 310 | 0.007381 | 907 | 0.021595 | 1.362 | A04 | MICL0.00941018/DBN
Build-In Floor | Mini Canal | MICL.00941018/DBR | 9 | 410 | 18 | 18 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00941018/DBR
Build-In Floor | Mini Canal | MICL.00941018/DBV | 9 | 410 | 18 | 18 | 796 | 796 | 796 | 0.018952 | 310 | 0.007381 | 907 | 0.021595 | 1.362 | A04 | MICL0.00941018/DBV
Build-In Floor | Mini Canal | MICL.00941018/DDB | 9 | 410 | 18 | 18 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00941018/DDB
Build-In Floor | Mini Canal | MICL.00941018/DMN | 9 | 410 | 18 | 18 | 796 | 796 | 796 | 0.018952 | 310 | 0.007381 | 907 | 0.021595 | 1.362 | A04 | MICL0.00941018/DMN
Build-In Floor | Mini Canal | MICL.00941018/DMV | 9 | 410 | 18 | 18 | 796 | 796 | 796 | 0.018952 | 310 | 0.007381 | 907 | 0.021595 | 1.362 | A04 | MICL0.00941018/DMV
Build-In Floor | Mini Canal | MICL.00941018/DNA | 9 | 410 | 18 | 18 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00941018/DNA
Build-In Floor | Mini Canal | MICL.00941018/DNC | 9 | 410 | 18 | 18 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00941018/DNC
Build-In Floor | Mini Canal | MICL.00941018/DON | 9 | 410 | 18 | 18 | 796 | 796 | 796 | 0.018952 | 310 | 0.007381 | 907 | 0.021595 | 1.362 | A04 | MICL0.00941018/DON
Build-In Floor | Mini Canal | MICL.00941018/DOV | 9 | 410 | 18 | 18 | 796 | 796 | 796 | 0.018952 | 310 | 0.007381 | 907 | 0.021595 | 1.362 | A04 | MICL0.00941018/DOV
Build-In Floor | Mini Canal | MICL.00941018/RBL | 9 | 410 | 18 | 18 | 856 | 856 | 856 | 0.020381 | 333 | 0.0079286 | 975 | 0.023214 | 1.362 | A04 | MICL0.00941018/RBL
Build-In Floor | Mini Canal | MICL.00941018/RBN | 9 | 410 | 18 | 18 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00941018/RBN
Build-In Floor | Mini Canal | MICL.00941018/RBR | 9 | 410 | 18 | 18 | 856 | 856 | 856 | 0.020381 | 333 | 0.0079286 | 975 | 0.023214 | 1.362 | A04 | MICL0.00941018/RBR
Build-In Floor | Mini Canal | MICL.00941018/RBV | 9 | 410 | 18 | 18 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00941018/RBV
Build-In Floor | Mini Canal | MICL.00941018/RDB | 9 | 410 | 18 | 18 | 856 | 856 | 856 | 0.020381 | 333 | 0.0079286 | 975 | 0.023214 | 1.362 | A04 | MICL0.00941018/RDB
Build-In Floor | Mini Canal | MICL.00941018/RMN | 9 | 410 | 18 | 18 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00941018/RMN
Build-In Floor | Mini Canal | MICL.00941018/RMV | 9 | 410 | 18 | 18 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00941018/RMV
Build-In Floor | Mini Canal | MICL.00941018/RNA | 9 | 410 | 18 | 18 | 856 | 856 | 856 | 0.020381 | 333 | 0.0079286 | 975 | 0.023214 | 1.362 | A04 | MICL0.00941018/RNA
Build-In Floor | Mini Canal | MICL.00941018/RON | 9 | 410 | 18 | 18 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00941018/RON
Build-In Floor | Mini Canal | MICL.00941018/ROV | 9 | 410 | 18 | 18 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.00941018/ROV
Build-In Floor | Mini Canal | MICL.00941018/RSS | 9 | 410 | 18 | 18 | 822 | 822 | 822 | 0.019571 | 320 | 0.007619 | 936 | 0.022286 | 1.362 | A04 | MICL0.00941018/RSS
Build-In Floor | Mini Canal | MICL.00941018/SBL | 9 | 410 | 18 | 18 | 856 | 856 | 856 | 0.020381 | 333 | 0.0079286 | 975 | 0.023214 | 1.362 | A04 | MICL0.00941018/SBL
Build-In Floor | Mini Canal | MICL.00941018/SBR | 9 | 410 | 18 | 18 | 856 | 856 | 856 | 0.020381 | 333 | 0.0079286 | 975 | 0.023214 | 1.362 | A04 | MICL0.00941018/SBR
Build-In Floor | Mini Canal | MICL.00941018/SDB | 9 | 410 | 18 | 18 | 856 | 856 | 856 | 0.020381 | 333 | 0.0079286 | 975 | 0.023214 | 1.362 | A04 | MICL0.00941018/SDB
Build-In Floor | Mini Canal | MICL.00941018/SNA | 9 | 410 | 18 | 18 | 856 | 856 | 856 | 0.020381 | 333 | 0.0079286 | 975 | 0.023214 | 1.362 | A04 | MICL0.00941018/SNA
Build-In Floor | Mini Canal | MICL.00941018/SNC | 9 | 410 | 18 | 18 | 856 | 856 | 856 | 0.020381 | 333 | 0.0079286 | 975 | 0.023214 | 1.362 | A04 | MICL0.00941018/SNC
Build-In Floor | Mini Canal | MICL.00941026/ANA | 9 | 410 | 26 | 26 | 845 | 845 | 845 | 0.020119 | 329 | 0.0078333 | 962 | 0.022905 | 1.362 | A04 | MICL0.00941026/ANA
Build-In Floor | Mini Canal | MICL.00941026/DBL | 9 | 410 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.00941026/DBL
Build-In Floor | Mini Canal | MICL.00941026/DBN | 9 | 410 | 26 | 26 | 1047 | 1047 | 1047 | 0.024929 | 407 | 0.0096905 | 1193 | 0.028405 | 1.362 | A04 | MICL0.00941026/DBN
Build-In Floor | Mini Canal | MICL.00941026/DBR | 9 | 410 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.00941026/DBR
Build-In Floor | Mini Canal | MICL.00941026/DBV | 9 | 410 | 26 | 26 | 1047 | 1047 | 1047 | 0.024929 | 407 | 0.0096905 | 1193 | 0.028405 | 1.362 | A04 | MICL0.00941026/DBV
Build-In Floor | Mini Canal | MICL.00941026/DDB | 9 | 410 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.00941026/DDB
Build-In Floor | Mini Canal | MICL.00941026/DMN | 9 | 410 | 26 | 26 | 1047 | 1047 | 1047 | 0.024929 | 407 | 0.0096905 | 1193 | 0.028405 | 1.362 | A04 | MICL0.00941026/DMN
Build-In Floor | Mini Canal | MICL.00941026/DMV | 9 | 410 | 26 | 26 | 1047 | 1047 | 1047 | 0.024929 | 407 | 0.0096905 | 1193 | 0.028405 | 1.362 | A04 | MICL0.00941026/DMV
Build-In Floor | Mini Canal | MICL.00941026/DNA | 9 | 410 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.00941026/DNA
Build-In Floor | Mini Canal | MICL.00941026/DNC | 9 | 410 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.00941026/DNC
Build-In Floor | Mini Canal | MICL.00941026/DON | 9 | 410 | 26 | 26 | 1047 | 1047 | 1047 | 0.024929 | 407 | 0.0096905 | 1193 | 0.028405 | 1.362 | A04 | MICL0.00941026/DON
Build-In Floor | Mini Canal | MICL.00941026/DOV | 9 | 410 | 26 | 26 | 1047 | 1047 | 1047 | 0.024929 | 407 | 0.0096905 | 1193 | 0.028405 | 1.362 | A04 | MICL0.00941026/DOV
Build-In Floor | Mini Canal | MICL.00941026/PNC | 9 | 410 | 26 | 26 | 957 | 957 | 957 | 0.022786 | 372 | 0.0088571 | 1090 | 0.025952 | 1.362 | A04 | MICL0.00941026/PNC
Build-In Floor | Mini Canal | MICL.00941026/RBL | 9 | 410 | 26 | 26 | 1126 | 1126 | 1126 | 0.02681 | 438 | 0.010429 | 1283 | 0.030548 | 1.362 | A04 | MICL0.00941026/RBL
Build-In Floor | Mini Canal | MICL.00941026/RBN | 9 | 410 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.00941026/RBN
Build-In Floor | Mini Canal | MICL.00941026/RBR | 9 | 410 | 26 | 26 | 1126 | 1126 | 1126 | 0.02681 | 438 | 0.010429 | 1283 | 0.030548 | 1.362 | A04 | MICL0.00941026/RBR
Build-In Floor | Mini Canal | MICL.00941026/RBV | 9 | 410 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.00941026/RBV
Build-In Floor | Mini Canal | MICL.00941026/RDB | 9 | 410 | 26 | 26 | 1126 | 1126 | 1126 | 0.02681 | 438 | 0.010429 | 1283 | 0.030548 | 1.362 | A04 | MICL0.00941026/RDB
Build-In Floor | Mini Canal | MICL.00941026/RMN | 9 | 410 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.00941026/RMN
Build-In Floor | Mini Canal | MICL.00941026/RMV | 9 | 410 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.00941026/RMV
Build-In Floor | Mini Canal | MICL.00941026/RNA | 9 | 410 | 26 | 26 | 1126 | 1126 | 1126 | 0.02681 | 438 | 0.010429 | 1283 | 0.030548 | 1.362 | A04 | MICL0.00941026/RNA
Build-In Floor | Mini Canal | MICL.00941026/RON | 9 | 410 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.00941026/RON
Build-In Floor | Mini Canal | MICL.00941026/ROV | 9 | 410 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.00941026/ROV
Build-In Floor | Mini Canal | MICL.00941026/RSS | 9 | 410 | 26 | 26 | 1081 | 1081 | 1081 | 0.025738 | 421 | 0.010024 | 1231 | 0.02931 | 1.362 | A04 | MICL0.00941026/RSS
Build-In Floor | Mini Canal | MICL.00941026/SBL | 9 | 410 | 26 | 26 | 1126 | 1126 | 1126 | 0.02681 | 438 | 0.010429 | 1283 | 0.030548 | 1.362 | A04 | MICL0.00941026/SBL
Build-In Floor | Mini Canal | MICL.00941026/SBR | 9 | 410 | 26 | 26 | 1126 | 1126 | 1126 | 0.02681 | 438 | 0.010429 | 1283 | 0.030548 | 1.362 | A04 | MICL0.00941026/SBR
Build-In Floor | Mini Canal | MICL.00941026/SDB | 9 | 410 | 26 | 26 | 1126 | 1126 | 1126 | 0.02681 | 438 | 0.010429 | 1283 | 0.030548 | 1.362 | A04 | MICL0.00941026/SDB
Build-In Floor | Mini Canal | MICL.00941026/SNA | 9 | 410 | 26 | 26 | 1126 | 1126 | 1126 | 0.02681 | 438 | 0.010429 | 1283 | 0.030548 | 1.362 | A04 | MICL0.00941026/SNA
Build-In Floor | Mini Canal | MICL.00941026/SNC | 9 | 410 | 26 | 26 | 1126 | 1126 | 1126 | 0.02681 | 438 | 0.010429 | 1283 | 0.030548 | 1.362 | A04 | MICL0.00941026/SNC
Build-In Floor | Mini Canal | MICL.00941034/ANA | 9 | 410 | 34 | 34 | 1096 | 1096 | 1096 | 0.026095 | 426 | 0.010143 | 1248 | 0.029714 | 1.362 | A04 | MICL0.00941034/ANA
Build-In Floor | Mini Canal | MICL.00941034/DBL | 9 | 410 | 34 | 34 | 1417 | 1417 | 1417 | 0.033738 | 551 | 0.013119 | 1614 | 0.038429 | 1.362 | A04 | MICL0.00941034/DBL
Build-In Floor | Mini Canal | MICL.00941034/DBN | 9 | 410 | 34 | 34 | 1359 | 1359 | 1359 | 0.032357 | 529 | 0.012595 | 1548 | 0.036857 | 1.362 | A04 | MICL0.00941034/DBN
Build-In Floor | Mini Canal | MICL.00941034/DBR | 9 | 410 | 34 | 34 | 1417 | 1417 | 1417 | 0.033738 | 551 | 0.013119 | 1614 | 0.038429 | 1.362 | A04 | MICL0.00941034/DBR
Build-In Floor | Mini Canal | MICL.00941034/DBV | 9 | 410 | 34 | 34 | 1359 | 1359 | 1359 | 0.032357 | 529 | 0.012595 | 1548 | 0.036857 | 1.362 | A04 | MICL0.00941034/DBV
Build-In Floor | Mini Canal | MICL.00941034/DDB | 9 | 410 | 34 | 34 | 1417 | 1417 | 1417 | 0.033738 | 551 | 0.013119 | 1614 | 0.038429 | 1.362 | A04 | MICL0.00941034/DDB
Build-In Floor | Mini Canal | MICL.00941034/DMN | 9 | 410 | 34 | 34 | 1359 | 1359 | 1359 | 0.032357 | 529 | 0.012595 | 1548 | 0.036857 | 1.362 | A04 | MICL0.00941034/DMN
Build-In Floor | Mini Canal | MICL.00941034/DMV | 9 | 410 | 34 | 34 | 1359 | 1359 | 1359 | 0.032357 | 529 | 0.012595 | 1548 | 0.036857 | 1.362 | A04 | MICL0.00941034/DMV
Build-In Floor | Mini Canal | MICL.00941034/DNA | 9 | 410 | 34 | 34 | 1417 | 1417 | 1417 | 0.033738 | 551 | 0.013119 | 1614 | 0.038429 | 1.362 | A04 | MICL0.00941034/DNA
Build-In Floor | Mini Canal | MICL.00941034/DNC | 9 | 410 | 34 | 34 | 1417 | 1417 | 1417 | 0.033738 | 551 | 0.013119 | 1614 | 0.038429 | 1.362 | A04 | MICL0.00941034/DNC
Build-In Floor | Mini Canal | MICL.00941034/DON | 9 | 410 | 34 | 34 | 1359 | 1359 | 1359 | 0.032357 | 529 | 0.012595 | 1548 | 0.036857 | 1.362 | A04 | MICL0.00941034/DON
Build-In Floor | Mini Canal | MICL.00941034/DOV | 9 | 410 | 34 | 34 | 1359 | 1359 | 1359 | 0.032357 | 529 | 0.012595 | 1548 | 0.036857 | 1.362 | A04 | MICL0.00941034/DOV
Build-In Floor | Mini Canal | MICL.00941034/PNC | 9 | 410 | 34 | 34 | 1242 | 1242 | 1242 | 0.029571 | 483 | 0.0115 | 1415 | 0.03369 | 1.362 | A04 | MICL0.00941034/PNC
Build-In Floor | Mini Canal | MICL.00941034/RBL | 9 | 410 | 34 | 34 | 1461 | 1461 | 1461 | 0.034786 | 568 | 0.013524 | 1664 | 0.039619 | 1.362 | A04 | MICL0.00941034/RBL
Build-In Floor | Mini Canal | MICL.00941034/RBN | 9 | 410 | 34 | 34 | 1417 | 1417 | 1417 | 0.033738 | 551 | 0.013119 | 1614 | 0.038429 | 1.362 | A04 | MICL0.00941034/RBN
Build-In Floor | Mini Canal | MICL.00941034/RBR | 9 | 410 | 34 | 34 | 1461 | 1461 | 1461 | 0.034786 | 568 | 0.013524 | 1664 | 0.039619 | 1.362 | A04 | MICL0.00941034/RBR
Build-In Floor | Mini Canal | MICL.00941034/RBV | 9 | 410 | 34 | 34 | 1417 | 1417 | 1417 | 0.033738 | 551 | 0.013119 | 1614 | 0.038429 | 1.362 | A04 | MICL0.00941034/RBV
Build-In Floor | Mini Canal | MICL.00941034/RDB | 9 | 410 | 34 | 34 | 1461 | 1461 | 1461 | 0.034786 | 568 | 0.013524 | 1664 | 0.039619 | 1.362 | A04 | MICL0.00941034/RDB
Build-In Floor | Mini Canal | MICL.00941034/RMN | 9 | 410 | 34 | 34 | 1417 | 1417 | 1417 | 0.033738 | 551 | 0.013119 | 1614 | 0.038429 | 1.362 | A04 | MICL0.00941034/RMN
Build-In Floor | Mini Canal | MICL.00941034/RMV | 9 | 410 | 34 | 34 | 1417 | 1417 | 1417 | 0.033738 | 551 | 0.013119 | 1614 | 0.038429 | 1.362 | A04 | MICL0.00941034/RMV
Build-In Floor | Mini Canal | MICL.00941034/RNA | 9 | 410 | 34 | 34 | 1461 | 1461 | 1461 | 0.034786 | 568 | 0.013524 | 1664 | 0.039619 | 1.362 | A04 | MICL0.00941034/RNA
Build-In Floor | Mini Canal | MICL.00941034/RON | 9 | 410 | 34 | 34 | 1417 | 1417 | 1417 | 0.033738 | 551 | 0.013119 | 1614 | 0.038429 | 1.362 | A04 | MICL0.00941034/RON
Build-In Floor | Mini Canal | MICL.00941034/ROV | 9 | 410 | 34 | 34 | 1417 | 1417 | 1417 | 0.033738 | 551 | 0.013119 | 1614 | 0.038429 | 1.362 | A04 | MICL0.00941034/ROV
Build-In Floor | Mini Canal | MICL.00941034/RSS | 9 | 410 | 34 | 34 | 1403 | 1403 | 1403 | 0.033405 | 546 | 0.013 | 1598 | 0.038048 | 1.362 | A04 | MICL0.00941034/RSS
Build-In Floor | Mini Canal | MICL.00941034/SBL | 9 | 410 | 34 | 34 | 1461 | 1461 | 1461 | 0.034786 | 568 | 0.013524 | 1664 | 0.039619 | 1.362 | A04 | MICL0.00941034/SBL
Build-In Floor | Mini Canal | MICL.00941034/SBR | 9 | 410 | 34 | 34 | 1461 | 1461 | 1461 | 0.034786 | 568 | 0.013524 | 1664 | 0.039619 | 1.362 | A04 | MICL0.00941034/SBR
Build-In Floor | Mini Canal | MICL.00941034/SDB | 9 | 410 | 34 | 34 | 1461 | 1461 | 1461 | 0.034786 | 568 | 0.013524 | 1664 | 0.039619 | 1.362 | A04 | MICL0.00941034/SDB
Build-In Floor | Mini Canal | MICL.00941034/SNA | 9 | 410 | 34 | 34 | 1461 | 1461 | 1461 | 0.034786 | 568 | 0.013524 | 1664 | 0.039619 | 1.362 | A04 | MICL0.00941034/SNA
Build-In Floor | Mini Canal | MICL.00941034/SNC | 9 | 410 | 34 | 34 | 1461 | 1461 | 1461 | 0.034786 | 568 | 0.013524 | 1664 | 0.039619 | 1.362 | A04 | MICL0.00941034/SNC
Build-In Floor | Mini Canal | MICL.00941042/ANA | 9 | 410 | 42 | 42 | 1583 | 1583 | 1583 | 0.03769 | 616 | 0.014667 | 1803 | 0.042929 | 1.362 | A04 | MICL0.00941042/ANA
Build-In Floor | Mini Canal | MICL.00941042/DBL | 9 | 410 | 42 | 42 | 2048 | 2048 | 2048 | 0.048762 | 797 | 0.018976 | 2333 | 0.055548 | 1.362 | A04 | MICL0.00941042/DBL
Build-In Floor | Mini Canal | MICL.00941042/DBN | 9 | 410 | 42 | 42 | 1963 | 1963 | 1963 | 0.046738 | 764 | 0.01819 | 2236 | 0.053238 | 1.362 | A04 | MICL0.00941042/DBN
Build-In Floor | Mini Canal | MICL.00941042/DBR | 9 | 410 | 42 | 42 | 2048 | 2048 | 2048 | 0.048762 | 797 | 0.018976 | 2333 | 0.055548 | 1.362 | A04 | MICL0.00941042/DBR
Build-In Floor | Mini Canal | MICL.00941042/DBV | 9 | 410 | 42 | 42 | 1963 | 1963 | 1963 | 0.046738 | 764 | 0.01819 | 2236 | 0.053238 | 1.362 | A04 | MICL0.00941042/DBV
Build-In Floor | Mini Canal | MICL.00941042/DDB | 9 | 410 | 42 | 42 | 2048 | 2048 | 2048 | 0.048762 | 797 | 0.018976 | 2333 | 0.055548 | 1.362 | A04 | MICL0.00941042/DDB
Build-In Floor | Mini Canal | MICL.00941042/DMN | 9 | 410 | 42 | 42 | 1963 | 1963 | 1963 | 0.046738 | 764 | 0.01819 | 2236 | 0.053238 | 1.362 | A04 | MICL0.00941042/DMN
Build-In Floor | Mini Canal | MICL.00941042/DMV | 9 | 410 | 42 | 42 | 1963 | 1963 | 1963 | 0.046738 | 764 | 0.01819 | 2236 | 0.053238 | 1.362 | A04 | MICL0.00941042/DMV
Build-In Floor | Mini Canal | MICL.00941042/DNA | 9 | 410 | 42 | 42 | 2048 | 2048 | 2048 | 0.048762 | 797 | 0.018976 | 2333 | 0.055548 | 1.362 | A04 | MICL0.00941042/DNA
Build-In Floor | Mini Canal | MICL.00941042/DNC | 9 | 410 | 42 | 42 | 2048 | 2048 | 2048 | 0.048762 | 797 | 0.018976 | 2333 | 0.055548 | 1.362 | A04 | MICL0.00941042/DNC
Build-In Floor | Mini Canal | MICL.00941042/DON | 9 | 410 | 42 | 42 | 1963 | 1963 | 1963 | 0.046738 | 764 | 0.01819 | 2236 | 0.053238 | 1.362 | A04 | MICL0.00941042/DON
Build-In Floor | Mini Canal | MICL.00941042/DOV | 9 | 410 | 42 | 42 | 1963 | 1963 | 1963 | 0.046738 | 764 | 0.01819 | 2236 | 0.053238 | 1.362 | A04 | MICL0.00941042/DOV
Build-In Floor | Mini Canal | MICL.00941042/PNC | 9 | 410 | 42 | 42 | 1794 | 1794 | 1794 | 0.042714 | 698 | 0.016619 | 2043 | 0.048643 | 1.362 | A04 | MICL0.00941042/PNC
Build-In Floor | Mini Canal | MICL.00941042/RBL | 9 | 410 | 42 | 42 | 2111 | 2111 | 2111 | 0.050262 | 821 | 0.019548 | 2404 | 0.057238 | 1.362 | A04 | MICL0.00941042/RBL
Build-In Floor | Mini Canal | MICL.00941042/RBN | 9 | 410 | 42 | 42 | 2048 | 2048 | 2048 | 0.048762 | 797 | 0.018976 | 2333 | 0.055548 | 1.362 | A04 | MICL0.00941042/RBN
Build-In Floor | Mini Canal | MICL.00941042/RBR | 9 | 410 | 42 | 42 | 2111 | 2111 | 2111 | 0.050262 | 821 | 0.019548 | 2404 | 0.057238 | 1.362 | A04 | MICL0.00941042/RBR
Build-In Floor | Mini Canal | MICL.00941042/RBV | 9 | 410 | 42 | 42 | 2048 | 2048 | 2048 | 0.048762 | 797 | 0.018976 | 2333 | 0.055548 | 1.362 | A04 | MICL0.00941042/RBV
Build-In Floor | Mini Canal | MICL.00941042/RDB | 9 | 410 | 42 | 42 | 2111 | 2111 | 2111 | 0.050262 | 821 | 0.019548 | 2404 | 0.057238 | 1.362 | A04 | MICL0.00941042/RDB
Build-In Floor | Mini Canal | MICL.00941042/RMN | 9 | 410 | 42 | 42 | 2048 | 2048 | 2048 | 0.048762 | 797 | 0.018976 | 2333 | 0.055548 | 1.362 | A04 | MICL0.00941042/RMN
Build-In Floor | Mini Canal | MICL.00941042/RMV | 9 | 410 | 42 | 42 | 2048 | 2048 | 2048 | 0.048762 | 797 | 0.018976 | 2333 | 0.055548 | 1.362 | A04 | MICL0.00941042/RMV
Build-In Floor | Mini Canal | MICL.00941042/RNA | 9 | 410 | 42 | 42 | 2111 | 2111 | 2111 | 0.050262 | 821 | 0.019548 | 2404 | 0.057238 | 1.362 | A04 | MICL0.00941042/RNA
Build-In Floor | Mini Canal | MICL.00941042/RON | 9 | 410 | 42 | 42 | 2048 | 2048 | 2048 | 0.048762 | 797 | 0.018976 | 2333 | 0.055548 | 1.362 | A04 | MICL0.00941042/RON
Build-In Floor | Mini Canal | MICL.00941042/ROV | 9 | 410 | 42 | 42 | 2048 | 2048 | 2048 | 0.048762 | 797 | 0.018976 | 2333 | 0.055548 | 1.362 | A04 | MICL0.00941042/ROV
Build-In Floor | Mini Canal | MICL.00941042/RSS | 9 | 410 | 42 | 42 | 2027 | 2027 | 2027 | 0.048262 | 789 | 0.018786 | 2309 | 0.054976 | 1.362 | A04 | MICL0.00941042/RSS
Build-In Floor | Mini Canal | MICL.00941042/SBL | 9 | 410 | 42 | 42 | 2111 | 2111 | 2111 | 0.050262 | 821 | 0.019548 | 2404 | 0.057238 | 1.362 | A04 | MICL0.00941042/SBL
Build-In Floor | Mini Canal | MICL.00941042/SBR | 9 | 410 | 42 | 42 | 2111 | 2111 | 2111 | 0.050262 | 821 | 0.019548 | 2404 | 0.057238 | 1.362 | A04 | MICL0.00941042/SBR
Build-In Floor | Mini Canal | MICL.00941042/SDB | 9 | 410 | 42 | 42 | 2111 | 2111 | 2111 | 0.050262 | 821 | 0.019548 | 2404 | 0.057238 | 1.362 | A04 | MICL0.00941042/SDB
Build-In Floor | Mini Canal | MICL.00941042/SNA | 9 | 410 | 42 | 42 | 2111 | 2111 | 2111 | 0.050262 | 821 | 0.019548 | 2404 | 0.057238 | 1.362 | A04 | MICL0.00941042/SNA
Build-In Floor | Mini Canal | MICL.00941042/SNC | 9 | 410 | 42 | 42 | 2111 | 2111 | 2111 | 0.050262 | 821 | 0.019548 | 2404 | 0.057238 | 1.362 | A04 | MICL0.00941042/SNC
Build-In Floor | Mini Canal | MICL.00943014/ANA | 9 | 430 | 14 | 14 | 571 | 571 | 571 | 0.013595 | 222 | 0.0052857 | 650 | 0.015476 | 1.362 | A04 | MICL0.00943014/ANA
Build-In Floor | Mini Canal | MICL.00943014/DBL | 9 | 430 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.00943014/DBL
Build-In Floor | Mini Canal | MICL.00943014/DBN | 9 | 430 | 14 | 14 | 708 | 708 | 708 | 0.016857 | 275 | 0.0065476 | 806 | 0.01919 | 1.362 | A04 | MICL0.00943014/DBN
Build-In Floor | Mini Canal | MICL.00943014/DBR | 9 | 430 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.00943014/DBR
Build-In Floor | Mini Canal | MICL.00943014/DBV | 9 | 430 | 14 | 14 | 708 | 708 | 708 | 0.016857 | 275 | 0.0065476 | 806 | 0.01919 | 1.362 | A04 | MICL0.00943014/DBV
Build-In Floor | Mini Canal | MICL.00943014/DDB | 9 | 430 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.00943014/DDB
Build-In Floor | Mini Canal | MICL.00943014/DMN | 9 | 430 | 14 | 14 | 708 | 708 | 708 | 0.016857 | 275 | 0.0065476 | 806 | 0.01919 | 1.362 | A04 | MICL0.00943014/DMN
Build-In Floor | Mini Canal | MICL.00943014/DMV | 9 | 430 | 14 | 14 | 708 | 708 | 708 | 0.016857 | 275 | 0.0065476 | 806 | 0.01919 | 1.362 | A04 | MICL0.00943014/DMV
Build-In Floor | Mini Canal | MICL.00943014/DNA | 9 | 430 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.00943014/DNA
Build-In Floor | Mini Canal | MICL.00943014/DNC | 9 | 430 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.00943014/DNC
Build-In Floor | Mini Canal | MICL.00943014/DON | 9 | 430 | 14 | 14 | 708 | 708 | 708 | 0.016857 | 275 | 0.0065476 | 806 | 0.01919 | 1.362 | A04 | MICL0.00943014/DON
Build-In Floor | Mini Canal | MICL.00943014/DOV | 9 | 430 | 14 | 14 | 708 | 708 | 708 | 0.016857 | 275 | 0.0065476 | 806 | 0.01919 | 1.362 | A04 | MICL0.00943014/DOV
Build-In Floor | Mini Canal | MICL.00943014/RBL | 9 | 430 | 14 | 14 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.00943014/RBL
Build-In Floor | Mini Canal | MICL.00943014/RBN | 9 | 430 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.00943014/RBN
Build-In Floor | Mini Canal | MICL.00943014/RBR | 9 | 430 | 14 | 14 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.00943014/RBR
Build-In Floor | Mini Canal | MICL.00943014/RBV | 9 | 430 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.00943014/RBV
Build-In Floor | Mini Canal | MICL.00943014/RDB | 9 | 430 | 14 | 14 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.00943014/RDB
Build-In Floor | Mini Canal | MICL.00943014/RMN | 9 | 430 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.00943014/RMN
Build-In Floor | Mini Canal | MICL.00943014/RMV | 9 | 430 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.00943014/RMV
Build-In Floor | Mini Canal | MICL.00943014/RNA | 9 | 430 | 14 | 14 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.00943014/RNA
Build-In Floor | Mini Canal | MICL.00943014/RON | 9 | 430 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.00943014/RON
Build-In Floor | Mini Canal | MICL.00943014/ROV | 9 | 430 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.00943014/ROV
Build-In Floor | Mini Canal | MICL.00943014/RSS | 9 | 430 | 14 | 14 | 731 | 731 | 731 | 0.017405 | 284 | 0.0067619 | 833 | 0.019833 | 1.362 | A04 | MICL0.00943014/RSS
Build-In Floor | Mini Canal | MICL.00943014/SBL | 9 | 430 | 14 | 14 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.00943014/SBL
Build-In Floor | Mini Canal | MICL.00943014/SBR | 9 | 430 | 14 | 14 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.00943014/SBR
Build-In Floor | Mini Canal | MICL.00943014/SDB | 9 | 430 | 14 | 14 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.00943014/SDB
Build-In Floor | Mini Canal | MICL.00943014/SNA | 9 | 430 | 14 | 14 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.00943014/SNA
Build-In Floor | Mini Canal | MICL.00943014/SNC | 9 | 430 | 14 | 14 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.00943014/SNC
Build-In Floor | Mini Canal | MICL.00943018/ANA | 9 | 430 | 18 | 18 | 677 | 677 | 677 | 0.016119 | 263 | 0.0062619 | 771 | 0.018357 | 1.362 | A04 | MICL0.00943018/ANA
Build-In Floor | Mini Canal | MICL.00943018/DBL | 9 | 430 | 18 | 18 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00943018/DBL
Build-In Floor | Mini Canal | MICL.00943018/DBN | 9 | 430 | 18 | 18 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.00943018/DBN
Build-In Floor | Mini Canal | MICL.00943018/DBR | 9 | 430 | 18 | 18 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00943018/DBR
Build-In Floor | Mini Canal | MICL.00943018/DBV | 9 | 430 | 18 | 18 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.00943018/DBV
Build-In Floor | Mini Canal | MICL.00943018/DDB | 9 | 430 | 18 | 18 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00943018/DDB
Build-In Floor | Mini Canal | MICL.00943018/DMN | 9 | 430 | 18 | 18 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.00943018/DMN
Build-In Floor | Mini Canal | MICL.00943018/DMV | 9 | 430 | 18 | 18 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.00943018/DMV
Build-In Floor | Mini Canal | MICL.00943018/DNA | 9 | 430 | 18 | 18 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00943018/DNA
Build-In Floor | Mini Canal | MICL.00943018/DNC | 9 | 430 | 18 | 18 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00943018/DNC
Build-In Floor | Mini Canal | MICL.00943018/DON | 9 | 430 | 18 | 18 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.00943018/DON
Build-In Floor | Mini Canal | MICL.00943018/DOV | 9 | 430 | 18 | 18 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.00943018/DOV
Build-In Floor | Mini Canal | MICL.00943018/RBL | 9 | 430 | 18 | 18 | 902 | 902 | 902 | 0.021476 | 351 | 0.0083571 | 1027 | 0.024452 | 1.362 | A04 | MICL0.00943018/RBL
Build-In Floor | Mini Canal | MICL.00943018/RBN | 9 | 430 | 18 | 18 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00943018/RBN
Build-In Floor | Mini Canal | MICL.00943018/RBR | 9 | 430 | 18 | 18 | 902 | 902 | 902 | 0.021476 | 351 | 0.0083571 | 1027 | 0.024452 | 1.362 | A04 | MICL0.00943018/RBR
Build-In Floor | Mini Canal | MICL.00943018/RBV | 9 | 430 | 18 | 18 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00943018/RBV
Build-In Floor | Mini Canal | MICL.00943018/RDB | 9 | 430 | 18 | 18 | 902 | 902 | 902 | 0.021476 | 351 | 0.0083571 | 1027 | 0.024452 | 1.362 | A04 | MICL0.00943018/RDB
Build-In Floor | Mini Canal | MICL.00943018/RMN | 9 | 430 | 18 | 18 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00943018/RMN
Build-In Floor | Mini Canal | MICL.00943018/RMV | 9 | 430 | 18 | 18 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00943018/RMV
Build-In Floor | Mini Canal | MICL.00943018/RNA | 9 | 430 | 18 | 18 | 902 | 902 | 902 | 0.021476 | 351 | 0.0083571 | 1027 | 0.024452 | 1.362 | A04 | MICL0.00943018/RNA
Build-In Floor | Mini Canal | MICL.00943018/RON | 9 | 430 | 18 | 18 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00943018/RON
Build-In Floor | Mini Canal | MICL.00943018/ROV | 9 | 430 | 18 | 18 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00943018/ROV
Build-In Floor | Mini Canal | MICL.00943018/RSS | 9 | 430 | 18 | 18 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.00943018/RSS
Build-In Floor | Mini Canal | MICL.00943018/SBL | 9 | 430 | 18 | 18 | 902 | 902 | 902 | 0.021476 | 351 | 0.0083571 | 1027 | 0.024452 | 1.362 | A04 | MICL0.00943018/SBL
Build-In Floor | Mini Canal | MICL.00943018/SBR | 9 | 430 | 18 | 18 | 902 | 902 | 902 | 0.021476 | 351 | 0.0083571 | 1027 | 0.024452 | 1.362 | A04 | MICL0.00943018/SBR
Build-In Floor | Mini Canal | MICL.00943018/SDB | 9 | 430 | 18 | 18 | 902 | 902 | 902 | 0.021476 | 351 | 0.0083571 | 1027 | 0.024452 | 1.362 | A04 | MICL0.00943018/SDB
Build-In Floor | Mini Canal | MICL.00943018/SNA | 9 | 430 | 18 | 18 | 902 | 902 | 902 | 0.021476 | 351 | 0.0083571 | 1027 | 0.024452 | 1.362 | A04 | MICL0.00943018/SNA
Build-In Floor | Mini Canal | MICL.00943018/SNC | 9 | 430 | 18 | 18 | 902 | 902 | 902 | 0.021476 | 351 | 0.0083571 | 1027 | 0.024452 | 1.362 | A04 | MICL0.00943018/SNC
Build-In Floor | Mini Canal | MICL.00943026/ANA | 9 | 430 | 26 | 26 | 890 | 890 | 890 | 0.02119 | 346 | 0.0082381 | 1014 | 0.024143 | 1.362 | A04 | MICL0.00943026/ANA
Build-In Floor | Mini Canal | MICL.00943026/DBL | 9 | 430 | 26 | 26 | 1150 | 1150 | 1150 | 0.027381 | 447 | 0.010643 | 1310 | 0.03119 | 1.362 | A04 | MICL0.00943026/DBL
Build-In Floor | Mini Canal | MICL.00943026/DBN | 9 | 430 | 26 | 26 | 1103 | 1103 | 1103 | 0.026262 | 429 | 0.010214 | 1256 | 0.029905 | 1.362 | A04 | MICL0.00943026/DBN
Build-In Floor | Mini Canal | MICL.00943026/DBR | 9 | 430 | 26 | 26 | 1150 | 1150 | 1150 | 0.027381 | 447 | 0.010643 | 1310 | 0.03119 | 1.362 | A04 | MICL0.00943026/DBR
Build-In Floor | Mini Canal | MICL.00943026/DBV | 9 | 430 | 26 | 26 | 1103 | 1103 | 1103 | 0.026262 | 429 | 0.010214 | 1256 | 0.029905 | 1.362 | A04 | MICL0.00943026/DBV
Build-In Floor | Mini Canal | MICL.00943026/DDB | 9 | 430 | 26 | 26 | 1150 | 1150 | 1150 | 0.027381 | 447 | 0.010643 | 1310 | 0.03119 | 1.362 | A04 | MICL0.00943026/DDB
Build-In Floor | Mini Canal | MICL.00943026/DMN | 9 | 430 | 26 | 26 | 1103 | 1103 | 1103 | 0.026262 | 429 | 0.010214 | 1256 | 0.029905 | 1.362 | A04 | MICL0.00943026/DMN
Build-In Floor | Mini Canal | MICL.00943026/DMV | 9 | 430 | 26 | 26 | 1103 | 1103 | 1103 | 0.026262 | 429 | 0.010214 | 1256 | 0.029905 | 1.362 | A04 | MICL0.00943026/DMV
Build-In Floor | Mini Canal | MICL.00943026/DNA | 9 | 430 | 26 | 26 | 1150 | 1150 | 1150 | 0.027381 | 447 | 0.010643 | 1310 | 0.03119 | 1.362 | A04 | MICL0.00943026/DNA
Build-In Floor | Mini Canal | MICL.00943026/DNC | 9 | 430 | 26 | 26 | 1150 | 1150 | 1150 | 0.027381 | 447 | 0.010643 | 1310 | 0.03119 | 1.362 | A04 | MICL0.00943026/DNC
Build-In Floor | Mini Canal | MICL.00943026/DON | 9 | 430 | 26 | 26 | 1103 | 1103 | 1103 | 0.026262 | 429 | 0.010214 | 1256 | 0.029905 | 1.362 | A04 | MICL0.00943026/DON
Build-In Floor | Mini Canal | MICL.00943026/DOV | 9 | 430 | 26 | 26 | 1103 | 1103 | 1103 | 0.026262 | 429 | 0.010214 | 1256 | 0.029905 | 1.362 | A04 | MICL0.00943026/DOV
Build-In Floor | Mini Canal | MICL.00943026/PNC | 9 | 430 | 26 | 26 | 1008 | 1008 | 1008 | 0.024 | 392 | 0.0093333 | 1148 | 0.027333 | 1.362 | A04 | MICL0.00943026/PNC
Build-In Floor | Mini Canal | MICL.00943026/RBL | 9 | 430 | 26 | 26 | 1186 | 1186 | 1186 | 0.028238 | 461 | 0.010976 | 1351 | 0.032167 | 1.362 | A04 | MICL0.00943026/RBL
Build-In Floor | Mini Canal | MICL.00943026/RBN | 9 | 430 | 26 | 26 | 1150 | 1150 | 1150 | 0.027381 | 447 | 0.010643 | 1310 | 0.03119 | 1.362 | A04 | MICL0.00943026/RBN
Build-In Floor | Mini Canal | MICL.00943026/RBR | 9 | 430 | 26 | 26 | 1186 | 1186 | 1186 | 0.028238 | 461 | 0.010976 | 1351 | 0.032167 | 1.362 | A04 | MICL0.00943026/RBR
Build-In Floor | Mini Canal | MICL.00943026/RBV | 9 | 430 | 26 | 26 | 1150 | 1150 | 1150 | 0.027381 | 447 | 0.010643 | 1310 | 0.03119 | 1.362 | A04 | MICL0.00943026/RBV
Build-In Floor | Mini Canal | MICL.00943026/RDB | 9 | 430 | 26 | 26 | 1186 | 1186 | 1186 | 0.028238 | 461 | 0.010976 | 1351 | 0.032167 | 1.362 | A04 | MICL0.00943026/RDB
Build-In Floor | Mini Canal | MICL.00943026/RMN | 9 | 430 | 26 | 26 | 1150 | 1150 | 1150 | 0.027381 | 447 | 0.010643 | 1310 | 0.03119 | 1.362 | A04 | MICL0.00943026/RMN
Build-In Floor | Mini Canal | MICL.00943026/RMV | 9 | 430 | 26 | 26 | 1150 | 1150 | 1150 | 0.027381 | 447 | 0.010643 | 1310 | 0.03119 | 1.362 | A04 | MICL0.00943026/RMV
Build-In Floor | Mini Canal | MICL.00943026/RNA | 9 | 430 | 26 | 26 | 1186 | 1186 | 1186 | 0.028238 | 461 | 0.010976 | 1351 | 0.032167 | 1.362 | A04 | MICL0.00943026/RNA
Build-In Floor | Mini Canal | MICL.00943026/RON | 9 | 430 | 26 | 26 | 1150 | 1150 | 1150 | 0.027381 | 447 | 0.010643 | 1310 | 0.03119 | 1.362 | A04 | MICL0.00943026/RON
Build-In Floor | Mini Canal | MICL.00943026/ROV | 9 | 430 | 26 | 26 | 1150 | 1150 | 1150 | 0.027381 | 447 | 0.010643 | 1310 | 0.03119 | 1.362 | A04 | MICL0.00943026/ROV
Build-In Floor | Mini Canal | MICL.00943026/RSS | 9 | 430 | 26 | 26 | 1139 | 1139 | 1139 | 0.027119 | 443 | 0.010548 | 1297 | 0.030881 | 1.362 | A04 | MICL0.00943026/RSS
Build-In Floor | Mini Canal | MICL.00943026/SBL | 9 | 430 | 26 | 26 | 1186 | 1186 | 1186 | 0.028238 | 461 | 0.010976 | 1351 | 0.032167 | 1.362 | A04 | MICL0.00943026/SBL
Build-In Floor | Mini Canal | MICL.00943026/SBR | 9 | 430 | 26 | 26 | 1186 | 1186 | 1186 | 0.028238 | 461 | 0.010976 | 1351 | 0.032167 | 1.362 | A04 | MICL0.00943026/SBR
Build-In Floor | Mini Canal | MICL.00943026/SDB | 9 | 430 | 26 | 26 | 1186 | 1186 | 1186 | 0.028238 | 461 | 0.010976 | 1351 | 0.032167 | 1.362 | A04 | MICL0.00943026/SDB
Build-In Floor | Mini Canal | MICL.00943026/SNA | 9 | 430 | 26 | 26 | 1186 | 1186 | 1186 | 0.028238 | 461 | 0.010976 | 1351 | 0.032167 | 1.362 | A04 | MICL0.00943026/SNA
Build-In Floor | Mini Canal | MICL.00943026/SNC | 9 | 430 | 26 | 26 | 1186 | 1186 | 1186 | 0.028238 | 461 | 0.010976 | 1351 | 0.032167 | 1.362 | A04 | MICL0.00943026/SNC
Build-In Floor | Mini Canal | MICL.00943034/ANA | 9 | 430 | 34 | 34 | 1154 | 1154 | 1154 | 0.027476 | 449 | 0.01069 | 1314 | 0.031286 | 1.362 | A04 | MICL0.00943034/ANA
Build-In Floor | Mini Canal | MICL.00943034/DBL | 9 | 430 | 34 | 34 | 1492 | 1492 | 1492 | 0.035524 | 580 | 0.01381 | 1699 | 0.040452 | 1.362 | A04 | MICL0.00943034/DBL
Build-In Floor | Mini Canal | MICL.00943034/DBN | 9 | 430 | 34 | 34 | 1430 | 1430 | 1430 | 0.034048 | 556 | 0.013238 | 1629 | 0.038786 | 1.362 | A04 | MICL0.00943034/DBN
Build-In Floor | Mini Canal | MICL.00943034/DBR | 9 | 430 | 34 | 34 | 1492 | 1492 | 1492 | 0.035524 | 580 | 0.01381 | 1699 | 0.040452 | 1.362 | A04 | MICL0.00943034/DBR
Build-In Floor | Mini Canal | MICL.00943034/DBV | 9 | 430 | 34 | 34 | 1430 | 1430 | 1430 | 0.034048 | 556 | 0.013238 | 1629 | 0.038786 | 1.362 | A04 | MICL0.00943034/DBV
Build-In Floor | Mini Canal | MICL.00943034/DDB | 9 | 430 | 34 | 34 | 1492 | 1492 | 1492 | 0.035524 | 580 | 0.01381 | 1699 | 0.040452 | 1.362 | A04 | MICL0.00943034/DDB
Build-In Floor | Mini Canal | MICL.00943034/DMN | 9 | 430 | 34 | 34 | 1430 | 1430 | 1430 | 0.034048 | 556 | 0.013238 | 1629 | 0.038786 | 1.362 | A04 | MICL0.00943034/DMN
Build-In Floor | Mini Canal | MICL.00943034/DMV | 9 | 430 | 34 | 34 | 1430 | 1430 | 1430 | 0.034048 | 556 | 0.013238 | 1629 | 0.038786 | 1.362 | A04 | MICL0.00943034/DMV
Build-In Floor | Mini Canal | MICL.00943034/DNA | 9 | 430 | 34 | 34 | 1492 | 1492 | 1492 | 0.035524 | 580 | 0.01381 | 1699 | 0.040452 | 1.362 | A04 | MICL0.00943034/DNA
Build-In Floor | Mini Canal | MICL.00943034/DNC | 9 | 430 | 34 | 34 | 1492 | 1492 | 1492 | 0.035524 | 580 | 0.01381 | 1699 | 0.040452 | 1.362 | A04 | MICL0.00943034/DNC
Build-In Floor | Mini Canal | MICL.00943034/DON | 9 | 430 | 34 | 34 | 1430 | 1430 | 1430 | 0.034048 | 556 | 0.013238 | 1629 | 0.038786 | 1.362 | A04 | MICL0.00943034/DON
Build-In Floor | Mini Canal | MICL.00943034/DOV | 9 | 430 | 34 | 34 | 1430 | 1430 | 1430 | 0.034048 | 556 | 0.013238 | 1629 | 0.038786 | 1.362 | A04 | MICL0.00943034/DOV
Build-In Floor | Mini Canal | MICL.00943034/PNC | 9 | 430 | 34 | 34 | 1307 | 1307 | 1307 | 0.031119 | 508 | 0.012095 | 1489 | 0.035452 | 1.362 | A04 | MICL0.00943034/PNC
Build-In Floor | Mini Canal | MICL.00943034/RBL | 9 | 430 | 34 | 34 | 1538 | 1538 | 1538 | 0.036619 | 598 | 0.014238 | 1752 | 0.041714 | 1.362 | A04 | MICL0.00943034/RBL
Build-In Floor | Mini Canal | MICL.00943034/RBN | 9 | 430 | 34 | 34 | 1492 | 1492 | 1492 | 0.035524 | 580 | 0.01381 | 1699 | 0.040452 | 1.362 | A04 | MICL0.00943034/RBN
Build-In Floor | Mini Canal | MICL.00943034/RBR | 9 | 430 | 34 | 34 | 1538 | 1538 | 1538 | 0.036619 | 598 | 0.014238 | 1752 | 0.041714 | 1.362 | A04 | MICL0.00943034/RBR
Build-In Floor | Mini Canal | MICL.00943034/RBV | 9 | 430 | 34 | 34 | 1492 | 1492 | 1492 | 0.035524 | 580 | 0.01381 | 1699 | 0.040452 | 1.362 | A04 | MICL0.00943034/RBV
Build-In Floor | Mini Canal | MICL.00943034/RDB | 9 | 430 | 34 | 34 | 1538 | 1538 | 1538 | 0.036619 | 598 | 0.014238 | 1752 | 0.041714 | 1.362 | A04 | MICL0.00943034/RDB
Build-In Floor | Mini Canal | MICL.00943034/RMN | 9 | 430 | 34 | 34 | 1492 | 1492 | 1492 | 0.035524 | 580 | 0.01381 | 1699 | 0.040452 | 1.362 | A04 | MICL0.00943034/RMN
Build-In Floor | Mini Canal | MICL.00943034/RMV | 9 | 430 | 34 | 34 | 1492 | 1492 | 1492 | 0.035524 | 580 | 0.01381 | 1699 | 0.040452 | 1.362 | A04 | MICL0.00943034/RMV
Build-In Floor | Mini Canal | MICL.00943034/RNA | 9 | 430 | 34 | 34 | 1538 | 1538 | 1538 | 0.036619 | 598 | 0.014238 | 1752 | 0.041714 | 1.362 | A04 | MICL0.00943034/RNA
Build-In Floor | Mini Canal | MICL.00943034/RON | 9 | 430 | 34 | 34 | 1492 | 1492 | 1492 | 0.035524 | 580 | 0.01381 | 1699 | 0.040452 | 1.362 | A04 | MICL0.00943034/RON
Build-In Floor | Mini Canal | MICL.00943034/ROV | 9 | 430 | 34 | 34 | 1492 | 1492 | 1492 | 0.035524 | 580 | 0.01381 | 1699 | 0.040452 | 1.362 | A04 | MICL0.00943034/ROV
Build-In Floor | Mini Canal | MICL.00943034/RSS | 9 | 430 | 34 | 34 | 1476 | 1476 | 1476 | 0.035143 | 574 | 0.013667 | 1681 | 0.040024 | 1.362 | A04 | MICL0.00943034/RSS
Build-In Floor | Mini Canal | MICL.00943034/SBL | 9 | 430 | 34 | 34 | 1538 | 1538 | 1538 | 0.036619 | 598 | 0.014238 | 1752 | 0.041714 | 1.362 | A04 | MICL0.00943034/SBL
Build-In Floor | Mini Canal | MICL.00943034/SBR | 9 | 430 | 34 | 34 | 1538 | 1538 | 1538 | 0.036619 | 598 | 0.014238 | 1752 | 0.041714 | 1.362 | A04 | MICL0.00943034/SBR
Build-In Floor | Mini Canal | MICL.00943034/SDB | 9 | 430 | 34 | 34 | 1538 | 1538 | 1538 | 0.036619 | 598 | 0.014238 | 1752 | 0.041714 | 1.362 | A04 | MICL0.00943034/SDB
Build-In Floor | Mini Canal | MICL.00943034/SNA | 9 | 430 | 34 | 34 | 1538 | 1538 | 1538 | 0.036619 | 598 | 0.014238 | 1752 | 0.041714 | 1.362 | A04 | MICL0.00943034/SNA
Build-In Floor | Mini Canal | MICL.00943034/SNC | 9 | 430 | 34 | 34 | 1538 | 1538 | 1538 | 0.036619 | 598 | 0.014238 | 1752 | 0.041714 | 1.362 | A04 | MICL0.00943034/SNC
Build-In Floor | Mini Canal | MICL.00943042/ANA | 9 | 430 | 42 | 42 | 1666 | 1666 | 1666 | 0.039667 | 648 | 0.015429 | 1898 | 0.04519 | 1.362 | A04 | MICL0.00943042/ANA
Build-In Floor | Mini Canal | MICL.00943042/DBL | 9 | 430 | 42 | 42 | 2154 | 2154 | 2154 | 0.051286 | 838 | 0.019952 | 2453 | 0.058405 | 1.362 | A04 | MICL0.00943042/DBL
Build-In Floor | Mini Canal | MICL.00943042/DBN | 9 | 430 | 42 | 42 | 2066 | 2066 | 2066 | 0.04919 | 804 | 0.019143 | 2353 | 0.056024 | 1.362 | A04 | MICL0.00943042/DBN
Build-In Floor | Mini Canal | MICL.00943042/DBR | 9 | 430 | 42 | 42 | 2154 | 2154 | 2154 | 0.051286 | 838 | 0.019952 | 2453 | 0.058405 | 1.362 | A04 | MICL0.00943042/DBR
Build-In Floor | Mini Canal | MICL.00943042/DBV | 9 | 430 | 42 | 42 | 2066 | 2066 | 2066 | 0.04919 | 804 | 0.019143 | 2353 | 0.056024 | 1.362 | A04 | MICL0.00943042/DBV
Build-In Floor | Mini Canal | MICL.00943042/DDB | 9 | 430 | 42 | 42 | 2154 | 2154 | 2154 | 0.051286 | 838 | 0.019952 | 2453 | 0.058405 | 1.362 | A04 | MICL0.00943042/DDB
Build-In Floor | Mini Canal | MICL.00943042/DMN | 9 | 430 | 42 | 42 | 2066 | 2066 | 2066 | 0.04919 | 804 | 0.019143 | 2353 | 0.056024 | 1.362 | A04 | MICL0.00943042/DMN
Build-In Floor | Mini Canal | MICL.00943042/DMV | 9 | 430 | 42 | 42 | 2066 | 2066 | 2066 | 0.04919 | 804 | 0.019143 | 2353 | 0.056024 | 1.362 | A04 | MICL0.00943042/DMV
Build-In Floor | Mini Canal | MICL.00943042/DNA | 9 | 430 | 42 | 42 | 2154 | 2154 | 2154 | 0.051286 | 838 | 0.019952 | 2453 | 0.058405 | 1.362 | A04 | MICL0.00943042/DNA
Build-In Floor | Mini Canal | MICL.00943042/DNC | 9 | 430 | 42 | 42 | 2154 | 2154 | 2154 | 0.051286 | 838 | 0.019952 | 2453 | 0.058405 | 1.362 | A04 | MICL0.00943042/DNC
Build-In Floor | Mini Canal | MICL.00943042/DON | 9 | 430 | 42 | 42 | 2066 | 2066 | 2066 | 0.04919 | 804 | 0.019143 | 2353 | 0.056024 | 1.362 | A04 | MICL0.00943042/DON
Build-In Floor | Mini Canal | MICL.00943042/DOV | 9 | 430 | 42 | 42 | 2066 | 2066 | 2066 | 0.04919 | 804 | 0.019143 | 2353 | 0.056024 | 1.362 | A04 | MICL0.00943042/DOV
Build-In Floor | Mini Canal | MICL.00943042/PNC | 9 | 430 | 42 | 42 | 1888 | 1888 | 1888 | 0.044952 | 734 | 0.017476 | 2150 | 0.05119 | 1.362 | A04 | MICL0.00943042/PNC
Build-In Floor | Mini Canal | MICL.00943042/RBL | 9 | 430 | 42 | 42 | 2221 | 2221 | 2221 | 0.052881 | 864 | 0.020571 | 2530 | 0.060238 | 1.362 | A04 | MICL0.00943042/RBL
Build-In Floor | Mini Canal | MICL.00943042/RBN | 9 | 430 | 42 | 42 | 2154 | 2154 | 2154 | 0.051286 | 838 | 0.019952 | 2453 | 0.058405 | 1.362 | A04 | MICL0.00943042/RBN
Build-In Floor | Mini Canal | MICL.00943042/RBR | 9 | 430 | 42 | 42 | 2221 | 2221 | 2221 | 0.052881 | 864 | 0.020571 | 2530 | 0.060238 | 1.362 | A04 | MICL0.00943042/RBR
Build-In Floor | Mini Canal | MICL.00943042/RBV | 9 | 430 | 42 | 42 | 2154 | 2154 | 2154 | 0.051286 | 838 | 0.019952 | 2453 | 0.058405 | 1.362 | A04 | MICL0.00943042/RBV
Build-In Floor | Mini Canal | MICL.00943042/RDB | 9 | 430 | 42 | 42 | 2221 | 2221 | 2221 | 0.052881 | 864 | 0.020571 | 2530 | 0.060238 | 1.362 | A04 | MICL0.00943042/RDB
Build-In Floor | Mini Canal | MICL.00943042/RMN | 9 | 430 | 42 | 42 | 2154 | 2154 | 2154 | 0.051286 | 838 | 0.019952 | 2453 | 0.058405 | 1.362 | A04 | MICL0.00943042/RMN
Build-In Floor | Mini Canal | MICL.00943042/RMV | 9 | 430 | 42 | 42 | 2154 | 2154 | 2154 | 0.051286 | 838 | 0.019952 | 2453 | 0.058405 | 1.362 | A04 | MICL0.00943042/RMV
Build-In Floor | Mini Canal | MICL.00943042/RNA | 9 | 430 | 42 | 42 | 2221 | 2221 | 2221 | 0.052881 | 864 | 0.020571 | 2530 | 0.060238 | 1.362 | A04 | MICL0.00943042/RNA
Build-In Floor | Mini Canal | MICL.00943042/RON | 9 | 430 | 42 | 42 | 2154 | 2154 | 2154 | 0.051286 | 838 | 0.019952 | 2453 | 0.058405 | 1.362 | A04 | MICL0.00943042/RON
Build-In Floor | Mini Canal | MICL.00943042/ROV | 9 | 430 | 42 | 42 | 2154 | 2154 | 2154 | 0.051286 | 838 | 0.019952 | 2453 | 0.058405 | 1.362 | A04 | MICL0.00943042/ROV
Build-In Floor | Mini Canal | MICL.00943042/RSS | 9 | 430 | 42 | 42 | 2132 | 2132 | 2132 | 0.050762 | 829 | 0.019738 | 2428 | 0.05781 | 1.362 | A04 | MICL0.00943042/RSS
Build-In Floor | Mini Canal | MICL.00943042/SBL | 9 | 430 | 42 | 42 | 2221 | 2221 | 2221 | 0.052881 | 864 | 0.020571 | 2530 | 0.060238 | 1.362 | A04 | MICL0.00943042/SBL
Build-In Floor | Mini Canal | MICL.00943042/SBR | 9 | 430 | 42 | 42 | 2221 | 2221 | 2221 | 0.052881 | 864 | 0.020571 | 2530 | 0.060238 | 1.362 | A04 | MICL0.00943042/SBR
Build-In Floor | Mini Canal | MICL.00943042/SDB | 9 | 430 | 42 | 42 | 2221 | 2221 | 2221 | 0.052881 | 864 | 0.020571 | 2530 | 0.060238 | 1.362 | A04 | MICL0.00943042/SDB
Build-In Floor | Mini Canal | MICL.00943042/SNA | 9 | 430 | 42 | 42 | 2221 | 2221 | 2221 | 0.052881 | 864 | 0.020571 | 2530 | 0.060238 | 1.362 | A04 | MICL0.00943042/SNA
Build-In Floor | Mini Canal | MICL.00943042/SNC | 9 | 430 | 42 | 42 | 2221 | 2221 | 2221 | 0.052881 | 864 | 0.020571 | 2530 | 0.060238 | 1.362 | A04 | MICL0.00943042/SNC
Build-In Floor | Mini Canal | MICL.00945014/ANA | 9 | 450 | 14 | 14 | 600 | 600 | 600 | 0.014286 | 233 | 0.0055476 | 683 | 0.016262 | 1.362 | A04 | MICL0.00945014/ANA
Build-In Floor | Mini Canal | MICL.00945014/DBL | 9 | 450 | 14 | 14 | 776 | 776 | 776 | 0.018476 | 302 | 0.0071905 | 884 | 0.021048 | 1.362 | A04 | MICL0.00945014/DBL
Build-In Floor | Mini Canal | MICL.00945014/DBN | 9 | 450 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00945014/DBN
Build-In Floor | Mini Canal | MICL.00945014/DBR | 9 | 450 | 14 | 14 | 776 | 776 | 776 | 0.018476 | 302 | 0.0071905 | 884 | 0.021048 | 1.362 | A04 | MICL0.00945014/DBR
Build-In Floor | Mini Canal | MICL.00945014/DBV | 9 | 450 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00945014/DBV
Build-In Floor | Mini Canal | MICL.00945014/DDB | 9 | 450 | 14 | 14 | 776 | 776 | 776 | 0.018476 | 302 | 0.0071905 | 884 | 0.021048 | 1.362 | A04 | MICL0.00945014/DDB
Build-In Floor | Mini Canal | MICL.00945014/DMN | 9 | 450 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00945014/DMN
Build-In Floor | Mini Canal | MICL.00945014/DMV | 9 | 450 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00945014/DMV
Build-In Floor | Mini Canal | MICL.00945014/DNA | 9 | 450 | 14 | 14 | 776 | 776 | 776 | 0.018476 | 302 | 0.0071905 | 884 | 0.021048 | 1.362 | A04 | MICL0.00945014/DNA
Build-In Floor | Mini Canal | MICL.00945014/DNC | 9 | 450 | 14 | 14 | 776 | 776 | 776 | 0.018476 | 302 | 0.0071905 | 884 | 0.021048 | 1.362 | A04 | MICL0.00945014/DNC
Build-In Floor | Mini Canal | MICL.00945014/DON | 9 | 450 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00945014/DON
Build-In Floor | Mini Canal | MICL.00945014/DOV | 9 | 450 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00945014/DOV
Build-In Floor | Mini Canal | MICL.00945014/RBL | 9 | 450 | 14 | 14 | 800 | 800 | 800 | 0.019048 | 311 | 0.0074048 | 911 | 0.02169 | 1.362 | A04 | MICL0.00945014/RBL
Build-In Floor | Mini Canal | MICL.00945014/RBN | 9 | 450 | 14 | 14 | 776 | 776 | 776 | 0.018476 | 302 | 0.0071905 | 884 | 0.021048 | 1.362 | A04 | MICL0.00945014/RBN
Build-In Floor | Mini Canal | MICL.00945014/RBR | 9 | 450 | 14 | 14 | 800 | 800 | 800 | 0.019048 | 311 | 0.0074048 | 911 | 0.02169 | 1.362 | A04 | MICL0.00945014/RBR
Build-In Floor | Mini Canal | MICL.00945014/RBV | 9 | 450 | 14 | 14 | 776 | 776 | 776 | 0.018476 | 302 | 0.0071905 | 884 | 0.021048 | 1.362 | A04 | MICL0.00945014/RBV
Build-In Floor | Mini Canal | MICL.00945014/RDB | 9 | 450 | 14 | 14 | 800 | 800 | 800 | 0.019048 | 311 | 0.0074048 | 911 | 0.02169 | 1.362 | A04 | MICL0.00945014/RDB
Build-In Floor | Mini Canal | MICL.00945014/RMN | 9 | 450 | 14 | 14 | 776 | 776 | 776 | 0.018476 | 302 | 0.0071905 | 884 | 0.021048 | 1.362 | A04 | MICL0.00945014/RMN
Build-In Floor | Mini Canal | MICL.00945014/RMV | 9 | 450 | 14 | 14 | 776 | 776 | 776 | 0.018476 | 302 | 0.0071905 | 884 | 0.021048 | 1.362 | A04 | MICL0.00945014/RMV
Build-In Floor | Mini Canal | MICL.00945014/RNA | 9 | 450 | 14 | 14 | 800 | 800 | 800 | 0.019048 | 311 | 0.0074048 | 911 | 0.02169 | 1.362 | A04 | MICL0.00945014/RNA
Build-In Floor | Mini Canal | MICL.00945014/RON | 9 | 450 | 14 | 14 | 776 | 776 | 776 | 0.018476 | 302 | 0.0071905 | 884 | 0.021048 | 1.362 | A04 | MICL0.00945014/RON
Build-In Floor | Mini Canal | MICL.00945014/ROV | 9 | 450 | 14 | 14 | 776 | 776 | 776 | 0.018476 | 302 | 0.0071905 | 884 | 0.021048 | 1.362 | A04 | MICL0.00945014/ROV
Build-In Floor | Mini Canal | MICL.00945014/RSS | 9 | 450 | 14 | 14 | 768 | 768 | 768 | 0.018286 | 299 | 0.007119 | 875 | 0.020833 | 1.362 | A04 | MICL0.00945014/RSS
Build-In Floor | Mini Canal | MICL.00945014/SBL | 9 | 450 | 14 | 14 | 800 | 800 | 800 | 0.019048 | 311 | 0.0074048 | 911 | 0.02169 | 1.362 | A04 | MICL0.00945014/SBL
Build-In Floor | Mini Canal | MICL.00945014/SBR | 9 | 450 | 14 | 14 | 800 | 800 | 800 | 0.019048 | 311 | 0.0074048 | 911 | 0.02169 | 1.362 | A04 | MICL0.00945014/SBR
Build-In Floor | Mini Canal | MICL.00945014/SDB | 9 | 450 | 14 | 14 | 800 | 800 | 800 | 0.019048 | 311 | 0.0074048 | 911 | 0.02169 | 1.362 | A04 | MICL0.00945014/SDB
Build-In Floor | Mini Canal | MICL.00945014/SNA | 9 | 450 | 14 | 14 | 800 | 800 | 800 | 0.019048 | 311 | 0.0074048 | 911 | 0.02169 | 1.362 | A04 | MICL0.00945014/SNA
Build-In Floor | Mini Canal | MICL.00945014/SNC | 9 | 450 | 14 | 14 | 800 | 800 | 800 | 0.019048 | 311 | 0.0074048 | 911 | 0.02169 | 1.362 | A04 | MICL0.00945014/SNC
Build-In Floor | Mini Canal | MICL.00945018/ANA | 9 | 450 | 18 | 18 | 710 | 710 | 710 | 0.016905 | 276 | 0.0065714 | 809 | 0.019262 | 1.362 | A04 | MICL0.00945018/ANA
Build-In Floor | Mini Canal | MICL.00945018/DBL | 9 | 450 | 18 | 18 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.00945018/DBL
Build-In Floor | Mini Canal | MICL.00945018/DBN | 9 | 450 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.00945018/DBN
Build-In Floor | Mini Canal | MICL.00945018/DBR | 9 | 450 | 18 | 18 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.00945018/DBR
Build-In Floor | Mini Canal | MICL.00945018/DBV | 9 | 450 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.00945018/DBV
Build-In Floor | Mini Canal | MICL.00945018/DDB | 9 | 450 | 18 | 18 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.00945018/DDB
Build-In Floor | Mini Canal | MICL.00945018/DMN | 9 | 450 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.00945018/DMN
Build-In Floor | Mini Canal | MICL.00945018/DMV | 9 | 450 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.00945018/DMV
Build-In Floor | Mini Canal | MICL.00945018/DNA | 9 | 450 | 18 | 18 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.00945018/DNA
Build-In Floor | Mini Canal | MICL.00945018/DNC | 9 | 450 | 18 | 18 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.00945018/DNC
Build-In Floor | Mini Canal | MICL.00945018/DON | 9 | 450 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.00945018/DON
Build-In Floor | Mini Canal | MICL.00945018/DOV | 9 | 450 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.00945018/DOV
Build-In Floor | Mini Canal | MICL.00945018/RBL | 9 | 450 | 18 | 18 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.00945018/RBL
Build-In Floor | Mini Canal | MICL.00945018/RBN | 9 | 450 | 18 | 18 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.00945018/RBN
Build-In Floor | Mini Canal | MICL.00945018/RBR | 9 | 450 | 18 | 18 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.00945018/RBR
Build-In Floor | Mini Canal | MICL.00945018/RBV | 9 | 450 | 18 | 18 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.00945018/RBV
Build-In Floor | Mini Canal | MICL.00945018/RDB | 9 | 450 | 18 | 18 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.00945018/RDB
Build-In Floor | Mini Canal | MICL.00945018/RMN | 9 | 450 | 18 | 18 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.00945018/RMN
Build-In Floor | Mini Canal | MICL.00945018/RMV | 9 | 450 | 18 | 18 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.00945018/RMV
Build-In Floor | Mini Canal | MICL.00945018/RNA | 9 | 450 | 18 | 18 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.00945018/RNA
Build-In Floor | Mini Canal | MICL.00945018/RON | 9 | 450 | 18 | 18 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.00945018/RON
Build-In Floor | Mini Canal | MICL.00945018/ROV | 9 | 450 | 18 | 18 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.00945018/ROV
Build-In Floor | Mini Canal | MICL.00945018/RSS | 9 | 450 | 18 | 18 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.00945018/RSS
Build-In Floor | Mini Canal | MICL.00945018/SBL | 9 | 450 | 18 | 18 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.00945018/SBL
Build-In Floor | Mini Canal | MICL.00945018/SBR | 9 | 450 | 18 | 18 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.00945018/SBR
Build-In Floor | Mini Canal | MICL.00945018/SDB | 9 | 450 | 18 | 18 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.00945018/SDB
Build-In Floor | Mini Canal | MICL.00945018/SNA | 9 | 450 | 18 | 18 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.00945018/SNA
Build-In Floor | Mini Canal | MICL.00945018/SNC | 9 | 450 | 18 | 18 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.00945018/SNC
Build-In Floor | Mini Canal | MICL.00945026/ANA | 9 | 450 | 26 | 26 | 934 | 934 | 934 | 0.022238 | 363 | 0.0086429 | 1064 | 0.025333 | 1.362 | A04 | MICL0.00945026/ANA
Build-In Floor | Mini Canal | MICL.00945026/DBL | 9 | 450 | 26 | 26 | 1208 | 1208 | 1208 | 0.028762 | 470 | 0.01119 | 1376 | 0.032762 | 1.362 | A04 | MICL0.00945026/DBL
Build-In Floor | Mini Canal | MICL.00945026/DBN | 9 | 450 | 26 | 26 | 1158 | 1158 | 1158 | 0.027571 | 450 | 0.010714 | 1319 | 0.031405 | 1.362 | A04 | MICL0.00945026/DBN
Build-In Floor | Mini Canal | MICL.00945026/DBR | 9 | 450 | 26 | 26 | 1208 | 1208 | 1208 | 0.028762 | 470 | 0.01119 | 1376 | 0.032762 | 1.362 | A04 | MICL0.00945026/DBR
Build-In Floor | Mini Canal | MICL.00945026/DBV | 9 | 450 | 26 | 26 | 1158 | 1158 | 1158 | 0.027571 | 450 | 0.010714 | 1319 | 0.031405 | 1.362 | A04 | MICL0.00945026/DBV
Build-In Floor | Mini Canal | MICL.00945026/DDB | 9 | 450 | 26 | 26 | 1208 | 1208 | 1208 | 0.028762 | 470 | 0.01119 | 1376 | 0.032762 | 1.362 | A04 | MICL0.00945026/DDB
Build-In Floor | Mini Canal | MICL.00945026/DMN | 9 | 450 | 26 | 26 | 1158 | 1158 | 1158 | 0.027571 | 450 | 0.010714 | 1319 | 0.031405 | 1.362 | A04 | MICL0.00945026/DMN
Build-In Floor | Mini Canal | MICL.00945026/DMV | 9 | 450 | 26 | 26 | 1158 | 1158 | 1158 | 0.027571 | 450 | 0.010714 | 1319 | 0.031405 | 1.362 | A04 | MICL0.00945026/DMV
Build-In Floor | Mini Canal | MICL.00945026/DNA | 9 | 450 | 26 | 26 | 1208 | 1208 | 1208 | 0.028762 | 470 | 0.01119 | 1376 | 0.032762 | 1.362 | A04 | MICL0.00945026/DNA
Build-In Floor | Mini Canal | MICL.00945026/DNC | 9 | 450 | 26 | 26 | 1208 | 1208 | 1208 | 0.028762 | 470 | 0.01119 | 1376 | 0.032762 | 1.362 | A04 | MICL0.00945026/DNC
Build-In Floor | Mini Canal | MICL.00945026/DON | 9 | 450 | 26 | 26 | 1158 | 1158 | 1158 | 0.027571 | 450 | 0.010714 | 1319 | 0.031405 | 1.362 | A04 | MICL0.00945026/DON
Build-In Floor | Mini Canal | MICL.00945026/DOV | 9 | 450 | 26 | 26 | 1158 | 1158 | 1158 | 0.027571 | 450 | 0.010714 | 1319 | 0.031405 | 1.362 | A04 | MICL0.00945026/DOV
Build-In Floor | Mini Canal | MICL.00945026/PNC | 9 | 450 | 26 | 26 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.00945026/PNC
Build-In Floor | Mini Canal | MICL.00945026/RBL | 9 | 450 | 26 | 26 | 1245 | 1245 | 1245 | 0.029643 | 484 | 0.011524 | 1418 | 0.033762 | 1.362 | A04 | MICL0.00945026/RBL
Build-In Floor | Mini Canal | MICL.00945026/RBN | 9 | 450 | 26 | 26 | 1208 | 1208 | 1208 | 0.028762 | 470 | 0.01119 | 1376 | 0.032762 | 1.362 | A04 | MICL0.00945026/RBN
Build-In Floor | Mini Canal | MICL.00945026/RBR | 9 | 450 | 26 | 26 | 1245 | 1245 | 1245 | 0.029643 | 484 | 0.011524 | 1418 | 0.033762 | 1.362 | A04 | MICL0.00945026/RBR
Build-In Floor | Mini Canal | MICL.00945026/RBV | 9 | 450 | 26 | 26 | 1208 | 1208 | 1208 | 0.028762 | 470 | 0.01119 | 1376 | 0.032762 | 1.362 | A04 | MICL0.00945026/RBV
Build-In Floor | Mini Canal | MICL.00945026/RDB | 9 | 450 | 26 | 26 | 1245 | 1245 | 1245 | 0.029643 | 484 | 0.011524 | 1418 | 0.033762 | 1.362 | A04 | MICL0.00945026/RDB
Build-In Floor | Mini Canal | MICL.00945026/RMN | 9 | 450 | 26 | 26 | 1208 | 1208 | 1208 | 0.028762 | 470 | 0.01119 | 1376 | 0.032762 | 1.362 | A04 | MICL0.00945026/RMN
Build-In Floor | Mini Canal | MICL.00945026/RMV | 9 | 450 | 26 | 26 | 1208 | 1208 | 1208 | 0.028762 | 470 | 0.01119 | 1376 | 0.032762 | 1.362 | A04 | MICL0.00945026/RMV
Build-In Floor | Mini Canal | MICL.00945026/RNA | 9 | 450 | 26 | 26 | 1245 | 1245 | 1245 | 0.029643 | 484 | 0.011524 | 1418 | 0.033762 | 1.362 | A04 | MICL0.00945026/RNA
Build-In Floor | Mini Canal | MICL.00945026/RON | 9 | 450 | 26 | 26 | 1208 | 1208 | 1208 | 0.028762 | 470 | 0.01119 | 1376 | 0.032762 | 1.362 | A04 | MICL0.00945026/RON
Build-In Floor | Mini Canal | MICL.00945026/ROV | 9 | 450 | 26 | 26 | 1208 | 1208 | 1208 | 0.028762 | 470 | 0.01119 | 1376 | 0.032762 | 1.362 | A04 | MICL0.00945026/ROV
Build-In Floor | Mini Canal | MICL.00945026/RSS | 9 | 450 | 26 | 26 | 1195 | 1195 | 1195 | 0.028452 | 465 | 0.011071 | 1361 | 0.032405 | 1.362 | A04 | MICL0.00945026/RSS
Build-In Floor | Mini Canal | MICL.00945026/SBL | 9 | 450 | 26 | 26 | 1245 | 1245 | 1245 | 0.029643 | 484 | 0.011524 | 1418 | 0.033762 | 1.362 | A04 | MICL0.00945026/SBL
Build-In Floor | Mini Canal | MICL.00945026/SBR | 9 | 450 | 26 | 26 | 1245 | 1245 | 1245 | 0.029643 | 484 | 0.011524 | 1418 | 0.033762 | 1.362 | A04 | MICL0.00945026/SBR
Build-In Floor | Mini Canal | MICL.00945026/SDB | 9 | 450 | 26 | 26 | 1245 | 1245 | 1245 | 0.029643 | 484 | 0.011524 | 1418 | 0.033762 | 1.362 | A04 | MICL0.00945026/SDB
Build-In Floor | Mini Canal | MICL.00945026/SNA | 9 | 450 | 26 | 26 | 1245 | 1245 | 1245 | 0.029643 | 484 | 0.011524 | 1418 | 0.033762 | 1.362 | A04 | MICL0.00945026/SNA
Build-In Floor | Mini Canal | MICL.00945026/SNC | 9 | 450 | 26 | 26 | 1245 | 1245 | 1245 | 0.029643 | 484 | 0.011524 | 1418 | 0.033762 | 1.362 | A04 | MICL0.00945026/SNC
Build-In Floor | Mini Canal | MICL.00945034/ANA | 9 | 450 | 34 | 34 | 1211 | 1211 | 1211 | 0.028833 | 471 | 0.011214 | 1379 | 0.032833 | 1.362 | A04 | MICL0.00945034/ANA
Build-In Floor | Mini Canal | MICL.00945034/DBL | 9 | 450 | 34 | 34 | 1567 | 1567 | 1567 | 0.03731 | 610 | 0.014524 | 1785 | 0.0425 | 1.362 | A04 | MICL0.00945034/DBL
Build-In Floor | Mini Canal | MICL.00945034/DBN | 9 | 450 | 34 | 34 | 1502 | 1502 | 1502 | 0.035762 | 584 | 0.013905 | 1711 | 0.040738 | 1.362 | A04 | MICL0.00945034/DBN
Build-In Floor | Mini Canal | MICL.00945034/DBR | 9 | 450 | 34 | 34 | 1567 | 1567 | 1567 | 0.03731 | 610 | 0.014524 | 1785 | 0.0425 | 1.362 | A04 | MICL0.00945034/DBR
Build-In Floor | Mini Canal | MICL.00945034/DBV | 9 | 450 | 34 | 34 | 1502 | 1502 | 1502 | 0.035762 | 584 | 0.013905 | 1711 | 0.040738 | 1.362 | A04 | MICL0.00945034/DBV
Build-In Floor | Mini Canal | MICL.00945034/DDB | 9 | 450 | 34 | 34 | 1567 | 1567 | 1567 | 0.03731 | 610 | 0.014524 | 1785 | 0.0425 | 1.362 | A04 | MICL0.00945034/DDB
Build-In Floor | Mini Canal | MICL.00945034/DMN | 9 | 450 | 34 | 34 | 1502 | 1502 | 1502 | 0.035762 | 584 | 0.013905 | 1711 | 0.040738 | 1.362 | A04 | MICL0.00945034/DMN
Build-In Floor | Mini Canal | MICL.00945034/DMV | 9 | 450 | 34 | 34 | 1502 | 1502 | 1502 | 0.035762 | 584 | 0.013905 | 1711 | 0.040738 | 1.362 | A04 | MICL0.00945034/DMV
Build-In Floor | Mini Canal | MICL.00945034/DNA | 9 | 450 | 34 | 34 | 1567 | 1567 | 1567 | 0.03731 | 610 | 0.014524 | 1785 | 0.0425 | 1.362 | A04 | MICL0.00945034/DNA
Build-In Floor | Mini Canal | MICL.00945034/DNC | 9 | 450 | 34 | 34 | 1567 | 1567 | 1567 | 0.03731 | 610 | 0.014524 | 1785 | 0.0425 | 1.362 | A04 | MICL0.00945034/DNC
Build-In Floor | Mini Canal | MICL.00945034/DON | 9 | 450 | 34 | 34 | 1502 | 1502 | 1502 | 0.035762 | 584 | 0.013905 | 1711 | 0.040738 | 1.362 | A04 | MICL0.00945034/DON
Build-In Floor | Mini Canal | MICL.00945034/DOV | 9 | 450 | 34 | 34 | 1502 | 1502 | 1502 | 0.035762 | 584 | 0.013905 | 1711 | 0.040738 | 1.362 | A04 | MICL0.00945034/DOV
Build-In Floor | Mini Canal | MICL.00945034/PNC | 9 | 450 | 34 | 34 | 1373 | 1373 | 1373 | 0.03269 | 534 | 0.012714 | 1564 | 0.037238 | 1.362 | A04 | MICL0.00945034/PNC
Build-In Floor | Mini Canal | MICL.00945034/RBL | 9 | 450 | 34 | 34 | 1615 | 1615 | 1615 | 0.038452 | 628 | 0.014952 | 1839 | 0.043786 | 1.362 | A04 | MICL0.00945034/RBL
Build-In Floor | Mini Canal | MICL.00945034/RBN | 9 | 450 | 34 | 34 | 1567 | 1567 | 1567 | 0.03731 | 610 | 0.014524 | 1785 | 0.0425 | 1.362 | A04 | MICL0.00945034/RBN
Build-In Floor | Mini Canal | MICL.00945034/RBR | 9 | 450 | 34 | 34 | 1615 | 1615 | 1615 | 0.038452 | 628 | 0.014952 | 1839 | 0.043786 | 1.362 | A04 | MICL0.00945034/RBR
Build-In Floor | Mini Canal | MICL.00945034/RBV | 9 | 450 | 34 | 34 | 1567 | 1567 | 1567 | 0.03731 | 610 | 0.014524 | 1785 | 0.0425 | 1.362 | A04 | MICL0.00945034/RBV
Build-In Floor | Mini Canal | MICL.00945034/RDB | 9 | 450 | 34 | 34 | 1615 | 1615 | 1615 | 0.038452 | 628 | 0.014952 | 1839 | 0.043786 | 1.362 | A04 | MICL0.00945034/RDB
Build-In Floor | Mini Canal | MICL.00945034/RMN | 9 | 450 | 34 | 34 | 1567 | 1567 | 1567 | 0.03731 | 610 | 0.014524 | 1785 | 0.0425 | 1.362 | A04 | MICL0.00945034/RMN
Build-In Floor | Mini Canal | MICL.00945034/RMV | 9 | 450 | 34 | 34 | 1567 | 1567 | 1567 | 0.03731 | 610 | 0.014524 | 1785 | 0.0425 | 1.362 | A04 | MICL0.00945034/RMV
Build-In Floor | Mini Canal | MICL.00945034/RNA | 9 | 450 | 34 | 34 | 1615 | 1615 | 1615 | 0.038452 | 628 | 0.014952 | 1839 | 0.043786 | 1.362 | A04 | MICL0.00945034/RNA
Build-In Floor | Mini Canal | MICL.00945034/RON | 9 | 450 | 34 | 34 | 1567 | 1567 | 1567 | 0.03731 | 610 | 0.014524 | 1785 | 0.0425 | 1.362 | A04 | MICL0.00945034/RON
Build-In Floor | Mini Canal | MICL.00945034/ROV | 9 | 450 | 34 | 34 | 1567 | 1567 | 1567 | 0.03731 | 610 | 0.014524 | 1785 | 0.0425 | 1.362 | A04 | MICL0.00945034/ROV
Build-In Floor | Mini Canal | MICL.00945034/RSS | 9 | 450 | 34 | 34 | 1550 | 1550 | 1550 | 0.036905 | 603 | 0.014357 | 1765 | 0.042024 | 1.362 | A04 | MICL0.00945034/RSS
Build-In Floor | Mini Canal | MICL.00945034/SBL | 9 | 450 | 34 | 34 | 1615 | 1615 | 1615 | 0.038452 | 628 | 0.014952 | 1839 | 0.043786 | 1.362 | A04 | MICL0.00945034/SBL
Build-In Floor | Mini Canal | MICL.00945034/SBR | 9 | 450 | 34 | 34 | 1615 | 1615 | 1615 | 0.038452 | 628 | 0.014952 | 1839 | 0.043786 | 1.362 | A04 | MICL0.00945034/SBR
Build-In Floor | Mini Canal | MICL.00945034/SDB | 9 | 450 | 34 | 34 | 1615 | 1615 | 1615 | 0.038452 | 628 | 0.014952 | 1839 | 0.043786 | 1.362 | A04 | MICL0.00945034/SDB
Build-In Floor | Mini Canal | MICL.00945034/SNA | 9 | 450 | 34 | 34 | 1615 | 1615 | 1615 | 0.038452 | 628 | 0.014952 | 1839 | 0.043786 | 1.362 | A04 | MICL0.00945034/SNA
Build-In Floor | Mini Canal | MICL.00945034/SNC | 9 | 450 | 34 | 34 | 1615 | 1615 | 1615 | 0.038452 | 628 | 0.014952 | 1839 | 0.043786 | 1.362 | A04 | MICL0.00945034/SNC
Build-In Floor | Mini Canal | MICL.00945042/ANA | 9 | 450 | 42 | 42 | 1749 | 1749 | 1749 | 0.041643 | 680 | 0.01619 | 1992 | 0.047429 | 1.362 | A04 | MICL0.00945042/ANA
Build-In Floor | Mini Canal | MICL.00945042/DBL | 9 | 450 | 42 | 42 | 2262 | 2262 | 2262 | 0.053857 | 880 | 0.020952 | 2576 | 0.061333 | 1.362 | A04 | MICL0.00945042/DBL
Build-In Floor | Mini Canal | MICL.00945042/DBN | 9 | 450 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.00945042/DBN
Build-In Floor | Mini Canal | MICL.00945042/DBR | 9 | 450 | 42 | 42 | 2262 | 2262 | 2262 | 0.053857 | 880 | 0.020952 | 2576 | 0.061333 | 1.362 | A04 | MICL0.00945042/DBR
Build-In Floor | Mini Canal | MICL.00945042/DBV | 9 | 450 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.00945042/DBV
Build-In Floor | Mini Canal | MICL.00945042/DDB | 9 | 450 | 42 | 42 | 2262 | 2262 | 2262 | 0.053857 | 880 | 0.020952 | 2576 | 0.061333 | 1.362 | A04 | MICL0.00945042/DDB
Build-In Floor | Mini Canal | MICL.00945042/DMN | 9 | 450 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.00945042/DMN
Build-In Floor | Mini Canal | MICL.00945042/DMV | 9 | 450 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.00945042/DMV
Build-In Floor | Mini Canal | MICL.00945042/DNA | 9 | 450 | 42 | 42 | 2262 | 2262 | 2262 | 0.053857 | 880 | 0.020952 | 2576 | 0.061333 | 1.362 | A04 | MICL0.00945042/DNA
Build-In Floor | Mini Canal | MICL.00945042/DNC | 9 | 450 | 42 | 42 | 2262 | 2262 | 2262 | 0.053857 | 880 | 0.020952 | 2576 | 0.061333 | 1.362 | A04 | MICL0.00945042/DNC
Build-In Floor | Mini Canal | MICL.00945042/DON | 9 | 450 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.00945042/DON
Build-In Floor | Mini Canal | MICL.00945042/DOV | 9 | 450 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.00945042/DOV
Build-In Floor | Mini Canal | MICL.00945042/PNC | 9 | 450 | 42 | 42 | 1982 | 1982 | 1982 | 0.04719 | 771 | 0.018357 | 2257 | 0.053738 | 1.362 | A04 | MICL0.00945042/PNC
Build-In Floor | Mini Canal | MICL.00945042/RBL | 9 | 450 | 42 | 42 | 2332 | 2332 | 2332 | 0.055524 | 907 | 0.021595 | 2656 | 0.063238 | 1.362 | A04 | MICL0.00945042/RBL
Build-In Floor | Mini Canal | MICL.00945042/RBN | 9 | 450 | 42 | 42 | 2262 | 2262 | 2262 | 0.053857 | 880 | 0.020952 | 2576 | 0.061333 | 1.362 | A04 | MICL0.00945042/RBN
Build-In Floor | Mini Canal | MICL.00945042/RBR | 9 | 450 | 42 | 42 | 2332 | 2332 | 2332 | 0.055524 | 907 | 0.021595 | 2656 | 0.063238 | 1.362 | A04 | MICL0.00945042/RBR
Build-In Floor | Mini Canal | MICL.00945042/RBV | 9 | 450 | 42 | 42 | 2262 | 2262 | 2262 | 0.053857 | 880 | 0.020952 | 2576 | 0.061333 | 1.362 | A04 | MICL0.00945042/RBV
Build-In Floor | Mini Canal | MICL.00945042/RDB | 9 | 450 | 42 | 42 | 2332 | 2332 | 2332 | 0.055524 | 907 | 0.021595 | 2656 | 0.063238 | 1.362 | A04 | MICL0.00945042/RDB
Build-In Floor | Mini Canal | MICL.00945042/RMN | 9 | 450 | 42 | 42 | 2262 | 2262 | 2262 | 0.053857 | 880 | 0.020952 | 2576 | 0.061333 | 1.362 | A04 | MICL0.00945042/RMN
Build-In Floor | Mini Canal | MICL.00945042/RMV | 9 | 450 | 42 | 42 | 2262 | 2262 | 2262 | 0.053857 | 880 | 0.020952 | 2576 | 0.061333 | 1.362 | A04 | MICL0.00945042/RMV
Build-In Floor | Mini Canal | MICL.00945042/RNA | 9 | 450 | 42 | 42 | 2332 | 2332 | 2332 | 0.055524 | 907 | 0.021595 | 2656 | 0.063238 | 1.362 | A04 | MICL0.00945042/RNA
Build-In Floor | Mini Canal | MICL.00945042/RON | 9 | 450 | 42 | 42 | 2262 | 2262 | 2262 | 0.053857 | 880 | 0.020952 | 2576 | 0.061333 | 1.362 | A04 | MICL0.00945042/RON
Build-In Floor | Mini Canal | MICL.00945042/ROV | 9 | 450 | 42 | 42 | 2262 | 2262 | 2262 | 0.053857 | 880 | 0.020952 | 2576 | 0.061333 | 1.362 | A04 | MICL0.00945042/ROV
Build-In Floor | Mini Canal | MICL.00945042/RSS | 9 | 450 | 42 | 42 | 2239 | 2239 | 2239 | 0.05331 | 871 | 0.020738 | 2550 | 0.060714 | 1.362 | A04 | MICL0.00945042/RSS
Build-In Floor | Mini Canal | MICL.00945042/SBL | 9 | 450 | 42 | 42 | 2332 | 2332 | 2332 | 0.055524 | 907 | 0.021595 | 2656 | 0.063238 | 1.362 | A04 | MICL0.00945042/SBL
Build-In Floor | Mini Canal | MICL.00945042/SBR | 9 | 450 | 42 | 42 | 2332 | 2332 | 2332 | 0.055524 | 907 | 0.021595 | 2656 | 0.063238 | 1.362 | A04 | MICL0.00945042/SBR
Build-In Floor | Mini Canal | MICL.00945042/SDB | 9 | 450 | 42 | 42 | 2332 | 2332 | 2332 | 0.055524 | 907 | 0.021595 | 2656 | 0.063238 | 1.362 | A04 | MICL0.00945042/SDB
Build-In Floor | Mini Canal | MICL.00945042/SNA | 9 | 450 | 42 | 42 | 2332 | 2332 | 2332 | 0.055524 | 907 | 0.021595 | 2656 | 0.063238 | 1.362 | A04 | MICL0.00945042/SNA
Build-In Floor | Mini Canal | MICL.00945042/SNC | 9 | 450 | 42 | 42 | 2332 | 2332 | 2332 | 0.055524 | 907 | 0.021595 | 2656 | 0.063238 | 1.362 | A04 | MICL0.00945042/SNC
Build-In Floor | Mini Canal | MICL.00947014/ANA | 9 | 470 | 14 | 14 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.00947014/ANA
Build-In Floor | Mini Canal | MICL.00947014/DBL | 9 | 470 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.00947014/DBL
Build-In Floor | Mini Canal | MICL.00947014/DBN | 9 | 470 | 14 | 14 | 779 | 779 | 779 | 0.018548 | 303 | 0.0072143 | 887 | 0.021119 | 1.362 | A04 | MICL0.00947014/DBN
Build-In Floor | Mini Canal | MICL.00947014/DBR | 9 | 470 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.00947014/DBR
Build-In Floor | Mini Canal | MICL.00947014/DBV | 9 | 470 | 14 | 14 | 779 | 779 | 779 | 0.018548 | 303 | 0.0072143 | 887 | 0.021119 | 1.362 | A04 | MICL0.00947014/DBV
Build-In Floor | Mini Canal | MICL.00947014/DDB | 9 | 470 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.00947014/DDB
Build-In Floor | Mini Canal | MICL.00947014/DMN | 9 | 470 | 14 | 14 | 779 | 779 | 779 | 0.018548 | 303 | 0.0072143 | 887 | 0.021119 | 1.362 | A04 | MICL0.00947014/DMN
Build-In Floor | Mini Canal | MICL.00947014/DMV | 9 | 470 | 14 | 14 | 779 | 779 | 779 | 0.018548 | 303 | 0.0072143 | 887 | 0.021119 | 1.362 | A04 | MICL0.00947014/DMV
Build-In Floor | Mini Canal | MICL.00947014/DNA | 9 | 470 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.00947014/DNA
Build-In Floor | Mini Canal | MICL.00947014/DNC | 9 | 470 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.00947014/DNC
Build-In Floor | Mini Canal | MICL.00947014/DON | 9 | 470 | 14 | 14 | 779 | 779 | 779 | 0.018548 | 303 | 0.0072143 | 887 | 0.021119 | 1.362 | A04 | MICL0.00947014/DON
Build-In Floor | Mini Canal | MICL.00947014/DOV | 9 | 470 | 14 | 14 | 779 | 779 | 779 | 0.018548 | 303 | 0.0072143 | 887 | 0.021119 | 1.362 | A04 | MICL0.00947014/DOV
Build-In Floor | Mini Canal | MICL.00947014/RBL | 9 | 470 | 14 | 14 | 838 | 838 | 838 | 0.019952 | 326 | 0.0077619 | 954 | 0.022714 | 1.362 | A04 | MICL0.00947014/RBL
Build-In Floor | Mini Canal | MICL.00947014/RBN | 9 | 470 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.00947014/RBN
Build-In Floor | Mini Canal | MICL.00947014/RBR | 9 | 470 | 14 | 14 | 838 | 838 | 838 | 0.019952 | 326 | 0.0077619 | 954 | 0.022714 | 1.362 | A04 | MICL0.00947014/RBR
Build-In Floor | Mini Canal | MICL.00947014/RBV | 9 | 470 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.00947014/RBV
Build-In Floor | Mini Canal | MICL.00947014/RDB | 9 | 470 | 14 | 14 | 838 | 838 | 838 | 0.019952 | 326 | 0.0077619 | 954 | 0.022714 | 1.362 | A04 | MICL0.00947014/RDB
Build-In Floor | Mini Canal | MICL.00947014/RMN | 9 | 470 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.00947014/RMN
Build-In Floor | Mini Canal | MICL.00947014/RMV | 9 | 470 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.00947014/RMV
Build-In Floor | Mini Canal | MICL.00947014/RNA | 9 | 470 | 14 | 14 | 838 | 838 | 838 | 0.019952 | 326 | 0.0077619 | 954 | 0.022714 | 1.362 | A04 | MICL0.00947014/RNA
Build-In Floor | Mini Canal | MICL.00947014/RON | 9 | 470 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.00947014/RON
Build-In Floor | Mini Canal | MICL.00947014/ROV | 9 | 470 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.00947014/ROV
Build-In Floor | Mini Canal | MICL.00947014/RSS | 9 | 470 | 14 | 14 | 804 | 804 | 804 | 0.019143 | 313 | 0.0074524 | 916 | 0.02181 | 1.362 | A04 | MICL0.00947014/RSS
Build-In Floor | Mini Canal | MICL.00947014/SBL | 9 | 470 | 14 | 14 | 838 | 838 | 838 | 0.019952 | 326 | 0.0077619 | 954 | 0.022714 | 1.362 | A04 | MICL0.00947014/SBL
Build-In Floor | Mini Canal | MICL.00947014/SBR | 9 | 470 | 14 | 14 | 838 | 838 | 838 | 0.019952 | 326 | 0.0077619 | 954 | 0.022714 | 1.362 | A04 | MICL0.00947014/SBR
Build-In Floor | Mini Canal | MICL.00947014/SDB | 9 | 470 | 14 | 14 | 838 | 838 | 838 | 0.019952 | 326 | 0.0077619 | 954 | 0.022714 | 1.362 | A04 | MICL0.00947014/SDB
Build-In Floor | Mini Canal | MICL.00947014/SNA | 9 | 470 | 14 | 14 | 838 | 838 | 838 | 0.019952 | 326 | 0.0077619 | 954 | 0.022714 | 1.362 | A04 | MICL0.00947014/SNA
Build-In Floor | Mini Canal | MICL.00947014/SNC | 9 | 470 | 14 | 14 | 838 | 838 | 838 | 0.019952 | 326 | 0.0077619 | 954 | 0.022714 | 1.362 | A04 | MICL0.00947014/SNC
Build-In Floor | Mini Canal | MICL.00947018/ANA | 9 | 470 | 18 | 18 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.00947018/ANA
Build-In Floor | Mini Canal | MICL.00947018/DBL | 9 | 470 | 18 | 18 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.00947018/DBL
Build-In Floor | Mini Canal | MICL.00947018/DBN | 9 | 470 | 18 | 18 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00947018/DBN
Build-In Floor | Mini Canal | MICL.00947018/DBR | 9 | 470 | 18 | 18 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.00947018/DBR
Build-In Floor | Mini Canal | MICL.00947018/DBV | 9 | 470 | 18 | 18 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00947018/DBV
Build-In Floor | Mini Canal | MICL.00947018/DDB | 9 | 470 | 18 | 18 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.00947018/DDB
Build-In Floor | Mini Canal | MICL.00947018/DMN | 9 | 470 | 18 | 18 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00947018/DMN
Build-In Floor | Mini Canal | MICL.00947018/DMV | 9 | 470 | 18 | 18 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00947018/DMV
Build-In Floor | Mini Canal | MICL.00947018/DNA | 9 | 470 | 18 | 18 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.00947018/DNA
Build-In Floor | Mini Canal | MICL.00947018/DNC | 9 | 470 | 18 | 18 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.00947018/DNC
Build-In Floor | Mini Canal | MICL.00947018/DON | 9 | 470 | 18 | 18 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00947018/DON
Build-In Floor | Mini Canal | MICL.00947018/DOV | 9 | 470 | 18 | 18 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.00947018/DOV
Build-In Floor | Mini Canal | MICL.00947018/RBL | 9 | 470 | 18 | 18 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00947018/RBL
Build-In Floor | Mini Canal | MICL.00947018/RBN | 9 | 470 | 18 | 18 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.00947018/RBN
Build-In Floor | Mini Canal | MICL.00947018/RBR | 9 | 470 | 18 | 18 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00947018/RBR
Build-In Floor | Mini Canal | MICL.00947018/RBV | 9 | 470 | 18 | 18 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.00947018/RBV
Build-In Floor | Mini Canal | MICL.00947018/RDB | 9 | 470 | 18 | 18 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00947018/RDB
Build-In Floor | Mini Canal | MICL.00947018/RMN | 9 | 470 | 18 | 18 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.00947018/RMN
Build-In Floor | Mini Canal | MICL.00947018/RMV | 9 | 470 | 18 | 18 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.00947018/RMV
Build-In Floor | Mini Canal | MICL.00947018/RNA | 9 | 470 | 18 | 18 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00947018/RNA
Build-In Floor | Mini Canal | MICL.00947018/RON | 9 | 470 | 18 | 18 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.00947018/RON
Build-In Floor | Mini Canal | MICL.00947018/ROV | 9 | 470 | 18 | 18 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.00947018/ROV
Build-In Floor | Mini Canal | MICL.00947018/RSS | 9 | 470 | 18 | 18 | 952 | 952 | 952 | 0.022667 | 370 | 0.0088095 | 1084 | 0.02581 | 1.362 | A04 | MICL0.00947018/RSS
Build-In Floor | Mini Canal | MICL.00947018/SBL | 9 | 470 | 18 | 18 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00947018/SBL
Build-In Floor | Mini Canal | MICL.00947018/SBR | 9 | 470 | 18 | 18 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00947018/SBR
Build-In Floor | Mini Canal | MICL.00947018/SDB | 9 | 470 | 18 | 18 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00947018/SDB
Build-In Floor | Mini Canal | MICL.00947018/SNA | 9 | 470 | 18 | 18 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00947018/SNA
Build-In Floor | Mini Canal | MICL.00947018/SNC | 9 | 470 | 18 | 18 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.00947018/SNC
Build-In Floor | Mini Canal | MICL.00947026/ANA | 9 | 470 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.00947026/ANA
Build-In Floor | Mini Canal | MICL.00947026/DBL | 9 | 470 | 26 | 26 | 1265 | 1265 | 1265 | 0.030119 | 492 | 0.011714 | 1441 | 0.03431 | 1.362 | A04 | MICL0.00947026/DBL
Build-In Floor | Mini Canal | MICL.00947026/DBN | 9 | 470 | 26 | 26 | 1213 | 1213 | 1213 | 0.028881 | 472 | 0.011238 | 1382 | 0.032905 | 1.362 | A04 | MICL0.00947026/DBN
Build-In Floor | Mini Canal | MICL.00947026/DBR | 9 | 470 | 26 | 26 | 1265 | 1265 | 1265 | 0.030119 | 492 | 0.011714 | 1441 | 0.03431 | 1.362 | A04 | MICL0.00947026/DBR
Build-In Floor | Mini Canal | MICL.00947026/DBV | 9 | 470 | 26 | 26 | 1213 | 1213 | 1213 | 0.028881 | 472 | 0.011238 | 1382 | 0.032905 | 1.362 | A04 | MICL0.00947026/DBV
Build-In Floor | Mini Canal | MICL.00947026/DDB | 9 | 470 | 26 | 26 | 1265 | 1265 | 1265 | 0.030119 | 492 | 0.011714 | 1441 | 0.03431 | 1.362 | A04 | MICL0.00947026/DDB
Build-In Floor | Mini Canal | MICL.00947026/DMN | 9 | 470 | 26 | 26 | 1213 | 1213 | 1213 | 0.028881 | 472 | 0.011238 | 1382 | 0.032905 | 1.362 | A04 | MICL0.00947026/DMN
Build-In Floor | Mini Canal | MICL.00947026/DMV | 9 | 470 | 26 | 26 | 1213 | 1213 | 1213 | 0.028881 | 472 | 0.011238 | 1382 | 0.032905 | 1.362 | A04 | MICL0.00947026/DMV
Build-In Floor | Mini Canal | MICL.00947026/DNA | 9 | 470 | 26 | 26 | 1265 | 1265 | 1265 | 0.030119 | 492 | 0.011714 | 1441 | 0.03431 | 1.362 | A04 | MICL0.00947026/DNA
Build-In Floor | Mini Canal | MICL.00947026/DNC | 9 | 470 | 26 | 26 | 1265 | 1265 | 1265 | 0.030119 | 492 | 0.011714 | 1441 | 0.03431 | 1.362 | A04 | MICL0.00947026/DNC
Build-In Floor | Mini Canal | MICL.00947026/DON | 9 | 470 | 26 | 26 | 1213 | 1213 | 1213 | 0.028881 | 472 | 0.011238 | 1382 | 0.032905 | 1.362 | A04 | MICL0.00947026/DON
Build-In Floor | Mini Canal | MICL.00947026/DOV | 9 | 470 | 26 | 26 | 1213 | 1213 | 1213 | 0.028881 | 472 | 0.011238 | 1382 | 0.032905 | 1.362 | A04 | MICL0.00947026/DOV
Build-In Floor | Mini Canal | MICL.00947026/PNC | 9 | 470 | 26 | 26 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.00947026/PNC
Build-In Floor | Mini Canal | MICL.00947026/RBL | 9 | 470 | 26 | 26 | 1304 | 1304 | 1304 | 0.031048 | 507 | 0.012071 | 1485 | 0.035357 | 1.362 | A04 | MICL0.00947026/RBL
Build-In Floor | Mini Canal | MICL.00947026/RBN | 9 | 470 | 26 | 26 | 1265 | 1265 | 1265 | 0.030119 | 492 | 0.011714 | 1441 | 0.03431 | 1.362 | A04 | MICL0.00947026/RBN
Build-In Floor | Mini Canal | MICL.00947026/RBR | 9 | 470 | 26 | 26 | 1304 | 1304 | 1304 | 0.031048 | 507 | 0.012071 | 1485 | 0.035357 | 1.362 | A04 | MICL0.00947026/RBR
Build-In Floor | Mini Canal | MICL.00947026/RBV | 9 | 470 | 26 | 26 | 1265 | 1265 | 1265 | 0.030119 | 492 | 0.011714 | 1441 | 0.03431 | 1.362 | A04 | MICL0.00947026/RBV
Build-In Floor | Mini Canal | MICL.00947026/RDB | 9 | 470 | 26 | 26 | 1304 | 1304 | 1304 | 0.031048 | 507 | 0.012071 | 1485 | 0.035357 | 1.362 | A04 | MICL0.00947026/RDB
Build-In Floor | Mini Canal | MICL.00947026/RMN | 9 | 470 | 26 | 26 | 1265 | 1265 | 1265 | 0.030119 | 492 | 0.011714 | 1441 | 0.03431 | 1.362 | A04 | MICL0.00947026/RMN
Build-In Floor | Mini Canal | MICL.00947026/RMV | 9 | 470 | 26 | 26 | 1265 | 1265 | 1265 | 0.030119 | 492 | 0.011714 | 1441 | 0.03431 | 1.362 | A04 | MICL0.00947026/RMV
Build-In Floor | Mini Canal | MICL.00947026/RNA | 9 | 470 | 26 | 26 | 1304 | 1304 | 1304 | 0.031048 | 507 | 0.012071 | 1485 | 0.035357 | 1.362 | A04 | MICL0.00947026/RNA
Build-In Floor | Mini Canal | MICL.00947026/RON | 9 | 470 | 26 | 26 | 1265 | 1265 | 1265 | 0.030119 | 492 | 0.011714 | 1441 | 0.03431 | 1.362 | A04 | MICL0.00947026/RON
Build-In Floor | Mini Canal | MICL.00947026/ROV | 9 | 470 | 26 | 26 | 1265 | 1265 | 1265 | 0.030119 | 492 | 0.011714 | 1441 | 0.03431 | 1.362 | A04 | MICL0.00947026/ROV
Build-In Floor | Mini Canal | MICL.00947026/RSS | 9 | 470 | 26 | 26 | 1252 | 1252 | 1252 | 0.02981 | 487 | 0.011595 | 1426 | 0.033952 | 1.362 | A04 | MICL0.00947026/RSS
Build-In Floor | Mini Canal | MICL.00947026/SBL | 9 | 470 | 26 | 26 | 1304 | 1304 | 1304 | 0.031048 | 507 | 0.012071 | 1485 | 0.035357 | 1.362 | A04 | MICL0.00947026/SBL
Build-In Floor | Mini Canal | MICL.00947026/SBR | 9 | 470 | 26 | 26 | 1304 | 1304 | 1304 | 0.031048 | 507 | 0.012071 | 1485 | 0.035357 | 1.362 | A04 | MICL0.00947026/SBR
Build-In Floor | Mini Canal | MICL.00947026/SDB | 9 | 470 | 26 | 26 | 1304 | 1304 | 1304 | 0.031048 | 507 | 0.012071 | 1485 | 0.035357 | 1.362 | A04 | MICL0.00947026/SDB
Build-In Floor | Mini Canal | MICL.00947026/SNA | 9 | 470 | 26 | 26 | 1304 | 1304 | 1304 | 0.031048 | 507 | 0.012071 | 1485 | 0.035357 | 1.362 | A04 | MICL0.00947026/SNA
Build-In Floor | Mini Canal | MICL.00947026/SNC | 9 | 470 | 26 | 26 | 1304 | 1304 | 1304 | 0.031048 | 507 | 0.012071 | 1485 | 0.035357 | 1.362 | A04 | MICL0.00947026/SNC
Build-In Floor | Mini Canal | MICL.00947034/ANA | 9 | 470 | 34 | 34 | 1269 | 1269 | 1269 | 0.030214 | 494 | 0.011762 | 1445 | 0.034405 | 1.362 | A04 | MICL0.00947034/ANA
Build-In Floor | Mini Canal | MICL.00947034/DBL | 9 | 470 | 34 | 34 | 1641 | 1641 | 1641 | 0.039071 | 638 | 0.01519 | 1869 | 0.0445 | 1.362 | A04 | MICL0.00947034/DBL
Build-In Floor | Mini Canal | MICL.00947034/DBN | 9 | 470 | 34 | 34 | 1574 | 1574 | 1574 | 0.037476 | 612 | 0.014571 | 1793 | 0.04269 | 1.362 | A04 | MICL0.00947034/DBN
Build-In Floor | Mini Canal | MICL.00947034/DBR | 9 | 470 | 34 | 34 | 1641 | 1641 | 1641 | 0.039071 | 638 | 0.01519 | 1869 | 0.0445 | 1.362 | A04 | MICL0.00947034/DBR
Build-In Floor | Mini Canal | MICL.00947034/DBV | 9 | 470 | 34 | 34 | 1574 | 1574 | 1574 | 0.037476 | 612 | 0.014571 | 1793 | 0.04269 | 1.362 | A04 | MICL0.00947034/DBV
Build-In Floor | Mini Canal | MICL.00947034/DDB | 9 | 470 | 34 | 34 | 1641 | 1641 | 1641 | 0.039071 | 638 | 0.01519 | 1869 | 0.0445 | 1.362 | A04 | MICL0.00947034/DDB
Build-In Floor | Mini Canal | MICL.00947034/DMN | 9 | 470 | 34 | 34 | 1574 | 1574 | 1574 | 0.037476 | 612 | 0.014571 | 1793 | 0.04269 | 1.362 | A04 | MICL0.00947034/DMN
Build-In Floor | Mini Canal | MICL.00947034/DMV | 9 | 470 | 34 | 34 | 1574 | 1574 | 1574 | 0.037476 | 612 | 0.014571 | 1793 | 0.04269 | 1.362 | A04 | MICL0.00947034/DMV
Build-In Floor | Mini Canal | MICL.00947034/DNA | 9 | 470 | 34 | 34 | 1641 | 1641 | 1641 | 0.039071 | 638 | 0.01519 | 1869 | 0.0445 | 1.362 | A04 | MICL0.00947034/DNA
Build-In Floor | Mini Canal | MICL.00947034/DNC | 9 | 470 | 34 | 34 | 1641 | 1641 | 1641 | 0.039071 | 638 | 0.01519 | 1869 | 0.0445 | 1.362 | A04 | MICL0.00947034/DNC
Build-In Floor | Mini Canal | MICL.00947034/DON | 9 | 470 | 34 | 34 | 1574 | 1574 | 1574 | 0.037476 | 612 | 0.014571 | 1793 | 0.04269 | 1.362 | A04 | MICL0.00947034/DON
Build-In Floor | Mini Canal | MICL.00947034/DOV | 9 | 470 | 34 | 34 | 1574 | 1574 | 1574 | 0.037476 | 612 | 0.014571 | 1793 | 0.04269 | 1.362 | A04 | MICL0.00947034/DOV
Build-In Floor | Mini Canal | MICL.00947034/PNC | 9 | 470 | 34 | 34 | 1438 | 1438 | 1438 | 0.034238 | 559 | 0.01331 | 1638 | 0.039 | 1.362 | A04 | MICL0.00947034/PNC
Build-In Floor | Mini Canal | MICL.00947034/RBL | 9 | 470 | 34 | 34 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.00947034/RBL
Build-In Floor | Mini Canal | MICL.00947034/RBN | 9 | 470 | 34 | 34 | 1641 | 1641 | 1641 | 0.039071 | 638 | 0.01519 | 1869 | 0.0445 | 1.362 | A04 | MICL0.00947034/RBN
Build-In Floor | Mini Canal | MICL.00947034/RBR | 9 | 470 | 34 | 34 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.00947034/RBR
Build-In Floor | Mini Canal | MICL.00947034/RBV | 9 | 470 | 34 | 34 | 1641 | 1641 | 1641 | 0.039071 | 638 | 0.01519 | 1869 | 0.0445 | 1.362 | A04 | MICL0.00947034/RBV
Build-In Floor | Mini Canal | MICL.00947034/RDB | 9 | 470 | 34 | 34 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.00947034/RDB
Build-In Floor | Mini Canal | MICL.00947034/RMN | 9 | 470 | 34 | 34 | 1641 | 1641 | 1641 | 0.039071 | 638 | 0.01519 | 1869 | 0.0445 | 1.362 | A04 | MICL0.00947034/RMN
Build-In Floor | Mini Canal | MICL.00947034/RMV | 9 | 470 | 34 | 34 | 1641 | 1641 | 1641 | 0.039071 | 638 | 0.01519 | 1869 | 0.0445 | 1.362 | A04 | MICL0.00947034/RMV
Build-In Floor | Mini Canal | MICL.00947034/RNA | 9 | 470 | 34 | 34 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.00947034/RNA
Build-In Floor | Mini Canal | MICL.00947034/RON | 9 | 470 | 34 | 34 | 1641 | 1641 | 1641 | 0.039071 | 638 | 0.01519 | 1869 | 0.0445 | 1.362 | A04 | MICL0.00947034/RON
Build-In Floor | Mini Canal | MICL.00947034/ROV | 9 | 470 | 34 | 34 | 1641 | 1641 | 1641 | 0.039071 | 638 | 0.01519 | 1869 | 0.0445 | 1.362 | A04 | MICL0.00947034/ROV
Build-In Floor | Mini Canal | MICL.00947034/RSS | 9 | 470 | 34 | 34 | 1624 | 1624 | 1624 | 0.038667 | 632 | 0.015048 | 1850 | 0.044048 | 1.362 | A04 | MICL0.00947034/RSS
Build-In Floor | Mini Canal | MICL.00947034/SBL | 9 | 470 | 34 | 34 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.00947034/SBL
Build-In Floor | Mini Canal | MICL.00947034/SBR | 9 | 470 | 34 | 34 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.00947034/SBR
Build-In Floor | Mini Canal | MICL.00947034/SDB | 9 | 470 | 34 | 34 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.00947034/SDB
Build-In Floor | Mini Canal | MICL.00947034/SNA | 9 | 470 | 34 | 34 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.00947034/SNA
Build-In Floor | Mini Canal | MICL.00947034/SNC | 9 | 470 | 34 | 34 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.00947034/SNC
Build-In Floor | Mini Canal | MICL.00947042/ANA | 9 | 470 | 42 | 42 | 1833 | 1833 | 1833 | 0.043643 | 713 | 0.016976 | 2088 | 0.049714 | 1.362 | A04 | MICL0.00947042/ANA
Build-In Floor | Mini Canal | MICL.00947042/DBL | 9 | 470 | 42 | 42 | 2371 | 2371 | 2371 | 0.056452 | 922 | 0.021952 | 2701 | 0.06431 | 1.362 | A04 | MICL0.00947042/DBL
Build-In Floor | Mini Canal | MICL.00947042/DBN | 9 | 470 | 42 | 42 | 2273 | 2273 | 2273 | 0.054119 | 884 | 0.021048 | 2589 | 0.061643 | 1.362 | A04 | MICL0.00947042/DBN
Build-In Floor | Mini Canal | MICL.00947042/DBR | 9 | 470 | 42 | 42 | 2371 | 2371 | 2371 | 0.056452 | 922 | 0.021952 | 2701 | 0.06431 | 1.362 | A04 | MICL0.00947042/DBR
Build-In Floor | Mini Canal | MICL.00947042/DBV | 9 | 470 | 42 | 42 | 2273 | 2273 | 2273 | 0.054119 | 884 | 0.021048 | 2589 | 0.061643 | 1.362 | A04 | MICL0.00947042/DBV
Build-In Floor | Mini Canal | MICL.00947042/DDB | 9 | 470 | 42 | 42 | 2371 | 2371 | 2371 | 0.056452 | 922 | 0.021952 | 2701 | 0.06431 | 1.362 | A04 | MICL0.00947042/DDB
Build-In Floor | Mini Canal | MICL.00947042/DMN | 9 | 470 | 42 | 42 | 2273 | 2273 | 2273 | 0.054119 | 884 | 0.021048 | 2589 | 0.061643 | 1.362 | A04 | MICL0.00947042/DMN
Build-In Floor | Mini Canal | MICL.00947042/DMV | 9 | 470 | 42 | 42 | 2273 | 2273 | 2273 | 0.054119 | 884 | 0.021048 | 2589 | 0.061643 | 1.362 | A04 | MICL0.00947042/DMV
Build-In Floor | Mini Canal | MICL.00947042/DNA | 9 | 470 | 42 | 42 | 2371 | 2371 | 2371 | 0.056452 | 922 | 0.021952 | 2701 | 0.06431 | 1.362 | A04 | MICL0.00947042/DNA
Build-In Floor | Mini Canal | MICL.00947042/DNC | 9 | 470 | 42 | 42 | 2371 | 2371 | 2371 | 0.056452 | 922 | 0.021952 | 2701 | 0.06431 | 1.362 | A04 | MICL0.00947042/DNC
Build-In Floor | Mini Canal | MICL.00947042/DON | 9 | 470 | 42 | 42 | 2273 | 2273 | 2273 | 0.054119 | 884 | 0.021048 | 2589 | 0.061643 | 1.362 | A04 | MICL0.00947042/DON
Build-In Floor | Mini Canal | MICL.00947042/DOV | 9 | 470 | 42 | 42 | 2273 | 2273 | 2273 | 0.054119 | 884 | 0.021048 | 2589 | 0.061643 | 1.362 | A04 | MICL0.00947042/DOV
Build-In Floor | Mini Canal | MICL.00947042/PNC | 9 | 470 | 42 | 42 | 2077 | 2077 | 2077 | 0.049452 | 808 | 0.019238 | 2366 | 0.056333 | 1.362 | A04 | MICL0.00947042/PNC
Build-In Floor | Mini Canal | MICL.00947042/RBL | 9 | 470 | 42 | 42 | 2444 | 2444 | 2444 | 0.05819 | 951 | 0.022643 | 2784 | 0.066286 | 1.362 | A04 | MICL0.00947042/RBL
Build-In Floor | Mini Canal | MICL.00947042/RBN | 9 | 470 | 42 | 42 | 2371 | 2371 | 2371 | 0.056452 | 922 | 0.021952 | 2701 | 0.06431 | 1.362 | A04 | MICL0.00947042/RBN
Build-In Floor | Mini Canal | MICL.00947042/RBR | 9 | 470 | 42 | 42 | 2444 | 2444 | 2444 | 0.05819 | 951 | 0.022643 | 2784 | 0.066286 | 1.362 | A04 | MICL0.00947042/RBR
Build-In Floor | Mini Canal | MICL.00947042/RBV | 9 | 470 | 42 | 42 | 2371 | 2371 | 2371 | 0.056452 | 922 | 0.021952 | 2701 | 0.06431 | 1.362 | A04 | MICL0.00947042/RBV
Build-In Floor | Mini Canal | MICL.00947042/RDB | 9 | 470 | 42 | 42 | 2444 | 2444 | 2444 | 0.05819 | 951 | 0.022643 | 2784 | 0.066286 | 1.362 | A04 | MICL0.00947042/RDB
Build-In Floor | Mini Canal | MICL.00947042/RMN | 9 | 470 | 42 | 42 | 2371 | 2371 | 2371 | 0.056452 | 922 | 0.021952 | 2701 | 0.06431 | 1.362 | A04 | MICL0.00947042/RMN
Build-In Floor | Mini Canal | MICL.00947042/RMV | 9 | 470 | 42 | 42 | 2371 | 2371 | 2371 | 0.056452 | 922 | 0.021952 | 2701 | 0.06431 | 1.362 | A04 | MICL0.00947042/RMV
Build-In Floor | Mini Canal | MICL.00947042/RNA | 9 | 470 | 42 | 42 | 2444 | 2444 | 2444 | 0.05819 | 951 | 0.022643 | 2784 | 0.066286 | 1.362 | A04 | MICL0.00947042/RNA
Build-In Floor | Mini Canal | MICL.00947042/RON | 9 | 470 | 42 | 42 | 2371 | 2371 | 2371 | 0.056452 | 922 | 0.021952 | 2701 | 0.06431 | 1.362 | A04 | MICL0.00947042/RON
Build-In Floor | Mini Canal | MICL.00947042/ROV | 9 | 470 | 42 | 42 | 2371 | 2371 | 2371 | 0.056452 | 922 | 0.021952 | 2701 | 0.06431 | 1.362 | A04 | MICL0.00947042/ROV
Build-In Floor | Mini Canal | MICL.00947042/RSS | 9 | 470 | 42 | 42 | 2346 | 2346 | 2346 | 0.055857 | 913 | 0.021738 | 2672 | 0.063619 | 1.362 | A04 | MICL0.00947042/RSS
Build-In Floor | Mini Canal | MICL.00947042/SBL | 9 | 470 | 42 | 42 | 2444 | 2444 | 2444 | 0.05819 | 951 | 0.022643 | 2784 | 0.066286 | 1.362 | A04 | MICL0.00947042/SBL
Build-In Floor | Mini Canal | MICL.00947042/SBR | 9 | 470 | 42 | 42 | 2444 | 2444 | 2444 | 0.05819 | 951 | 0.022643 | 2784 | 0.066286 | 1.362 | A04 | MICL0.00947042/SBR
Build-In Floor | Mini Canal | MICL.00947042/SDB | 9 | 470 | 42 | 42 | 2444 | 2444 | 2444 | 0.05819 | 951 | 0.022643 | 2784 | 0.066286 | 1.362 | A04 | MICL0.00947042/SDB
Build-In Floor | Mini Canal | MICL.00947042/SNA | 9 | 470 | 42 | 42 | 2444 | 2444 | 2444 | 0.05819 | 951 | 0.022643 | 2784 | 0.066286 | 1.362 | A04 | MICL0.00947042/SNA
Build-In Floor | Mini Canal | MICL.00947042/SNC | 9 | 470 | 42 | 42 | 2444 | 2444 | 2444 | 0.05819 | 951 | 0.022643 | 2784 | 0.066286 | 1.362 | A04 | MICL0.00947042/SNC
Build-In Floor | Mini Canal | MICL.00949014/ANA | 9 | 490 | 14 | 14 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.00949014/ANA
Build-In Floor | Mini Canal | MICL.00949014/DBL | 9 | 490 | 14 | 14 | 849 | 849 | 849 | 0.020214 | 330 | 0.0078571 | 967 | 0.023024 | 1.362 | A04 | MICL0.00949014/DBL
Build-In Floor | Mini Canal | MICL.00949014/DBN | 9 | 490 | 14 | 14 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.00949014/DBN
Build-In Floor | Mini Canal | MICL.00949014/DBR | 9 | 490 | 14 | 14 | 849 | 849 | 849 | 0.020214 | 330 | 0.0078571 | 967 | 0.023024 | 1.362 | A04 | MICL0.00949014/DBR
Build-In Floor | Mini Canal | MICL.00949014/DBV | 9 | 490 | 14 | 14 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.00949014/DBV
Build-In Floor | Mini Canal | MICL.00949014/DDB | 9 | 490 | 14 | 14 | 849 | 849 | 849 | 0.020214 | 330 | 0.0078571 | 967 | 0.023024 | 1.362 | A04 | MICL0.00949014/DDB
Build-In Floor | Mini Canal | MICL.00949014/DMN | 9 | 490 | 14 | 14 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.00949014/DMN
Build-In Floor | Mini Canal | MICL.00949014/DMV | 9 | 490 | 14 | 14 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.00949014/DMV
Build-In Floor | Mini Canal | MICL.00949014/DNA | 9 | 490 | 14 | 14 | 849 | 849 | 849 | 0.020214 | 330 | 0.0078571 | 967 | 0.023024 | 1.362 | A04 | MICL0.00949014/DNA
Build-In Floor | Mini Canal | MICL.00949014/DNC | 9 | 490 | 14 | 14 | 849 | 849 | 849 | 0.020214 | 330 | 0.0078571 | 967 | 0.023024 | 1.362 | A04 | MICL0.00949014/DNC
Build-In Floor | Mini Canal | MICL.00949014/DON | 9 | 490 | 14 | 14 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.00949014/DON
Build-In Floor | Mini Canal | MICL.00949014/DOV | 9 | 490 | 14 | 14 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.00949014/DOV
Build-In Floor | Mini Canal | MICL.00949014/RBL | 9 | 490 | 14 | 14 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00949014/RBL
Build-In Floor | Mini Canal | MICL.00949014/RBN | 9 | 490 | 14 | 14 | 849 | 849 | 849 | 0.020214 | 330 | 0.0078571 | 967 | 0.023024 | 1.362 | A04 | MICL0.00949014/RBN
Build-In Floor | Mini Canal | MICL.00949014/RBR | 9 | 490 | 14 | 14 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00949014/RBR
Build-In Floor | Mini Canal | MICL.00949014/RBV | 9 | 490 | 14 | 14 | 849 | 849 | 849 | 0.020214 | 330 | 0.0078571 | 967 | 0.023024 | 1.362 | A04 | MICL0.00949014/RBV
Build-In Floor | Mini Canal | MICL.00949014/RDB | 9 | 490 | 14 | 14 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00949014/RDB
Build-In Floor | Mini Canal | MICL.00949014/RMN | 9 | 490 | 14 | 14 | 849 | 849 | 849 | 0.020214 | 330 | 0.0078571 | 967 | 0.023024 | 1.362 | A04 | MICL0.00949014/RMN
Build-In Floor | Mini Canal | MICL.00949014/RMV | 9 | 490 | 14 | 14 | 849 | 849 | 849 | 0.020214 | 330 | 0.0078571 | 967 | 0.023024 | 1.362 | A04 | MICL0.00949014/RMV
Build-In Floor | Mini Canal | MICL.00949014/RNA | 9 | 490 | 14 | 14 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00949014/RNA
Build-In Floor | Mini Canal | MICL.00949014/RON | 9 | 490 | 14 | 14 | 849 | 849 | 849 | 0.020214 | 330 | 0.0078571 | 967 | 0.023024 | 1.362 | A04 | MICL0.00949014/RON
Build-In Floor | Mini Canal | MICL.00949014/ROV | 9 | 490 | 14 | 14 | 849 | 849 | 849 | 0.020214 | 330 | 0.0078571 | 967 | 0.023024 | 1.362 | A04 | MICL0.00949014/ROV
Build-In Floor | Mini Canal | MICL.00949014/RSS | 9 | 490 | 14 | 14 | 840 | 840 | 840 | 0.02 | 327 | 0.0077857 | 957 | 0.022786 | 1.362 | A04 | MICL0.00949014/RSS
Build-In Floor | Mini Canal | MICL.00949014/SBL | 9 | 490 | 14 | 14 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00949014/SBL
Build-In Floor | Mini Canal | MICL.00949014/SBR | 9 | 490 | 14 | 14 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00949014/SBR
Build-In Floor | Mini Canal | MICL.00949014/SDB | 9 | 490 | 14 | 14 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00949014/SDB
Build-In Floor | Mini Canal | MICL.00949014/SNA | 9 | 490 | 14 | 14 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00949014/SNA
Build-In Floor | Mini Canal | MICL.00949014/SNC | 9 | 490 | 14 | 14 | 875 | 875 | 875 | 0.020833 | 340 | 0.0080952 | 997 | 0.023738 | 1.362 | A04 | MICL0.00949014/SNC
Build-In Floor | Mini Canal | MICL.00949018/ANA | 9 | 490 | 18 | 18 | 778 | 778 | 778 | 0.018524 | 303 | 0.0072143 | 886 | 0.021095 | 1.362 | A04 | MICL0.00949018/ANA
Build-In Floor | Mini Canal | MICL.00949018/DBL | 9 | 490 | 18 | 18 | 1006 | 1006 | 1006 | 0.023952 | 391 | 0.0093095 | 1146 | 0.027286 | 1.362 | A04 | MICL0.00949018/DBL
Build-In Floor | Mini Canal | MICL.00949018/DBN | 9 | 490 | 18 | 18 | 964 | 964 | 964 | 0.022952 | 375 | 0.0089286 | 1098 | 0.026143 | 1.362 | A04 | MICL0.00949018/DBN
Build-In Floor | Mini Canal | MICL.00949018/DBR | 9 | 490 | 18 | 18 | 1006 | 1006 | 1006 | 0.023952 | 391 | 0.0093095 | 1146 | 0.027286 | 1.362 | A04 | MICL0.00949018/DBR
Build-In Floor | Mini Canal | MICL.00949018/DBV | 9 | 490 | 18 | 18 | 964 | 964 | 964 | 0.022952 | 375 | 0.0089286 | 1098 | 0.026143 | 1.362 | A04 | MICL0.00949018/DBV
Build-In Floor | Mini Canal | MICL.00949018/DDB | 9 | 490 | 18 | 18 | 1006 | 1006 | 1006 | 0.023952 | 391 | 0.0093095 | 1146 | 0.027286 | 1.362 | A04 | MICL0.00949018/DDB
Build-In Floor | Mini Canal | MICL.00949018/DMN | 9 | 490 | 18 | 18 | 964 | 964 | 964 | 0.022952 | 375 | 0.0089286 | 1098 | 0.026143 | 1.362 | A04 | MICL0.00949018/DMN
Build-In Floor | Mini Canal | MICL.00949018/DMV | 9 | 490 | 18 | 18 | 964 | 964 | 964 | 0.022952 | 375 | 0.0089286 | 1098 | 0.026143 | 1.362 | A04 | MICL0.00949018/DMV
Build-In Floor | Mini Canal | MICL.00949018/DNA | 9 | 490 | 18 | 18 | 1006 | 1006 | 1006 | 0.023952 | 391 | 0.0093095 | 1146 | 0.027286 | 1.362 | A04 | MICL0.00949018/DNA
Build-In Floor | Mini Canal | MICL.00949018/DNC | 9 | 490 | 18 | 18 | 1006 | 1006 | 1006 | 0.023952 | 391 | 0.0093095 | 1146 | 0.027286 | 1.362 | A04 | MICL0.00949018/DNC
Build-In Floor | Mini Canal | MICL.00949018/DON | 9 | 490 | 18 | 18 | 964 | 964 | 964 | 0.022952 | 375 | 0.0089286 | 1098 | 0.026143 | 1.362 | A04 | MICL0.00949018/DON
Build-In Floor | Mini Canal | MICL.00949018/DOV | 9 | 490 | 18 | 18 | 964 | 964 | 964 | 0.022952 | 375 | 0.0089286 | 1098 | 0.026143 | 1.362 | A04 | MICL0.00949018/DOV
Build-In Floor | Mini Canal | MICL.00949018/RBL | 9 | 490 | 18 | 18 | 1037 | 1037 | 1037 | 0.02469 | 403 | 0.0095952 | 1181 | 0.028119 | 1.362 | A04 | MICL0.00949018/RBL
Build-In Floor | Mini Canal | MICL.00949018/RBN | 9 | 490 | 18 | 18 | 1006 | 1006 | 1006 | 0.023952 | 391 | 0.0093095 | 1146 | 0.027286 | 1.362 | A04 | MICL0.00949018/RBN
Build-In Floor | Mini Canal | MICL.00949018/RBR | 9 | 490 | 18 | 18 | 1037 | 1037 | 1037 | 0.02469 | 403 | 0.0095952 | 1181 | 0.028119 | 1.362 | A04 | MICL0.00949018/RBR
Build-In Floor | Mini Canal | MICL.00949018/RBV | 9 | 490 | 18 | 18 | 1006 | 1006 | 1006 | 0.023952 | 391 | 0.0093095 | 1146 | 0.027286 | 1.362 | A04 | MICL0.00949018/RBV
Build-In Floor | Mini Canal | MICL.00949018/RDB | 9 | 490 | 18 | 18 | 1037 | 1037 | 1037 | 0.02469 | 403 | 0.0095952 | 1181 | 0.028119 | 1.362 | A04 | MICL0.00949018/RDB
Build-In Floor | Mini Canal | MICL.00949018/RMN | 9 | 490 | 18 | 18 | 1006 | 1006 | 1006 | 0.023952 | 391 | 0.0093095 | 1146 | 0.027286 | 1.362 | A04 | MICL0.00949018/RMN
Build-In Floor | Mini Canal | MICL.00949018/RMV | 9 | 490 | 18 | 18 | 1006 | 1006 | 1006 | 0.023952 | 391 | 0.0093095 | 1146 | 0.027286 | 1.362 | A04 | MICL0.00949018/RMV
Build-In Floor | Mini Canal | MICL.00949018/RNA | 9 | 490 | 18 | 18 | 1037 | 1037 | 1037 | 0.02469 | 403 | 0.0095952 | 1181 | 0.028119 | 1.362 | A04 | MICL0.00949018/RNA
Build-In Floor | Mini Canal | MICL.00949018/RON | 9 | 490 | 18 | 18 | 1006 | 1006 | 1006 | 0.023952 | 391 | 0.0093095 | 1146 | 0.027286 | 1.362 | A04 | MICL0.00949018/RON
Build-In Floor | Mini Canal | MICL.00949018/ROV | 9 | 490 | 18 | 18 | 1006 | 1006 | 1006 | 0.023952 | 391 | 0.0093095 | 1146 | 0.027286 | 1.362 | A04 | MICL0.00949018/ROV
Build-In Floor | Mini Canal | MICL.00949018/RSS | 9 | 490 | 18 | 18 | 996 | 996 | 996 | 0.023714 | 387 | 0.0092143 | 1134 | 0.027 | 1.362 | A04 | MICL0.00949018/RSS
Build-In Floor | Mini Canal | MICL.00949018/SBL | 9 | 490 | 18 | 18 | 1037 | 1037 | 1037 | 0.02469 | 403 | 0.0095952 | 1181 | 0.028119 | 1.362 | A04 | MICL0.00949018/SBL
Build-In Floor | Mini Canal | MICL.00949018/SBR | 9 | 490 | 18 | 18 | 1037 | 1037 | 1037 | 0.02469 | 403 | 0.0095952 | 1181 | 0.028119 | 1.362 | A04 | MICL0.00949018/SBR
Build-In Floor | Mini Canal | MICL.00949018/SDB | 9 | 490 | 18 | 18 | 1037 | 1037 | 1037 | 0.02469 | 403 | 0.0095952 | 1181 | 0.028119 | 1.362 | A04 | MICL0.00949018/SDB
Build-In Floor | Mini Canal | MICL.00949018/SNA | 9 | 490 | 18 | 18 | 1037 | 1037 | 1037 | 0.02469 | 403 | 0.0095952 | 1181 | 0.028119 | 1.362 | A04 | MICL0.00949018/SNA
Build-In Floor | Mini Canal | MICL.00949018/SNC | 9 | 490 | 18 | 18 | 1037 | 1037 | 1037 | 0.02469 | 403 | 0.0095952 | 1181 | 0.028119 | 1.362 | A04 | MICL0.00949018/SNC
Build-In Floor | Mini Canal | MICL.00949026/ANA | 9 | 490 | 26 | 26 | 1022 | 1022 | 1022 | 0.024333 | 398 | 0.0094762 | 1164 | 0.027714 | 1.362 | A04 | MICL0.00949026/ANA
Build-In Floor | Mini Canal | MICL.00949026/DBL | 9 | 490 | 26 | 26 | 1322 | 1322 | 1322 | 0.031476 | 514 | 0.012238 | 1506 | 0.035857 | 1.362 | A04 | MICL0.00949026/DBL
Build-In Floor | Mini Canal | MICL.00949026/DBN | 9 | 490 | 26 | 26 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00949026/DBN
Build-In Floor | Mini Canal | MICL.00949026/DBR | 9 | 490 | 26 | 26 | 1322 | 1322 | 1322 | 0.031476 | 514 | 0.012238 | 1506 | 0.035857 | 1.362 | A04 | MICL0.00949026/DBR
Build-In Floor | Mini Canal | MICL.00949026/DBV | 9 | 490 | 26 | 26 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00949026/DBV
Build-In Floor | Mini Canal | MICL.00949026/DDB | 9 | 490 | 26 | 26 | 1322 | 1322 | 1322 | 0.031476 | 514 | 0.012238 | 1506 | 0.035857 | 1.362 | A04 | MICL0.00949026/DDB
Build-In Floor | Mini Canal | MICL.00949026/DMN | 9 | 490 | 26 | 26 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00949026/DMN
Build-In Floor | Mini Canal | MICL.00949026/DMV | 9 | 490 | 26 | 26 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00949026/DMV
Build-In Floor | Mini Canal | MICL.00949026/DNA | 9 | 490 | 26 | 26 | 1322 | 1322 | 1322 | 0.031476 | 514 | 0.012238 | 1506 | 0.035857 | 1.362 | A04 | MICL0.00949026/DNA
Build-In Floor | Mini Canal | MICL.00949026/DNC | 9 | 490 | 26 | 26 | 1322 | 1322 | 1322 | 0.031476 | 514 | 0.012238 | 1506 | 0.035857 | 1.362 | A04 | MICL0.00949026/DNC
Build-In Floor | Mini Canal | MICL.00949026/DON | 9 | 490 | 26 | 26 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00949026/DON
Build-In Floor | Mini Canal | MICL.00949026/DOV | 9 | 490 | 26 | 26 | 1268 | 1268 | 1268 | 0.03019 | 493 | 0.011738 | 1444 | 0.034381 | 1.362 | A04 | MICL0.00949026/DOV
Build-In Floor | Mini Canal | MICL.00949026/PNC | 9 | 490 | 26 | 26 | 1159 | 1159 | 1159 | 0.027595 | 451 | 0.010738 | 1320 | 0.031429 | 1.362 | A04 | MICL0.00949026/PNC
Build-In Floor | Mini Canal | MICL.00949026/RBL | 9 | 490 | 26 | 26 | 1363 | 1363 | 1363 | 0.032452 | 530 | 0.012619 | 1552 | 0.036952 | 1.362 | A04 | MICL0.00949026/RBL
Build-In Floor | Mini Canal | MICL.00949026/RBN | 9 | 490 | 26 | 26 | 1322 | 1322 | 1322 | 0.031476 | 514 | 0.012238 | 1506 | 0.035857 | 1.362 | A04 | MICL0.00949026/RBN
Build-In Floor | Mini Canal | MICL.00949026/RBR | 9 | 490 | 26 | 26 | 1363 | 1363 | 1363 | 0.032452 | 530 | 0.012619 | 1552 | 0.036952 | 1.362 | A04 | MICL0.00949026/RBR
Build-In Floor | Mini Canal | MICL.00949026/RBV | 9 | 490 | 26 | 26 | 1322 | 1322 | 1322 | 0.031476 | 514 | 0.012238 | 1506 | 0.035857 | 1.362 | A04 | MICL0.00949026/RBV
Build-In Floor | Mini Canal | MICL.00949026/RDB | 9 | 490 | 26 | 26 | 1363 | 1363 | 1363 | 0.032452 | 530 | 0.012619 | 1552 | 0.036952 | 1.362 | A04 | MICL0.00949026/RDB
Build-In Floor | Mini Canal | MICL.00949026/RMN | 9 | 490 | 26 | 26 | 1322 | 1322 | 1322 | 0.031476 | 514 | 0.012238 | 1506 | 0.035857 | 1.362 | A04 | MICL0.00949026/RMN
Build-In Floor | Mini Canal | MICL.00949026/RMV | 9 | 490 | 26 | 26 | 1322 | 1322 | 1322 | 0.031476 | 514 | 0.012238 | 1506 | 0.035857 | 1.362 | A04 | MICL0.00949026/RMV
Build-In Floor | Mini Canal | MICL.00949026/RNA | 9 | 490 | 26 | 26 | 1363 | 1363 | 1363 | 0.032452 | 530 | 0.012619 | 1552 | 0.036952 | 1.362 | A04 | MICL0.00949026/RNA
Build-In Floor | Mini Canal | MICL.00949026/RON | 9 | 490 | 26 | 26 | 1322 | 1322 | 1322 | 0.031476 | 514 | 0.012238 | 1506 | 0.035857 | 1.362 | A04 | MICL0.00949026/RON
Build-In Floor | Mini Canal | MICL.00949026/ROV | 9 | 490 | 26 | 26 | 1322 | 1322 | 1322 | 0.031476 | 514 | 0.012238 | 1506 | 0.035857 | 1.362 | A04 | MICL0.00949026/ROV
Build-In Floor | Mini Canal | MICL.00949026/RSS | 9 | 490 | 26 | 26 | 1308 | 1308 | 1308 | 0.031143 | 509 | 0.012119 | 1490 | 0.035476 | 1.362 | A04 | MICL0.00949026/RSS
Build-In Floor | Mini Canal | MICL.00949026/SBL | 9 | 490 | 26 | 26 | 1363 | 1363 | 1363 | 0.032452 | 530 | 0.012619 | 1552 | 0.036952 | 1.362 | A04 | MICL0.00949026/SBL
Build-In Floor | Mini Canal | MICL.00949026/SBR | 9 | 490 | 26 | 26 | 1363 | 1363 | 1363 | 0.032452 | 530 | 0.012619 | 1552 | 0.036952 | 1.362 | A04 | MICL0.00949026/SBR
Build-In Floor | Mini Canal | MICL.00949026/SDB | 9 | 490 | 26 | 26 | 1363 | 1363 | 1363 | 0.032452 | 530 | 0.012619 | 1552 | 0.036952 | 1.362 | A04 | MICL0.00949026/SDB
Build-In Floor | Mini Canal | MICL.00949026/SNA | 9 | 490 | 26 | 26 | 1363 | 1363 | 1363 | 0.032452 | 530 | 0.012619 | 1552 | 0.036952 | 1.362 | A04 | MICL0.00949026/SNA
Build-In Floor | Mini Canal | MICL.00949026/SNC | 9 | 490 | 26 | 26 | 1363 | 1363 | 1363 | 0.032452 | 530 | 0.012619 | 1552 | 0.036952 | 1.362 | A04 | MICL0.00949026/SNC
Build-In Floor | Mini Canal | MICL.00949034/ANA | 9 | 490 | 34 | 34 | 1327 | 1327 | 1327 | 0.031595 | 516 | 0.012286 | 1511 | 0.035976 | 1.362 | A04 | MICL0.00949034/ANA
Build-In Floor | Mini Canal | MICL.00949034/DBL | 9 | 490 | 34 | 34 | 1716 | 1716 | 1716 | 0.040857 | 668 | 0.015905 | 1955 | 0.046548 | 1.362 | A04 | MICL0.00949034/DBL
Build-In Floor | Mini Canal | MICL.00949034/DBN | 9 | 490 | 34 | 34 | 1645 | 1645 | 1645 | 0.039167 | 640 | 0.015238 | 1874 | 0.044619 | 1.362 | A04 | MICL0.00949034/DBN
Build-In Floor | Mini Canal | MICL.00949034/DBR | 9 | 490 | 34 | 34 | 1716 | 1716 | 1716 | 0.040857 | 668 | 0.015905 | 1955 | 0.046548 | 1.362 | A04 | MICL0.00949034/DBR
Build-In Floor | Mini Canal | MICL.00949034/DBV | 9 | 490 | 34 | 34 | 1645 | 1645 | 1645 | 0.039167 | 640 | 0.015238 | 1874 | 0.044619 | 1.362 | A04 | MICL0.00949034/DBV
Build-In Floor | Mini Canal | MICL.00949034/DDB | 9 | 490 | 34 | 34 | 1716 | 1716 | 1716 | 0.040857 | 668 | 0.015905 | 1955 | 0.046548 | 1.362 | A04 | MICL0.00949034/DDB
Build-In Floor | Mini Canal | MICL.00949034/DMN | 9 | 490 | 34 | 34 | 1645 | 1645 | 1645 | 0.039167 | 640 | 0.015238 | 1874 | 0.044619 | 1.362 | A04 | MICL0.00949034/DMN
Build-In Floor | Mini Canal | MICL.00949034/DMV | 9 | 490 | 34 | 34 | 1645 | 1645 | 1645 | 0.039167 | 640 | 0.015238 | 1874 | 0.044619 | 1.362 | A04 | MICL0.00949034/DMV
Build-In Floor | Mini Canal | MICL.00949034/DNA | 9 | 490 | 34 | 34 | 1716 | 1716 | 1716 | 0.040857 | 668 | 0.015905 | 1955 | 0.046548 | 1.362 | A04 | MICL0.00949034/DNA
Build-In Floor | Mini Canal | MICL.00949034/DNC | 9 | 490 | 34 | 34 | 1716 | 1716 | 1716 | 0.040857 | 668 | 0.015905 | 1955 | 0.046548 | 1.362 | A04 | MICL0.00949034/DNC
Build-In Floor | Mini Canal | MICL.00949034/DON | 9 | 490 | 34 | 34 | 1645 | 1645 | 1645 | 0.039167 | 640 | 0.015238 | 1874 | 0.044619 | 1.362 | A04 | MICL0.00949034/DON
Build-In Floor | Mini Canal | MICL.00949034/DOV | 9 | 490 | 34 | 34 | 1645 | 1645 | 1645 | 0.039167 | 640 | 0.015238 | 1874 | 0.044619 | 1.362 | A04 | MICL0.00949034/DOV
Build-In Floor | Mini Canal | MICL.00949034/PNC | 9 | 490 | 34 | 34 | 1504 | 1504 | 1504 | 0.03581 | 585 | 0.013929 | 1713 | 0.040786 | 1.362 | A04 | MICL0.00949034/PNC
Build-In Floor | Mini Canal | MICL.00949034/RBL | 9 | 490 | 34 | 34 | 1769 | 1769 | 1769 | 0.042119 | 688 | 0.016381 | 2015 | 0.047976 | 1.362 | A04 | MICL0.00949034/RBL
Build-In Floor | Mini Canal | MICL.00949034/RBN | 9 | 490 | 34 | 34 | 1716 | 1716 | 1716 | 0.040857 | 668 | 0.015905 | 1955 | 0.046548 | 1.362 | A04 | MICL0.00949034/RBN
Build-In Floor | Mini Canal | MICL.00949034/RBR | 9 | 490 | 34 | 34 | 1769 | 1769 | 1769 | 0.042119 | 688 | 0.016381 | 2015 | 0.047976 | 1.362 | A04 | MICL0.00949034/RBR
Build-In Floor | Mini Canal | MICL.00949034/RBV | 9 | 490 | 34 | 34 | 1716 | 1716 | 1716 | 0.040857 | 668 | 0.015905 | 1955 | 0.046548 | 1.362 | A04 | MICL0.00949034/RBV
Build-In Floor | Mini Canal | MICL.00949034/RDB | 9 | 490 | 34 | 34 | 1769 | 1769 | 1769 | 0.042119 | 688 | 0.016381 | 2015 | 0.047976 | 1.362 | A04 | MICL0.00949034/RDB
Build-In Floor | Mini Canal | MICL.00949034/RMN | 9 | 490 | 34 | 34 | 1716 | 1716 | 1716 | 0.040857 | 668 | 0.015905 | 1955 | 0.046548 | 1.362 | A04 | MICL0.00949034/RMN
Build-In Floor | Mini Canal | MICL.00949034/RMV | 9 | 490 | 34 | 34 | 1716 | 1716 | 1716 | 0.040857 | 668 | 0.015905 | 1955 | 0.046548 | 1.362 | A04 | MICL0.00949034/RMV
Build-In Floor | Mini Canal | MICL.00949034/RNA | 9 | 490 | 34 | 34 | 1769 | 1769 | 1769 | 0.042119 | 688 | 0.016381 | 2015 | 0.047976 | 1.362 | A04 | MICL0.00949034/RNA
Build-In Floor | Mini Canal | MICL.00949034/RON | 9 | 490 | 34 | 34 | 1716 | 1716 | 1716 | 0.040857 | 668 | 0.015905 | 1955 | 0.046548 | 1.362 | A04 | MICL0.00949034/RON
Build-In Floor | Mini Canal | MICL.00949034/ROV | 9 | 490 | 34 | 34 | 1716 | 1716 | 1716 | 0.040857 | 668 | 0.015905 | 1955 | 0.046548 | 1.362 | A04 | MICL0.00949034/ROV
Build-In Floor | Mini Canal | MICL.00949034/RSS | 9 | 490 | 34 | 34 | 1698 | 1698 | 1698 | 0.040429 | 661 | 0.015738 | 1934 | 0.046048 | 1.362 | A04 | MICL0.00949034/RSS
Build-In Floor | Mini Canal | MICL.00949034/SBL | 9 | 490 | 34 | 34 | 1769 | 1769 | 1769 | 0.042119 | 688 | 0.016381 | 2015 | 0.047976 | 1.362 | A04 | MICL0.00949034/SBL
Build-In Floor | Mini Canal | MICL.00949034/SBR | 9 | 490 | 34 | 34 | 1769 | 1769 | 1769 | 0.042119 | 688 | 0.016381 | 2015 | 0.047976 | 1.362 | A04 | MICL0.00949034/SBR
Build-In Floor | Mini Canal | MICL.00949034/SDB | 9 | 490 | 34 | 34 | 1769 | 1769 | 1769 | 0.042119 | 688 | 0.016381 | 2015 | 0.047976 | 1.362 | A04 | MICL0.00949034/SDB
Build-In Floor | Mini Canal | MICL.00949034/SNA | 9 | 490 | 34 | 34 | 1769 | 1769 | 1769 | 0.042119 | 688 | 0.016381 | 2015 | 0.047976 | 1.362 | A04 | MICL0.00949034/SNA
Build-In Floor | Mini Canal | MICL.00949034/SNC | 9 | 490 | 34 | 34 | 1769 | 1769 | 1769 | 0.042119 | 688 | 0.016381 | 2015 | 0.047976 | 1.362 | A04 | MICL0.00949034/SNC
Build-In Floor | Mini Canal | MICL.00949042/ANA | 9 | 490 | 42 | 42 | 1916 | 1916 | 1916 | 0.045619 | 745 | 0.017738 | 2182 | 0.051952 | 1.362 | A04 | MICL0.00949042/ANA
Build-In Floor | Mini Canal | MICL.00949042/DBL | 9 | 490 | 42 | 42 | 2478 | 2478 | 2478 | 0.059 | 964 | 0.022952 | 2822 | 0.06719 | 1.362 | A04 | MICL0.00949042/DBL
Build-In Floor | Mini Canal | MICL.00949042/DBN | 9 | 490 | 42 | 42 | 2376 | 2376 | 2376 | 0.056571 | 924 | 0.022 | 2706 | 0.064429 | 1.362 | A04 | MICL0.00949042/DBN
Build-In Floor | Mini Canal | MICL.00949042/DBR | 9 | 490 | 42 | 42 | 2478 | 2478 | 2478 | 0.059 | 964 | 0.022952 | 2822 | 0.06719 | 1.362 | A04 | MICL0.00949042/DBR
Build-In Floor | Mini Canal | MICL.00949042/DBV | 9 | 490 | 42 | 42 | 2376 | 2376 | 2376 | 0.056571 | 924 | 0.022 | 2706 | 0.064429 | 1.362 | A04 | MICL0.00949042/DBV
Build-In Floor | Mini Canal | MICL.00949042/DDB | 9 | 490 | 42 | 42 | 2478 | 2478 | 2478 | 0.059 | 964 | 0.022952 | 2822 | 0.06719 | 1.362 | A04 | MICL0.00949042/DDB
Build-In Floor | Mini Canal | MICL.00949042/DMN | 9 | 490 | 42 | 42 | 2376 | 2376 | 2376 | 0.056571 | 924 | 0.022 | 2706 | 0.064429 | 1.362 | A04 | MICL0.00949042/DMN
Build-In Floor | Mini Canal | MICL.00949042/DMV | 9 | 490 | 42 | 42 | 2376 | 2376 | 2376 | 0.056571 | 924 | 0.022 | 2706 | 0.064429 | 1.362 | A04 | MICL0.00949042/DMV
Build-In Floor | Mini Canal | MICL.00949042/DNA | 9 | 490 | 42 | 42 | 2478 | 2478 | 2478 | 0.059 | 964 | 0.022952 | 2822 | 0.06719 | 1.362 | A04 | MICL0.00949042/DNA
Build-In Floor | Mini Canal | MICL.00949042/DNC | 9 | 490 | 42 | 42 | 2478 | 2478 | 2478 | 0.059 | 964 | 0.022952 | 2822 | 0.06719 | 1.362 | A04 | MICL0.00949042/DNC
Build-In Floor | Mini Canal | MICL.00949042/DON | 9 | 490 | 42 | 42 | 2376 | 2376 | 2376 | 0.056571 | 924 | 0.022 | 2706 | 0.064429 | 1.362 | A04 | MICL0.00949042/DON
Build-In Floor | Mini Canal | MICL.00949042/DOV | 9 | 490 | 42 | 42 | 2376 | 2376 | 2376 | 0.056571 | 924 | 0.022 | 2706 | 0.064429 | 1.362 | A04 | MICL0.00949042/DOV
Build-In Floor | Mini Canal | MICL.00949042/PNC | 9 | 490 | 42 | 42 | 2172 | 2172 | 2172 | 0.051714 | 845 | 0.020119 | 2474 | 0.058905 | 1.362 | A04 | MICL0.00949042/PNC
Build-In Floor | Mini Canal | MICL.00949042/RBL | 9 | 490 | 42 | 42 | 2555 | 2555 | 2555 | 0.060833 | 994 | 0.023667 | 2910 | 0.069286 | 1.362 | A04 | MICL0.00949042/RBL
Build-In Floor | Mini Canal | MICL.00949042/RBN | 9 | 490 | 42 | 42 | 2478 | 2478 | 2478 | 0.059 | 964 | 0.022952 | 2822 | 0.06719 | 1.362 | A04 | MICL0.00949042/RBN
Build-In Floor | Mini Canal | MICL.00949042/RBR | 9 | 490 | 42 | 42 | 2555 | 2555 | 2555 | 0.060833 | 994 | 0.023667 | 2910 | 0.069286 | 1.362 | A04 | MICL0.00949042/RBR
Build-In Floor | Mini Canal | MICL.00949042/RBV | 9 | 490 | 42 | 42 | 2478 | 2478 | 2478 | 0.059 | 964 | 0.022952 | 2822 | 0.06719 | 1.362 | A04 | MICL0.00949042/RBV
Build-In Floor | Mini Canal | MICL.00949042/RDB | 9 | 490 | 42 | 42 | 2555 | 2555 | 2555 | 0.060833 | 994 | 0.023667 | 2910 | 0.069286 | 1.362 | A04 | MICL0.00949042/RDB
Build-In Floor | Mini Canal | MICL.00949042/RMN | 9 | 490 | 42 | 42 | 2478 | 2478 | 2478 | 0.059 | 964 | 0.022952 | 2822 | 0.06719 | 1.362 | A04 | MICL0.00949042/RMN
Build-In Floor | Mini Canal | MICL.00949042/RMV | 9 | 490 | 42 | 42 | 2478 | 2478 | 2478 | 0.059 | 964 | 0.022952 | 2822 | 0.06719 | 1.362 | A04 | MICL0.00949042/RMV
Build-In Floor | Mini Canal | MICL.00949042/RNA | 9 | 490 | 42 | 42 | 2555 | 2555 | 2555 | 0.060833 | 994 | 0.023667 | 2910 | 0.069286 | 1.362 | A04 | MICL0.00949042/RNA
Build-In Floor | Mini Canal | MICL.00949042/RON | 9 | 490 | 42 | 42 | 2478 | 2478 | 2478 | 0.059 | 964 | 0.022952 | 2822 | 0.06719 | 1.362 | A04 | MICL0.00949042/RON
Build-In Floor | Mini Canal | MICL.00949042/ROV | 9 | 490 | 42 | 42 | 2478 | 2478 | 2478 | 0.059 | 964 | 0.022952 | 2822 | 0.06719 | 1.362 | A04 | MICL0.00949042/ROV
Build-In Floor | Mini Canal | MICL.00949042/RSS | 9 | 490 | 42 | 42 | 2453 | 2453 | 2453 | 0.058405 | 954 | 0.022714 | 2794 | 0.066524 | 1.362 | A04 | MICL0.00949042/RSS
Build-In Floor | Mini Canal | MICL.00949042/SBL | 9 | 490 | 42 | 42 | 2555 | 2555 | 2555 | 0.060833 | 994 | 0.023667 | 2910 | 0.069286 | 1.362 | A04 | MICL0.00949042/SBL
Build-In Floor | Mini Canal | MICL.00949042/SBR | 9 | 490 | 42 | 42 | 2555 | 2555 | 2555 | 0.060833 | 994 | 0.023667 | 2910 | 0.069286 | 1.362 | A04 | MICL0.00949042/SBR
Build-In Floor | Mini Canal | MICL.00949042/SDB | 9 | 490 | 42 | 42 | 2555 | 2555 | 2555 | 0.060833 | 994 | 0.023667 | 2910 | 0.069286 | 1.362 | A04 | MICL0.00949042/SDB
Build-In Floor | Mini Canal | MICL.00949042/SNA | 9 | 490 | 42 | 42 | 2555 | 2555 | 2555 | 0.060833 | 994 | 0.023667 | 2910 | 0.069286 | 1.362 | A04 | MICL0.00949042/SNA
Build-In Floor | Mini Canal | MICL.00949042/SNC | 9 | 490 | 42 | 42 | 2555 | 2555 | 2555 | 0.060833 | 994 | 0.023667 | 2910 | 0.069286 | 1.362 | A04 | MICL0.00949042/SNC
Build-In Floor | Mini Canal | MICL.01107014/ANA | 11 | 70 | 14 | 14 | 65 | 65 | 65 | 0.0015476 | 25 | 0.00059524 | 74 | 0.0017619 | 1.362 | A04 | MICL0.01107014/ANA
Build-In Floor | Mini Canal | MICL.01107014/DBL | 11 | 70 | 14 | 14 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.01107014/DBL
Build-In Floor | Mini Canal | MICL.01107014/DBN | 11 | 70 | 14 | 14 | 81 | 81 | 81 | 0.0019286 | 32 | 0.0007619 | 92 | 0.0021905 | 1.362 | A04 | MICL0.01107014/DBN
Build-In Floor | Mini Canal | MICL.01107014/DBR | 11 | 70 | 14 | 14 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.01107014/DBR
Build-In Floor | Mini Canal | MICL.01107014/DBV | 11 | 70 | 14 | 14 | 81 | 81 | 81 | 0.0019286 | 32 | 0.0007619 | 92 | 0.0021905 | 1.362 | A04 | MICL0.01107014/DBV
Build-In Floor | Mini Canal | MICL.01107014/DDB | 11 | 70 | 14 | 14 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.01107014/DDB
Build-In Floor | Mini Canal | MICL.01107014/DMN | 11 | 70 | 14 | 14 | 81 | 81 | 81 | 0.0019286 | 32 | 0.0007619 | 92 | 0.0021905 | 1.362 | A04 | MICL0.01107014/DMN
Build-In Floor | Mini Canal | MICL.01107014/DMV | 11 | 70 | 14 | 14 | 81 | 81 | 81 | 0.0019286 | 32 | 0.0007619 | 92 | 0.0021905 | 1.362 | A04 | MICL0.01107014/DMV
Build-In Floor | Mini Canal | MICL.01107014/DNA | 11 | 70 | 14 | 14 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.01107014/DNA
Build-In Floor | Mini Canal | MICL.01107014/DNC | 11 | 70 | 14 | 14 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.01107014/DNC
Build-In Floor | Mini Canal | MICL.01107014/DON | 11 | 70 | 14 | 14 | 81 | 81 | 81 | 0.0019286 | 32 | 0.0007619 | 92 | 0.0021905 | 1.362 | A04 | MICL0.01107014/DON
Build-In Floor | Mini Canal | MICL.01107014/DOV | 11 | 70 | 14 | 14 | 81 | 81 | 81 | 0.0019286 | 32 | 0.0007619 | 92 | 0.0021905 | 1.362 | A04 | MICL0.01107014/DOV
Build-In Floor | Mini Canal | MICL.01107014/RBL | 11 | 70 | 14 | 14 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.01107014/RBL
Build-In Floor | Mini Canal | MICL.01107014/RBN | 11 | 70 | 14 | 14 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.01107014/RBN
Build-In Floor | Mini Canal | MICL.01107014/RBR | 11 | 70 | 14 | 14 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.01107014/RBR
Build-In Floor | Mini Canal | MICL.01107014/RBV | 11 | 70 | 14 | 14 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.01107014/RBV
Build-In Floor | Mini Canal | MICL.01107014/RDB | 11 | 70 | 14 | 14 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.01107014/RDB
Build-In Floor | Mini Canal | MICL.01107014/RMN | 11 | 70 | 14 | 14 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.01107014/RMN
Build-In Floor | Mini Canal | MICL.01107014/RMV | 11 | 70 | 14 | 14 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.01107014/RMV
Build-In Floor | Mini Canal | MICL.01107014/RNA | 11 | 70 | 14 | 14 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.01107014/RNA
Build-In Floor | Mini Canal | MICL.01107014/RON | 11 | 70 | 14 | 14 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.01107014/RON
Build-In Floor | Mini Canal | MICL.01107014/ROV | 11 | 70 | 14 | 14 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.01107014/ROV
Build-In Floor | Mini Canal | MICL.01107014/RSS | 11 | 70 | 14 | 14 | 84 | 84 | 84 | 0.002 | 33 | 0.00078571 | 96 | 0.0022857 | 1.362 | A04 | MICL0.01107014/RSS
Build-In Floor | Mini Canal | MICL.01107014/SBL | 11 | 70 | 14 | 14 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.01107014/SBL
Build-In Floor | Mini Canal | MICL.01107014/SBR | 11 | 70 | 14 | 14 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.01107014/SBR
Build-In Floor | Mini Canal | MICL.01107014/SDB | 11 | 70 | 14 | 14 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.01107014/SDB
Build-In Floor | Mini Canal | MICL.01107014/SNA | 11 | 70 | 14 | 14 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.01107014/SNA
Build-In Floor | Mini Canal | MICL.01107014/SNC | 11 | 70 | 14 | 14 | 87 | 87 | 87 | 0.0020714 | 34 | 0.00080952 | 99 | 0.0023571 | 1.362 | A04 | MICL0.01107014/SNC
Build-In Floor | Mini Canal | MICL.01107018/ANA | 11 | 70 | 18 | 18 | 78 | 78 | 78 | 0.0018571 | 30 | 0.00071429 | 89 | 0.002119 | 1.362 | A04 | MICL0.01107018/ANA
Build-In Floor | Mini Canal | MICL.01107018/DBL | 11 | 70 | 18 | 18 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01107018/DBL
Build-In Floor | Mini Canal | MICL.01107018/DBN | 11 | 70 | 18 | 18 | 97 | 97 | 97 | 0.0023095 | 38 | 0.00090476 | 110 | 0.002619 | 1.362 | A04 | MICL0.01107018/DBN
Build-In Floor | Mini Canal | MICL.01107018/DBR | 11 | 70 | 18 | 18 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01107018/DBR
Build-In Floor | Mini Canal | MICL.01107018/DBV | 11 | 70 | 18 | 18 | 97 | 97 | 97 | 0.0023095 | 38 | 0.00090476 | 110 | 0.002619 | 1.362 | A04 | MICL0.01107018/DBV
Build-In Floor | Mini Canal | MICL.01107018/DDB | 11 | 70 | 18 | 18 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01107018/DDB
Build-In Floor | Mini Canal | MICL.01107018/DMN | 11 | 70 | 18 | 18 | 97 | 97 | 97 | 0.0023095 | 38 | 0.00090476 | 110 | 0.002619 | 1.362 | A04 | MICL0.01107018/DMN
Build-In Floor | Mini Canal | MICL.01107018/DMV | 11 | 70 | 18 | 18 | 97 | 97 | 97 | 0.0023095 | 38 | 0.00090476 | 110 | 0.002619 | 1.362 | A04 | MICL0.01107018/DMV
Build-In Floor | Mini Canal | MICL.01107018/DNA | 11 | 70 | 18 | 18 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01107018/DNA
Build-In Floor | Mini Canal | MICL.01107018/DNC | 11 | 70 | 18 | 18 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01107018/DNC
Build-In Floor | Mini Canal | MICL.01107018/DON | 11 | 70 | 18 | 18 | 97 | 97 | 97 | 0.0023095 | 38 | 0.00090476 | 110 | 0.002619 | 1.362 | A04 | MICL0.01107018/DON
Build-In Floor | Mini Canal | MICL.01107018/DOV | 11 | 70 | 18 | 18 | 97 | 97 | 97 | 0.0023095 | 38 | 0.00090476 | 110 | 0.002619 | 1.362 | A04 | MICL0.01107018/DOV
Build-In Floor | Mini Canal | MICL.01107018/RBL | 11 | 70 | 18 | 18 | 104 | 104 | 104 | 0.0024762 | 40 | 0.00095238 | 118 | 0.0028095 | 1.362 | A04 | MICL0.01107018/RBL
Build-In Floor | Mini Canal | MICL.01107018/RBN | 11 | 70 | 18 | 18 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01107018/RBN
Build-In Floor | Mini Canal | MICL.01107018/RBR | 11 | 70 | 18 | 18 | 104 | 104 | 104 | 0.0024762 | 40 | 0.00095238 | 118 | 0.0028095 | 1.362 | A04 | MICL0.01107018/RBR
Build-In Floor | Mini Canal | MICL.01107018/RBV | 11 | 70 | 18 | 18 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01107018/RBV
Build-In Floor | Mini Canal | MICL.01107018/RDB | 11 | 70 | 18 | 18 | 104 | 104 | 104 | 0.0024762 | 40 | 0.00095238 | 118 | 0.0028095 | 1.362 | A04 | MICL0.01107018/RDB
Build-In Floor | Mini Canal | MICL.01107018/RMN | 11 | 70 | 18 | 18 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01107018/RMN
Build-In Floor | Mini Canal | MICL.01107018/RMV | 11 | 70 | 18 | 18 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01107018/RMV
Build-In Floor | Mini Canal | MICL.01107018/RNA | 11 | 70 | 18 | 18 | 104 | 104 | 104 | 0.0024762 | 40 | 0.00095238 | 118 | 0.0028095 | 1.362 | A04 | MICL0.01107018/RNA
Build-In Floor | Mini Canal | MICL.01107018/RON | 11 | 70 | 18 | 18 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01107018/RON
Build-In Floor | Mini Canal | MICL.01107018/ROV | 11 | 70 | 18 | 18 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01107018/ROV
Build-In Floor | Mini Canal | MICL.01107018/RSS | 11 | 70 | 18 | 18 | 100 | 100 | 100 | 0.002381 | 39 | 0.00092857 | 114 | 0.0027143 | 1.362 | A04 | MICL0.01107018/RSS
Build-In Floor | Mini Canal | MICL.01107018/SBL | 11 | 70 | 18 | 18 | 104 | 104 | 104 | 0.0024762 | 40 | 0.00095238 | 118 | 0.0028095 | 1.362 | A04 | MICL0.01107018/SBL
Build-In Floor | Mini Canal | MICL.01107018/SBR | 11 | 70 | 18 | 18 | 104 | 104 | 104 | 0.0024762 | 40 | 0.00095238 | 118 | 0.0028095 | 1.362 | A04 | MICL0.01107018/SBR
Build-In Floor | Mini Canal | MICL.01107018/SDB | 11 | 70 | 18 | 18 | 104 | 104 | 104 | 0.0024762 | 40 | 0.00095238 | 118 | 0.0028095 | 1.362 | A04 | MICL0.01107018/SDB
Build-In Floor | Mini Canal | MICL.01107018/SNA | 11 | 70 | 18 | 18 | 104 | 104 | 104 | 0.0024762 | 40 | 0.00095238 | 118 | 0.0028095 | 1.362 | A04 | MICL0.01107018/SNA
Build-In Floor | Mini Canal | MICL.01107018/SNC | 11 | 70 | 18 | 18 | 104 | 104 | 104 | 0.0024762 | 40 | 0.00095238 | 118 | 0.0028095 | 1.362 | A04 | MICL0.01107018/SNC
Build-In Floor | Mini Canal | MICL.01107026/ANA | 11 | 70 | 26 | 26 | 105 | 105 | 105 | 0.0025 | 41 | 0.00097619 | 120 | 0.0028571 | 1.362 | A04 | MICL0.01107026/ANA
Build-In Floor | Mini Canal | MICL.01107026/DBL | 11 | 70 | 26 | 26 | 136 | 136 | 136 | 0.0032381 | 53 | 0.0012619 | 155 | 0.0036905 | 1.362 | A04 | MICL0.01107026/DBL
Build-In Floor | Mini Canal | MICL.01107026/DBN | 11 | 70 | 26 | 26 | 130 | 130 | 130 | 0.0030952 | 51 | 0.0012143 | 148 | 0.0035238 | 1.362 | A04 | MICL0.01107026/DBN
Build-In Floor | Mini Canal | MICL.01107026/DBR | 11 | 70 | 26 | 26 | 136 | 136 | 136 | 0.0032381 | 53 | 0.0012619 | 155 | 0.0036905 | 1.362 | A04 | MICL0.01107026/DBR
Build-In Floor | Mini Canal | MICL.01107026/DBV | 11 | 70 | 26 | 26 | 130 | 130 | 130 | 0.0030952 | 51 | 0.0012143 | 148 | 0.0035238 | 1.362 | A04 | MICL0.01107026/DBV
Build-In Floor | Mini Canal | MICL.01107026/DDB | 11 | 70 | 26 | 26 | 136 | 136 | 136 | 0.0032381 | 53 | 0.0012619 | 155 | 0.0036905 | 1.362 | A04 | MICL0.01107026/DDB
Build-In Floor | Mini Canal | MICL.01107026/DMN | 11 | 70 | 26 | 26 | 130 | 130 | 130 | 0.0030952 | 51 | 0.0012143 | 148 | 0.0035238 | 1.362 | A04 | MICL0.01107026/DMN
Build-In Floor | Mini Canal | MICL.01107026/DMV | 11 | 70 | 26 | 26 | 130 | 130 | 130 | 0.0030952 | 51 | 0.0012143 | 148 | 0.0035238 | 1.362 | A04 | MICL0.01107026/DMV
Build-In Floor | Mini Canal | MICL.01107026/DNA | 11 | 70 | 26 | 26 | 136 | 136 | 136 | 0.0032381 | 53 | 0.0012619 | 155 | 0.0036905 | 1.362 | A04 | MICL0.01107026/DNA
Build-In Floor | Mini Canal | MICL.01107026/DNC | 11 | 70 | 26 | 26 | 136 | 136 | 136 | 0.0032381 | 53 | 0.0012619 | 155 | 0.0036905 | 1.362 | A04 | MICL0.01107026/DNC
Build-In Floor | Mini Canal | MICL.01107026/DON | 11 | 70 | 26 | 26 | 130 | 130 | 130 | 0.0030952 | 51 | 0.0012143 | 148 | 0.0035238 | 1.362 | A04 | MICL0.01107026/DON
Build-In Floor | Mini Canal | MICL.01107026/DOV | 11 | 70 | 26 | 26 | 130 | 130 | 130 | 0.0030952 | 51 | 0.0012143 | 148 | 0.0035238 | 1.362 | A04 | MICL0.01107026/DOV
Build-In Floor | Mini Canal | MICL.01107026/PNC | 11 | 70 | 26 | 26 | 119 | 119 | 119 | 0.0028333 | 46 | 0.0010952 | 136 | 0.0032381 | 1.362 | A04 | MICL0.01107026/PNC
Build-In Floor | Mini Canal | MICL.01107026/RBL | 11 | 70 | 26 | 26 | 140 | 140 | 140 | 0.0033333 | 54 | 0.0012857 | 159 | 0.0037857 | 1.362 | A04 | MICL0.01107026/RBL
Build-In Floor | Mini Canal | MICL.01107026/RBN | 11 | 70 | 26 | 26 | 136 | 136 | 136 | 0.0032381 | 53 | 0.0012619 | 155 | 0.0036905 | 1.362 | A04 | MICL0.01107026/RBN
Build-In Floor | Mini Canal | MICL.01107026/RBR | 11 | 70 | 26 | 26 | 140 | 140 | 140 | 0.0033333 | 54 | 0.0012857 | 159 | 0.0037857 | 1.362 | A04 | MICL0.01107026/RBR
Build-In Floor | Mini Canal | MICL.01107026/RBV | 11 | 70 | 26 | 26 | 136 | 136 | 136 | 0.0032381 | 53 | 0.0012619 | 155 | 0.0036905 | 1.362 | A04 | MICL0.01107026/RBV
Build-In Floor | Mini Canal | MICL.01107026/RDB | 11 | 70 | 26 | 26 | 140 | 140 | 140 | 0.0033333 | 54 | 0.0012857 | 159 | 0.0037857 | 1.362 | A04 | MICL0.01107026/RDB
Build-In Floor | Mini Canal | MICL.01107026/RMN | 11 | 70 | 26 | 26 | 136 | 136 | 136 | 0.0032381 | 53 | 0.0012619 | 155 | 0.0036905 | 1.362 | A04 | MICL0.01107026/RMN
Build-In Floor | Mini Canal | MICL.01107026/RMV | 11 | 70 | 26 | 26 | 136 | 136 | 136 | 0.0032381 | 53 | 0.0012619 | 155 | 0.0036905 | 1.362 | A04 | MICL0.01107026/RMV
Build-In Floor | Mini Canal | MICL.01107026/RNA | 11 | 70 | 26 | 26 | 140 | 140 | 140 | 0.0033333 | 54 | 0.0012857 | 159 | 0.0037857 | 1.362 | A04 | MICL0.01107026/RNA
Build-In Floor | Mini Canal | MICL.01107026/RON | 11 | 70 | 26 | 26 | 136 | 136 | 136 | 0.0032381 | 53 | 0.0012619 | 155 | 0.0036905 | 1.362 | A04 | MICL0.01107026/RON
Build-In Floor | Mini Canal | MICL.01107026/ROV | 11 | 70 | 26 | 26 | 136 | 136 | 136 | 0.0032381 | 53 | 0.0012619 | 155 | 0.0036905 | 1.362 | A04 | MICL0.01107026/ROV
Build-In Floor | Mini Canal | MICL.01107026/RSS | 11 | 70 | 26 | 26 | 134 | 134 | 134 | 0.0031905 | 52 | 0.0012381 | 153 | 0.0036429 | 1.362 | A04 | MICL0.01107026/RSS
Build-In Floor | Mini Canal | MICL.01107026/SBL | 11 | 70 | 26 | 26 | 140 | 140 | 140 | 0.0033333 | 54 | 0.0012857 | 159 | 0.0037857 | 1.362 | A04 | MICL0.01107026/SBL
Build-In Floor | Mini Canal | MICL.01107026/SBR | 11 | 70 | 26 | 26 | 140 | 140 | 140 | 0.0033333 | 54 | 0.0012857 | 159 | 0.0037857 | 1.362 | A04 | MICL0.01107026/SBR
Build-In Floor | Mini Canal | MICL.01107026/SDB | 11 | 70 | 26 | 26 | 140 | 140 | 140 | 0.0033333 | 54 | 0.0012857 | 159 | 0.0037857 | 1.362 | A04 | MICL0.01107026/SDB
Build-In Floor | Mini Canal | MICL.01107026/SNA | 11 | 70 | 26 | 26 | 140 | 140 | 140 | 0.0033333 | 54 | 0.0012857 | 159 | 0.0037857 | 1.362 | A04 | MICL0.01107026/SNA
Build-In Floor | Mini Canal | MICL.01107026/SNC | 11 | 70 | 26 | 26 | 140 | 140 | 140 | 0.0033333 | 54 | 0.0012857 | 159 | 0.0037857 | 1.362 | A04 | MICL0.01107026/SNC
Build-In Floor | Mini Canal | MICL.01107034/ANA | 11 | 70 | 34 | 34 | 137 | 137 | 137 | 0.0032619 | 53 | 0.0012619 | 156 | 0.0037143 | 1.362 | A04 | MICL0.01107034/ANA
Build-In Floor | Mini Canal | MICL.01107034/DBL | 11 | 70 | 34 | 34 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.01107034/DBL
Build-In Floor | Mini Canal | MICL.01107034/DBN | 11 | 70 | 34 | 34 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01107034/DBN
Build-In Floor | Mini Canal | MICL.01107034/DBR | 11 | 70 | 34 | 34 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.01107034/DBR
Build-In Floor | Mini Canal | MICL.01107034/DBV | 11 | 70 | 34 | 34 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01107034/DBV
Build-In Floor | Mini Canal | MICL.01107034/DDB | 11 | 70 | 34 | 34 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.01107034/DDB
Build-In Floor | Mini Canal | MICL.01107034/DMN | 11 | 70 | 34 | 34 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01107034/DMN
Build-In Floor | Mini Canal | MICL.01107034/DMV | 11 | 70 | 34 | 34 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01107034/DMV
Build-In Floor | Mini Canal | MICL.01107034/DNA | 11 | 70 | 34 | 34 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.01107034/DNA
Build-In Floor | Mini Canal | MICL.01107034/DNC | 11 | 70 | 34 | 34 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.01107034/DNC
Build-In Floor | Mini Canal | MICL.01107034/DON | 11 | 70 | 34 | 34 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01107034/DON
Build-In Floor | Mini Canal | MICL.01107034/DOV | 11 | 70 | 34 | 34 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01107034/DOV
Build-In Floor | Mini Canal | MICL.01107034/PNC | 11 | 70 | 34 | 34 | 155 | 155 | 155 | 0.0036905 | 60 | 0.0014286 | 177 | 0.0042143 | 1.362 | A04 | MICL0.01107034/PNC
Build-In Floor | Mini Canal | MICL.01107034/RBL | 11 | 70 | 34 | 34 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01107034/RBL
Build-In Floor | Mini Canal | MICL.01107034/RBN | 11 | 70 | 34 | 34 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.01107034/RBN
Build-In Floor | Mini Canal | MICL.01107034/RBR | 11 | 70 | 34 | 34 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01107034/RBR
Build-In Floor | Mini Canal | MICL.01107034/RBV | 11 | 70 | 34 | 34 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.01107034/RBV
Build-In Floor | Mini Canal | MICL.01107034/RDB | 11 | 70 | 34 | 34 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01107034/RDB
Build-In Floor | Mini Canal | MICL.01107034/RMN | 11 | 70 | 34 | 34 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.01107034/RMN
Build-In Floor | Mini Canal | MICL.01107034/RMV | 11 | 70 | 34 | 34 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.01107034/RMV
Build-In Floor | Mini Canal | MICL.01107034/RNA | 11 | 70 | 34 | 34 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01107034/RNA
Build-In Floor | Mini Canal | MICL.01107034/RON | 11 | 70 | 34 | 34 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.01107034/RON
Build-In Floor | Mini Canal | MICL.01107034/ROV | 11 | 70 | 34 | 34 | 177 | 177 | 177 | 0.0042143 | 69 | 0.0016429 | 202 | 0.0048095 | 1.362 | A04 | MICL0.01107034/ROV
Build-In Floor | Mini Canal | MICL.01107034/RSS | 11 | 70 | 34 | 34 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01107034/RSS
Build-In Floor | Mini Canal | MICL.01107034/SBL | 11 | 70 | 34 | 34 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01107034/SBL
Build-In Floor | Mini Canal | MICL.01107034/SBR | 11 | 70 | 34 | 34 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01107034/SBR
Build-In Floor | Mini Canal | MICL.01107034/SDB | 11 | 70 | 34 | 34 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01107034/SDB
Build-In Floor | Mini Canal | MICL.01107034/SNA | 11 | 70 | 34 | 34 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01107034/SNA
Build-In Floor | Mini Canal | MICL.01107034/SNC | 11 | 70 | 34 | 34 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01107034/SNC
Build-In Floor | Mini Canal | MICL.01107042/ANA | 11 | 70 | 42 | 42 | 191 | 191 | 191 | 0.0045476 | 74 | 0.0017619 | 218 | 0.0051905 | 1.362 | A04 | MICL0.01107042/ANA
Build-In Floor | Mini Canal | MICL.01107042/DBL | 11 | 70 | 42 | 42 | 247 | 247 | 247 | 0.005881 | 96 | 0.0022857 | 281 | 0.0066905 | 1.362 | A04 | MICL0.01107042/DBL
Build-In Floor | Mini Canal | MICL.01107042/DBN | 11 | 70 | 42 | 42 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.01107042/DBN
Build-In Floor | Mini Canal | MICL.01107042/DBR | 11 | 70 | 42 | 42 | 247 | 247 | 247 | 0.005881 | 96 | 0.0022857 | 281 | 0.0066905 | 1.362 | A04 | MICL0.01107042/DBR
Build-In Floor | Mini Canal | MICL.01107042/DBV | 11 | 70 | 42 | 42 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.01107042/DBV
Build-In Floor | Mini Canal | MICL.01107042/DDB | 11 | 70 | 42 | 42 | 247 | 247 | 247 | 0.005881 | 96 | 0.0022857 | 281 | 0.0066905 | 1.362 | A04 | MICL0.01107042/DDB
Build-In Floor | Mini Canal | MICL.01107042/DMN | 11 | 70 | 42 | 42 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.01107042/DMN
Build-In Floor | Mini Canal | MICL.01107042/DMV | 11 | 70 | 42 | 42 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.01107042/DMV
Build-In Floor | Mini Canal | MICL.01107042/DNA | 11 | 70 | 42 | 42 | 247 | 247 | 247 | 0.005881 | 96 | 0.0022857 | 281 | 0.0066905 | 1.362 | A04 | MICL0.01107042/DNA
Build-In Floor | Mini Canal | MICL.01107042/DNC | 11 | 70 | 42 | 42 | 247 | 247 | 247 | 0.005881 | 96 | 0.0022857 | 281 | 0.0066905 | 1.362 | A04 | MICL0.01107042/DNC
Build-In Floor | Mini Canal | MICL.01107042/DON | 11 | 70 | 42 | 42 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.01107042/DON
Build-In Floor | Mini Canal | MICL.01107042/DOV | 11 | 70 | 42 | 42 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.01107042/DOV
Build-In Floor | Mini Canal | MICL.01107042/PNC | 11 | 70 | 42 | 42 | 217 | 217 | 217 | 0.0051667 | 84 | 0.002 | 247 | 0.005881 | 1.362 | A04 | MICL0.01107042/PNC
Build-In Floor | Mini Canal | MICL.01107042/RBL | 11 | 70 | 42 | 42 | 255 | 255 | 255 | 0.0060714 | 99 | 0.0023571 | 290 | 0.0069048 | 1.362 | A04 | MICL0.01107042/RBL
Build-In Floor | Mini Canal | MICL.01107042/RBN | 11 | 70 | 42 | 42 | 247 | 247 | 247 | 0.005881 | 96 | 0.0022857 | 281 | 0.0066905 | 1.362 | A04 | MICL0.01107042/RBN
Build-In Floor | Mini Canal | MICL.01107042/RBR | 11 | 70 | 42 | 42 | 255 | 255 | 255 | 0.0060714 | 99 | 0.0023571 | 290 | 0.0069048 | 1.362 | A04 | MICL0.01107042/RBR
Build-In Floor | Mini Canal | MICL.01107042/RBV | 11 | 70 | 42 | 42 | 247 | 247 | 247 | 0.005881 | 96 | 0.0022857 | 281 | 0.0066905 | 1.362 | A04 | MICL0.01107042/RBV
Build-In Floor | Mini Canal | MICL.01107042/RDB | 11 | 70 | 42 | 42 | 255 | 255 | 255 | 0.0060714 | 99 | 0.0023571 | 290 | 0.0069048 | 1.362 | A04 | MICL0.01107042/RDB
Build-In Floor | Mini Canal | MICL.01107042/RMN | 11 | 70 | 42 | 42 | 247 | 247 | 247 | 0.005881 | 96 | 0.0022857 | 281 | 0.0066905 | 1.362 | A04 | MICL0.01107042/RMN
Build-In Floor | Mini Canal | MICL.01107042/RMV | 11 | 70 | 42 | 42 | 247 | 247 | 247 | 0.005881 | 96 | 0.0022857 | 281 | 0.0066905 | 1.362 | A04 | MICL0.01107042/RMV
Build-In Floor | Mini Canal | MICL.01107042/RNA | 11 | 70 | 42 | 42 | 255 | 255 | 255 | 0.0060714 | 99 | 0.0023571 | 290 | 0.0069048 | 1.362 | A04 | MICL0.01107042/RNA
Build-In Floor | Mini Canal | MICL.01107042/RON | 11 | 70 | 42 | 42 | 247 | 247 | 247 | 0.005881 | 96 | 0.0022857 | 281 | 0.0066905 | 1.362 | A04 | MICL0.01107042/RON
Build-In Floor | Mini Canal | MICL.01107042/ROV | 11 | 70 | 42 | 42 | 247 | 247 | 247 | 0.005881 | 96 | 0.0022857 | 281 | 0.0066905 | 1.362 | A04 | MICL0.01107042/ROV
Build-In Floor | Mini Canal | MICL.01107042/RSS | 11 | 70 | 42 | 42 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01107042/RSS
Build-In Floor | Mini Canal | MICL.01107042/SBL | 11 | 70 | 42 | 42 | 255 | 255 | 255 | 0.0060714 | 99 | 0.0023571 | 290 | 0.0069048 | 1.362 | A04 | MICL0.01107042/SBL
Build-In Floor | Mini Canal | MICL.01107042/SBR | 11 | 70 | 42 | 42 | 255 | 255 | 255 | 0.0060714 | 99 | 0.0023571 | 290 | 0.0069048 | 1.362 | A04 | MICL0.01107042/SBR
Build-In Floor | Mini Canal | MICL.01107042/SDB | 11 | 70 | 42 | 42 | 255 | 255 | 255 | 0.0060714 | 99 | 0.0023571 | 290 | 0.0069048 | 1.362 | A04 | MICL0.01107042/SDB
Build-In Floor | Mini Canal | MICL.01107042/SNA | 11 | 70 | 42 | 42 | 255 | 255 | 255 | 0.0060714 | 99 | 0.0023571 | 290 | 0.0069048 | 1.362 | A04 | MICL0.01107042/SNA
Build-In Floor | Mini Canal | MICL.01107042/SNC | 11 | 70 | 42 | 42 | 255 | 255 | 255 | 0.0060714 | 99 | 0.0023571 | 290 | 0.0069048 | 1.362 | A04 | MICL0.01107042/SNC
Build-In Floor | Mini Canal | MICL.01108014/ANA | 11 | 80 | 14 | 14 | 82 | 82 | 82 | 0.0019524 | 32 | 0.0007619 | 93 | 0.0022143 | 1.362 | A04 | MICL0.01108014/ANA
Build-In Floor | Mini Canal | MICL.01108014/DBL | 11 | 80 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.01108014/DBL
Build-In Floor | Mini Canal | MICL.01108014/DBN | 11 | 80 | 14 | 14 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01108014/DBN
Build-In Floor | Mini Canal | MICL.01108014/DBR | 11 | 80 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.01108014/DBR
Build-In Floor | Mini Canal | MICL.01108014/DBV | 11 | 80 | 14 | 14 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01108014/DBV
Build-In Floor | Mini Canal | MICL.01108014/DDB | 11 | 80 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.01108014/DDB
Build-In Floor | Mini Canal | MICL.01108014/DMN | 11 | 80 | 14 | 14 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01108014/DMN
Build-In Floor | Mini Canal | MICL.01108014/DMV | 11 | 80 | 14 | 14 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01108014/DMV
Build-In Floor | Mini Canal | MICL.01108014/DNA | 11 | 80 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.01108014/DNA
Build-In Floor | Mini Canal | MICL.01108014/DNC | 11 | 80 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.01108014/DNC
Build-In Floor | Mini Canal | MICL.01108014/DON | 11 | 80 | 14 | 14 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01108014/DON
Build-In Floor | Mini Canal | MICL.01108014/DOV | 11 | 80 | 14 | 14 | 101 | 101 | 101 | 0.0024048 | 39 | 0.00092857 | 115 | 0.0027381 | 1.362 | A04 | MICL0.01108014/DOV
Build-In Floor | Mini Canal | MICL.01108014/RBL | 11 | 80 | 14 | 14 | 109 | 109 | 109 | 0.0025952 | 42 | 0.001 | 124 | 0.0029524 | 1.362 | A04 | MICL0.01108014/RBL
Build-In Floor | Mini Canal | MICL.01108014/RBN | 11 | 80 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.01108014/RBN
Build-In Floor | Mini Canal | MICL.01108014/RBR | 11 | 80 | 14 | 14 | 109 | 109 | 109 | 0.0025952 | 42 | 0.001 | 124 | 0.0029524 | 1.362 | A04 | MICL0.01108014/RBR
Build-In Floor | Mini Canal | MICL.01108014/RBV | 11 | 80 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.01108014/RBV
Build-In Floor | Mini Canal | MICL.01108014/RDB | 11 | 80 | 14 | 14 | 109 | 109 | 109 | 0.0025952 | 42 | 0.001 | 124 | 0.0029524 | 1.362 | A04 | MICL0.01108014/RDB
Build-In Floor | Mini Canal | MICL.01108014/RMN | 11 | 80 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.01108014/RMN
Build-In Floor | Mini Canal | MICL.01108014/RMV | 11 | 80 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.01108014/RMV
Build-In Floor | Mini Canal | MICL.01108014/RNA | 11 | 80 | 14 | 14 | 109 | 109 | 109 | 0.0025952 | 42 | 0.001 | 124 | 0.0029524 | 1.362 | A04 | MICL0.01108014/RNA
Build-In Floor | Mini Canal | MICL.01108014/RON | 11 | 80 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.01108014/RON
Build-In Floor | Mini Canal | MICL.01108014/ROV | 11 | 80 | 14 | 14 | 106 | 106 | 106 | 0.0025238 | 41 | 0.00097619 | 121 | 0.002881 | 1.362 | A04 | MICL0.01108014/ROV
Build-In Floor | Mini Canal | MICL.01108014/RSS | 11 | 80 | 14 | 14 | 105 | 105 | 105 | 0.0025 | 41 | 0.00097619 | 120 | 0.0028571 | 1.362 | A04 | MICL0.01108014/RSS
Build-In Floor | Mini Canal | MICL.01108014/SBL | 11 | 80 | 14 | 14 | 109 | 109 | 109 | 0.0025952 | 42 | 0.001 | 124 | 0.0029524 | 1.362 | A04 | MICL0.01108014/SBL
Build-In Floor | Mini Canal | MICL.01108014/SBR | 11 | 80 | 14 | 14 | 109 | 109 | 109 | 0.0025952 | 42 | 0.001 | 124 | 0.0029524 | 1.362 | A04 | MICL0.01108014/SBR
Build-In Floor | Mini Canal | MICL.01108014/SDB | 11 | 80 | 14 | 14 | 109 | 109 | 109 | 0.0025952 | 42 | 0.001 | 124 | 0.0029524 | 1.362 | A04 | MICL0.01108014/SDB
Build-In Floor | Mini Canal | MICL.01108014/SNA | 11 | 80 | 14 | 14 | 109 | 109 | 109 | 0.0025952 | 42 | 0.001 | 124 | 0.0029524 | 1.362 | A04 | MICL0.01108014/SNA
Build-In Floor | Mini Canal | MICL.01108014/SNC | 11 | 80 | 14 | 14 | 109 | 109 | 109 | 0.0025952 | 42 | 0.001 | 124 | 0.0029524 | 1.362 | A04 | MICL0.01108014/SNC
Build-In Floor | Mini Canal | MICL.01108018/ANA | 11 | 80 | 18 | 18 | 97 | 97 | 97 | 0.0023095 | 38 | 0.00090476 | 110 | 0.002619 | 1.362 | A04 | MICL0.01108018/ANA
Build-In Floor | Mini Canal | MICL.01108018/DBL | 11 | 80 | 18 | 18 | 125 | 125 | 125 | 0.0029762 | 49 | 0.0011667 | 142 | 0.003381 | 1.362 | A04 | MICL0.01108018/DBL
Build-In Floor | Mini Canal | MICL.01108018/DBN | 11 | 80 | 18 | 18 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01108018/DBN
Build-In Floor | Mini Canal | MICL.01108018/DBR | 11 | 80 | 18 | 18 | 125 | 125 | 125 | 0.0029762 | 49 | 0.0011667 | 142 | 0.003381 | 1.362 | A04 | MICL0.01108018/DBR
Build-In Floor | Mini Canal | MICL.01108018/DBV | 11 | 80 | 18 | 18 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01108018/DBV
Build-In Floor | Mini Canal | MICL.01108018/DDB | 11 | 80 | 18 | 18 | 125 | 125 | 125 | 0.0029762 | 49 | 0.0011667 | 142 | 0.003381 | 1.362 | A04 | MICL0.01108018/DDB
Build-In Floor | Mini Canal | MICL.01108018/DMN | 11 | 80 | 18 | 18 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01108018/DMN
Build-In Floor | Mini Canal | MICL.01108018/DMV | 11 | 80 | 18 | 18 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01108018/DMV
Build-In Floor | Mini Canal | MICL.01108018/DNA | 11 | 80 | 18 | 18 | 125 | 125 | 125 | 0.0029762 | 49 | 0.0011667 | 142 | 0.003381 | 1.362 | A04 | MICL0.01108018/DNA
Build-In Floor | Mini Canal | MICL.01108018/DNC | 11 | 80 | 18 | 18 | 125 | 125 | 125 | 0.0029762 | 49 | 0.0011667 | 142 | 0.003381 | 1.362 | A04 | MICL0.01108018/DNC
Build-In Floor | Mini Canal | MICL.01108018/DON | 11 | 80 | 18 | 18 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01108018/DON
Build-In Floor | Mini Canal | MICL.01108018/DOV | 11 | 80 | 18 | 18 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01108018/DOV
Build-In Floor | Mini Canal | MICL.01108018/RBL | 11 | 80 | 18 | 18 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.01108018/RBL
Build-In Floor | Mini Canal | MICL.01108018/RBN | 11 | 80 | 18 | 18 | 125 | 125 | 125 | 0.0029762 | 49 | 0.0011667 | 142 | 0.003381 | 1.362 | A04 | MICL0.01108018/RBN
Build-In Floor | Mini Canal | MICL.01108018/RBR | 11 | 80 | 18 | 18 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.01108018/RBR
Build-In Floor | Mini Canal | MICL.01108018/RBV | 11 | 80 | 18 | 18 | 125 | 125 | 125 | 0.0029762 | 49 | 0.0011667 | 142 | 0.003381 | 1.362 | A04 | MICL0.01108018/RBV
Build-In Floor | Mini Canal | MICL.01108018/RDB | 11 | 80 | 18 | 18 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.01108018/RDB
Build-In Floor | Mini Canal | MICL.01108018/RMN | 11 | 80 | 18 | 18 | 125 | 125 | 125 | 0.0029762 | 49 | 0.0011667 | 142 | 0.003381 | 1.362 | A04 | MICL0.01108018/RMN
Build-In Floor | Mini Canal | MICL.01108018/RMV | 11 | 80 | 18 | 18 | 125 | 125 | 125 | 0.0029762 | 49 | 0.0011667 | 142 | 0.003381 | 1.362 | A04 | MICL0.01108018/RMV
Build-In Floor | Mini Canal | MICL.01108018/RNA | 11 | 80 | 18 | 18 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.01108018/RNA
Build-In Floor | Mini Canal | MICL.01108018/RON | 11 | 80 | 18 | 18 | 125 | 125 | 125 | 0.0029762 | 49 | 0.0011667 | 142 | 0.003381 | 1.362 | A04 | MICL0.01108018/RON
Build-In Floor | Mini Canal | MICL.01108018/ROV | 11 | 80 | 18 | 18 | 125 | 125 | 125 | 0.0029762 | 49 | 0.0011667 | 142 | 0.003381 | 1.362 | A04 | MICL0.01108018/ROV
Build-In Floor | Mini Canal | MICL.01108018/RSS | 11 | 80 | 18 | 18 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.01108018/RSS
Build-In Floor | Mini Canal | MICL.01108018/SBL | 11 | 80 | 18 | 18 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.01108018/SBL
Build-In Floor | Mini Canal | MICL.01108018/SBR | 11 | 80 | 18 | 18 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.01108018/SBR
Build-In Floor | Mini Canal | MICL.01108018/SDB | 11 | 80 | 18 | 18 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.01108018/SDB
Build-In Floor | Mini Canal | MICL.01108018/SNA | 11 | 80 | 18 | 18 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.01108018/SNA
Build-In Floor | Mini Canal | MICL.01108018/SNC | 11 | 80 | 18 | 18 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.01108018/SNC
Build-In Floor | Mini Canal | MICL.01108026/ANA | 11 | 80 | 26 | 26 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.01108026/ANA
Build-In Floor | Mini Canal | MICL.01108026/DBL | 11 | 80 | 26 | 26 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01108026/DBL
Build-In Floor | Mini Canal | MICL.01108026/DBN | 11 | 80 | 26 | 26 | 163 | 163 | 163 | 0.003881 | 63 | 0.0015 | 186 | 0.0044286 | 1.362 | A04 | MICL0.01108026/DBN
Build-In Floor | Mini Canal | MICL.01108026/DBR | 11 | 80 | 26 | 26 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01108026/DBR
Build-In Floor | Mini Canal | MICL.01108026/DBV | 11 | 80 | 26 | 26 | 163 | 163 | 163 | 0.003881 | 63 | 0.0015 | 186 | 0.0044286 | 1.362 | A04 | MICL0.01108026/DBV
Build-In Floor | Mini Canal | MICL.01108026/DDB | 11 | 80 | 26 | 26 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01108026/DDB
Build-In Floor | Mini Canal | MICL.01108026/DMN | 11 | 80 | 26 | 26 | 163 | 163 | 163 | 0.003881 | 63 | 0.0015 | 186 | 0.0044286 | 1.362 | A04 | MICL0.01108026/DMN
Build-In Floor | Mini Canal | MICL.01108026/DMV | 11 | 80 | 26 | 26 | 163 | 163 | 163 | 0.003881 | 63 | 0.0015 | 186 | 0.0044286 | 1.362 | A04 | MICL0.01108026/DMV
Build-In Floor | Mini Canal | MICL.01108026/DNA | 11 | 80 | 26 | 26 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01108026/DNA
Build-In Floor | Mini Canal | MICL.01108026/DNC | 11 | 80 | 26 | 26 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01108026/DNC
Build-In Floor | Mini Canal | MICL.01108026/DON | 11 | 80 | 26 | 26 | 163 | 163 | 163 | 0.003881 | 63 | 0.0015 | 186 | 0.0044286 | 1.362 | A04 | MICL0.01108026/DON
Build-In Floor | Mini Canal | MICL.01108026/DOV | 11 | 80 | 26 | 26 | 163 | 163 | 163 | 0.003881 | 63 | 0.0015 | 186 | 0.0044286 | 1.362 | A04 | MICL0.01108026/DOV
Build-In Floor | Mini Canal | MICL.01108026/PNC | 11 | 80 | 26 | 26 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.01108026/PNC
Build-In Floor | Mini Canal | MICL.01108026/RBL | 11 | 80 | 26 | 26 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01108026/RBL
Build-In Floor | Mini Canal | MICL.01108026/RBN | 11 | 80 | 26 | 26 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01108026/RBN
Build-In Floor | Mini Canal | MICL.01108026/RBR | 11 | 80 | 26 | 26 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01108026/RBR
Build-In Floor | Mini Canal | MICL.01108026/RBV | 11 | 80 | 26 | 26 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01108026/RBV
Build-In Floor | Mini Canal | MICL.01108026/RDB | 11 | 80 | 26 | 26 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01108026/RDB
Build-In Floor | Mini Canal | MICL.01108026/RMN | 11 | 80 | 26 | 26 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01108026/RMN
Build-In Floor | Mini Canal | MICL.01108026/RMV | 11 | 80 | 26 | 26 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01108026/RMV
Build-In Floor | Mini Canal | MICL.01108026/RNA | 11 | 80 | 26 | 26 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01108026/RNA
Build-In Floor | Mini Canal | MICL.01108026/RON | 11 | 80 | 26 | 26 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01108026/RON
Build-In Floor | Mini Canal | MICL.01108026/ROV | 11 | 80 | 26 | 26 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01108026/ROV
Build-In Floor | Mini Canal | MICL.01108026/RSS | 11 | 80 | 26 | 26 | 168 | 168 | 168 | 0.004 | 65 | 0.0015476 | 191 | 0.0045476 | 1.362 | A04 | MICL0.01108026/RSS
Build-In Floor | Mini Canal | MICL.01108026/SBL | 11 | 80 | 26 | 26 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01108026/SBL
Build-In Floor | Mini Canal | MICL.01108026/SBR | 11 | 80 | 26 | 26 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01108026/SBR
Build-In Floor | Mini Canal | MICL.01108026/SDB | 11 | 80 | 26 | 26 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01108026/SDB
Build-In Floor | Mini Canal | MICL.01108026/SNA | 11 | 80 | 26 | 26 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01108026/SNA
Build-In Floor | Mini Canal | MICL.01108026/SNC | 11 | 80 | 26 | 26 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01108026/SNC
Build-In Floor | Mini Canal | MICL.01108034/ANA | 11 | 80 | 34 | 34 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01108034/ANA
Build-In Floor | Mini Canal | MICL.01108034/DBL | 11 | 80 | 34 | 34 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.01108034/DBL
Build-In Floor | Mini Canal | MICL.01108034/DBN | 11 | 80 | 34 | 34 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01108034/DBN
Build-In Floor | Mini Canal | MICL.01108034/DBR | 11 | 80 | 34 | 34 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.01108034/DBR
Build-In Floor | Mini Canal | MICL.01108034/DBV | 11 | 80 | 34 | 34 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01108034/DBV
Build-In Floor | Mini Canal | MICL.01108034/DDB | 11 | 80 | 34 | 34 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.01108034/DDB
Build-In Floor | Mini Canal | MICL.01108034/DMN | 11 | 80 | 34 | 34 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01108034/DMN
Build-In Floor | Mini Canal | MICL.01108034/DMV | 11 | 80 | 34 | 34 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01108034/DMV
Build-In Floor | Mini Canal | MICL.01108034/DNA | 11 | 80 | 34 | 34 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.01108034/DNA
Build-In Floor | Mini Canal | MICL.01108034/DNC | 11 | 80 | 34 | 34 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.01108034/DNC
Build-In Floor | Mini Canal | MICL.01108034/DON | 11 | 80 | 34 | 34 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01108034/DON
Build-In Floor | Mini Canal | MICL.01108034/DOV | 11 | 80 | 34 | 34 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01108034/DOV
Build-In Floor | Mini Canal | MICL.01108034/PNC | 11 | 80 | 34 | 34 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.01108034/PNC
Build-In Floor | Mini Canal | MICL.01108034/RBL | 11 | 80 | 34 | 34 | 227 | 227 | 227 | 0.0054048 | 88 | 0.0020952 | 259 | 0.0061667 | 1.362 | A04 | MICL0.01108034/RBL
Build-In Floor | Mini Canal | MICL.01108034/RBN | 11 | 80 | 34 | 34 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.01108034/RBN
Build-In Floor | Mini Canal | MICL.01108034/RBR | 11 | 80 | 34 | 34 | 227 | 227 | 227 | 0.0054048 | 88 | 0.0020952 | 259 | 0.0061667 | 1.362 | A04 | MICL0.01108034/RBR
Build-In Floor | Mini Canal | MICL.01108034/RBV | 11 | 80 | 34 | 34 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.01108034/RBV
Build-In Floor | Mini Canal | MICL.01108034/RDB | 11 | 80 | 34 | 34 | 227 | 227 | 227 | 0.0054048 | 88 | 0.0020952 | 259 | 0.0061667 | 1.362 | A04 | MICL0.01108034/RDB
Build-In Floor | Mini Canal | MICL.01108034/RMN | 11 | 80 | 34 | 34 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.01108034/RMN
Build-In Floor | Mini Canal | MICL.01108034/RMV | 11 | 80 | 34 | 34 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.01108034/RMV
Build-In Floor | Mini Canal | MICL.01108034/RNA | 11 | 80 | 34 | 34 | 227 | 227 | 227 | 0.0054048 | 88 | 0.0020952 | 259 | 0.0061667 | 1.362 | A04 | MICL0.01108034/RNA
Build-In Floor | Mini Canal | MICL.01108034/RON | 11 | 80 | 34 | 34 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.01108034/RON
Build-In Floor | Mini Canal | MICL.01108034/ROV | 11 | 80 | 34 | 34 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.01108034/ROV
Build-In Floor | Mini Canal | MICL.01108034/RSS | 11 | 80 | 34 | 34 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.01108034/RSS
Build-In Floor | Mini Canal | MICL.01108034/SBL | 11 | 80 | 34 | 34 | 227 | 227 | 227 | 0.0054048 | 88 | 0.0020952 | 259 | 0.0061667 | 1.362 | A04 | MICL0.01108034/SBL
Build-In Floor | Mini Canal | MICL.01108034/SBR | 11 | 80 | 34 | 34 | 227 | 227 | 227 | 0.0054048 | 88 | 0.0020952 | 259 | 0.0061667 | 1.362 | A04 | MICL0.01108034/SBR
Build-In Floor | Mini Canal | MICL.01108034/SDB | 11 | 80 | 34 | 34 | 227 | 227 | 227 | 0.0054048 | 88 | 0.0020952 | 259 | 0.0061667 | 1.362 | A04 | MICL0.01108034/SDB
Build-In Floor | Mini Canal | MICL.01108034/SNA | 11 | 80 | 34 | 34 | 227 | 227 | 227 | 0.0054048 | 88 | 0.0020952 | 259 | 0.0061667 | 1.362 | A04 | MICL0.01108034/SNA
Build-In Floor | Mini Canal | MICL.01108034/SNC | 11 | 80 | 34 | 34 | 227 | 227 | 227 | 0.0054048 | 88 | 0.0020952 | 259 | 0.0061667 | 1.362 | A04 | MICL0.01108034/SNC
Build-In Floor | Mini Canal | MICL.01108042/ANA | 11 | 80 | 42 | 42 | 239 | 239 | 239 | 0.0056905 | 93 | 0.0022143 | 272 | 0.0064762 | 1.362 | A04 | MICL0.01108042/ANA
Build-In Floor | Mini Canal | MICL.01108042/DBL | 11 | 80 | 42 | 42 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01108042/DBL
Build-In Floor | Mini Canal | MICL.01108042/DBN | 11 | 80 | 42 | 42 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01108042/DBN
Build-In Floor | Mini Canal | MICL.01108042/DBR | 11 | 80 | 42 | 42 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01108042/DBR
Build-In Floor | Mini Canal | MICL.01108042/DBV | 11 | 80 | 42 | 42 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01108042/DBV
Build-In Floor | Mini Canal | MICL.01108042/DDB | 11 | 80 | 42 | 42 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01108042/DDB
Build-In Floor | Mini Canal | MICL.01108042/DMN | 11 | 80 | 42 | 42 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01108042/DMN
Build-In Floor | Mini Canal | MICL.01108042/DMV | 11 | 80 | 42 | 42 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01108042/DMV
Build-In Floor | Mini Canal | MICL.01108042/DNA | 11 | 80 | 42 | 42 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01108042/DNA
Build-In Floor | Mini Canal | MICL.01108042/DNC | 11 | 80 | 42 | 42 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01108042/DNC
Build-In Floor | Mini Canal | MICL.01108042/DON | 11 | 80 | 42 | 42 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01108042/DON
Build-In Floor | Mini Canal | MICL.01108042/DOV | 11 | 80 | 42 | 42 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01108042/DOV
Build-In Floor | Mini Canal | MICL.01108042/PNC | 11 | 80 | 42 | 42 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.01108042/PNC
Build-In Floor | Mini Canal | MICL.01108042/RBL | 11 | 80 | 42 | 42 | 319 | 319 | 319 | 0.0075952 | 124 | 0.0029524 | 363 | 0.0086429 | 1.362 | A04 | MICL0.01108042/RBL
Build-In Floor | Mini Canal | MICL.01108042/RBN | 11 | 80 | 42 | 42 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01108042/RBN
Build-In Floor | Mini Canal | MICL.01108042/RBR | 11 | 80 | 42 | 42 | 319 | 319 | 319 | 0.0075952 | 124 | 0.0029524 | 363 | 0.0086429 | 1.362 | A04 | MICL0.01108042/RBR
Build-In Floor | Mini Canal | MICL.01108042/RBV | 11 | 80 | 42 | 42 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01108042/RBV
Build-In Floor | Mini Canal | MICL.01108042/RDB | 11 | 80 | 42 | 42 | 319 | 319 | 319 | 0.0075952 | 124 | 0.0029524 | 363 | 0.0086429 | 1.362 | A04 | MICL0.01108042/RDB
Build-In Floor | Mini Canal | MICL.01108042/RMN | 11 | 80 | 42 | 42 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01108042/RMN
Build-In Floor | Mini Canal | MICL.01108042/RMV | 11 | 80 | 42 | 42 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01108042/RMV
Build-In Floor | Mini Canal | MICL.01108042/RNA | 11 | 80 | 42 | 42 | 319 | 319 | 319 | 0.0075952 | 124 | 0.0029524 | 363 | 0.0086429 | 1.362 | A04 | MICL0.01108042/RNA
Build-In Floor | Mini Canal | MICL.01108042/RON | 11 | 80 | 42 | 42 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01108042/RON
Build-In Floor | Mini Canal | MICL.01108042/ROV | 11 | 80 | 42 | 42 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01108042/ROV
Build-In Floor | Mini Canal | MICL.01108042/RSS | 11 | 80 | 42 | 42 | 306 | 306 | 306 | 0.0072857 | 119 | 0.0028333 | 349 | 0.0083095 | 1.362 | A04 | MICL0.01108042/RSS
Build-In Floor | Mini Canal | MICL.01108042/SBL | 11 | 80 | 42 | 42 | 319 | 319 | 319 | 0.0075952 | 124 | 0.0029524 | 363 | 0.0086429 | 1.362 | A04 | MICL0.01108042/SBL
Build-In Floor | Mini Canal | MICL.01108042/SBR | 11 | 80 | 42 | 42 | 319 | 319 | 319 | 0.0075952 | 124 | 0.0029524 | 363 | 0.0086429 | 1.362 | A04 | MICL0.01108042/SBR
Build-In Floor | Mini Canal | MICL.01108042/SDB | 11 | 80 | 42 | 42 | 319 | 319 | 319 | 0.0075952 | 124 | 0.0029524 | 363 | 0.0086429 | 1.362 | A04 | MICL0.01108042/SDB
Build-In Floor | Mini Canal | MICL.01108042/SNA | 11 | 80 | 42 | 42 | 319 | 319 | 319 | 0.0075952 | 124 | 0.0029524 | 363 | 0.0086429 | 1.362 | A04 | MICL0.01108042/SNA
Build-In Floor | Mini Canal | MICL.01108042/SNC | 11 | 80 | 42 | 42 | 319 | 319 | 319 | 0.0075952 | 124 | 0.0029524 | 363 | 0.0086429 | 1.362 | A04 | MICL0.01108042/SNC
Build-In Floor | Mini Canal | MICL.01109014/ANA | 11 | 90 | 14 | 14 | 98 | 98 | 98 | 0.0023333 | 38 | 0.00090476 | 112 | 0.0026667 | 1.362 | A04 | MICL0.01109014/ANA
Build-In Floor | Mini Canal | MICL.01109014/DBL | 11 | 90 | 14 | 14 | 127 | 127 | 127 | 0.0030238 | 49 | 0.0011667 | 145 | 0.0034524 | 1.362 | A04 | MICL0.01109014/DBL
Build-In Floor | Mini Canal | MICL.01109014/DBN | 11 | 90 | 14 | 14 | 122 | 122 | 122 | 0.0029048 | 47 | 0.001119 | 139 | 0.0033095 | 1.362 | A04 | MICL0.01109014/DBN
Build-In Floor | Mini Canal | MICL.01109014/DBR | 11 | 90 | 14 | 14 | 127 | 127 | 127 | 0.0030238 | 49 | 0.0011667 | 145 | 0.0034524 | 1.362 | A04 | MICL0.01109014/DBR
Build-In Floor | Mini Canal | MICL.01109014/DBV | 11 | 90 | 14 | 14 | 122 | 122 | 122 | 0.0029048 | 47 | 0.001119 | 139 | 0.0033095 | 1.362 | A04 | MICL0.01109014/DBV
Build-In Floor | Mini Canal | MICL.01109014/DDB | 11 | 90 | 14 | 14 | 127 | 127 | 127 | 0.0030238 | 49 | 0.0011667 | 145 | 0.0034524 | 1.362 | A04 | MICL0.01109014/DDB
Build-In Floor | Mini Canal | MICL.01109014/DMN | 11 | 90 | 14 | 14 | 122 | 122 | 122 | 0.0029048 | 47 | 0.001119 | 139 | 0.0033095 | 1.362 | A04 | MICL0.01109014/DMN
Build-In Floor | Mini Canal | MICL.01109014/DMV | 11 | 90 | 14 | 14 | 122 | 122 | 122 | 0.0029048 | 47 | 0.001119 | 139 | 0.0033095 | 1.362 | A04 | MICL0.01109014/DMV
Build-In Floor | Mini Canal | MICL.01109014/DNA | 11 | 90 | 14 | 14 | 127 | 127 | 127 | 0.0030238 | 49 | 0.0011667 | 145 | 0.0034524 | 1.362 | A04 | MICL0.01109014/DNA
Build-In Floor | Mini Canal | MICL.01109014/DNC | 11 | 90 | 14 | 14 | 127 | 127 | 127 | 0.0030238 | 49 | 0.0011667 | 145 | 0.0034524 | 1.362 | A04 | MICL0.01109014/DNC
Build-In Floor | Mini Canal | MICL.01109014/DON | 11 | 90 | 14 | 14 | 122 | 122 | 122 | 0.0029048 | 47 | 0.001119 | 139 | 0.0033095 | 1.362 | A04 | MICL0.01109014/DON
Build-In Floor | Mini Canal | MICL.01109014/DOV | 11 | 90 | 14 | 14 | 122 | 122 | 122 | 0.0029048 | 47 | 0.001119 | 139 | 0.0033095 | 1.362 | A04 | MICL0.01109014/DOV
Build-In Floor | Mini Canal | MICL.01109014/RBL | 11 | 90 | 14 | 14 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.01109014/RBL
Build-In Floor | Mini Canal | MICL.01109014/RBN | 11 | 90 | 14 | 14 | 127 | 127 | 127 | 0.0030238 | 49 | 0.0011667 | 145 | 0.0034524 | 1.362 | A04 | MICL0.01109014/RBN
Build-In Floor | Mini Canal | MICL.01109014/RBR | 11 | 90 | 14 | 14 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.01109014/RBR
Build-In Floor | Mini Canal | MICL.01109014/RBV | 11 | 90 | 14 | 14 | 127 | 127 | 127 | 0.0030238 | 49 | 0.0011667 | 145 | 0.0034524 | 1.362 | A04 | MICL0.01109014/RBV
Build-In Floor | Mini Canal | MICL.01109014/RDB | 11 | 90 | 14 | 14 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.01109014/RDB
Build-In Floor | Mini Canal | MICL.01109014/RMN | 11 | 90 | 14 | 14 | 127 | 127 | 127 | 0.0030238 | 49 | 0.0011667 | 145 | 0.0034524 | 1.362 | A04 | MICL0.01109014/RMN
Build-In Floor | Mini Canal | MICL.01109014/RMV | 11 | 90 | 14 | 14 | 127 | 127 | 127 | 0.0030238 | 49 | 0.0011667 | 145 | 0.0034524 | 1.362 | A04 | MICL0.01109014/RMV
Build-In Floor | Mini Canal | MICL.01109014/RNA | 11 | 90 | 14 | 14 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.01109014/RNA
Build-In Floor | Mini Canal | MICL.01109014/RON | 11 | 90 | 14 | 14 | 127 | 127 | 127 | 0.0030238 | 49 | 0.0011667 | 145 | 0.0034524 | 1.362 | A04 | MICL0.01109014/RON
Build-In Floor | Mini Canal | MICL.01109014/ROV | 11 | 90 | 14 | 14 | 127 | 127 | 127 | 0.0030238 | 49 | 0.0011667 | 145 | 0.0034524 | 1.362 | A04 | MICL0.01109014/ROV
Build-In Floor | Mini Canal | MICL.01109014/RSS | 11 | 90 | 14 | 14 | 126 | 126 | 126 | 0.003 | 49 | 0.0011667 | 144 | 0.0034286 | 1.362 | A04 | MICL0.01109014/RSS
Build-In Floor | Mini Canal | MICL.01109014/SBL | 11 | 90 | 14 | 14 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.01109014/SBL
Build-In Floor | Mini Canal | MICL.01109014/SBR | 11 | 90 | 14 | 14 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.01109014/SBR
Build-In Floor | Mini Canal | MICL.01109014/SDB | 11 | 90 | 14 | 14 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.01109014/SDB
Build-In Floor | Mini Canal | MICL.01109014/SNA | 11 | 90 | 14 | 14 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.01109014/SNA
Build-In Floor | Mini Canal | MICL.01109014/SNC | 11 | 90 | 14 | 14 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.01109014/SNC
Build-In Floor | Mini Canal | MICL.01109018/ANA | 11 | 90 | 18 | 18 | 116 | 116 | 116 | 0.0027619 | 45 | 0.0010714 | 132 | 0.0031429 | 1.362 | A04 | MICL0.01109018/ANA
Build-In Floor | Mini Canal | MICL.01109018/DBL | 11 | 90 | 18 | 18 | 150 | 150 | 150 | 0.0035714 | 58 | 0.001381 | 171 | 0.0040714 | 1.362 | A04 | MICL0.01109018/DBL
Build-In Floor | Mini Canal | MICL.01109018/DBN | 11 | 90 | 18 | 18 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.01109018/DBN
Build-In Floor | Mini Canal | MICL.01109018/DBR | 11 | 90 | 18 | 18 | 150 | 150 | 150 | 0.0035714 | 58 | 0.001381 | 171 | 0.0040714 | 1.362 | A04 | MICL0.01109018/DBR
Build-In Floor | Mini Canal | MICL.01109018/DBV | 11 | 90 | 18 | 18 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.01109018/DBV
Build-In Floor | Mini Canal | MICL.01109018/DDB | 11 | 90 | 18 | 18 | 150 | 150 | 150 | 0.0035714 | 58 | 0.001381 | 171 | 0.0040714 | 1.362 | A04 | MICL0.01109018/DDB
Build-In Floor | Mini Canal | MICL.01109018/DMN | 11 | 90 | 18 | 18 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.01109018/DMN
Build-In Floor | Mini Canal | MICL.01109018/DMV | 11 | 90 | 18 | 18 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.01109018/DMV
Build-In Floor | Mini Canal | MICL.01109018/DNA | 11 | 90 | 18 | 18 | 150 | 150 | 150 | 0.0035714 | 58 | 0.001381 | 171 | 0.0040714 | 1.362 | A04 | MICL0.01109018/DNA
Build-In Floor | Mini Canal | MICL.01109018/DNC | 11 | 90 | 18 | 18 | 150 | 150 | 150 | 0.0035714 | 58 | 0.001381 | 171 | 0.0040714 | 1.362 | A04 | MICL0.01109018/DNC
Build-In Floor | Mini Canal | MICL.01109018/DON | 11 | 90 | 18 | 18 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.01109018/DON
Build-In Floor | Mini Canal | MICL.01109018/DOV | 11 | 90 | 18 | 18 | 144 | 144 | 144 | 0.0034286 | 56 | 0.0013333 | 164 | 0.0039048 | 1.362 | A04 | MICL0.01109018/DOV
Build-In Floor | Mini Canal | MICL.01109018/RBL | 11 | 90 | 18 | 18 | 155 | 155 | 155 | 0.0036905 | 60 | 0.0014286 | 177 | 0.0042143 | 1.362 | A04 | MICL0.01109018/RBL
Build-In Floor | Mini Canal | MICL.01109018/RBN | 11 | 90 | 18 | 18 | 150 | 150 | 150 | 0.0035714 | 58 | 0.001381 | 171 | 0.0040714 | 1.362 | A04 | MICL0.01109018/RBN
Build-In Floor | Mini Canal | MICL.01109018/RBR | 11 | 90 | 18 | 18 | 155 | 155 | 155 | 0.0036905 | 60 | 0.0014286 | 177 | 0.0042143 | 1.362 | A04 | MICL0.01109018/RBR
Build-In Floor | Mini Canal | MICL.01109018/RBV | 11 | 90 | 18 | 18 | 150 | 150 | 150 | 0.0035714 | 58 | 0.001381 | 171 | 0.0040714 | 1.362 | A04 | MICL0.01109018/RBV
Build-In Floor | Mini Canal | MICL.01109018/RDB | 11 | 90 | 18 | 18 | 155 | 155 | 155 | 0.0036905 | 60 | 0.0014286 | 177 | 0.0042143 | 1.362 | A04 | MICL0.01109018/RDB
Build-In Floor | Mini Canal | MICL.01109018/RMN | 11 | 90 | 18 | 18 | 150 | 150 | 150 | 0.0035714 | 58 | 0.001381 | 171 | 0.0040714 | 1.362 | A04 | MICL0.01109018/RMN
Build-In Floor | Mini Canal | MICL.01109018/RMV | 11 | 90 | 18 | 18 | 150 | 150 | 150 | 0.0035714 | 58 | 0.001381 | 171 | 0.0040714 | 1.362 | A04 | MICL0.01109018/RMV
Build-In Floor | Mini Canal | MICL.01109018/RNA | 11 | 90 | 18 | 18 | 155 | 155 | 155 | 0.0036905 | 60 | 0.0014286 | 177 | 0.0042143 | 1.362 | A04 | MICL0.01109018/RNA
Build-In Floor | Mini Canal | MICL.01109018/RON | 11 | 90 | 18 | 18 | 150 | 150 | 150 | 0.0035714 | 58 | 0.001381 | 171 | 0.0040714 | 1.362 | A04 | MICL0.01109018/RON
Build-In Floor | Mini Canal | MICL.01109018/ROV | 11 | 90 | 18 | 18 | 150 | 150 | 150 | 0.0035714 | 58 | 0.001381 | 171 | 0.0040714 | 1.362 | A04 | MICL0.01109018/ROV
Build-In Floor | Mini Canal | MICL.01109018/RSS | 11 | 90 | 18 | 18 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.01109018/RSS
Build-In Floor | Mini Canal | MICL.01109018/SBL | 11 | 90 | 18 | 18 | 155 | 155 | 155 | 0.0036905 | 60 | 0.0014286 | 177 | 0.0042143 | 1.362 | A04 | MICL0.01109018/SBL
Build-In Floor | Mini Canal | MICL.01109018/SBR | 11 | 90 | 18 | 18 | 155 | 155 | 155 | 0.0036905 | 60 | 0.0014286 | 177 | 0.0042143 | 1.362 | A04 | MICL0.01109018/SBR
Build-In Floor | Mini Canal | MICL.01109018/SDB | 11 | 90 | 18 | 18 | 155 | 155 | 155 | 0.0036905 | 60 | 0.0014286 | 177 | 0.0042143 | 1.362 | A04 | MICL0.01109018/SDB
Build-In Floor | Mini Canal | MICL.01109018/SNA | 11 | 90 | 18 | 18 | 155 | 155 | 155 | 0.0036905 | 60 | 0.0014286 | 177 | 0.0042143 | 1.362 | A04 | MICL0.01109018/SNA
Build-In Floor | Mini Canal | MICL.01109018/SNC | 11 | 90 | 18 | 18 | 155 | 155 | 155 | 0.0036905 | 60 | 0.0014286 | 177 | 0.0042143 | 1.362 | A04 | MICL0.01109018/SNC
Build-In Floor | Mini Canal | MICL.01109026/ANA | 11 | 90 | 26 | 26 | 158 | 158 | 158 | 0.0037619 | 61 | 0.0014524 | 180 | 0.0042857 | 1.362 | A04 | MICL0.01109026/ANA
Build-In Floor | Mini Canal | MICL.01109026/DBL | 11 | 90 | 26 | 26 | 204 | 204 | 204 | 0.0048571 | 79 | 0.001881 | 232 | 0.0055238 | 1.362 | A04 | MICL0.01109026/DBL
Build-In Floor | Mini Canal | MICL.01109026/DBN | 11 | 90 | 26 | 26 | 195 | 195 | 195 | 0.0046429 | 76 | 0.0018095 | 222 | 0.0052857 | 1.362 | A04 | MICL0.01109026/DBN
Build-In Floor | Mini Canal | MICL.01109026/DBR | 11 | 90 | 26 | 26 | 204 | 204 | 204 | 0.0048571 | 79 | 0.001881 | 232 | 0.0055238 | 1.362 | A04 | MICL0.01109026/DBR
Build-In Floor | Mini Canal | MICL.01109026/DBV | 11 | 90 | 26 | 26 | 195 | 195 | 195 | 0.0046429 | 76 | 0.0018095 | 222 | 0.0052857 | 1.362 | A04 | MICL0.01109026/DBV
Build-In Floor | Mini Canal | MICL.01109026/DDB | 11 | 90 | 26 | 26 | 204 | 204 | 204 | 0.0048571 | 79 | 0.001881 | 232 | 0.0055238 | 1.362 | A04 | MICL0.01109026/DDB
Build-In Floor | Mini Canal | MICL.01109026/DMN | 11 | 90 | 26 | 26 | 195 | 195 | 195 | 0.0046429 | 76 | 0.0018095 | 222 | 0.0052857 | 1.362 | A04 | MICL0.01109026/DMN
Build-In Floor | Mini Canal | MICL.01109026/DMV | 11 | 90 | 26 | 26 | 195 | 195 | 195 | 0.0046429 | 76 | 0.0018095 | 222 | 0.0052857 | 1.362 | A04 | MICL0.01109026/DMV
Build-In Floor | Mini Canal | MICL.01109026/DNA | 11 | 90 | 26 | 26 | 204 | 204 | 204 | 0.0048571 | 79 | 0.001881 | 232 | 0.0055238 | 1.362 | A04 | MICL0.01109026/DNA
Build-In Floor | Mini Canal | MICL.01109026/DNC | 11 | 90 | 26 | 26 | 204 | 204 | 204 | 0.0048571 | 79 | 0.001881 | 232 | 0.0055238 | 1.362 | A04 | MICL0.01109026/DNC
Build-In Floor | Mini Canal | MICL.01109026/DON | 11 | 90 | 26 | 26 | 195 | 195 | 195 | 0.0046429 | 76 | 0.0018095 | 222 | 0.0052857 | 1.362 | A04 | MICL0.01109026/DON
Build-In Floor | Mini Canal | MICL.01109026/DOV | 11 | 90 | 26 | 26 | 195 | 195 | 195 | 0.0046429 | 76 | 0.0018095 | 222 | 0.0052857 | 1.362 | A04 | MICL0.01109026/DOV
Build-In Floor | Mini Canal | MICL.01109026/PNC | 11 | 90 | 26 | 26 | 179 | 179 | 179 | 0.0042619 | 70 | 0.0016667 | 204 | 0.0048571 | 1.362 | A04 | MICL0.01109026/PNC
Build-In Floor | Mini Canal | MICL.01109026/RBL | 11 | 90 | 26 | 26 | 210 | 210 | 210 | 0.005 | 82 | 0.0019524 | 239 | 0.0056905 | 1.362 | A04 | MICL0.01109026/RBL
Build-In Floor | Mini Canal | MICL.01109026/RBN | 11 | 90 | 26 | 26 | 204 | 204 | 204 | 0.0048571 | 79 | 0.001881 | 232 | 0.0055238 | 1.362 | A04 | MICL0.01109026/RBN
Build-In Floor | Mini Canal | MICL.01109026/RBR | 11 | 90 | 26 | 26 | 210 | 210 | 210 | 0.005 | 82 | 0.0019524 | 239 | 0.0056905 | 1.362 | A04 | MICL0.01109026/RBR
Build-In Floor | Mini Canal | MICL.01109026/RBV | 11 | 90 | 26 | 26 | 204 | 204 | 204 | 0.0048571 | 79 | 0.001881 | 232 | 0.0055238 | 1.362 | A04 | MICL0.01109026/RBV
Build-In Floor | Mini Canal | MICL.01109026/RDB | 11 | 90 | 26 | 26 | 210 | 210 | 210 | 0.005 | 82 | 0.0019524 | 239 | 0.0056905 | 1.362 | A04 | MICL0.01109026/RDB
Build-In Floor | Mini Canal | MICL.01109026/RMN | 11 | 90 | 26 | 26 | 204 | 204 | 204 | 0.0048571 | 79 | 0.001881 | 232 | 0.0055238 | 1.362 | A04 | MICL0.01109026/RMN
Build-In Floor | Mini Canal | MICL.01109026/RMV | 11 | 90 | 26 | 26 | 204 | 204 | 204 | 0.0048571 | 79 | 0.001881 | 232 | 0.0055238 | 1.362 | A04 | MICL0.01109026/RMV
Build-In Floor | Mini Canal | MICL.01109026/RNA | 11 | 90 | 26 | 26 | 210 | 210 | 210 | 0.005 | 82 | 0.0019524 | 239 | 0.0056905 | 1.362 | A04 | MICL0.01109026/RNA
Build-In Floor | Mini Canal | MICL.01109026/RON | 11 | 90 | 26 | 26 | 204 | 204 | 204 | 0.0048571 | 79 | 0.001881 | 232 | 0.0055238 | 1.362 | A04 | MICL0.01109026/RON
Build-In Floor | Mini Canal | MICL.01109026/ROV | 11 | 90 | 26 | 26 | 204 | 204 | 204 | 0.0048571 | 79 | 0.001881 | 232 | 0.0055238 | 1.362 | A04 | MICL0.01109026/ROV
Build-In Floor | Mini Canal | MICL.01109026/RSS | 11 | 90 | 26 | 26 | 202 | 202 | 202 | 0.0048095 | 79 | 0.001881 | 230 | 0.0054762 | 1.362 | A04 | MICL0.01109026/RSS
Build-In Floor | Mini Canal | MICL.01109026/SBL | 11 | 90 | 26 | 26 | 210 | 210 | 210 | 0.005 | 82 | 0.0019524 | 239 | 0.0056905 | 1.362 | A04 | MICL0.01109026/SBL
Build-In Floor | Mini Canal | MICL.01109026/SBR | 11 | 90 | 26 | 26 | 210 | 210 | 210 | 0.005 | 82 | 0.0019524 | 239 | 0.0056905 | 1.362 | A04 | MICL0.01109026/SBR
Build-In Floor | Mini Canal | MICL.01109026/SDB | 11 | 90 | 26 | 26 | 210 | 210 | 210 | 0.005 | 82 | 0.0019524 | 239 | 0.0056905 | 1.362 | A04 | MICL0.01109026/SDB
Build-In Floor | Mini Canal | MICL.01109026/SNA | 11 | 90 | 26 | 26 | 210 | 210 | 210 | 0.005 | 82 | 0.0019524 | 239 | 0.0056905 | 1.362 | A04 | MICL0.01109026/SNA
Build-In Floor | Mini Canal | MICL.01109026/SNC | 11 | 90 | 26 | 26 | 210 | 210 | 210 | 0.005 | 82 | 0.0019524 | 239 | 0.0056905 | 1.362 | A04 | MICL0.01109026/SNC
Build-In Floor | Mini Canal | MICL.01109034/ANA | 11 | 90 | 34 | 34 | 204 | 204 | 204 | 0.0048571 | 79 | 0.001881 | 232 | 0.0055238 | 1.362 | A04 | MICL0.01109034/ANA
Build-In Floor | Mini Canal | MICL.01109034/DBL | 11 | 90 | 34 | 34 | 264 | 264 | 264 | 0.0062857 | 103 | 0.0024524 | 301 | 0.0071667 | 1.362 | A04 | MICL0.01109034/DBL
Build-In Floor | Mini Canal | MICL.01109034/DBN | 11 | 90 | 34 | 34 | 253 | 253 | 253 | 0.0060238 | 98 | 0.0023333 | 288 | 0.0068571 | 1.362 | A04 | MICL0.01109034/DBN
Build-In Floor | Mini Canal | MICL.01109034/DBR | 11 | 90 | 34 | 34 | 264 | 264 | 264 | 0.0062857 | 103 | 0.0024524 | 301 | 0.0071667 | 1.362 | A04 | MICL0.01109034/DBR
Build-In Floor | Mini Canal | MICL.01109034/DBV | 11 | 90 | 34 | 34 | 253 | 253 | 253 | 0.0060238 | 98 | 0.0023333 | 288 | 0.0068571 | 1.362 | A04 | MICL0.01109034/DBV
Build-In Floor | Mini Canal | MICL.01109034/DDB | 11 | 90 | 34 | 34 | 264 | 264 | 264 | 0.0062857 | 103 | 0.0024524 | 301 | 0.0071667 | 1.362 | A04 | MICL0.01109034/DDB
Build-In Floor | Mini Canal | MICL.01109034/DMN | 11 | 90 | 34 | 34 | 253 | 253 | 253 | 0.0060238 | 98 | 0.0023333 | 288 | 0.0068571 | 1.362 | A04 | MICL0.01109034/DMN
Build-In Floor | Mini Canal | MICL.01109034/DMV | 11 | 90 | 34 | 34 | 253 | 253 | 253 | 0.0060238 | 98 | 0.0023333 | 288 | 0.0068571 | 1.362 | A04 | MICL0.01109034/DMV
Build-In Floor | Mini Canal | MICL.01109034/DNA | 11 | 90 | 34 | 34 | 264 | 264 | 264 | 0.0062857 | 103 | 0.0024524 | 301 | 0.0071667 | 1.362 | A04 | MICL0.01109034/DNA
Build-In Floor | Mini Canal | MICL.01109034/DNC | 11 | 90 | 34 | 34 | 264 | 264 | 264 | 0.0062857 | 103 | 0.0024524 | 301 | 0.0071667 | 1.362 | A04 | MICL0.01109034/DNC
Build-In Floor | Mini Canal | MICL.01109034/DON | 11 | 90 | 34 | 34 | 253 | 253 | 253 | 0.0060238 | 98 | 0.0023333 | 288 | 0.0068571 | 1.362 | A04 | MICL0.01109034/DON
Build-In Floor | Mini Canal | MICL.01109034/DOV | 11 | 90 | 34 | 34 | 253 | 253 | 253 | 0.0060238 | 98 | 0.0023333 | 288 | 0.0068571 | 1.362 | A04 | MICL0.01109034/DOV
Build-In Floor | Mini Canal | MICL.01109034/PNC | 11 | 90 | 34 | 34 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.01109034/PNC
Build-In Floor | Mini Canal | MICL.01109034/RBL | 11 | 90 | 34 | 34 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01109034/RBL
Build-In Floor | Mini Canal | MICL.01109034/RBN | 11 | 90 | 34 | 34 | 264 | 264 | 264 | 0.0062857 | 103 | 0.0024524 | 301 | 0.0071667 | 1.362 | A04 | MICL0.01109034/RBN
Build-In Floor | Mini Canal | MICL.01109034/RBR | 11 | 90 | 34 | 34 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01109034/RBR
Build-In Floor | Mini Canal | MICL.01109034/RBV | 11 | 90 | 34 | 34 | 264 | 264 | 264 | 0.0062857 | 103 | 0.0024524 | 301 | 0.0071667 | 1.362 | A04 | MICL0.01109034/RBV
Build-In Floor | Mini Canal | MICL.01109034/RDB | 11 | 90 | 34 | 34 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01109034/RDB
Build-In Floor | Mini Canal | MICL.01109034/RMN | 11 | 90 | 34 | 34 | 264 | 264 | 264 | 0.0062857 | 103 | 0.0024524 | 301 | 0.0071667 | 1.362 | A04 | MICL0.01109034/RMN
Build-In Floor | Mini Canal | MICL.01109034/RMV | 11 | 90 | 34 | 34 | 264 | 264 | 264 | 0.0062857 | 103 | 0.0024524 | 301 | 0.0071667 | 1.362 | A04 | MICL0.01109034/RMV
Build-In Floor | Mini Canal | MICL.01109034/RNA | 11 | 90 | 34 | 34 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01109034/RNA
Build-In Floor | Mini Canal | MICL.01109034/RON | 11 | 90 | 34 | 34 | 264 | 264 | 264 | 0.0062857 | 103 | 0.0024524 | 301 | 0.0071667 | 1.362 | A04 | MICL0.01109034/RON
Build-In Floor | Mini Canal | MICL.01109034/ROV | 11 | 90 | 34 | 34 | 264 | 264 | 264 | 0.0062857 | 103 | 0.0024524 | 301 | 0.0071667 | 1.362 | A04 | MICL0.01109034/ROV
Build-In Floor | Mini Canal | MICL.01109034/RSS | 11 | 90 | 34 | 34 | 261 | 261 | 261 | 0.0062143 | 102 | 0.0024286 | 297 | 0.0070714 | 1.362 | A04 | MICL0.01109034/RSS
Build-In Floor | Mini Canal | MICL.01109034/SBL | 11 | 90 | 34 | 34 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01109034/SBL
Build-In Floor | Mini Canal | MICL.01109034/SBR | 11 | 90 | 34 | 34 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01109034/SBR
Build-In Floor | Mini Canal | MICL.01109034/SDB | 11 | 90 | 34 | 34 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01109034/SDB
Build-In Floor | Mini Canal | MICL.01109034/SNA | 11 | 90 | 34 | 34 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01109034/SNA
Build-In Floor | Mini Canal | MICL.01109034/SNC | 11 | 90 | 34 | 34 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01109034/SNC
Build-In Floor | Mini Canal | MICL.01109042/ANA | 11 | 90 | 42 | 42 | 287 | 287 | 287 | 0.0068333 | 112 | 0.0026667 | 327 | 0.0077857 | 1.362 | A04 | MICL0.01109042/ANA
Build-In Floor | Mini Canal | MICL.01109042/DBL | 11 | 90 | 42 | 42 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.01109042/DBL
Build-In Floor | Mini Canal | MICL.01109042/DBN | 11 | 90 | 42 | 42 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.01109042/DBN
Build-In Floor | Mini Canal | MICL.01109042/DBR | 11 | 90 | 42 | 42 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.01109042/DBR
Build-In Floor | Mini Canal | MICL.01109042/DBV | 11 | 90 | 42 | 42 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.01109042/DBV
Build-In Floor | Mini Canal | MICL.01109042/DDB | 11 | 90 | 42 | 42 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.01109042/DDB
Build-In Floor | Mini Canal | MICL.01109042/DMN | 11 | 90 | 42 | 42 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.01109042/DMN
Build-In Floor | Mini Canal | MICL.01109042/DMV | 11 | 90 | 42 | 42 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.01109042/DMV
Build-In Floor | Mini Canal | MICL.01109042/DNA | 11 | 90 | 42 | 42 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.01109042/DNA
Build-In Floor | Mini Canal | MICL.01109042/DNC | 11 | 90 | 42 | 42 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.01109042/DNC
Build-In Floor | Mini Canal | MICL.01109042/DON | 11 | 90 | 42 | 42 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.01109042/DON
Build-In Floor | Mini Canal | MICL.01109042/DOV | 11 | 90 | 42 | 42 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.01109042/DOV
Build-In Floor | Mini Canal | MICL.01109042/PNC | 11 | 90 | 42 | 42 | 326 | 326 | 326 | 0.0077619 | 127 | 0.0030238 | 371 | 0.0088333 | 1.362 | A04 | MICL0.01109042/PNC
Build-In Floor | Mini Canal | MICL.01109042/RBL | 11 | 90 | 42 | 42 | 383 | 383 | 383 | 0.009119 | 149 | 0.0035476 | 436 | 0.010381 | 1.362 | A04 | MICL0.01109042/RBL
Build-In Floor | Mini Canal | MICL.01109042/RBN | 11 | 90 | 42 | 42 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.01109042/RBN
Build-In Floor | Mini Canal | MICL.01109042/RBR | 11 | 90 | 42 | 42 | 383 | 383 | 383 | 0.009119 | 149 | 0.0035476 | 436 | 0.010381 | 1.362 | A04 | MICL0.01109042/RBR
Build-In Floor | Mini Canal | MICL.01109042/RBV | 11 | 90 | 42 | 42 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.01109042/RBV
Build-In Floor | Mini Canal | MICL.01109042/RDB | 11 | 90 | 42 | 42 | 383 | 383 | 383 | 0.009119 | 149 | 0.0035476 | 436 | 0.010381 | 1.362 | A04 | MICL0.01109042/RDB
Build-In Floor | Mini Canal | MICL.01109042/RMN | 11 | 90 | 42 | 42 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.01109042/RMN
Build-In Floor | Mini Canal | MICL.01109042/RMV | 11 | 90 | 42 | 42 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.01109042/RMV
Build-In Floor | Mini Canal | MICL.01109042/RNA | 11 | 90 | 42 | 42 | 383 | 383 | 383 | 0.009119 | 149 | 0.0035476 | 436 | 0.010381 | 1.362 | A04 | MICL0.01109042/RNA
Build-In Floor | Mini Canal | MICL.01109042/RON | 11 | 90 | 42 | 42 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.01109042/RON
Build-In Floor | Mini Canal | MICL.01109042/ROV | 11 | 90 | 42 | 42 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.01109042/ROV
Build-In Floor | Mini Canal | MICL.01109042/RSS | 11 | 90 | 42 | 42 | 368 | 368 | 368 | 0.0087619 | 143 | 0.0034048 | 419 | 0.0099762 | 1.362 | A04 | MICL0.01109042/RSS
Build-In Floor | Mini Canal | MICL.01109042/SBL | 11 | 90 | 42 | 42 | 383 | 383 | 383 | 0.009119 | 149 | 0.0035476 | 436 | 0.010381 | 1.362 | A04 | MICL0.01109042/SBL
Build-In Floor | Mini Canal | MICL.01109042/SBR | 11 | 90 | 42 | 42 | 383 | 383 | 383 | 0.009119 | 149 | 0.0035476 | 436 | 0.010381 | 1.362 | A04 | MICL0.01109042/SBR
Build-In Floor | Mini Canal | MICL.01109042/SDB | 11 | 90 | 42 | 42 | 383 | 383 | 383 | 0.009119 | 149 | 0.0035476 | 436 | 0.010381 | 1.362 | A04 | MICL0.01109042/SDB
Build-In Floor | Mini Canal | MICL.01109042/SNA | 11 | 90 | 42 | 42 | 383 | 383 | 383 | 0.009119 | 149 | 0.0035476 | 436 | 0.010381 | 1.362 | A04 | MICL0.01109042/SNA
Build-In Floor | Mini Canal | MICL.01109042/SNC | 11 | 90 | 42 | 42 | 383 | 383 | 383 | 0.009119 | 149 | 0.0035476 | 436 | 0.010381 | 1.362 | A04 | MICL0.01109042/SNC
Build-In Floor | Mini Canal | MICL.01110014/ANA | 11 | 100 | 14 | 14 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.01110014/ANA
Build-In Floor | Mini Canal | MICL.01110014/DBL | 11 | 100 | 14 | 14 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.01110014/DBL
Build-In Floor | Mini Canal | MICL.01110014/DBN | 11 | 100 | 14 | 14 | 142 | 142 | 142 | 0.003381 | 55 | 0.0013095 | 162 | 0.0038571 | 1.362 | A04 | MICL0.01110014/DBN
Build-In Floor | Mini Canal | MICL.01110014/DBR | 11 | 100 | 14 | 14 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.01110014/DBR
Build-In Floor | Mini Canal | MICL.01110014/DBV | 11 | 100 | 14 | 14 | 142 | 142 | 142 | 0.003381 | 55 | 0.0013095 | 162 | 0.0038571 | 1.362 | A04 | MICL0.01110014/DBV
Build-In Floor | Mini Canal | MICL.01110014/DDB | 11 | 100 | 14 | 14 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.01110014/DDB
Build-In Floor | Mini Canal | MICL.01110014/DMN | 11 | 100 | 14 | 14 | 142 | 142 | 142 | 0.003381 | 55 | 0.0013095 | 162 | 0.0038571 | 1.362 | A04 | MICL0.01110014/DMN
Build-In Floor | Mini Canal | MICL.01110014/DMV | 11 | 100 | 14 | 14 | 142 | 142 | 142 | 0.003381 | 55 | 0.0013095 | 162 | 0.0038571 | 1.362 | A04 | MICL0.01110014/DMV
Build-In Floor | Mini Canal | MICL.01110014/DNA | 11 | 100 | 14 | 14 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.01110014/DNA
Build-In Floor | Mini Canal | MICL.01110014/DNC | 11 | 100 | 14 | 14 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.01110014/DNC
Build-In Floor | Mini Canal | MICL.01110014/DON | 11 | 100 | 14 | 14 | 142 | 142 | 142 | 0.003381 | 55 | 0.0013095 | 162 | 0.0038571 | 1.362 | A04 | MICL0.01110014/DON
Build-In Floor | Mini Canal | MICL.01110014/DOV | 11 | 100 | 14 | 14 | 142 | 142 | 142 | 0.003381 | 55 | 0.0013095 | 162 | 0.0038571 | 1.362 | A04 | MICL0.01110014/DOV
Build-In Floor | Mini Canal | MICL.01110014/RBL | 11 | 100 | 14 | 14 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.01110014/RBL
Build-In Floor | Mini Canal | MICL.01110014/RBN | 11 | 100 | 14 | 14 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.01110014/RBN
Build-In Floor | Mini Canal | MICL.01110014/RBR | 11 | 100 | 14 | 14 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.01110014/RBR
Build-In Floor | Mini Canal | MICL.01110014/RBV | 11 | 100 | 14 | 14 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.01110014/RBV
Build-In Floor | Mini Canal | MICL.01110014/RDB | 11 | 100 | 14 | 14 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.01110014/RDB
Build-In Floor | Mini Canal | MICL.01110014/RMN | 11 | 100 | 14 | 14 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.01110014/RMN
Build-In Floor | Mini Canal | MICL.01110014/RMV | 11 | 100 | 14 | 14 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.01110014/RMV
Build-In Floor | Mini Canal | MICL.01110014/RNA | 11 | 100 | 14 | 14 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.01110014/RNA
Build-In Floor | Mini Canal | MICL.01110014/RON | 11 | 100 | 14 | 14 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.01110014/RON
Build-In Floor | Mini Canal | MICL.01110014/ROV | 11 | 100 | 14 | 14 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.01110014/ROV
Build-In Floor | Mini Canal | MICL.01110014/RSS | 11 | 100 | 14 | 14 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.01110014/RSS
Build-In Floor | Mini Canal | MICL.01110014/SBL | 11 | 100 | 14 | 14 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.01110014/SBL
Build-In Floor | Mini Canal | MICL.01110014/SBR | 11 | 100 | 14 | 14 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.01110014/SBR
Build-In Floor | Mini Canal | MICL.01110014/SDB | 11 | 100 | 14 | 14 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.01110014/SDB
Build-In Floor | Mini Canal | MICL.01110014/SNA | 11 | 100 | 14 | 14 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.01110014/SNA
Build-In Floor | Mini Canal | MICL.01110014/SNC | 11 | 100 | 14 | 14 | 153 | 153 | 153 | 0.0036429 | 60 | 0.0014286 | 174 | 0.0041429 | 1.362 | A04 | MICL0.01110014/SNC
Build-In Floor | Mini Canal | MICL.01110018/ANA | 11 | 100 | 18 | 18 | 136 | 136 | 136 | 0.0032381 | 53 | 0.0012619 | 155 | 0.0036905 | 1.362 | A04 | MICL0.01110018/ANA
Build-In Floor | Mini Canal | MICL.01110018/DBL | 11 | 100 | 18 | 18 | 176 | 176 | 176 | 0.0041905 | 68 | 0.001619 | 200 | 0.0047619 | 1.362 | A04 | MICL0.01110018/DBL
Build-In Floor | Mini Canal | MICL.01110018/DBN | 11 | 100 | 18 | 18 | 168 | 168 | 168 | 0.004 | 65 | 0.0015476 | 191 | 0.0045476 | 1.362 | A04 | MICL0.01110018/DBN
Build-In Floor | Mini Canal | MICL.01110018/DBR | 11 | 100 | 18 | 18 | 176 | 176 | 176 | 0.0041905 | 68 | 0.001619 | 200 | 0.0047619 | 1.362 | A04 | MICL0.01110018/DBR
Build-In Floor | Mini Canal | MICL.01110018/DBV | 11 | 100 | 18 | 18 | 168 | 168 | 168 | 0.004 | 65 | 0.0015476 | 191 | 0.0045476 | 1.362 | A04 | MICL0.01110018/DBV
Build-In Floor | Mini Canal | MICL.01110018/DDB | 11 | 100 | 18 | 18 | 176 | 176 | 176 | 0.0041905 | 68 | 0.001619 | 200 | 0.0047619 | 1.362 | A04 | MICL0.01110018/DDB
Build-In Floor | Mini Canal | MICL.01110018/DMN | 11 | 100 | 18 | 18 | 168 | 168 | 168 | 0.004 | 65 | 0.0015476 | 191 | 0.0045476 | 1.362 | A04 | MICL0.01110018/DMN
Build-In Floor | Mini Canal | MICL.01110018/DMV | 11 | 100 | 18 | 18 | 168 | 168 | 168 | 0.004 | 65 | 0.0015476 | 191 | 0.0045476 | 1.362 | A04 | MICL0.01110018/DMV
Build-In Floor | Mini Canal | MICL.01110018/DNA | 11 | 100 | 18 | 18 | 176 | 176 | 176 | 0.0041905 | 68 | 0.001619 | 200 | 0.0047619 | 1.362 | A04 | MICL0.01110018/DNA
Build-In Floor | Mini Canal | MICL.01110018/DNC | 11 | 100 | 18 | 18 | 176 | 176 | 176 | 0.0041905 | 68 | 0.001619 | 200 | 0.0047619 | 1.362 | A04 | MICL0.01110018/DNC
Build-In Floor | Mini Canal | MICL.01110018/DON | 11 | 100 | 18 | 18 | 168 | 168 | 168 | 0.004 | 65 | 0.0015476 | 191 | 0.0045476 | 1.362 | A04 | MICL0.01110018/DON
Build-In Floor | Mini Canal | MICL.01110018/DOV | 11 | 100 | 18 | 18 | 168 | 168 | 168 | 0.004 | 65 | 0.0015476 | 191 | 0.0045476 | 1.362 | A04 | MICL0.01110018/DOV
Build-In Floor | Mini Canal | MICL.01110018/RBL | 11 | 100 | 18 | 18 | 181 | 181 | 181 | 0.0043095 | 70 | 0.0016667 | 206 | 0.0049048 | 1.362 | A04 | MICL0.01110018/RBL
Build-In Floor | Mini Canal | MICL.01110018/RBN | 11 | 100 | 18 | 18 | 176 | 176 | 176 | 0.0041905 | 68 | 0.001619 | 200 | 0.0047619 | 1.362 | A04 | MICL0.01110018/RBN
Build-In Floor | Mini Canal | MICL.01110018/RBR | 11 | 100 | 18 | 18 | 181 | 181 | 181 | 0.0043095 | 70 | 0.0016667 | 206 | 0.0049048 | 1.362 | A04 | MICL0.01110018/RBR
Build-In Floor | Mini Canal | MICL.01110018/RBV | 11 | 100 | 18 | 18 | 176 | 176 | 176 | 0.0041905 | 68 | 0.001619 | 200 | 0.0047619 | 1.362 | A04 | MICL0.01110018/RBV
Build-In Floor | Mini Canal | MICL.01110018/RDB | 11 | 100 | 18 | 18 | 181 | 181 | 181 | 0.0043095 | 70 | 0.0016667 | 206 | 0.0049048 | 1.362 | A04 | MICL0.01110018/RDB
Build-In Floor | Mini Canal | MICL.01110018/RMN | 11 | 100 | 18 | 18 | 176 | 176 | 176 | 0.0041905 | 68 | 0.001619 | 200 | 0.0047619 | 1.362 | A04 | MICL0.01110018/RMN
Build-In Floor | Mini Canal | MICL.01110018/RMV | 11 | 100 | 18 | 18 | 176 | 176 | 176 | 0.0041905 | 68 | 0.001619 | 200 | 0.0047619 | 1.362 | A04 | MICL0.01110018/RMV
Build-In Floor | Mini Canal | MICL.01110018/RNA | 11 | 100 | 18 | 18 | 181 | 181 | 181 | 0.0043095 | 70 | 0.0016667 | 206 | 0.0049048 | 1.362 | A04 | MICL0.01110018/RNA
Build-In Floor | Mini Canal | MICL.01110018/RON | 11 | 100 | 18 | 18 | 176 | 176 | 176 | 0.0041905 | 68 | 0.001619 | 200 | 0.0047619 | 1.362 | A04 | MICL0.01110018/RON
Build-In Floor | Mini Canal | MICL.01110018/ROV | 11 | 100 | 18 | 18 | 176 | 176 | 176 | 0.0041905 | 68 | 0.001619 | 200 | 0.0047619 | 1.362 | A04 | MICL0.01110018/ROV
Build-In Floor | Mini Canal | MICL.01110018/RSS | 11 | 100 | 18 | 18 | 174 | 174 | 174 | 0.0041429 | 68 | 0.001619 | 198 | 0.0047143 | 1.362 | A04 | MICL0.01110018/RSS
Build-In Floor | Mini Canal | MICL.01110018/SBL | 11 | 100 | 18 | 18 | 181 | 181 | 181 | 0.0043095 | 70 | 0.0016667 | 206 | 0.0049048 | 1.362 | A04 | MICL0.01110018/SBL
Build-In Floor | Mini Canal | MICL.01110018/SBR | 11 | 100 | 18 | 18 | 181 | 181 | 181 | 0.0043095 | 70 | 0.0016667 | 206 | 0.0049048 | 1.362 | A04 | MICL0.01110018/SBR
Build-In Floor | Mini Canal | MICL.01110018/SDB | 11 | 100 | 18 | 18 | 181 | 181 | 181 | 0.0043095 | 70 | 0.0016667 | 206 | 0.0049048 | 1.362 | A04 | MICL0.01110018/SDB
Build-In Floor | Mini Canal | MICL.01110018/SNA | 11 | 100 | 18 | 18 | 181 | 181 | 181 | 0.0043095 | 70 | 0.0016667 | 206 | 0.0049048 | 1.362 | A04 | MICL0.01110018/SNA
Build-In Floor | Mini Canal | MICL.01110018/SNC | 11 | 100 | 18 | 18 | 181 | 181 | 181 | 0.0043095 | 70 | 0.0016667 | 206 | 0.0049048 | 1.362 | A04 | MICL0.01110018/SNC
Build-In Floor | Mini Canal | MICL.01110026/ANA | 11 | 100 | 26 | 26 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.01110026/ANA
Build-In Floor | Mini Canal | MICL.01110026/DBL | 11 | 100 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01110026/DBL
Build-In Floor | Mini Canal | MICL.01110026/DBN | 11 | 100 | 26 | 26 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01110026/DBN
Build-In Floor | Mini Canal | MICL.01110026/DBR | 11 | 100 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01110026/DBR
Build-In Floor | Mini Canal | MICL.01110026/DBV | 11 | 100 | 26 | 26 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01110026/DBV
Build-In Floor | Mini Canal | MICL.01110026/DDB | 11 | 100 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01110026/DDB
Build-In Floor | Mini Canal | MICL.01110026/DMN | 11 | 100 | 26 | 26 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01110026/DMN
Build-In Floor | Mini Canal | MICL.01110026/DMV | 11 | 100 | 26 | 26 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01110026/DMV
Build-In Floor | Mini Canal | MICL.01110026/DNA | 11 | 100 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01110026/DNA
Build-In Floor | Mini Canal | MICL.01110026/DNC | 11 | 100 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01110026/DNC
Build-In Floor | Mini Canal | MICL.01110026/DON | 11 | 100 | 26 | 26 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01110026/DON
Build-In Floor | Mini Canal | MICL.01110026/DOV | 11 | 100 | 26 | 26 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01110026/DOV
Build-In Floor | Mini Canal | MICL.01110026/PNC | 11 | 100 | 26 | 26 | 208 | 208 | 208 | 0.0049524 | 81 | 0.0019286 | 237 | 0.0056429 | 1.362 | A04 | MICL0.01110026/PNC
Build-In Floor | Mini Canal | MICL.01110026/RBL | 11 | 100 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01110026/RBL
Build-In Floor | Mini Canal | MICL.01110026/RBN | 11 | 100 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01110026/RBN
Build-In Floor | Mini Canal | MICL.01110026/RBR | 11 | 100 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01110026/RBR
Build-In Floor | Mini Canal | MICL.01110026/RBV | 11 | 100 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01110026/RBV
Build-In Floor | Mini Canal | MICL.01110026/RDB | 11 | 100 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01110026/RDB
Build-In Floor | Mini Canal | MICL.01110026/RMN | 11 | 100 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01110026/RMN
Build-In Floor | Mini Canal | MICL.01110026/RMV | 11 | 100 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01110026/RMV
Build-In Floor | Mini Canal | MICL.01110026/RNA | 11 | 100 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01110026/RNA
Build-In Floor | Mini Canal | MICL.01110026/RON | 11 | 100 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01110026/RON
Build-In Floor | Mini Canal | MICL.01110026/ROV | 11 | 100 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01110026/ROV
Build-In Floor | Mini Canal | MICL.01110026/RSS | 11 | 100 | 26 | 26 | 235 | 235 | 235 | 0.0055952 | 91 | 0.0021667 | 268 | 0.006381 | 1.362 | A04 | MICL0.01110026/RSS
Build-In Floor | Mini Canal | MICL.01110026/SBL | 11 | 100 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01110026/SBL
Build-In Floor | Mini Canal | MICL.01110026/SBR | 11 | 100 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01110026/SBR
Build-In Floor | Mini Canal | MICL.01110026/SDB | 11 | 100 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01110026/SDB
Build-In Floor | Mini Canal | MICL.01110026/SNA | 11 | 100 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01110026/SNA
Build-In Floor | Mini Canal | MICL.01110026/SNC | 11 | 100 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01110026/SNC
Build-In Floor | Mini Canal | MICL.01110034/ANA | 11 | 100 | 34 | 34 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01110034/ANA
Build-In Floor | Mini Canal | MICL.01110034/DBL | 11 | 100 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01110034/DBL
Build-In Floor | Mini Canal | MICL.01110034/DBN | 11 | 100 | 34 | 34 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.01110034/DBN
Build-In Floor | Mini Canal | MICL.01110034/DBR | 11 | 100 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01110034/DBR
Build-In Floor | Mini Canal | MICL.01110034/DBV | 11 | 100 | 34 | 34 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.01110034/DBV
Build-In Floor | Mini Canal | MICL.01110034/DDB | 11 | 100 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01110034/DDB
Build-In Floor | Mini Canal | MICL.01110034/DMN | 11 | 100 | 34 | 34 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.01110034/DMN
Build-In Floor | Mini Canal | MICL.01110034/DMV | 11 | 100 | 34 | 34 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.01110034/DMV
Build-In Floor | Mini Canal | MICL.01110034/DNA | 11 | 100 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01110034/DNA
Build-In Floor | Mini Canal | MICL.01110034/DNC | 11 | 100 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01110034/DNC
Build-In Floor | Mini Canal | MICL.01110034/DON | 11 | 100 | 34 | 34 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.01110034/DON
Build-In Floor | Mini Canal | MICL.01110034/DOV | 11 | 100 | 34 | 34 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.01110034/DOV
Build-In Floor | Mini Canal | MICL.01110034/PNC | 11 | 100 | 34 | 34 | 269 | 269 | 269 | 0.0064048 | 105 | 0.0025 | 306 | 0.0072857 | 1.362 | A04 | MICL0.01110034/PNC
Build-In Floor | Mini Canal | MICL.01110034/RBL | 11 | 100 | 34 | 34 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01110034/RBL
Build-In Floor | Mini Canal | MICL.01110034/RBN | 11 | 100 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01110034/RBN
Build-In Floor | Mini Canal | MICL.01110034/RBR | 11 | 100 | 34 | 34 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01110034/RBR
Build-In Floor | Mini Canal | MICL.01110034/RBV | 11 | 100 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01110034/RBV
Build-In Floor | Mini Canal | MICL.01110034/RDB | 11 | 100 | 34 | 34 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01110034/RDB
Build-In Floor | Mini Canal | MICL.01110034/RMN | 11 | 100 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01110034/RMN
Build-In Floor | Mini Canal | MICL.01110034/RMV | 11 | 100 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01110034/RMV
Build-In Floor | Mini Canal | MICL.01110034/RNA | 11 | 100 | 34 | 34 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01110034/RNA
Build-In Floor | Mini Canal | MICL.01110034/RON | 11 | 100 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01110034/RON
Build-In Floor | Mini Canal | MICL.01110034/ROV | 11 | 100 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01110034/ROV
Build-In Floor | Mini Canal | MICL.01110034/RSS | 11 | 100 | 34 | 34 | 304 | 304 | 304 | 0.0072381 | 118 | 0.0028095 | 346 | 0.0082381 | 1.362 | A04 | MICL0.01110034/RSS
Build-In Floor | Mini Canal | MICL.01110034/SBL | 11 | 100 | 34 | 34 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01110034/SBL
Build-In Floor | Mini Canal | MICL.01110034/SBR | 11 | 100 | 34 | 34 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01110034/SBR
Build-In Floor | Mini Canal | MICL.01110034/SDB | 11 | 100 | 34 | 34 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01110034/SDB
Build-In Floor | Mini Canal | MICL.01110034/SNA | 11 | 100 | 34 | 34 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01110034/SNA
Build-In Floor | Mini Canal | MICL.01110034/SNC | 11 | 100 | 34 | 34 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01110034/SNC
Build-In Floor | Mini Canal | MICL.01110042/ANA | 11 | 100 | 42 | 42 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01110042/ANA
Build-In Floor | Mini Canal | MICL.01110042/DBL | 11 | 100 | 42 | 42 | 434 | 434 | 434 | 0.010333 | 169 | 0.0040238 | 494 | 0.011762 | 1.362 | A04 | MICL0.01110042/DBL
Build-In Floor | Mini Canal | MICL.01110042/DBN | 11 | 100 | 42 | 42 | 416 | 416 | 416 | 0.0099048 | 162 | 0.0038571 | 474 | 0.011286 | 1.362 | A04 | MICL0.01110042/DBN
Build-In Floor | Mini Canal | MICL.01110042/DBR | 11 | 100 | 42 | 42 | 434 | 434 | 434 | 0.010333 | 169 | 0.0040238 | 494 | 0.011762 | 1.362 | A04 | MICL0.01110042/DBR
Build-In Floor | Mini Canal | MICL.01110042/DBV | 11 | 100 | 42 | 42 | 416 | 416 | 416 | 0.0099048 | 162 | 0.0038571 | 474 | 0.011286 | 1.362 | A04 | MICL0.01110042/DBV
Build-In Floor | Mini Canal | MICL.01110042/DDB | 11 | 100 | 42 | 42 | 434 | 434 | 434 | 0.010333 | 169 | 0.0040238 | 494 | 0.011762 | 1.362 | A04 | MICL0.01110042/DDB
Build-In Floor | Mini Canal | MICL.01110042/DMN | 11 | 100 | 42 | 42 | 416 | 416 | 416 | 0.0099048 | 162 | 0.0038571 | 474 | 0.011286 | 1.362 | A04 | MICL0.01110042/DMN
Build-In Floor | Mini Canal | MICL.01110042/DMV | 11 | 100 | 42 | 42 | 416 | 416 | 416 | 0.0099048 | 162 | 0.0038571 | 474 | 0.011286 | 1.362 | A04 | MICL0.01110042/DMV
Build-In Floor | Mini Canal | MICL.01110042/DNA | 11 | 100 | 42 | 42 | 434 | 434 | 434 | 0.010333 | 169 | 0.0040238 | 494 | 0.011762 | 1.362 | A04 | MICL0.01110042/DNA
Build-In Floor | Mini Canal | MICL.01110042/DNC | 11 | 100 | 42 | 42 | 434 | 434 | 434 | 0.010333 | 169 | 0.0040238 | 494 | 0.011762 | 1.362 | A04 | MICL0.01110042/DNC
Build-In Floor | Mini Canal | MICL.01110042/DON | 11 | 100 | 42 | 42 | 416 | 416 | 416 | 0.0099048 | 162 | 0.0038571 | 474 | 0.011286 | 1.362 | A04 | MICL0.01110042/DON
Build-In Floor | Mini Canal | MICL.01110042/DOV | 11 | 100 | 42 | 42 | 416 | 416 | 416 | 0.0099048 | 162 | 0.0038571 | 474 | 0.011286 | 1.362 | A04 | MICL0.01110042/DOV
Build-In Floor | Mini Canal | MICL.01110042/PNC | 11 | 100 | 42 | 42 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01110042/PNC
Build-In Floor | Mini Canal | MICL.01110042/RBL | 11 | 100 | 42 | 42 | 447 | 447 | 447 | 0.010643 | 174 | 0.0041429 | 509 | 0.012119 | 1.362 | A04 | MICL0.01110042/RBL
Build-In Floor | Mini Canal | MICL.01110042/RBN | 11 | 100 | 42 | 42 | 434 | 434 | 434 | 0.010333 | 169 | 0.0040238 | 494 | 0.011762 | 1.362 | A04 | MICL0.01110042/RBN
Build-In Floor | Mini Canal | MICL.01110042/RBR | 11 | 100 | 42 | 42 | 447 | 447 | 447 | 0.010643 | 174 | 0.0041429 | 509 | 0.012119 | 1.362 | A04 | MICL0.01110042/RBR
Build-In Floor | Mini Canal | MICL.01110042/RBV | 11 | 100 | 42 | 42 | 434 | 434 | 434 | 0.010333 | 169 | 0.0040238 | 494 | 0.011762 | 1.362 | A04 | MICL0.01110042/RBV
Build-In Floor | Mini Canal | MICL.01110042/RDB | 11 | 100 | 42 | 42 | 447 | 447 | 447 | 0.010643 | 174 | 0.0041429 | 509 | 0.012119 | 1.362 | A04 | MICL0.01110042/RDB
Build-In Floor | Mini Canal | MICL.01110042/RMN | 11 | 100 | 42 | 42 | 434 | 434 | 434 | 0.010333 | 169 | 0.0040238 | 494 | 0.011762 | 1.362 | A04 | MICL0.01110042/RMN
Build-In Floor | Mini Canal | MICL.01110042/RMV | 11 | 100 | 42 | 42 | 434 | 434 | 434 | 0.010333 | 169 | 0.0040238 | 494 | 0.011762 | 1.362 | A04 | MICL0.01110042/RMV
Build-In Floor | Mini Canal | MICL.01110042/RNA | 11 | 100 | 42 | 42 | 447 | 447 | 447 | 0.010643 | 174 | 0.0041429 | 509 | 0.012119 | 1.362 | A04 | MICL0.01110042/RNA
Build-In Floor | Mini Canal | MICL.01110042/RON | 11 | 100 | 42 | 42 | 434 | 434 | 434 | 0.010333 | 169 | 0.0040238 | 494 | 0.011762 | 1.362 | A04 | MICL0.01110042/RON
Build-In Floor | Mini Canal | MICL.01110042/ROV | 11 | 100 | 42 | 42 | 434 | 434 | 434 | 0.010333 | 169 | 0.0040238 | 494 | 0.011762 | 1.362 | A04 | MICL0.01110042/ROV
Build-In Floor | Mini Canal | MICL.01110042/RSS | 11 | 100 | 42 | 42 | 429 | 429 | 429 | 0.010214 | 167 | 0.0039762 | 489 | 0.011643 | 1.362 | A04 | MICL0.01110042/RSS
Build-In Floor | Mini Canal | MICL.01110042/SBL | 11 | 100 | 42 | 42 | 447 | 447 | 447 | 0.010643 | 174 | 0.0041429 | 509 | 0.012119 | 1.362 | A04 | MICL0.01110042/SBL
Build-In Floor | Mini Canal | MICL.01110042/SBR | 11 | 100 | 42 | 42 | 447 | 447 | 447 | 0.010643 | 174 | 0.0041429 | 509 | 0.012119 | 1.362 | A04 | MICL0.01110042/SBR
Build-In Floor | Mini Canal | MICL.01110042/SDB | 11 | 100 | 42 | 42 | 447 | 447 | 447 | 0.010643 | 174 | 0.0041429 | 509 | 0.012119 | 1.362 | A04 | MICL0.01110042/SDB
Build-In Floor | Mini Canal | MICL.01110042/SNA | 11 | 100 | 42 | 42 | 447 | 447 | 447 | 0.010643 | 174 | 0.0041429 | 509 | 0.012119 | 1.362 | A04 | MICL0.01110042/SNA
Build-In Floor | Mini Canal | MICL.01110042/SNC | 11 | 100 | 42 | 42 | 447 | 447 | 447 | 0.010643 | 174 | 0.0041429 | 509 | 0.012119 | 1.362 | A04 | MICL0.01110042/SNC
Build-In Floor | Mini Canal | MICL.01111014/ANA | 11 | 110 | 14 | 14 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.01111014/ANA
Build-In Floor | Mini Canal | MICL.01111014/DBL | 11 | 110 | 14 | 14 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01111014/DBL
Build-In Floor | Mini Canal | MICL.01111014/DBN | 11 | 110 | 14 | 14 | 163 | 163 | 163 | 0.003881 | 63 | 0.0015 | 186 | 0.0044286 | 1.362 | A04 | MICL0.01111014/DBN
Build-In Floor | Mini Canal | MICL.01111014/DBR | 11 | 110 | 14 | 14 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01111014/DBR
Build-In Floor | Mini Canal | MICL.01111014/DBV | 11 | 110 | 14 | 14 | 163 | 163 | 163 | 0.003881 | 63 | 0.0015 | 186 | 0.0044286 | 1.362 | A04 | MICL0.01111014/DBV
Build-In Floor | Mini Canal | MICL.01111014/DDB | 11 | 110 | 14 | 14 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01111014/DDB
Build-In Floor | Mini Canal | MICL.01111014/DMN | 11 | 110 | 14 | 14 | 163 | 163 | 163 | 0.003881 | 63 | 0.0015 | 186 | 0.0044286 | 1.362 | A04 | MICL0.01111014/DMN
Build-In Floor | Mini Canal | MICL.01111014/DMV | 11 | 110 | 14 | 14 | 163 | 163 | 163 | 0.003881 | 63 | 0.0015 | 186 | 0.0044286 | 1.362 | A04 | MICL0.01111014/DMV
Build-In Floor | Mini Canal | MICL.01111014/DNA | 11 | 110 | 14 | 14 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01111014/DNA
Build-In Floor | Mini Canal | MICL.01111014/DNC | 11 | 110 | 14 | 14 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01111014/DNC
Build-In Floor | Mini Canal | MICL.01111014/DON | 11 | 110 | 14 | 14 | 163 | 163 | 163 | 0.003881 | 63 | 0.0015 | 186 | 0.0044286 | 1.362 | A04 | MICL0.01111014/DON
Build-In Floor | Mini Canal | MICL.01111014/DOV | 11 | 110 | 14 | 14 | 163 | 163 | 163 | 0.003881 | 63 | 0.0015 | 186 | 0.0044286 | 1.362 | A04 | MICL0.01111014/DOV
Build-In Floor | Mini Canal | MICL.01111014/RBL | 11 | 110 | 14 | 14 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01111014/RBL
Build-In Floor | Mini Canal | MICL.01111014/RBN | 11 | 110 | 14 | 14 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01111014/RBN
Build-In Floor | Mini Canal | MICL.01111014/RBR | 11 | 110 | 14 | 14 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01111014/RBR
Build-In Floor | Mini Canal | MICL.01111014/RBV | 11 | 110 | 14 | 14 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01111014/RBV
Build-In Floor | Mini Canal | MICL.01111014/RDB | 11 | 110 | 14 | 14 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01111014/RDB
Build-In Floor | Mini Canal | MICL.01111014/RMN | 11 | 110 | 14 | 14 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01111014/RMN
Build-In Floor | Mini Canal | MICL.01111014/RMV | 11 | 110 | 14 | 14 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01111014/RMV
Build-In Floor | Mini Canal | MICL.01111014/RNA | 11 | 110 | 14 | 14 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01111014/RNA
Build-In Floor | Mini Canal | MICL.01111014/RON | 11 | 110 | 14 | 14 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01111014/RON
Build-In Floor | Mini Canal | MICL.01111014/ROV | 11 | 110 | 14 | 14 | 170 | 170 | 170 | 0.0040476 | 66 | 0.0015714 | 194 | 0.004619 | 1.362 | A04 | MICL0.01111014/ROV
Build-In Floor | Mini Canal | MICL.01111014/RSS | 11 | 110 | 14 | 14 | 168 | 168 | 168 | 0.004 | 65 | 0.0015476 | 191 | 0.0045476 | 1.362 | A04 | MICL0.01111014/RSS
Build-In Floor | Mini Canal | MICL.01111014/SBL | 11 | 110 | 14 | 14 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01111014/SBL
Build-In Floor | Mini Canal | MICL.01111014/SBR | 11 | 110 | 14 | 14 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01111014/SBR
Build-In Floor | Mini Canal | MICL.01111014/SDB | 11 | 110 | 14 | 14 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01111014/SDB
Build-In Floor | Mini Canal | MICL.01111014/SNA | 11 | 110 | 14 | 14 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01111014/SNA
Build-In Floor | Mini Canal | MICL.01111014/SNC | 11 | 110 | 14 | 14 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01111014/SNC
Build-In Floor | Mini Canal | MICL.01111018/ANA | 11 | 110 | 18 | 18 | 155 | 155 | 155 | 0.0036905 | 60 | 0.0014286 | 177 | 0.0042143 | 1.362 | A04 | MICL0.01111018/ANA
Build-In Floor | Mini Canal | MICL.01111018/DBL | 11 | 110 | 18 | 18 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.01111018/DBL
Build-In Floor | Mini Canal | MICL.01111018/DBN | 11 | 110 | 18 | 18 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.01111018/DBN
Build-In Floor | Mini Canal | MICL.01111018/DBR | 11 | 110 | 18 | 18 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.01111018/DBR
Build-In Floor | Mini Canal | MICL.01111018/DBV | 11 | 110 | 18 | 18 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.01111018/DBV
Build-In Floor | Mini Canal | MICL.01111018/DDB | 11 | 110 | 18 | 18 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.01111018/DDB
Build-In Floor | Mini Canal | MICL.01111018/DMN | 11 | 110 | 18 | 18 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.01111018/DMN
Build-In Floor | Mini Canal | MICL.01111018/DMV | 11 | 110 | 18 | 18 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.01111018/DMV
Build-In Floor | Mini Canal | MICL.01111018/DNA | 11 | 110 | 18 | 18 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.01111018/DNA
Build-In Floor | Mini Canal | MICL.01111018/DNC | 11 | 110 | 18 | 18 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.01111018/DNC
Build-In Floor | Mini Canal | MICL.01111018/DON | 11 | 110 | 18 | 18 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.01111018/DON
Build-In Floor | Mini Canal | MICL.01111018/DOV | 11 | 110 | 18 | 18 | 193 | 193 | 193 | 0.0045952 | 75 | 0.0017857 | 220 | 0.0052381 | 1.362 | A04 | MICL0.01111018/DOV
Build-In Floor | Mini Canal | MICL.01111018/RBL | 11 | 110 | 18 | 18 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01111018/RBL
Build-In Floor | Mini Canal | MICL.01111018/RBN | 11 | 110 | 18 | 18 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.01111018/RBN
Build-In Floor | Mini Canal | MICL.01111018/RBR | 11 | 110 | 18 | 18 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01111018/RBR
Build-In Floor | Mini Canal | MICL.01111018/RBV | 11 | 110 | 18 | 18 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.01111018/RBV
Build-In Floor | Mini Canal | MICL.01111018/RDB | 11 | 110 | 18 | 18 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01111018/RDB
Build-In Floor | Mini Canal | MICL.01111018/RMN | 11 | 110 | 18 | 18 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.01111018/RMN
Build-In Floor | Mini Canal | MICL.01111018/RMV | 11 | 110 | 18 | 18 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.01111018/RMV
Build-In Floor | Mini Canal | MICL.01111018/RNA | 11 | 110 | 18 | 18 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01111018/RNA
Build-In Floor | Mini Canal | MICL.01111018/RON | 11 | 110 | 18 | 18 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.01111018/RON
Build-In Floor | Mini Canal | MICL.01111018/ROV | 11 | 110 | 18 | 18 | 201 | 201 | 201 | 0.0047857 | 78 | 0.0018571 | 229 | 0.0054524 | 1.362 | A04 | MICL0.01111018/ROV
Build-In Floor | Mini Canal | MICL.01111018/RSS | 11 | 110 | 18 | 18 | 199 | 199 | 199 | 0.0047381 | 77 | 0.0018333 | 227 | 0.0054048 | 1.362 | A04 | MICL0.01111018/RSS
Build-In Floor | Mini Canal | MICL.01111018/SBL | 11 | 110 | 18 | 18 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01111018/SBL
Build-In Floor | Mini Canal | MICL.01111018/SBR | 11 | 110 | 18 | 18 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01111018/SBR
Build-In Floor | Mini Canal | MICL.01111018/SDB | 11 | 110 | 18 | 18 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01111018/SDB
Build-In Floor | Mini Canal | MICL.01111018/SNA | 11 | 110 | 18 | 18 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01111018/SNA
Build-In Floor | Mini Canal | MICL.01111018/SNC | 11 | 110 | 18 | 18 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01111018/SNC
Build-In Floor | Mini Canal | MICL.01111026/ANA | 11 | 110 | 26 | 26 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.01111026/ANA
Build-In Floor | Mini Canal | MICL.01111026/DBL | 11 | 110 | 26 | 26 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.01111026/DBL
Build-In Floor | Mini Canal | MICL.01111026/DBN | 11 | 110 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01111026/DBN
Build-In Floor | Mini Canal | MICL.01111026/DBR | 11 | 110 | 26 | 26 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.01111026/DBR
Build-In Floor | Mini Canal | MICL.01111026/DBV | 11 | 110 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01111026/DBV
Build-In Floor | Mini Canal | MICL.01111026/DDB | 11 | 110 | 26 | 26 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.01111026/DDB
Build-In Floor | Mini Canal | MICL.01111026/DMN | 11 | 110 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01111026/DMN
Build-In Floor | Mini Canal | MICL.01111026/DMV | 11 | 110 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01111026/DMV
Build-In Floor | Mini Canal | MICL.01111026/DNA | 11 | 110 | 26 | 26 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.01111026/DNA
Build-In Floor | Mini Canal | MICL.01111026/DNC | 11 | 110 | 26 | 26 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.01111026/DNC
Build-In Floor | Mini Canal | MICL.01111026/DON | 11 | 110 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01111026/DON
Build-In Floor | Mini Canal | MICL.01111026/DOV | 11 | 110 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01111026/DOV
Build-In Floor | Mini Canal | MICL.01111026/PNC | 11 | 110 | 26 | 26 | 237 | 237 | 237 | 0.0056429 | 92 | 0.0021905 | 270 | 0.0064286 | 1.362 | A04 | MICL0.01111026/PNC
Build-In Floor | Mini Canal | MICL.01111026/RBL | 11 | 110 | 26 | 26 | 279 | 279 | 279 | 0.0066429 | 109 | 0.0025952 | 318 | 0.0075714 | 1.362 | A04 | MICL0.01111026/RBL
Build-In Floor | Mini Canal | MICL.01111026/RBN | 11 | 110 | 26 | 26 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.01111026/RBN
Build-In Floor | Mini Canal | MICL.01111026/RBR | 11 | 110 | 26 | 26 | 279 | 279 | 279 | 0.0066429 | 109 | 0.0025952 | 318 | 0.0075714 | 1.362 | A04 | MICL0.01111026/RBR
Build-In Floor | Mini Canal | MICL.01111026/RBV | 11 | 110 | 26 | 26 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.01111026/RBV
Build-In Floor | Mini Canal | MICL.01111026/RDB | 11 | 110 | 26 | 26 | 279 | 279 | 279 | 0.0066429 | 109 | 0.0025952 | 318 | 0.0075714 | 1.362 | A04 | MICL0.01111026/RDB
Build-In Floor | Mini Canal | MICL.01111026/RMN | 11 | 110 | 26 | 26 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.01111026/RMN
Build-In Floor | Mini Canal | MICL.01111026/RMV | 11 | 110 | 26 | 26 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.01111026/RMV
Build-In Floor | Mini Canal | MICL.01111026/RNA | 11 | 110 | 26 | 26 | 279 | 279 | 279 | 0.0066429 | 109 | 0.0025952 | 318 | 0.0075714 | 1.362 | A04 | MICL0.01111026/RNA
Build-In Floor | Mini Canal | MICL.01111026/RON | 11 | 110 | 26 | 26 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.01111026/RON
Build-In Floor | Mini Canal | MICL.01111026/ROV | 11 | 110 | 26 | 26 | 271 | 271 | 271 | 0.0064524 | 105 | 0.0025 | 309 | 0.0073571 | 1.362 | A04 | MICL0.01111026/ROV
Build-In Floor | Mini Canal | MICL.01111026/RSS | 11 | 110 | 26 | 26 | 268 | 268 | 268 | 0.006381 | 104 | 0.0024762 | 305 | 0.0072619 | 1.362 | A04 | MICL0.01111026/RSS
Build-In Floor | Mini Canal | MICL.01111026/SBL | 11 | 110 | 26 | 26 | 279 | 279 | 279 | 0.0066429 | 109 | 0.0025952 | 318 | 0.0075714 | 1.362 | A04 | MICL0.01111026/SBL
Build-In Floor | Mini Canal | MICL.01111026/SBR | 11 | 110 | 26 | 26 | 279 | 279 | 279 | 0.0066429 | 109 | 0.0025952 | 318 | 0.0075714 | 1.362 | A04 | MICL0.01111026/SBR
Build-In Floor | Mini Canal | MICL.01111026/SDB | 11 | 110 | 26 | 26 | 279 | 279 | 279 | 0.0066429 | 109 | 0.0025952 | 318 | 0.0075714 | 1.362 | A04 | MICL0.01111026/SDB
Build-In Floor | Mini Canal | MICL.01111026/SNA | 11 | 110 | 26 | 26 | 279 | 279 | 279 | 0.0066429 | 109 | 0.0025952 | 318 | 0.0075714 | 1.362 | A04 | MICL0.01111026/SNA
Build-In Floor | Mini Canal | MICL.01111026/SNC | 11 | 110 | 26 | 26 | 279 | 279 | 279 | 0.0066429 | 109 | 0.0025952 | 318 | 0.0075714 | 1.362 | A04 | MICL0.01111026/SNC
Build-In Floor | Mini Canal | MICL.01111034/ANA | 11 | 110 | 34 | 34 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01111034/ANA
Build-In Floor | Mini Canal | MICL.01111034/DBL | 11 | 110 | 34 | 34 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01111034/DBL
Build-In Floor | Mini Canal | MICL.01111034/DBN | 11 | 110 | 34 | 34 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01111034/DBN
Build-In Floor | Mini Canal | MICL.01111034/DBR | 11 | 110 | 34 | 34 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01111034/DBR
Build-In Floor | Mini Canal | MICL.01111034/DBV | 11 | 110 | 34 | 34 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01111034/DBV
Build-In Floor | Mini Canal | MICL.01111034/DDB | 11 | 110 | 34 | 34 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01111034/DDB
Build-In Floor | Mini Canal | MICL.01111034/DMN | 11 | 110 | 34 | 34 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01111034/DMN
Build-In Floor | Mini Canal | MICL.01111034/DMV | 11 | 110 | 34 | 34 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01111034/DMV
Build-In Floor | Mini Canal | MICL.01111034/DNA | 11 | 110 | 34 | 34 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01111034/DNA
Build-In Floor | Mini Canal | MICL.01111034/DNC | 11 | 110 | 34 | 34 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01111034/DNC
Build-In Floor | Mini Canal | MICL.01111034/DON | 11 | 110 | 34 | 34 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01111034/DON
Build-In Floor | Mini Canal | MICL.01111034/DOV | 11 | 110 | 34 | 34 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01111034/DOV
Build-In Floor | Mini Canal | MICL.01111034/PNC | 11 | 110 | 34 | 34 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01111034/PNC
Build-In Floor | Mini Canal | MICL.01111034/RBL | 11 | 110 | 34 | 34 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01111034/RBL
Build-In Floor | Mini Canal | MICL.01111034/RBN | 11 | 110 | 34 | 34 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01111034/RBN
Build-In Floor | Mini Canal | MICL.01111034/RBR | 11 | 110 | 34 | 34 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01111034/RBR
Build-In Floor | Mini Canal | MICL.01111034/RBV | 11 | 110 | 34 | 34 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01111034/RBV
Build-In Floor | Mini Canal | MICL.01111034/RDB | 11 | 110 | 34 | 34 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01111034/RDB
Build-In Floor | Mini Canal | MICL.01111034/RMN | 11 | 110 | 34 | 34 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01111034/RMN
Build-In Floor | Mini Canal | MICL.01111034/RMV | 11 | 110 | 34 | 34 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01111034/RMV
Build-In Floor | Mini Canal | MICL.01111034/RNA | 11 | 110 | 34 | 34 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01111034/RNA
Build-In Floor | Mini Canal | MICL.01111034/RON | 11 | 110 | 34 | 34 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01111034/RON
Build-In Floor | Mini Canal | MICL.01111034/ROV | 11 | 110 | 34 | 34 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01111034/ROV
Build-In Floor | Mini Canal | MICL.01111034/RSS | 11 | 110 | 34 | 34 | 348 | 348 | 348 | 0.0082857 | 135 | 0.0032143 | 396 | 0.0094286 | 1.362 | A04 | MICL0.01111034/RSS
Build-In Floor | Mini Canal | MICL.01111034/SBL | 11 | 110 | 34 | 34 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01111034/SBL
Build-In Floor | Mini Canal | MICL.01111034/SBR | 11 | 110 | 34 | 34 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01111034/SBR
Build-In Floor | Mini Canal | MICL.01111034/SDB | 11 | 110 | 34 | 34 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01111034/SDB
Build-In Floor | Mini Canal | MICL.01111034/SNA | 11 | 110 | 34 | 34 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01111034/SNA
Build-In Floor | Mini Canal | MICL.01111034/SNC | 11 | 110 | 34 | 34 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01111034/SNC
Build-In Floor | Mini Canal | MICL.01111042/ANA | 11 | 110 | 42 | 42 | 383 | 383 | 383 | 0.009119 | 149 | 0.0035476 | 436 | 0.010381 | 1.362 | A04 | MICL0.01111042/ANA
Build-In Floor | Mini Canal | MICL.01111042/DBL | 11 | 110 | 42 | 42 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.01111042/DBL
Build-In Floor | Mini Canal | MICL.01111042/DBN | 11 | 110 | 42 | 42 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01111042/DBN
Build-In Floor | Mini Canal | MICL.01111042/DBR | 11 | 110 | 42 | 42 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.01111042/DBR
Build-In Floor | Mini Canal | MICL.01111042/DBV | 11 | 110 | 42 | 42 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01111042/DBV
Build-In Floor | Mini Canal | MICL.01111042/DDB | 11 | 110 | 42 | 42 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.01111042/DDB
Build-In Floor | Mini Canal | MICL.01111042/DMN | 11 | 110 | 42 | 42 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01111042/DMN
Build-In Floor | Mini Canal | MICL.01111042/DMV | 11 | 110 | 42 | 42 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01111042/DMV
Build-In Floor | Mini Canal | MICL.01111042/DNA | 11 | 110 | 42 | 42 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.01111042/DNA
Build-In Floor | Mini Canal | MICL.01111042/DNC | 11 | 110 | 42 | 42 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.01111042/DNC
Build-In Floor | Mini Canal | MICL.01111042/DON | 11 | 110 | 42 | 42 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01111042/DON
Build-In Floor | Mini Canal | MICL.01111042/DOV | 11 | 110 | 42 | 42 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01111042/DOV
Build-In Floor | Mini Canal | MICL.01111042/PNC | 11 | 110 | 42 | 42 | 434 | 434 | 434 | 0.010333 | 169 | 0.0040238 | 494 | 0.011762 | 1.362 | A04 | MICL0.01111042/PNC
Build-In Floor | Mini Canal | MICL.01111042/RBL | 11 | 110 | 42 | 42 | 510 | 510 | 510 | 0.012143 | 198 | 0.0047143 | 581 | 0.013833 | 1.362 | A04 | MICL0.01111042/RBL
Build-In Floor | Mini Canal | MICL.01111042/RBN | 11 | 110 | 42 | 42 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.01111042/RBN
Build-In Floor | Mini Canal | MICL.01111042/RBR | 11 | 110 | 42 | 42 | 510 | 510 | 510 | 0.012143 | 198 | 0.0047143 | 581 | 0.013833 | 1.362 | A04 | MICL0.01111042/RBR
Build-In Floor | Mini Canal | MICL.01111042/RBV | 11 | 110 | 42 | 42 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.01111042/RBV
Build-In Floor | Mini Canal | MICL.01111042/RDB | 11 | 110 | 42 | 42 | 510 | 510 | 510 | 0.012143 | 198 | 0.0047143 | 581 | 0.013833 | 1.362 | A04 | MICL0.01111042/RDB
Build-In Floor | Mini Canal | MICL.01111042/RMN | 11 | 110 | 42 | 42 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.01111042/RMN
Build-In Floor | Mini Canal | MICL.01111042/RMV | 11 | 110 | 42 | 42 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.01111042/RMV
Build-In Floor | Mini Canal | MICL.01111042/RNA | 11 | 110 | 42 | 42 | 510 | 510 | 510 | 0.012143 | 198 | 0.0047143 | 581 | 0.013833 | 1.362 | A04 | MICL0.01111042/RNA
Build-In Floor | Mini Canal | MICL.01111042/RON | 11 | 110 | 42 | 42 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.01111042/RON
Build-In Floor | Mini Canal | MICL.01111042/ROV | 11 | 110 | 42 | 42 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.01111042/ROV
Build-In Floor | Mini Canal | MICL.01111042/RSS | 11 | 110 | 42 | 42 | 490 | 490 | 490 | 0.011667 | 191 | 0.0045476 | 558 | 0.013286 | 1.362 | A04 | MICL0.01111042/RSS
Build-In Floor | Mini Canal | MICL.01111042/SBL | 11 | 110 | 42 | 42 | 510 | 510 | 510 | 0.012143 | 198 | 0.0047143 | 581 | 0.013833 | 1.362 | A04 | MICL0.01111042/SBL
Build-In Floor | Mini Canal | MICL.01111042/SBR | 11 | 110 | 42 | 42 | 510 | 510 | 510 | 0.012143 | 198 | 0.0047143 | 581 | 0.013833 | 1.362 | A04 | MICL0.01111042/SBR
Build-In Floor | Mini Canal | MICL.01111042/SDB | 11 | 110 | 42 | 42 | 510 | 510 | 510 | 0.012143 | 198 | 0.0047143 | 581 | 0.013833 | 1.362 | A04 | MICL0.01111042/SDB
Build-In Floor | Mini Canal | MICL.01111042/SNA | 11 | 110 | 42 | 42 | 510 | 510 | 510 | 0.012143 | 198 | 0.0047143 | 581 | 0.013833 | 1.362 | A04 | MICL0.01111042/SNA
Build-In Floor | Mini Canal | MICL.01111042/SNC | 11 | 110 | 42 | 42 | 510 | 510 | 510 | 0.012143 | 198 | 0.0047143 | 581 | 0.013833 | 1.362 | A04 | MICL0.01111042/SNC
Build-In Floor | Mini Canal | MICL.01112014/ANA | 11 | 120 | 14 | 14 | 148 | 148 | 148 | 0.0035238 | 58 | 0.001381 | 169 | 0.0040238 | 1.362 | A04 | MICL0.01112014/ANA
Build-In Floor | Mini Canal | MICL.01112014/DBL | 11 | 120 | 14 | 14 | 191 | 191 | 191 | 0.0045476 | 74 | 0.0017619 | 218 | 0.0051905 | 1.362 | A04 | MICL0.01112014/DBL
Build-In Floor | Mini Canal | MICL.01112014/DBN | 11 | 120 | 14 | 14 | 183 | 183 | 183 | 0.0043571 | 71 | 0.0016905 | 208 | 0.0049524 | 1.362 | A04 | MICL0.01112014/DBN
Build-In Floor | Mini Canal | MICL.01112014/DBR | 11 | 120 | 14 | 14 | 191 | 191 | 191 | 0.0045476 | 74 | 0.0017619 | 218 | 0.0051905 | 1.362 | A04 | MICL0.01112014/DBR
Build-In Floor | Mini Canal | MICL.01112014/DBV | 11 | 120 | 14 | 14 | 183 | 183 | 183 | 0.0043571 | 71 | 0.0016905 | 208 | 0.0049524 | 1.362 | A04 | MICL0.01112014/DBV
Build-In Floor | Mini Canal | MICL.01112014/DDB | 11 | 120 | 14 | 14 | 191 | 191 | 191 | 0.0045476 | 74 | 0.0017619 | 218 | 0.0051905 | 1.362 | A04 | MICL0.01112014/DDB
Build-In Floor | Mini Canal | MICL.01112014/DMN | 11 | 120 | 14 | 14 | 183 | 183 | 183 | 0.0043571 | 71 | 0.0016905 | 208 | 0.0049524 | 1.362 | A04 | MICL0.01112014/DMN
Build-In Floor | Mini Canal | MICL.01112014/DMV | 11 | 120 | 14 | 14 | 183 | 183 | 183 | 0.0043571 | 71 | 0.0016905 | 208 | 0.0049524 | 1.362 | A04 | MICL0.01112014/DMV
Build-In Floor | Mini Canal | MICL.01112014/DNA | 11 | 120 | 14 | 14 | 191 | 191 | 191 | 0.0045476 | 74 | 0.0017619 | 218 | 0.0051905 | 1.362 | A04 | MICL0.01112014/DNA
Build-In Floor | Mini Canal | MICL.01112014/DNC | 11 | 120 | 14 | 14 | 191 | 191 | 191 | 0.0045476 | 74 | 0.0017619 | 218 | 0.0051905 | 1.362 | A04 | MICL0.01112014/DNC
Build-In Floor | Mini Canal | MICL.01112014/DON | 11 | 120 | 14 | 14 | 183 | 183 | 183 | 0.0043571 | 71 | 0.0016905 | 208 | 0.0049524 | 1.362 | A04 | MICL0.01112014/DON
Build-In Floor | Mini Canal | MICL.01112014/DOV | 11 | 120 | 14 | 14 | 183 | 183 | 183 | 0.0043571 | 71 | 0.0016905 | 208 | 0.0049524 | 1.362 | A04 | MICL0.01112014/DOV
Build-In Floor | Mini Canal | MICL.01112014/RBL | 11 | 120 | 14 | 14 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.01112014/RBL
Build-In Floor | Mini Canal | MICL.01112014/RBN | 11 | 120 | 14 | 14 | 191 | 191 | 191 | 0.0045476 | 74 | 0.0017619 | 218 | 0.0051905 | 1.362 | A04 | MICL0.01112014/RBN
Build-In Floor | Mini Canal | MICL.01112014/RBR | 11 | 120 | 14 | 14 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.01112014/RBR
Build-In Floor | Mini Canal | MICL.01112014/RBV | 11 | 120 | 14 | 14 | 191 | 191 | 191 | 0.0045476 | 74 | 0.0017619 | 218 | 0.0051905 | 1.362 | A04 | MICL0.01112014/RBV
Build-In Floor | Mini Canal | MICL.01112014/RDB | 11 | 120 | 14 | 14 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.01112014/RDB
Build-In Floor | Mini Canal | MICL.01112014/RMN | 11 | 120 | 14 | 14 | 191 | 191 | 191 | 0.0045476 | 74 | 0.0017619 | 218 | 0.0051905 | 1.362 | A04 | MICL0.01112014/RMN
Build-In Floor | Mini Canal | MICL.01112014/RMV | 11 | 120 | 14 | 14 | 191 | 191 | 191 | 0.0045476 | 74 | 0.0017619 | 218 | 0.0051905 | 1.362 | A04 | MICL0.01112014/RMV
Build-In Floor | Mini Canal | MICL.01112014/RNA | 11 | 120 | 14 | 14 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.01112014/RNA
Build-In Floor | Mini Canal | MICL.01112014/RON | 11 | 120 | 14 | 14 | 191 | 191 | 191 | 0.0045476 | 74 | 0.0017619 | 218 | 0.0051905 | 1.362 | A04 | MICL0.01112014/RON
Build-In Floor | Mini Canal | MICL.01112014/ROV | 11 | 120 | 14 | 14 | 191 | 191 | 191 | 0.0045476 | 74 | 0.0017619 | 218 | 0.0051905 | 1.362 | A04 | MICL0.01112014/ROV
Build-In Floor | Mini Canal | MICL.01112014/RSS | 11 | 120 | 14 | 14 | 189 | 189 | 189 | 0.0045 | 74 | 0.0017619 | 215 | 0.005119 | 1.362 | A04 | MICL0.01112014/RSS
Build-In Floor | Mini Canal | MICL.01112014/SBL | 11 | 120 | 14 | 14 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.01112014/SBL
Build-In Floor | Mini Canal | MICL.01112014/SBR | 11 | 120 | 14 | 14 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.01112014/SBR
Build-In Floor | Mini Canal | MICL.01112014/SDB | 11 | 120 | 14 | 14 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.01112014/SDB
Build-In Floor | Mini Canal | MICL.01112014/SNA | 11 | 120 | 14 | 14 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.01112014/SNA
Build-In Floor | Mini Canal | MICL.01112014/SNC | 11 | 120 | 14 | 14 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.01112014/SNC
Build-In Floor | Mini Canal | MICL.01112018/ANA | 11 | 120 | 18 | 18 | 175 | 175 | 175 | 0.0041667 | 68 | 0.001619 | 199 | 0.0047381 | 1.362 | A04 | MICL0.01112018/ANA
Build-In Floor | Mini Canal | MICL.01112018/DBL | 11 | 120 | 18 | 18 | 226 | 226 | 226 | 0.005381 | 88 | 0.0020952 | 257 | 0.006119 | 1.362 | A04 | MICL0.01112018/DBL
Build-In Floor | Mini Canal | MICL.01112018/DBN | 11 | 120 | 18 | 18 | 217 | 217 | 217 | 0.0051667 | 84 | 0.002 | 247 | 0.005881 | 1.362 | A04 | MICL0.01112018/DBN
Build-In Floor | Mini Canal | MICL.01112018/DBR | 11 | 120 | 18 | 18 | 226 | 226 | 226 | 0.005381 | 88 | 0.0020952 | 257 | 0.006119 | 1.362 | A04 | MICL0.01112018/DBR
Build-In Floor | Mini Canal | MICL.01112018/DBV | 11 | 120 | 18 | 18 | 217 | 217 | 217 | 0.0051667 | 84 | 0.002 | 247 | 0.005881 | 1.362 | A04 | MICL0.01112018/DBV
Build-In Floor | Mini Canal | MICL.01112018/DDB | 11 | 120 | 18 | 18 | 226 | 226 | 226 | 0.005381 | 88 | 0.0020952 | 257 | 0.006119 | 1.362 | A04 | MICL0.01112018/DDB
Build-In Floor | Mini Canal | MICL.01112018/DMN | 11 | 120 | 18 | 18 | 217 | 217 | 217 | 0.0051667 | 84 | 0.002 | 247 | 0.005881 | 1.362 | A04 | MICL0.01112018/DMN
Build-In Floor | Mini Canal | MICL.01112018/DMV | 11 | 120 | 18 | 18 | 217 | 217 | 217 | 0.0051667 | 84 | 0.002 | 247 | 0.005881 | 1.362 | A04 | MICL0.01112018/DMV
Build-In Floor | Mini Canal | MICL.01112018/DNA | 11 | 120 | 18 | 18 | 226 | 226 | 226 | 0.005381 | 88 | 0.0020952 | 257 | 0.006119 | 1.362 | A04 | MICL0.01112018/DNA
Build-In Floor | Mini Canal | MICL.01112018/DNC | 11 | 120 | 18 | 18 | 226 | 226 | 226 | 0.005381 | 88 | 0.0020952 | 257 | 0.006119 | 1.362 | A04 | MICL0.01112018/DNC
Build-In Floor | Mini Canal | MICL.01112018/DON | 11 | 120 | 18 | 18 | 217 | 217 | 217 | 0.0051667 | 84 | 0.002 | 247 | 0.005881 | 1.362 | A04 | MICL0.01112018/DON
Build-In Floor | Mini Canal | MICL.01112018/DOV | 11 | 120 | 18 | 18 | 217 | 217 | 217 | 0.0051667 | 84 | 0.002 | 247 | 0.005881 | 1.362 | A04 | MICL0.01112018/DOV
Build-In Floor | Mini Canal | MICL.01112018/RBL | 11 | 120 | 18 | 18 | 233 | 233 | 233 | 0.0055476 | 91 | 0.0021667 | 265 | 0.0063095 | 1.362 | A04 | MICL0.01112018/RBL
Build-In Floor | Mini Canal | MICL.01112018/RBN | 11 | 120 | 18 | 18 | 226 | 226 | 226 | 0.005381 | 88 | 0.0020952 | 257 | 0.006119 | 1.362 | A04 | MICL0.01112018/RBN
Build-In Floor | Mini Canal | MICL.01112018/RBR | 11 | 120 | 18 | 18 | 233 | 233 | 233 | 0.0055476 | 91 | 0.0021667 | 265 | 0.0063095 | 1.362 | A04 | MICL0.01112018/RBR
Build-In Floor | Mini Canal | MICL.01112018/RBV | 11 | 120 | 18 | 18 | 226 | 226 | 226 | 0.005381 | 88 | 0.0020952 | 257 | 0.006119 | 1.362 | A04 | MICL0.01112018/RBV
Build-In Floor | Mini Canal | MICL.01112018/RDB | 11 | 120 | 18 | 18 | 233 | 233 | 233 | 0.0055476 | 91 | 0.0021667 | 265 | 0.0063095 | 1.362 | A04 | MICL0.01112018/RDB
Build-In Floor | Mini Canal | MICL.01112018/RMN | 11 | 120 | 18 | 18 | 226 | 226 | 226 | 0.005381 | 88 | 0.0020952 | 257 | 0.006119 | 1.362 | A04 | MICL0.01112018/RMN
Build-In Floor | Mini Canal | MICL.01112018/RMV | 11 | 120 | 18 | 18 | 226 | 226 | 226 | 0.005381 | 88 | 0.0020952 | 257 | 0.006119 | 1.362 | A04 | MICL0.01112018/RMV
Build-In Floor | Mini Canal | MICL.01112018/RNA | 11 | 120 | 18 | 18 | 233 | 233 | 233 | 0.0055476 | 91 | 0.0021667 | 265 | 0.0063095 | 1.362 | A04 | MICL0.01112018/RNA
Build-In Floor | Mini Canal | MICL.01112018/RON | 11 | 120 | 18 | 18 | 226 | 226 | 226 | 0.005381 | 88 | 0.0020952 | 257 | 0.006119 | 1.362 | A04 | MICL0.01112018/RON
Build-In Floor | Mini Canal | MICL.01112018/ROV | 11 | 120 | 18 | 18 | 226 | 226 | 226 | 0.005381 | 88 | 0.0020952 | 257 | 0.006119 | 1.362 | A04 | MICL0.01112018/ROV
Build-In Floor | Mini Canal | MICL.01112018/RSS | 11 | 120 | 18 | 18 | 224 | 224 | 224 | 0.0053333 | 87 | 0.0020714 | 255 | 0.0060714 | 1.362 | A04 | MICL0.01112018/RSS
Build-In Floor | Mini Canal | MICL.01112018/SBL | 11 | 120 | 18 | 18 | 233 | 233 | 233 | 0.0055476 | 91 | 0.0021667 | 265 | 0.0063095 | 1.362 | A04 | MICL0.01112018/SBL
Build-In Floor | Mini Canal | MICL.01112018/SBR | 11 | 120 | 18 | 18 | 233 | 233 | 233 | 0.0055476 | 91 | 0.0021667 | 265 | 0.0063095 | 1.362 | A04 | MICL0.01112018/SBR
Build-In Floor | Mini Canal | MICL.01112018/SDB | 11 | 120 | 18 | 18 | 233 | 233 | 233 | 0.0055476 | 91 | 0.0021667 | 265 | 0.0063095 | 1.362 | A04 | MICL0.01112018/SDB
Build-In Floor | Mini Canal | MICL.01112018/SNA | 11 | 120 | 18 | 18 | 233 | 233 | 233 | 0.0055476 | 91 | 0.0021667 | 265 | 0.0063095 | 1.362 | A04 | MICL0.01112018/SNA
Build-In Floor | Mini Canal | MICL.01112018/SNC | 11 | 120 | 18 | 18 | 233 | 233 | 233 | 0.0055476 | 91 | 0.0021667 | 265 | 0.0063095 | 1.362 | A04 | MICL0.01112018/SNC
Build-In Floor | Mini Canal | MICL.01112026/ANA | 11 | 120 | 26 | 26 | 236 | 236 | 236 | 0.005619 | 92 | 0.0021905 | 269 | 0.0064048 | 1.362 | A04 | MICL0.01112026/ANA
Build-In Floor | Mini Canal | MICL.01112026/DBL | 11 | 120 | 26 | 26 | 305 | 305 | 305 | 0.0072619 | 119 | 0.0028333 | 347 | 0.0082619 | 1.362 | A04 | MICL0.01112026/DBL
Build-In Floor | Mini Canal | MICL.01112026/DBN | 11 | 120 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01112026/DBN
Build-In Floor | Mini Canal | MICL.01112026/DBR | 11 | 120 | 26 | 26 | 305 | 305 | 305 | 0.0072619 | 119 | 0.0028333 | 347 | 0.0082619 | 1.362 | A04 | MICL0.01112026/DBR
Build-In Floor | Mini Canal | MICL.01112026/DBV | 11 | 120 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01112026/DBV
Build-In Floor | Mini Canal | MICL.01112026/DDB | 11 | 120 | 26 | 26 | 305 | 305 | 305 | 0.0072619 | 119 | 0.0028333 | 347 | 0.0082619 | 1.362 | A04 | MICL0.01112026/DDB
Build-In Floor | Mini Canal | MICL.01112026/DMN | 11 | 120 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01112026/DMN
Build-In Floor | Mini Canal | MICL.01112026/DMV | 11 | 120 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01112026/DMV
Build-In Floor | Mini Canal | MICL.01112026/DNA | 11 | 120 | 26 | 26 | 305 | 305 | 305 | 0.0072619 | 119 | 0.0028333 | 347 | 0.0082619 | 1.362 | A04 | MICL0.01112026/DNA
Build-In Floor | Mini Canal | MICL.01112026/DNC | 11 | 120 | 26 | 26 | 305 | 305 | 305 | 0.0072619 | 119 | 0.0028333 | 347 | 0.0082619 | 1.362 | A04 | MICL0.01112026/DNC
Build-In Floor | Mini Canal | MICL.01112026/DON | 11 | 120 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01112026/DON
Build-In Floor | Mini Canal | MICL.01112026/DOV | 11 | 120 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01112026/DOV
Build-In Floor | Mini Canal | MICL.01112026/PNC | 11 | 120 | 26 | 26 | 267 | 267 | 267 | 0.0063571 | 104 | 0.0024762 | 304 | 0.0072381 | 1.362 | A04 | MICL0.01112026/PNC
Build-In Floor | Mini Canal | MICL.01112026/RBL | 11 | 120 | 26 | 26 | 314 | 314 | 314 | 0.0074762 | 122 | 0.0029048 | 358 | 0.0085238 | 1.362 | A04 | MICL0.01112026/RBL
Build-In Floor | Mini Canal | MICL.01112026/RBN | 11 | 120 | 26 | 26 | 305 | 305 | 305 | 0.0072619 | 119 | 0.0028333 | 347 | 0.0082619 | 1.362 | A04 | MICL0.01112026/RBN
Build-In Floor | Mini Canal | MICL.01112026/RBR | 11 | 120 | 26 | 26 | 314 | 314 | 314 | 0.0074762 | 122 | 0.0029048 | 358 | 0.0085238 | 1.362 | A04 | MICL0.01112026/RBR
Build-In Floor | Mini Canal | MICL.01112026/RBV | 11 | 120 | 26 | 26 | 305 | 305 | 305 | 0.0072619 | 119 | 0.0028333 | 347 | 0.0082619 | 1.362 | A04 | MICL0.01112026/RBV
Build-In Floor | Mini Canal | MICL.01112026/RDB | 11 | 120 | 26 | 26 | 314 | 314 | 314 | 0.0074762 | 122 | 0.0029048 | 358 | 0.0085238 | 1.362 | A04 | MICL0.01112026/RDB
Build-In Floor | Mini Canal | MICL.01112026/RMN | 11 | 120 | 26 | 26 | 305 | 305 | 305 | 0.0072619 | 119 | 0.0028333 | 347 | 0.0082619 | 1.362 | A04 | MICL0.01112026/RMN
Build-In Floor | Mini Canal | MICL.01112026/RMV | 11 | 120 | 26 | 26 | 305 | 305 | 305 | 0.0072619 | 119 | 0.0028333 | 347 | 0.0082619 | 1.362 | A04 | MICL0.01112026/RMV
Build-In Floor | Mini Canal | MICL.01112026/RNA | 11 | 120 | 26 | 26 | 314 | 314 | 314 | 0.0074762 | 122 | 0.0029048 | 358 | 0.0085238 | 1.362 | A04 | MICL0.01112026/RNA
Build-In Floor | Mini Canal | MICL.01112026/RON | 11 | 120 | 26 | 26 | 305 | 305 | 305 | 0.0072619 | 119 | 0.0028333 | 347 | 0.0082619 | 1.362 | A04 | MICL0.01112026/RON
Build-In Floor | Mini Canal | MICL.01112026/ROV | 11 | 120 | 26 | 26 | 305 | 305 | 305 | 0.0072619 | 119 | 0.0028333 | 347 | 0.0082619 | 1.362 | A04 | MICL0.01112026/ROV
Build-In Floor | Mini Canal | MICL.01112026/RSS | 11 | 120 | 26 | 26 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01112026/RSS
Build-In Floor | Mini Canal | MICL.01112026/SBL | 11 | 120 | 26 | 26 | 314 | 314 | 314 | 0.0074762 | 122 | 0.0029048 | 358 | 0.0085238 | 1.362 | A04 | MICL0.01112026/SBL
Build-In Floor | Mini Canal | MICL.01112026/SBR | 11 | 120 | 26 | 26 | 314 | 314 | 314 | 0.0074762 | 122 | 0.0029048 | 358 | 0.0085238 | 1.362 | A04 | MICL0.01112026/SBR
Build-In Floor | Mini Canal | MICL.01112026/SDB | 11 | 120 | 26 | 26 | 314 | 314 | 314 | 0.0074762 | 122 | 0.0029048 | 358 | 0.0085238 | 1.362 | A04 | MICL0.01112026/SDB
Build-In Floor | Mini Canal | MICL.01112026/SNA | 11 | 120 | 26 | 26 | 314 | 314 | 314 | 0.0074762 | 122 | 0.0029048 | 358 | 0.0085238 | 1.362 | A04 | MICL0.01112026/SNA
Build-In Floor | Mini Canal | MICL.01112026/SNC | 11 | 120 | 26 | 26 | 314 | 314 | 314 | 0.0074762 | 122 | 0.0029048 | 358 | 0.0085238 | 1.362 | A04 | MICL0.01112026/SNC
Build-In Floor | Mini Canal | MICL.01112034/ANA | 11 | 120 | 34 | 34 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01112034/ANA
Build-In Floor | Mini Canal | MICL.01112034/DBL | 11 | 120 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01112034/DBL
Build-In Floor | Mini Canal | MICL.01112034/DBN | 11 | 120 | 34 | 34 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01112034/DBN
Build-In Floor | Mini Canal | MICL.01112034/DBR | 11 | 120 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01112034/DBR
Build-In Floor | Mini Canal | MICL.01112034/DBV | 11 | 120 | 34 | 34 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01112034/DBV
Build-In Floor | Mini Canal | MICL.01112034/DDB | 11 | 120 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01112034/DDB
Build-In Floor | Mini Canal | MICL.01112034/DMN | 11 | 120 | 34 | 34 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01112034/DMN
Build-In Floor | Mini Canal | MICL.01112034/DMV | 11 | 120 | 34 | 34 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01112034/DMV
Build-In Floor | Mini Canal | MICL.01112034/DNA | 11 | 120 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01112034/DNA
Build-In Floor | Mini Canal | MICL.01112034/DNC | 11 | 120 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01112034/DNC
Build-In Floor | Mini Canal | MICL.01112034/DON | 11 | 120 | 34 | 34 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01112034/DON
Build-In Floor | Mini Canal | MICL.01112034/DOV | 11 | 120 | 34 | 34 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01112034/DOV
Build-In Floor | Mini Canal | MICL.01112034/PNC | 11 | 120 | 34 | 34 | 348 | 348 | 348 | 0.0082857 | 135 | 0.0032143 | 396 | 0.0094286 | 1.362 | A04 | MICL0.01112034/PNC
Build-In Floor | Mini Canal | MICL.01112034/RBL | 11 | 120 | 34 | 34 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01112034/RBL
Build-In Floor | Mini Canal | MICL.01112034/RBN | 11 | 120 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01112034/RBN
Build-In Floor | Mini Canal | MICL.01112034/RBR | 11 | 120 | 34 | 34 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01112034/RBR
Build-In Floor | Mini Canal | MICL.01112034/RBV | 11 | 120 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01112034/RBV
Build-In Floor | Mini Canal | MICL.01112034/RDB | 11 | 120 | 34 | 34 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01112034/RDB
Build-In Floor | Mini Canal | MICL.01112034/RMN | 11 | 120 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01112034/RMN
Build-In Floor | Mini Canal | MICL.01112034/RMV | 11 | 120 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01112034/RMV
Build-In Floor | Mini Canal | MICL.01112034/RNA | 11 | 120 | 34 | 34 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01112034/RNA
Build-In Floor | Mini Canal | MICL.01112034/RON | 11 | 120 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01112034/RON
Build-In Floor | Mini Canal | MICL.01112034/ROV | 11 | 120 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01112034/ROV
Build-In Floor | Mini Canal | MICL.01112034/RSS | 11 | 120 | 34 | 34 | 393 | 393 | 393 | 0.0093571 | 153 | 0.0036429 | 448 | 0.010667 | 1.362 | A04 | MICL0.01112034/RSS
Build-In Floor | Mini Canal | MICL.01112034/SBL | 11 | 120 | 34 | 34 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01112034/SBL
Build-In Floor | Mini Canal | MICL.01112034/SBR | 11 | 120 | 34 | 34 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01112034/SBR
Build-In Floor | Mini Canal | MICL.01112034/SDB | 11 | 120 | 34 | 34 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01112034/SDB
Build-In Floor | Mini Canal | MICL.01112034/SNA | 11 | 120 | 34 | 34 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01112034/SNA
Build-In Floor | Mini Canal | MICL.01112034/SNC | 11 | 120 | 34 | 34 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01112034/SNC
Build-In Floor | Mini Canal | MICL.01112042/ANA | 11 | 120 | 42 | 42 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01112042/ANA
Build-In Floor | Mini Canal | MICL.01112042/DBL | 11 | 120 | 42 | 42 | 557 | 557 | 557 | 0.013262 | 217 | 0.0051667 | 634 | 0.015095 | 1.362 | A04 | MICL0.01112042/DBL
Build-In Floor | Mini Canal | MICL.01112042/DBN | 11 | 120 | 42 | 42 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.01112042/DBN
Build-In Floor | Mini Canal | MICL.01112042/DBR | 11 | 120 | 42 | 42 | 557 | 557 | 557 | 0.013262 | 217 | 0.0051667 | 634 | 0.015095 | 1.362 | A04 | MICL0.01112042/DBR
Build-In Floor | Mini Canal | MICL.01112042/DBV | 11 | 120 | 42 | 42 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.01112042/DBV
Build-In Floor | Mini Canal | MICL.01112042/DDB | 11 | 120 | 42 | 42 | 557 | 557 | 557 | 0.013262 | 217 | 0.0051667 | 634 | 0.015095 | 1.362 | A04 | MICL0.01112042/DDB
Build-In Floor | Mini Canal | MICL.01112042/DMN | 11 | 120 | 42 | 42 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.01112042/DMN
Build-In Floor | Mini Canal | MICL.01112042/DMV | 11 | 120 | 42 | 42 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.01112042/DMV
Build-In Floor | Mini Canal | MICL.01112042/DNA | 11 | 120 | 42 | 42 | 557 | 557 | 557 | 0.013262 | 217 | 0.0051667 | 634 | 0.015095 | 1.362 | A04 | MICL0.01112042/DNA
Build-In Floor | Mini Canal | MICL.01112042/DNC | 11 | 120 | 42 | 42 | 557 | 557 | 557 | 0.013262 | 217 | 0.0051667 | 634 | 0.015095 | 1.362 | A04 | MICL0.01112042/DNC
Build-In Floor | Mini Canal | MICL.01112042/DON | 11 | 120 | 42 | 42 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.01112042/DON
Build-In Floor | Mini Canal | MICL.01112042/DOV | 11 | 120 | 42 | 42 | 534 | 534 | 534 | 0.012714 | 208 | 0.0049524 | 608 | 0.014476 | 1.362 | A04 | MICL0.01112042/DOV
Build-In Floor | Mini Canal | MICL.01112042/PNC | 11 | 120 | 42 | 42 | 488 | 488 | 488 | 0.011619 | 190 | 0.0045238 | 556 | 0.013238 | 1.362 | A04 | MICL0.01112042/PNC
Build-In Floor | Mini Canal | MICL.01112042/RBL | 11 | 120 | 42 | 42 | 574 | 574 | 574 | 0.013667 | 223 | 0.0053095 | 654 | 0.015571 | 1.362 | A04 | MICL0.01112042/RBL
Build-In Floor | Mini Canal | MICL.01112042/RBN | 11 | 120 | 42 | 42 | 557 | 557 | 557 | 0.013262 | 217 | 0.0051667 | 634 | 0.015095 | 1.362 | A04 | MICL0.01112042/RBN
Build-In Floor | Mini Canal | MICL.01112042/RBR | 11 | 120 | 42 | 42 | 574 | 574 | 574 | 0.013667 | 223 | 0.0053095 | 654 | 0.015571 | 1.362 | A04 | MICL0.01112042/RBR
Build-In Floor | Mini Canal | MICL.01112042/RBV | 11 | 120 | 42 | 42 | 557 | 557 | 557 | 0.013262 | 217 | 0.0051667 | 634 | 0.015095 | 1.362 | A04 | MICL0.01112042/RBV
Build-In Floor | Mini Canal | MICL.01112042/RDB | 11 | 120 | 42 | 42 | 574 | 574 | 574 | 0.013667 | 223 | 0.0053095 | 654 | 0.015571 | 1.362 | A04 | MICL0.01112042/RDB
Build-In Floor | Mini Canal | MICL.01112042/RMN | 11 | 120 | 42 | 42 | 557 | 557 | 557 | 0.013262 | 217 | 0.0051667 | 634 | 0.015095 | 1.362 | A04 | MICL0.01112042/RMN
Build-In Floor | Mini Canal | MICL.01112042/RMV | 11 | 120 | 42 | 42 | 557 | 557 | 557 | 0.013262 | 217 | 0.0051667 | 634 | 0.015095 | 1.362 | A04 | MICL0.01112042/RMV
Build-In Floor | Mini Canal | MICL.01112042/RNA | 11 | 120 | 42 | 42 | 574 | 574 | 574 | 0.013667 | 223 | 0.0053095 | 654 | 0.015571 | 1.362 | A04 | MICL0.01112042/RNA
Build-In Floor | Mini Canal | MICL.01112042/RON | 11 | 120 | 42 | 42 | 557 | 557 | 557 | 0.013262 | 217 | 0.0051667 | 634 | 0.015095 | 1.362 | A04 | MICL0.01112042/RON
Build-In Floor | Mini Canal | MICL.01112042/ROV | 11 | 120 | 42 | 42 | 557 | 557 | 557 | 0.013262 | 217 | 0.0051667 | 634 | 0.015095 | 1.362 | A04 | MICL0.01112042/ROV
Build-In Floor | Mini Canal | MICL.01112042/RSS | 11 | 120 | 42 | 42 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.01112042/RSS
Build-In Floor | Mini Canal | MICL.01112042/SBL | 11 | 120 | 42 | 42 | 574 | 574 | 574 | 0.013667 | 223 | 0.0053095 | 654 | 0.015571 | 1.362 | A04 | MICL0.01112042/SBL
Build-In Floor | Mini Canal | MICL.01112042/SBR | 11 | 120 | 42 | 42 | 574 | 574 | 574 | 0.013667 | 223 | 0.0053095 | 654 | 0.015571 | 1.362 | A04 | MICL0.01112042/SBR
Build-In Floor | Mini Canal | MICL.01112042/SDB | 11 | 120 | 42 | 42 | 574 | 574 | 574 | 0.013667 | 223 | 0.0053095 | 654 | 0.015571 | 1.362 | A04 | MICL0.01112042/SDB
Build-In Floor | Mini Canal | MICL.01112042/SNA | 11 | 120 | 42 | 42 | 574 | 574 | 574 | 0.013667 | 223 | 0.0053095 | 654 | 0.015571 | 1.362 | A04 | MICL0.01112042/SNA
Build-In Floor | Mini Canal | MICL.01112042/SNC | 11 | 120 | 42 | 42 | 574 | 574 | 574 | 0.013667 | 223 | 0.0053095 | 654 | 0.015571 | 1.362 | A04 | MICL0.01112042/SNC
Build-In Floor | Mini Canal | MICL.01113014/ANA | 11 | 130 | 14 | 14 | 164 | 164 | 164 | 0.0039048 | 64 | 0.0015238 | 187 | 0.0044524 | 1.362 | A04 | MICL0.01113014/ANA
Build-In Floor | Mini Canal | MICL.01113014/DBL | 11 | 130 | 14 | 14 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01113014/DBL
Build-In Floor | Mini Canal | MICL.01113014/DBN | 11 | 130 | 14 | 14 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.01113014/DBN
Build-In Floor | Mini Canal | MICL.01113014/DBR | 11 | 130 | 14 | 14 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01113014/DBR
Build-In Floor | Mini Canal | MICL.01113014/DBV | 11 | 130 | 14 | 14 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.01113014/DBV
Build-In Floor | Mini Canal | MICL.01113014/DDB | 11 | 130 | 14 | 14 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01113014/DDB
Build-In Floor | Mini Canal | MICL.01113014/DMN | 11 | 130 | 14 | 14 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.01113014/DMN
Build-In Floor | Mini Canal | MICL.01113014/DMV | 11 | 130 | 14 | 14 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.01113014/DMV
Build-In Floor | Mini Canal | MICL.01113014/DNA | 11 | 130 | 14 | 14 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01113014/DNA
Build-In Floor | Mini Canal | MICL.01113014/DNC | 11 | 130 | 14 | 14 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01113014/DNC
Build-In Floor | Mini Canal | MICL.01113014/DON | 11 | 130 | 14 | 14 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.01113014/DON
Build-In Floor | Mini Canal | MICL.01113014/DOV | 11 | 130 | 14 | 14 | 203 | 203 | 203 | 0.0048333 | 79 | 0.001881 | 231 | 0.0055 | 1.362 | A04 | MICL0.01113014/DOV
Build-In Floor | Mini Canal | MICL.01113014/RBL | 11 | 130 | 14 | 14 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.01113014/RBL
Build-In Floor | Mini Canal | MICL.01113014/RBN | 11 | 130 | 14 | 14 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01113014/RBN
Build-In Floor | Mini Canal | MICL.01113014/RBR | 11 | 130 | 14 | 14 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.01113014/RBR
Build-In Floor | Mini Canal | MICL.01113014/RBV | 11 | 130 | 14 | 14 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01113014/RBV
Build-In Floor | Mini Canal | MICL.01113014/RDB | 11 | 130 | 14 | 14 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.01113014/RDB
Build-In Floor | Mini Canal | MICL.01113014/RMN | 11 | 130 | 14 | 14 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01113014/RMN
Build-In Floor | Mini Canal | MICL.01113014/RMV | 11 | 130 | 14 | 14 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01113014/RMV
Build-In Floor | Mini Canal | MICL.01113014/RNA | 11 | 130 | 14 | 14 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.01113014/RNA
Build-In Floor | Mini Canal | MICL.01113014/RON | 11 | 130 | 14 | 14 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01113014/RON
Build-In Floor | Mini Canal | MICL.01113014/ROV | 11 | 130 | 14 | 14 | 211 | 211 | 211 | 0.0050238 | 82 | 0.0019524 | 240 | 0.0057143 | 1.362 | A04 | MICL0.01113014/ROV
Build-In Floor | Mini Canal | MICL.01113014/RSS | 11 | 130 | 14 | 14 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.01113014/RSS
Build-In Floor | Mini Canal | MICL.01113014/SBL | 11 | 130 | 14 | 14 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.01113014/SBL
Build-In Floor | Mini Canal | MICL.01113014/SBR | 11 | 130 | 14 | 14 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.01113014/SBR
Build-In Floor | Mini Canal | MICL.01113014/SDB | 11 | 130 | 14 | 14 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.01113014/SDB
Build-In Floor | Mini Canal | MICL.01113014/SNA | 11 | 130 | 14 | 14 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.01113014/SNA
Build-In Floor | Mini Canal | MICL.01113014/SNC | 11 | 130 | 14 | 14 | 218 | 218 | 218 | 0.0051905 | 85 | 0.0020238 | 248 | 0.0059048 | 1.362 | A04 | MICL0.01113014/SNC
Build-In Floor | Mini Canal | MICL.01113018/ANA | 11 | 130 | 18 | 18 | 194 | 194 | 194 | 0.004619 | 75 | 0.0017857 | 221 | 0.0052619 | 1.362 | A04 | MICL0.01113018/ANA
Build-In Floor | Mini Canal | MICL.01113018/DBL | 11 | 130 | 18 | 18 | 251 | 251 | 251 | 0.0059762 | 98 | 0.0023333 | 286 | 0.0068095 | 1.362 | A04 | MICL0.01113018/DBL
Build-In Floor | Mini Canal | MICL.01113018/DBN | 11 | 130 | 18 | 18 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01113018/DBN
Build-In Floor | Mini Canal | MICL.01113018/DBR | 11 | 130 | 18 | 18 | 251 | 251 | 251 | 0.0059762 | 98 | 0.0023333 | 286 | 0.0068095 | 1.362 | A04 | MICL0.01113018/DBR
Build-In Floor | Mini Canal | MICL.01113018/DBV | 11 | 130 | 18 | 18 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01113018/DBV
Build-In Floor | Mini Canal | MICL.01113018/DDB | 11 | 130 | 18 | 18 | 251 | 251 | 251 | 0.0059762 | 98 | 0.0023333 | 286 | 0.0068095 | 1.362 | A04 | MICL0.01113018/DDB
Build-In Floor | Mini Canal | MICL.01113018/DMN | 11 | 130 | 18 | 18 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01113018/DMN
Build-In Floor | Mini Canal | MICL.01113018/DMV | 11 | 130 | 18 | 18 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01113018/DMV
Build-In Floor | Mini Canal | MICL.01113018/DNA | 11 | 130 | 18 | 18 | 251 | 251 | 251 | 0.0059762 | 98 | 0.0023333 | 286 | 0.0068095 | 1.362 | A04 | MICL0.01113018/DNA
Build-In Floor | Mini Canal | MICL.01113018/DNC | 11 | 130 | 18 | 18 | 251 | 251 | 251 | 0.0059762 | 98 | 0.0023333 | 286 | 0.0068095 | 1.362 | A04 | MICL0.01113018/DNC
Build-In Floor | Mini Canal | MICL.01113018/DON | 11 | 130 | 18 | 18 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01113018/DON
Build-In Floor | Mini Canal | MICL.01113018/DOV | 11 | 130 | 18 | 18 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01113018/DOV
Build-In Floor | Mini Canal | MICL.01113018/RBL | 11 | 130 | 18 | 18 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01113018/RBL
Build-In Floor | Mini Canal | MICL.01113018/RBN | 11 | 130 | 18 | 18 | 251 | 251 | 251 | 0.0059762 | 98 | 0.0023333 | 286 | 0.0068095 | 1.362 | A04 | MICL0.01113018/RBN
Build-In Floor | Mini Canal | MICL.01113018/RBR | 11 | 130 | 18 | 18 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01113018/RBR
Build-In Floor | Mini Canal | MICL.01113018/RBV | 11 | 130 | 18 | 18 | 251 | 251 | 251 | 0.0059762 | 98 | 0.0023333 | 286 | 0.0068095 | 1.362 | A04 | MICL0.01113018/RBV
Build-In Floor | Mini Canal | MICL.01113018/RDB | 11 | 130 | 18 | 18 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01113018/RDB
Build-In Floor | Mini Canal | MICL.01113018/RMN | 11 | 130 | 18 | 18 | 251 | 251 | 251 | 0.0059762 | 98 | 0.0023333 | 286 | 0.0068095 | 1.362 | A04 | MICL0.01113018/RMN
Build-In Floor | Mini Canal | MICL.01113018/RMV | 11 | 130 | 18 | 18 | 251 | 251 | 251 | 0.0059762 | 98 | 0.0023333 | 286 | 0.0068095 | 1.362 | A04 | MICL0.01113018/RMV
Build-In Floor | Mini Canal | MICL.01113018/RNA | 11 | 130 | 18 | 18 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01113018/RNA
Build-In Floor | Mini Canal | MICL.01113018/RON | 11 | 130 | 18 | 18 | 251 | 251 | 251 | 0.0059762 | 98 | 0.0023333 | 286 | 0.0068095 | 1.362 | A04 | MICL0.01113018/RON
Build-In Floor | Mini Canal | MICL.01113018/ROV | 11 | 130 | 18 | 18 | 251 | 251 | 251 | 0.0059762 | 98 | 0.0023333 | 286 | 0.0068095 | 1.362 | A04 | MICL0.01113018/ROV
Build-In Floor | Mini Canal | MICL.01113018/RSS | 11 | 130 | 18 | 18 | 249 | 249 | 249 | 0.0059286 | 97 | 0.0023095 | 284 | 0.0067619 | 1.362 | A04 | MICL0.01113018/RSS
Build-In Floor | Mini Canal | MICL.01113018/SBL | 11 | 130 | 18 | 18 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01113018/SBL
Build-In Floor | Mini Canal | MICL.01113018/SBR | 11 | 130 | 18 | 18 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01113018/SBR
Build-In Floor | Mini Canal | MICL.01113018/SDB | 11 | 130 | 18 | 18 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01113018/SDB
Build-In Floor | Mini Canal | MICL.01113018/SNA | 11 | 130 | 18 | 18 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01113018/SNA
Build-In Floor | Mini Canal | MICL.01113018/SNC | 11 | 130 | 18 | 18 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01113018/SNC
Build-In Floor | Mini Canal | MICL.01113026/ANA | 11 | 130 | 26 | 26 | 262 | 262 | 262 | 0.0062381 | 102 | 0.0024286 | 298 | 0.0070952 | 1.362 | A04 | MICL0.01113026/ANA
Build-In Floor | Mini Canal | MICL.01113026/DBL | 11 | 130 | 26 | 26 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01113026/DBL
Build-In Floor | Mini Canal | MICL.01113026/DBN | 11 | 130 | 26 | 26 | 325 | 325 | 325 | 0.0077381 | 126 | 0.003 | 370 | 0.0088095 | 1.362 | A04 | MICL0.01113026/DBN
Build-In Floor | Mini Canal | MICL.01113026/DBR | 11 | 130 | 26 | 26 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01113026/DBR
Build-In Floor | Mini Canal | MICL.01113026/DBV | 11 | 130 | 26 | 26 | 325 | 325 | 325 | 0.0077381 | 126 | 0.003 | 370 | 0.0088095 | 1.362 | A04 | MICL0.01113026/DBV
Build-In Floor | Mini Canal | MICL.01113026/DDB | 11 | 130 | 26 | 26 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01113026/DDB
Build-In Floor | Mini Canal | MICL.01113026/DMN | 11 | 130 | 26 | 26 | 325 | 325 | 325 | 0.0077381 | 126 | 0.003 | 370 | 0.0088095 | 1.362 | A04 | MICL0.01113026/DMN
Build-In Floor | Mini Canal | MICL.01113026/DMV | 11 | 130 | 26 | 26 | 325 | 325 | 325 | 0.0077381 | 126 | 0.003 | 370 | 0.0088095 | 1.362 | A04 | MICL0.01113026/DMV
Build-In Floor | Mini Canal | MICL.01113026/DNA | 11 | 130 | 26 | 26 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01113026/DNA
Build-In Floor | Mini Canal | MICL.01113026/DNC | 11 | 130 | 26 | 26 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01113026/DNC
Build-In Floor | Mini Canal | MICL.01113026/DON | 11 | 130 | 26 | 26 | 325 | 325 | 325 | 0.0077381 | 126 | 0.003 | 370 | 0.0088095 | 1.362 | A04 | MICL0.01113026/DON
Build-In Floor | Mini Canal | MICL.01113026/DOV | 11 | 130 | 26 | 26 | 325 | 325 | 325 | 0.0077381 | 126 | 0.003 | 370 | 0.0088095 | 1.362 | A04 | MICL0.01113026/DOV
Build-In Floor | Mini Canal | MICL.01113026/PNC | 11 | 130 | 26 | 26 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01113026/PNC
Build-In Floor | Mini Canal | MICL.01113026/RBL | 11 | 130 | 26 | 26 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01113026/RBL
Build-In Floor | Mini Canal | MICL.01113026/RBN | 11 | 130 | 26 | 26 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01113026/RBN
Build-In Floor | Mini Canal | MICL.01113026/RBR | 11 | 130 | 26 | 26 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01113026/RBR
Build-In Floor | Mini Canal | MICL.01113026/RBV | 11 | 130 | 26 | 26 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01113026/RBV
Build-In Floor | Mini Canal | MICL.01113026/RDB | 11 | 130 | 26 | 26 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01113026/RDB
Build-In Floor | Mini Canal | MICL.01113026/RMN | 11 | 130 | 26 | 26 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01113026/RMN
Build-In Floor | Mini Canal | MICL.01113026/RMV | 11 | 130 | 26 | 26 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01113026/RMV
Build-In Floor | Mini Canal | MICL.01113026/RNA | 11 | 130 | 26 | 26 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01113026/RNA
Build-In Floor | Mini Canal | MICL.01113026/RON | 11 | 130 | 26 | 26 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01113026/RON
Build-In Floor | Mini Canal | MICL.01113026/ROV | 11 | 130 | 26 | 26 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01113026/ROV
Build-In Floor | Mini Canal | MICL.01113026/RSS | 11 | 130 | 26 | 26 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01113026/RSS
Build-In Floor | Mini Canal | MICL.01113026/SBL | 11 | 130 | 26 | 26 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01113026/SBL
Build-In Floor | Mini Canal | MICL.01113026/SBR | 11 | 130 | 26 | 26 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01113026/SBR
Build-In Floor | Mini Canal | MICL.01113026/SDB | 11 | 130 | 26 | 26 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01113026/SDB
Build-In Floor | Mini Canal | MICL.01113026/SNA | 11 | 130 | 26 | 26 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01113026/SNA
Build-In Floor | Mini Canal | MICL.01113026/SNC | 11 | 130 | 26 | 26 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01113026/SNC
Build-In Floor | Mini Canal | MICL.01113034/ANA | 11 | 130 | 34 | 34 | 341 | 341 | 341 | 0.008119 | 133 | 0.0031667 | 388 | 0.0092381 | 1.362 | A04 | MICL0.01113034/ANA
Build-In Floor | Mini Canal | MICL.01113034/DBL | 11 | 130 | 34 | 34 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01113034/DBL
Build-In Floor | Mini Canal | MICL.01113034/DBN | 11 | 130 | 34 | 34 | 422 | 422 | 422 | 0.010048 | 164 | 0.0039048 | 481 | 0.011452 | 1.362 | A04 | MICL0.01113034/DBN
Build-In Floor | Mini Canal | MICL.01113034/DBR | 11 | 130 | 34 | 34 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01113034/DBR
Build-In Floor | Mini Canal | MICL.01113034/DBV | 11 | 130 | 34 | 34 | 422 | 422 | 422 | 0.010048 | 164 | 0.0039048 | 481 | 0.011452 | 1.362 | A04 | MICL0.01113034/DBV
Build-In Floor | Mini Canal | MICL.01113034/DDB | 11 | 130 | 34 | 34 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01113034/DDB
Build-In Floor | Mini Canal | MICL.01113034/DMN | 11 | 130 | 34 | 34 | 422 | 422 | 422 | 0.010048 | 164 | 0.0039048 | 481 | 0.011452 | 1.362 | A04 | MICL0.01113034/DMN
Build-In Floor | Mini Canal | MICL.01113034/DMV | 11 | 130 | 34 | 34 | 422 | 422 | 422 | 0.010048 | 164 | 0.0039048 | 481 | 0.011452 | 1.362 | A04 | MICL0.01113034/DMV
Build-In Floor | Mini Canal | MICL.01113034/DNA | 11 | 130 | 34 | 34 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01113034/DNA
Build-In Floor | Mini Canal | MICL.01113034/DNC | 11 | 130 | 34 | 34 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01113034/DNC
Build-In Floor | Mini Canal | MICL.01113034/DON | 11 | 130 | 34 | 34 | 422 | 422 | 422 | 0.010048 | 164 | 0.0039048 | 481 | 0.011452 | 1.362 | A04 | MICL0.01113034/DON
Build-In Floor | Mini Canal | MICL.01113034/DOV | 11 | 130 | 34 | 34 | 422 | 422 | 422 | 0.010048 | 164 | 0.0039048 | 481 | 0.011452 | 1.362 | A04 | MICL0.01113034/DOV
Build-In Floor | Mini Canal | MICL.01113034/PNC | 11 | 130 | 34 | 34 | 386 | 386 | 386 | 0.0091905 | 150 | 0.0035714 | 440 | 0.010476 | 1.362 | A04 | MICL0.01113034/PNC
Build-In Floor | Mini Canal | MICL.01113034/RBL | 11 | 130 | 34 | 34 | 454 | 454 | 454 | 0.01081 | 177 | 0.0042143 | 517 | 0.01231 | 1.362 | A04 | MICL0.01113034/RBL
Build-In Floor | Mini Canal | MICL.01113034/RBN | 11 | 130 | 34 | 34 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01113034/RBN
Build-In Floor | Mini Canal | MICL.01113034/RBR | 11 | 130 | 34 | 34 | 454 | 454 | 454 | 0.01081 | 177 | 0.0042143 | 517 | 0.01231 | 1.362 | A04 | MICL0.01113034/RBR
Build-In Floor | Mini Canal | MICL.01113034/RBV | 11 | 130 | 34 | 34 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01113034/RBV
Build-In Floor | Mini Canal | MICL.01113034/RDB | 11 | 130 | 34 | 34 | 454 | 454 | 454 | 0.01081 | 177 | 0.0042143 | 517 | 0.01231 | 1.362 | A04 | MICL0.01113034/RDB
Build-In Floor | Mini Canal | MICL.01113034/RMN | 11 | 130 | 34 | 34 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01113034/RMN
Build-In Floor | Mini Canal | MICL.01113034/RMV | 11 | 130 | 34 | 34 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01113034/RMV
Build-In Floor | Mini Canal | MICL.01113034/RNA | 11 | 130 | 34 | 34 | 454 | 454 | 454 | 0.01081 | 177 | 0.0042143 | 517 | 0.01231 | 1.362 | A04 | MICL0.01113034/RNA
Build-In Floor | Mini Canal | MICL.01113034/RON | 11 | 130 | 34 | 34 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01113034/RON
Build-In Floor | Mini Canal | MICL.01113034/ROV | 11 | 130 | 34 | 34 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01113034/ROV
Build-In Floor | Mini Canal | MICL.01113034/RSS | 11 | 130 | 34 | 34 | 436 | 436 | 436 | 0.010381 | 170 | 0.0040476 | 497 | 0.011833 | 1.362 | A04 | MICL0.01113034/RSS
Build-In Floor | Mini Canal | MICL.01113034/SBL | 11 | 130 | 34 | 34 | 454 | 454 | 454 | 0.01081 | 177 | 0.0042143 | 517 | 0.01231 | 1.362 | A04 | MICL0.01113034/SBL
Build-In Floor | Mini Canal | MICL.01113034/SBR | 11 | 130 | 34 | 34 | 454 | 454 | 454 | 0.01081 | 177 | 0.0042143 | 517 | 0.01231 | 1.362 | A04 | MICL0.01113034/SBR
Build-In Floor | Mini Canal | MICL.01113034/SDB | 11 | 130 | 34 | 34 | 454 | 454 | 454 | 0.01081 | 177 | 0.0042143 | 517 | 0.01231 | 1.362 | A04 | MICL0.01113034/SDB
Build-In Floor | Mini Canal | MICL.01113034/SNA | 11 | 130 | 34 | 34 | 454 | 454 | 454 | 0.01081 | 177 | 0.0042143 | 517 | 0.01231 | 1.362 | A04 | MICL0.01113034/SNA
Build-In Floor | Mini Canal | MICL.01113034/SNC | 11 | 130 | 34 | 34 | 454 | 454 | 454 | 0.01081 | 177 | 0.0042143 | 517 | 0.01231 | 1.362 | A04 | MICL0.01113034/SNC
Build-In Floor | Mini Canal | MICL.01113042/ANA | 11 | 130 | 42 | 42 | 479 | 479 | 479 | 0.011405 | 186 | 0.0044286 | 546 | 0.013 | 1.362 | A04 | MICL0.01113042/ANA
Build-In Floor | Mini Canal | MICL.01113042/DBL | 11 | 130 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.01113042/DBL
Build-In Floor | Mini Canal | MICL.01113042/DBN | 11 | 130 | 42 | 42 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.01113042/DBN
Build-In Floor | Mini Canal | MICL.01113042/DBR | 11 | 130 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.01113042/DBR
Build-In Floor | Mini Canal | MICL.01113042/DBV | 11 | 130 | 42 | 42 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.01113042/DBV
Build-In Floor | Mini Canal | MICL.01113042/DDB | 11 | 130 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.01113042/DDB
Build-In Floor | Mini Canal | MICL.01113042/DMN | 11 | 130 | 42 | 42 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.01113042/DMN
Build-In Floor | Mini Canal | MICL.01113042/DMV | 11 | 130 | 42 | 42 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.01113042/DMV
Build-In Floor | Mini Canal | MICL.01113042/DNA | 11 | 130 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.01113042/DNA
Build-In Floor | Mini Canal | MICL.01113042/DNC | 11 | 130 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.01113042/DNC
Build-In Floor | Mini Canal | MICL.01113042/DON | 11 | 130 | 42 | 42 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.01113042/DON
Build-In Floor | Mini Canal | MICL.01113042/DOV | 11 | 130 | 42 | 42 | 593 | 593 | 593 | 0.014119 | 231 | 0.0055 | 675 | 0.016071 | 1.362 | A04 | MICL0.01113042/DOV
Build-In Floor | Mini Canal | MICL.01113042/PNC | 11 | 130 | 42 | 42 | 542 | 542 | 542 | 0.012905 | 211 | 0.0050238 | 617 | 0.01469 | 1.362 | A04 | MICL0.01113042/PNC
Build-In Floor | Mini Canal | MICL.01113042/RBL | 11 | 130 | 42 | 42 | 638 | 638 | 638 | 0.01519 | 248 | 0.0059048 | 727 | 0.01731 | 1.362 | A04 | MICL0.01113042/RBL
Build-In Floor | Mini Canal | MICL.01113042/RBN | 11 | 130 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.01113042/RBN
Build-In Floor | Mini Canal | MICL.01113042/RBR | 11 | 130 | 42 | 42 | 638 | 638 | 638 | 0.01519 | 248 | 0.0059048 | 727 | 0.01731 | 1.362 | A04 | MICL0.01113042/RBR
Build-In Floor | Mini Canal | MICL.01113042/RBV | 11 | 130 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.01113042/RBV
Build-In Floor | Mini Canal | MICL.01113042/RDB | 11 | 130 | 42 | 42 | 638 | 638 | 638 | 0.01519 | 248 | 0.0059048 | 727 | 0.01731 | 1.362 | A04 | MICL0.01113042/RDB
Build-In Floor | Mini Canal | MICL.01113042/RMN | 11 | 130 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.01113042/RMN
Build-In Floor | Mini Canal | MICL.01113042/RMV | 11 | 130 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.01113042/RMV
Build-In Floor | Mini Canal | MICL.01113042/RNA | 11 | 130 | 42 | 42 | 638 | 638 | 638 | 0.01519 | 248 | 0.0059048 | 727 | 0.01731 | 1.362 | A04 | MICL0.01113042/RNA
Build-In Floor | Mini Canal | MICL.01113042/RON | 11 | 130 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.01113042/RON
Build-In Floor | Mini Canal | MICL.01113042/ROV | 11 | 130 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.01113042/ROV
Build-In Floor | Mini Canal | MICL.01113042/RSS | 11 | 130 | 42 | 42 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.01113042/RSS
Build-In Floor | Mini Canal | MICL.01113042/SBL | 11 | 130 | 42 | 42 | 638 | 638 | 638 | 0.01519 | 248 | 0.0059048 | 727 | 0.01731 | 1.362 | A04 | MICL0.01113042/SBL
Build-In Floor | Mini Canal | MICL.01113042/SBR | 11 | 130 | 42 | 42 | 638 | 638 | 638 | 0.01519 | 248 | 0.0059048 | 727 | 0.01731 | 1.362 | A04 | MICL0.01113042/SBR
Build-In Floor | Mini Canal | MICL.01113042/SDB | 11 | 130 | 42 | 42 | 638 | 638 | 638 | 0.01519 | 248 | 0.0059048 | 727 | 0.01731 | 1.362 | A04 | MICL0.01113042/SDB
Build-In Floor | Mini Canal | MICL.01113042/SNA | 11 | 130 | 42 | 42 | 638 | 638 | 638 | 0.01519 | 248 | 0.0059048 | 727 | 0.01731 | 1.362 | A04 | MICL0.01113042/SNA
Build-In Floor | Mini Canal | MICL.01113042/SNC | 11 | 130 | 42 | 42 | 638 | 638 | 638 | 0.01519 | 248 | 0.0059048 | 727 | 0.01731 | 1.362 | A04 | MICL0.01113042/SNC
Build-In Floor | Mini Canal | MICL.01115014/ANA | 11 | 150 | 14 | 14 | 197 | 197 | 197 | 0.0046905 | 77 | 0.0018333 | 224 | 0.0053333 | 1.362 | A04 | MICL0.01115014/ANA
Build-In Floor | Mini Canal | MICL.01115014/DBL | 11 | 150 | 14 | 14 | 254 | 254 | 254 | 0.0060476 | 99 | 0.0023571 | 289 | 0.006881 | 1.362 | A04 | MICL0.01115014/DBL
Build-In Floor | Mini Canal | MICL.01115014/DBN | 11 | 150 | 14 | 14 | 244 | 244 | 244 | 0.0058095 | 95 | 0.0022619 | 278 | 0.006619 | 1.362 | A04 | MICL0.01115014/DBN
Build-In Floor | Mini Canal | MICL.01115014/DBR | 11 | 150 | 14 | 14 | 254 | 254 | 254 | 0.0060476 | 99 | 0.0023571 | 289 | 0.006881 | 1.362 | A04 | MICL0.01115014/DBR
Build-In Floor | Mini Canal | MICL.01115014/DBV | 11 | 150 | 14 | 14 | 244 | 244 | 244 | 0.0058095 | 95 | 0.0022619 | 278 | 0.006619 | 1.362 | A04 | MICL0.01115014/DBV
Build-In Floor | Mini Canal | MICL.01115014/DDB | 11 | 150 | 14 | 14 | 254 | 254 | 254 | 0.0060476 | 99 | 0.0023571 | 289 | 0.006881 | 1.362 | A04 | MICL0.01115014/DDB
Build-In Floor | Mini Canal | MICL.01115014/DMN | 11 | 150 | 14 | 14 | 244 | 244 | 244 | 0.0058095 | 95 | 0.0022619 | 278 | 0.006619 | 1.362 | A04 | MICL0.01115014/DMN
Build-In Floor | Mini Canal | MICL.01115014/DMV | 11 | 150 | 14 | 14 | 244 | 244 | 244 | 0.0058095 | 95 | 0.0022619 | 278 | 0.006619 | 1.362 | A04 | MICL0.01115014/DMV
Build-In Floor | Mini Canal | MICL.01115014/DNA | 11 | 150 | 14 | 14 | 254 | 254 | 254 | 0.0060476 | 99 | 0.0023571 | 289 | 0.006881 | 1.362 | A04 | MICL0.01115014/DNA
Build-In Floor | Mini Canal | MICL.01115014/DNC | 11 | 150 | 14 | 14 | 254 | 254 | 254 | 0.0060476 | 99 | 0.0023571 | 289 | 0.006881 | 1.362 | A04 | MICL0.01115014/DNC
Build-In Floor | Mini Canal | MICL.01115014/DON | 11 | 150 | 14 | 14 | 244 | 244 | 244 | 0.0058095 | 95 | 0.0022619 | 278 | 0.006619 | 1.362 | A04 | MICL0.01115014/DON
Build-In Floor | Mini Canal | MICL.01115014/DOV | 11 | 150 | 14 | 14 | 244 | 244 | 244 | 0.0058095 | 95 | 0.0022619 | 278 | 0.006619 | 1.362 | A04 | MICL0.01115014/DOV
Build-In Floor | Mini Canal | MICL.01115014/RBL | 11 | 150 | 14 | 14 | 262 | 262 | 262 | 0.0062381 | 102 | 0.0024286 | 298 | 0.0070952 | 1.362 | A04 | MICL0.01115014/RBL
Build-In Floor | Mini Canal | MICL.01115014/RBN | 11 | 150 | 14 | 14 | 254 | 254 | 254 | 0.0060476 | 99 | 0.0023571 | 289 | 0.006881 | 1.362 | A04 | MICL0.01115014/RBN
Build-In Floor | Mini Canal | MICL.01115014/RBR | 11 | 150 | 14 | 14 | 262 | 262 | 262 | 0.0062381 | 102 | 0.0024286 | 298 | 0.0070952 | 1.362 | A04 | MICL0.01115014/RBR
Build-In Floor | Mini Canal | MICL.01115014/RBV | 11 | 150 | 14 | 14 | 254 | 254 | 254 | 0.0060476 | 99 | 0.0023571 | 289 | 0.006881 | 1.362 | A04 | MICL0.01115014/RBV
Build-In Floor | Mini Canal | MICL.01115014/RDB | 11 | 150 | 14 | 14 | 262 | 262 | 262 | 0.0062381 | 102 | 0.0024286 | 298 | 0.0070952 | 1.362 | A04 | MICL0.01115014/RDB
Build-In Floor | Mini Canal | MICL.01115014/RMN | 11 | 150 | 14 | 14 | 254 | 254 | 254 | 0.0060476 | 99 | 0.0023571 | 289 | 0.006881 | 1.362 | A04 | MICL0.01115014/RMN
Build-In Floor | Mini Canal | MICL.01115014/RMV | 11 | 150 | 14 | 14 | 254 | 254 | 254 | 0.0060476 | 99 | 0.0023571 | 289 | 0.006881 | 1.362 | A04 | MICL0.01115014/RMV
Build-In Floor | Mini Canal | MICL.01115014/RNA | 11 | 150 | 14 | 14 | 262 | 262 | 262 | 0.0062381 | 102 | 0.0024286 | 298 | 0.0070952 | 1.362 | A04 | MICL0.01115014/RNA
Build-In Floor | Mini Canal | MICL.01115014/RON | 11 | 150 | 14 | 14 | 254 | 254 | 254 | 0.0060476 | 99 | 0.0023571 | 289 | 0.006881 | 1.362 | A04 | MICL0.01115014/RON
Build-In Floor | Mini Canal | MICL.01115014/ROV | 11 | 150 | 14 | 14 | 254 | 254 | 254 | 0.0060476 | 99 | 0.0023571 | 289 | 0.006881 | 1.362 | A04 | MICL0.01115014/ROV
Build-In Floor | Mini Canal | MICL.01115014/RSS | 11 | 150 | 14 | 14 | 252 | 252 | 252 | 0.006 | 98 | 0.0023333 | 287 | 0.0068333 | 1.362 | A04 | MICL0.01115014/RSS
Build-In Floor | Mini Canal | MICL.01115014/SBL | 11 | 150 | 14 | 14 | 262 | 262 | 262 | 0.0062381 | 102 | 0.0024286 | 298 | 0.0070952 | 1.362 | A04 | MICL0.01115014/SBL
Build-In Floor | Mini Canal | MICL.01115014/SBR | 11 | 150 | 14 | 14 | 262 | 262 | 262 | 0.0062381 | 102 | 0.0024286 | 298 | 0.0070952 | 1.362 | A04 | MICL0.01115014/SBR
Build-In Floor | Mini Canal | MICL.01115014/SDB | 11 | 150 | 14 | 14 | 262 | 262 | 262 | 0.0062381 | 102 | 0.0024286 | 298 | 0.0070952 | 1.362 | A04 | MICL0.01115014/SDB
Build-In Floor | Mini Canal | MICL.01115014/SNA | 11 | 150 | 14 | 14 | 262 | 262 | 262 | 0.0062381 | 102 | 0.0024286 | 298 | 0.0070952 | 1.362 | A04 | MICL0.01115014/SNA
Build-In Floor | Mini Canal | MICL.01115014/SNC | 11 | 150 | 14 | 14 | 262 | 262 | 262 | 0.0062381 | 102 | 0.0024286 | 298 | 0.0070952 | 1.362 | A04 | MICL0.01115014/SNC
Build-In Floor | Mini Canal | MICL.01115018/ANA | 11 | 150 | 18 | 18 | 233 | 233 | 233 | 0.0055476 | 91 | 0.0021667 | 265 | 0.0063095 | 1.362 | A04 | MICL0.01115018/ANA
Build-In Floor | Mini Canal | MICL.01115018/DBL | 11 | 150 | 18 | 18 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01115018/DBL
Build-In Floor | Mini Canal | MICL.01115018/DBN | 11 | 150 | 18 | 18 | 288 | 288 | 288 | 0.0068571 | 112 | 0.0026667 | 328 | 0.0078095 | 1.362 | A04 | MICL0.01115018/DBN
Build-In Floor | Mini Canal | MICL.01115018/DBR | 11 | 150 | 18 | 18 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01115018/DBR
Build-In Floor | Mini Canal | MICL.01115018/DBV | 11 | 150 | 18 | 18 | 288 | 288 | 288 | 0.0068571 | 112 | 0.0026667 | 328 | 0.0078095 | 1.362 | A04 | MICL0.01115018/DBV
Build-In Floor | Mini Canal | MICL.01115018/DDB | 11 | 150 | 18 | 18 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01115018/DDB
Build-In Floor | Mini Canal | MICL.01115018/DMN | 11 | 150 | 18 | 18 | 288 | 288 | 288 | 0.0068571 | 112 | 0.0026667 | 328 | 0.0078095 | 1.362 | A04 | MICL0.01115018/DMN
Build-In Floor | Mini Canal | MICL.01115018/DMV | 11 | 150 | 18 | 18 | 288 | 288 | 288 | 0.0068571 | 112 | 0.0026667 | 328 | 0.0078095 | 1.362 | A04 | MICL0.01115018/DMV
Build-In Floor | Mini Canal | MICL.01115018/DNA | 11 | 150 | 18 | 18 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01115018/DNA
Build-In Floor | Mini Canal | MICL.01115018/DNC | 11 | 150 | 18 | 18 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01115018/DNC
Build-In Floor | Mini Canal | MICL.01115018/DON | 11 | 150 | 18 | 18 | 288 | 288 | 288 | 0.0068571 | 112 | 0.0026667 | 328 | 0.0078095 | 1.362 | A04 | MICL0.01115018/DON
Build-In Floor | Mini Canal | MICL.01115018/DOV | 11 | 150 | 18 | 18 | 288 | 288 | 288 | 0.0068571 | 112 | 0.0026667 | 328 | 0.0078095 | 1.362 | A04 | MICL0.01115018/DOV
Build-In Floor | Mini Canal | MICL.01115018/RBL | 11 | 150 | 18 | 18 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.01115018/RBL
Build-In Floor | Mini Canal | MICL.01115018/RBN | 11 | 150 | 18 | 18 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01115018/RBN
Build-In Floor | Mini Canal | MICL.01115018/RBR | 11 | 150 | 18 | 18 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.01115018/RBR
Build-In Floor | Mini Canal | MICL.01115018/RBV | 11 | 150 | 18 | 18 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01115018/RBV
Build-In Floor | Mini Canal | MICL.01115018/RDB | 11 | 150 | 18 | 18 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.01115018/RDB
Build-In Floor | Mini Canal | MICL.01115018/RMN | 11 | 150 | 18 | 18 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01115018/RMN
Build-In Floor | Mini Canal | MICL.01115018/RMV | 11 | 150 | 18 | 18 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01115018/RMV
Build-In Floor | Mini Canal | MICL.01115018/RNA | 11 | 150 | 18 | 18 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.01115018/RNA
Build-In Floor | Mini Canal | MICL.01115018/RON | 11 | 150 | 18 | 18 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01115018/RON
Build-In Floor | Mini Canal | MICL.01115018/ROV | 11 | 150 | 18 | 18 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01115018/ROV
Build-In Floor | Mini Canal | MICL.01115018/RSS | 11 | 150 | 18 | 18 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.01115018/RSS
Build-In Floor | Mini Canal | MICL.01115018/SBL | 11 | 150 | 18 | 18 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.01115018/SBL
Build-In Floor | Mini Canal | MICL.01115018/SBR | 11 | 150 | 18 | 18 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.01115018/SBR
Build-In Floor | Mini Canal | MICL.01115018/SDB | 11 | 150 | 18 | 18 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.01115018/SDB
Build-In Floor | Mini Canal | MICL.01115018/SNA | 11 | 150 | 18 | 18 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.01115018/SNA
Build-In Floor | Mini Canal | MICL.01115018/SNC | 11 | 150 | 18 | 18 | 310 | 310 | 310 | 0.007381 | 121 | 0.002881 | 353 | 0.0084048 | 1.362 | A04 | MICL0.01115018/SNC
Build-In Floor | Mini Canal | MICL.01115026/ANA | 11 | 150 | 26 | 26 | 315 | 315 | 315 | 0.0075 | 123 | 0.0029286 | 359 | 0.0085476 | 1.362 | A04 | MICL0.01115026/ANA
Build-In Floor | Mini Canal | MICL.01115026/DBL | 11 | 150 | 26 | 26 | 407 | 407 | 407 | 0.0096905 | 158 | 0.0037619 | 464 | 0.011048 | 1.362 | A04 | MICL0.01115026/DBL
Build-In Floor | Mini Canal | MICL.01115026/DBN | 11 | 150 | 26 | 26 | 391 | 391 | 391 | 0.0093095 | 152 | 0.003619 | 445 | 0.010595 | 1.362 | A04 | MICL0.01115026/DBN
Build-In Floor | Mini Canal | MICL.01115026/DBR | 11 | 150 | 26 | 26 | 407 | 407 | 407 | 0.0096905 | 158 | 0.0037619 | 464 | 0.011048 | 1.362 | A04 | MICL0.01115026/DBR
Build-In Floor | Mini Canal | MICL.01115026/DBV | 11 | 150 | 26 | 26 | 391 | 391 | 391 | 0.0093095 | 152 | 0.003619 | 445 | 0.010595 | 1.362 | A04 | MICL0.01115026/DBV
Build-In Floor | Mini Canal | MICL.01115026/DDB | 11 | 150 | 26 | 26 | 407 | 407 | 407 | 0.0096905 | 158 | 0.0037619 | 464 | 0.011048 | 1.362 | A04 | MICL0.01115026/DDB
Build-In Floor | Mini Canal | MICL.01115026/DMN | 11 | 150 | 26 | 26 | 391 | 391 | 391 | 0.0093095 | 152 | 0.003619 | 445 | 0.010595 | 1.362 | A04 | MICL0.01115026/DMN
Build-In Floor | Mini Canal | MICL.01115026/DMV | 11 | 150 | 26 | 26 | 391 | 391 | 391 | 0.0093095 | 152 | 0.003619 | 445 | 0.010595 | 1.362 | A04 | MICL0.01115026/DMV
Build-In Floor | Mini Canal | MICL.01115026/DNA | 11 | 150 | 26 | 26 | 407 | 407 | 407 | 0.0096905 | 158 | 0.0037619 | 464 | 0.011048 | 1.362 | A04 | MICL0.01115026/DNA
Build-In Floor | Mini Canal | MICL.01115026/DNC | 11 | 150 | 26 | 26 | 407 | 407 | 407 | 0.0096905 | 158 | 0.0037619 | 464 | 0.011048 | 1.362 | A04 | MICL0.01115026/DNC
Build-In Floor | Mini Canal | MICL.01115026/DON | 11 | 150 | 26 | 26 | 391 | 391 | 391 | 0.0093095 | 152 | 0.003619 | 445 | 0.010595 | 1.362 | A04 | MICL0.01115026/DON
Build-In Floor | Mini Canal | MICL.01115026/DOV | 11 | 150 | 26 | 26 | 391 | 391 | 391 | 0.0093095 | 152 | 0.003619 | 445 | 0.010595 | 1.362 | A04 | MICL0.01115026/DOV
Build-In Floor | Mini Canal | MICL.01115026/PNC | 11 | 150 | 26 | 26 | 357 | 357 | 357 | 0.0085 | 139 | 0.0033095 | 407 | 0.0096905 | 1.362 | A04 | MICL0.01115026/PNC
Build-In Floor | Mini Canal | MICL.01115026/RBL | 11 | 150 | 26 | 26 | 420 | 420 | 420 | 0.01 | 163 | 0.003881 | 478 | 0.011381 | 1.362 | A04 | MICL0.01115026/RBL
Build-In Floor | Mini Canal | MICL.01115026/RBN | 11 | 150 | 26 | 26 | 407 | 407 | 407 | 0.0096905 | 158 | 0.0037619 | 464 | 0.011048 | 1.362 | A04 | MICL0.01115026/RBN
Build-In Floor | Mini Canal | MICL.01115026/RBR | 11 | 150 | 26 | 26 | 420 | 420 | 420 | 0.01 | 163 | 0.003881 | 478 | 0.011381 | 1.362 | A04 | MICL0.01115026/RBR
Build-In Floor | Mini Canal | MICL.01115026/RBV | 11 | 150 | 26 | 26 | 407 | 407 | 407 | 0.0096905 | 158 | 0.0037619 | 464 | 0.011048 | 1.362 | A04 | MICL0.01115026/RBV
Build-In Floor | Mini Canal | MICL.01115026/RDB | 11 | 150 | 26 | 26 | 420 | 420 | 420 | 0.01 | 163 | 0.003881 | 478 | 0.011381 | 1.362 | A04 | MICL0.01115026/RDB
Build-In Floor | Mini Canal | MICL.01115026/RMN | 11 | 150 | 26 | 26 | 407 | 407 | 407 | 0.0096905 | 158 | 0.0037619 | 464 | 0.011048 | 1.362 | A04 | MICL0.01115026/RMN
Build-In Floor | Mini Canal | MICL.01115026/RMV | 11 | 150 | 26 | 26 | 407 | 407 | 407 | 0.0096905 | 158 | 0.0037619 | 464 | 0.011048 | 1.362 | A04 | MICL0.01115026/RMV
Build-In Floor | Mini Canal | MICL.01115026/RNA | 11 | 150 | 26 | 26 | 420 | 420 | 420 | 0.01 | 163 | 0.003881 | 478 | 0.011381 | 1.362 | A04 | MICL0.01115026/RNA
Build-In Floor | Mini Canal | MICL.01115026/RON | 11 | 150 | 26 | 26 | 407 | 407 | 407 | 0.0096905 | 158 | 0.0037619 | 464 | 0.011048 | 1.362 | A04 | MICL0.01115026/RON
Build-In Floor | Mini Canal | MICL.01115026/ROV | 11 | 150 | 26 | 26 | 407 | 407 | 407 | 0.0096905 | 158 | 0.0037619 | 464 | 0.011048 | 1.362 | A04 | MICL0.01115026/ROV
Build-In Floor | Mini Canal | MICL.01115026/RSS | 11 | 150 | 26 | 26 | 403 | 403 | 403 | 0.0095952 | 157 | 0.0037381 | 459 | 0.010929 | 1.362 | A04 | MICL0.01115026/RSS
Build-In Floor | Mini Canal | MICL.01115026/SBL | 11 | 150 | 26 | 26 | 420 | 420 | 420 | 0.01 | 163 | 0.003881 | 478 | 0.011381 | 1.362 | A04 | MICL0.01115026/SBL
Build-In Floor | Mini Canal | MICL.01115026/SBR | 11 | 150 | 26 | 26 | 420 | 420 | 420 | 0.01 | 163 | 0.003881 | 478 | 0.011381 | 1.362 | A04 | MICL0.01115026/SBR
Build-In Floor | Mini Canal | MICL.01115026/SDB | 11 | 150 | 26 | 26 | 420 | 420 | 420 | 0.01 | 163 | 0.003881 | 478 | 0.011381 | 1.362 | A04 | MICL0.01115026/SDB
Build-In Floor | Mini Canal | MICL.01115026/SNA | 11 | 150 | 26 | 26 | 420 | 420 | 420 | 0.01 | 163 | 0.003881 | 478 | 0.011381 | 1.362 | A04 | MICL0.01115026/SNA
Build-In Floor | Mini Canal | MICL.01115026/SNC | 11 | 150 | 26 | 26 | 420 | 420 | 420 | 0.01 | 163 | 0.003881 | 478 | 0.011381 | 1.362 | A04 | MICL0.01115026/SNC
Build-In Floor | Mini Canal | MICL.01115034/ANA | 11 | 150 | 34 | 34 | 408 | 408 | 408 | 0.0097143 | 159 | 0.0037857 | 465 | 0.011071 | 1.362 | A04 | MICL0.01115034/ANA
Build-In Floor | Mini Canal | MICL.01115034/DBL | 11 | 150 | 34 | 34 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01115034/DBL
Build-In Floor | Mini Canal | MICL.01115034/DBN | 11 | 150 | 34 | 34 | 506 | 506 | 506 | 0.012048 | 197 | 0.0046905 | 576 | 0.013714 | 1.362 | A04 | MICL0.01115034/DBN
Build-In Floor | Mini Canal | MICL.01115034/DBR | 11 | 150 | 34 | 34 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01115034/DBR
Build-In Floor | Mini Canal | MICL.01115034/DBV | 11 | 150 | 34 | 34 | 506 | 506 | 506 | 0.012048 | 197 | 0.0046905 | 576 | 0.013714 | 1.362 | A04 | MICL0.01115034/DBV
Build-In Floor | Mini Canal | MICL.01115034/DDB | 11 | 150 | 34 | 34 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01115034/DDB
Build-In Floor | Mini Canal | MICL.01115034/DMN | 11 | 150 | 34 | 34 | 506 | 506 | 506 | 0.012048 | 197 | 0.0046905 | 576 | 0.013714 | 1.362 | A04 | MICL0.01115034/DMN
Build-In Floor | Mini Canal | MICL.01115034/DMV | 11 | 150 | 34 | 34 | 506 | 506 | 506 | 0.012048 | 197 | 0.0046905 | 576 | 0.013714 | 1.362 | A04 | MICL0.01115034/DMV
Build-In Floor | Mini Canal | MICL.01115034/DNA | 11 | 150 | 34 | 34 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01115034/DNA
Build-In Floor | Mini Canal | MICL.01115034/DNC | 11 | 150 | 34 | 34 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01115034/DNC
Build-In Floor | Mini Canal | MICL.01115034/DON | 11 | 150 | 34 | 34 | 506 | 506 | 506 | 0.012048 | 197 | 0.0046905 | 576 | 0.013714 | 1.362 | A04 | MICL0.01115034/DON
Build-In Floor | Mini Canal | MICL.01115034/DOV | 11 | 150 | 34 | 34 | 506 | 506 | 506 | 0.012048 | 197 | 0.0046905 | 576 | 0.013714 | 1.362 | A04 | MICL0.01115034/DOV
Build-In Floor | Mini Canal | MICL.01115034/PNC | 11 | 150 | 34 | 34 | 462 | 462 | 462 | 0.011 | 180 | 0.0042857 | 526 | 0.012524 | 1.362 | A04 | MICL0.01115034/PNC
Build-In Floor | Mini Canal | MICL.01115034/RBL | 11 | 150 | 34 | 34 | 544 | 544 | 544 | 0.012952 | 212 | 0.0050476 | 620 | 0.014762 | 1.362 | A04 | MICL0.01115034/RBL
Build-In Floor | Mini Canal | MICL.01115034/RBN | 11 | 150 | 34 | 34 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01115034/RBN
Build-In Floor | Mini Canal | MICL.01115034/RBR | 11 | 150 | 34 | 34 | 544 | 544 | 544 | 0.012952 | 212 | 0.0050476 | 620 | 0.014762 | 1.362 | A04 | MICL0.01115034/RBR
Build-In Floor | Mini Canal | MICL.01115034/RBV | 11 | 150 | 34 | 34 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01115034/RBV
Build-In Floor | Mini Canal | MICL.01115034/RDB | 11 | 150 | 34 | 34 | 544 | 544 | 544 | 0.012952 | 212 | 0.0050476 | 620 | 0.014762 | 1.362 | A04 | MICL0.01115034/RDB
Build-In Floor | Mini Canal | MICL.01115034/RMN | 11 | 150 | 34 | 34 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01115034/RMN
Build-In Floor | Mini Canal | MICL.01115034/RMV | 11 | 150 | 34 | 34 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01115034/RMV
Build-In Floor | Mini Canal | MICL.01115034/RNA | 11 | 150 | 34 | 34 | 544 | 544 | 544 | 0.012952 | 212 | 0.0050476 | 620 | 0.014762 | 1.362 | A04 | MICL0.01115034/RNA
Build-In Floor | Mini Canal | MICL.01115034/RON | 11 | 150 | 34 | 34 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01115034/RON
Build-In Floor | Mini Canal | MICL.01115034/ROV | 11 | 150 | 34 | 34 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01115034/ROV
Build-In Floor | Mini Canal | MICL.01115034/RSS | 11 | 150 | 34 | 34 | 522 | 522 | 522 | 0.012429 | 203 | 0.0048333 | 595 | 0.014167 | 1.362 | A04 | MICL0.01115034/RSS
Build-In Floor | Mini Canal | MICL.01115034/SBL | 11 | 150 | 34 | 34 | 544 | 544 | 544 | 0.012952 | 212 | 0.0050476 | 620 | 0.014762 | 1.362 | A04 | MICL0.01115034/SBL
Build-In Floor | Mini Canal | MICL.01115034/SBR | 11 | 150 | 34 | 34 | 544 | 544 | 544 | 0.012952 | 212 | 0.0050476 | 620 | 0.014762 | 1.362 | A04 | MICL0.01115034/SBR
Build-In Floor | Mini Canal | MICL.01115034/SDB | 11 | 150 | 34 | 34 | 544 | 544 | 544 | 0.012952 | 212 | 0.0050476 | 620 | 0.014762 | 1.362 | A04 | MICL0.01115034/SDB
Build-In Floor | Mini Canal | MICL.01115034/SNA | 11 | 150 | 34 | 34 | 544 | 544 | 544 | 0.012952 | 212 | 0.0050476 | 620 | 0.014762 | 1.362 | A04 | MICL0.01115034/SNA
Build-In Floor | Mini Canal | MICL.01115034/SNC | 11 | 150 | 34 | 34 | 544 | 544 | 544 | 0.012952 | 212 | 0.0050476 | 620 | 0.014762 | 1.362 | A04 | MICL0.01115034/SNC
Build-In Floor | Mini Canal | MICL.01115042/ANA | 11 | 150 | 42 | 42 | 575 | 575 | 575 | 0.01369 | 224 | 0.0053333 | 655 | 0.015595 | 1.362 | A04 | MICL0.01115042/ANA
Build-In Floor | Mini Canal | MICL.01115042/DBL | 11 | 150 | 42 | 42 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01115042/DBL
Build-In Floor | Mini Canal | MICL.01115042/DBN | 11 | 150 | 42 | 42 | 712 | 712 | 712 | 0.016952 | 277 | 0.0065952 | 811 | 0.01931 | 1.362 | A04 | MICL0.01115042/DBN
Build-In Floor | Mini Canal | MICL.01115042/DBR | 11 | 150 | 42 | 42 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01115042/DBR
Build-In Floor | Mini Canal | MICL.01115042/DBV | 11 | 150 | 42 | 42 | 712 | 712 | 712 | 0.016952 | 277 | 0.0065952 | 811 | 0.01931 | 1.362 | A04 | MICL0.01115042/DBV
Build-In Floor | Mini Canal | MICL.01115042/DDB | 11 | 150 | 42 | 42 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01115042/DDB
Build-In Floor | Mini Canal | MICL.01115042/DMN | 11 | 150 | 42 | 42 | 712 | 712 | 712 | 0.016952 | 277 | 0.0065952 | 811 | 0.01931 | 1.362 | A04 | MICL0.01115042/DMN
Build-In Floor | Mini Canal | MICL.01115042/DMV | 11 | 150 | 42 | 42 | 712 | 712 | 712 | 0.016952 | 277 | 0.0065952 | 811 | 0.01931 | 1.362 | A04 | MICL0.01115042/DMV
Build-In Floor | Mini Canal | MICL.01115042/DNA | 11 | 150 | 42 | 42 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01115042/DNA
Build-In Floor | Mini Canal | MICL.01115042/DNC | 11 | 150 | 42 | 42 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01115042/DNC
Build-In Floor | Mini Canal | MICL.01115042/DON | 11 | 150 | 42 | 42 | 712 | 712 | 712 | 0.016952 | 277 | 0.0065952 | 811 | 0.01931 | 1.362 | A04 | MICL0.01115042/DON
Build-In Floor | Mini Canal | MICL.01115042/DOV | 11 | 150 | 42 | 42 | 712 | 712 | 712 | 0.016952 | 277 | 0.0065952 | 811 | 0.01931 | 1.362 | A04 | MICL0.01115042/DOV
Build-In Floor | Mini Canal | MICL.01115042/PNC | 11 | 150 | 42 | 42 | 651 | 651 | 651 | 0.0155 | 253 | 0.0060238 | 741 | 0.017643 | 1.362 | A04 | MICL0.01115042/PNC
Build-In Floor | Mini Canal | MICL.01115042/RBL | 11 | 150 | 42 | 42 | 766 | 766 | 766 | 0.018238 | 298 | 0.0070952 | 872 | 0.020762 | 1.362 | A04 | MICL0.01115042/RBL
Build-In Floor | Mini Canal | MICL.01115042/RBN | 11 | 150 | 42 | 42 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01115042/RBN
Build-In Floor | Mini Canal | MICL.01115042/RBR | 11 | 150 | 42 | 42 | 766 | 766 | 766 | 0.018238 | 298 | 0.0070952 | 872 | 0.020762 | 1.362 | A04 | MICL0.01115042/RBR
Build-In Floor | Mini Canal | MICL.01115042/RBV | 11 | 150 | 42 | 42 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01115042/RBV
Build-In Floor | Mini Canal | MICL.01115042/RDB | 11 | 150 | 42 | 42 | 766 | 766 | 766 | 0.018238 | 298 | 0.0070952 | 872 | 0.020762 | 1.362 | A04 | MICL0.01115042/RDB
Build-In Floor | Mini Canal | MICL.01115042/RMN | 11 | 150 | 42 | 42 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01115042/RMN
Build-In Floor | Mini Canal | MICL.01115042/RMV | 11 | 150 | 42 | 42 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01115042/RMV
Build-In Floor | Mini Canal | MICL.01115042/RNA | 11 | 150 | 42 | 42 | 766 | 766 | 766 | 0.018238 | 298 | 0.0070952 | 872 | 0.020762 | 1.362 | A04 | MICL0.01115042/RNA
Build-In Floor | Mini Canal | MICL.01115042/RON | 11 | 150 | 42 | 42 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01115042/RON
Build-In Floor | Mini Canal | MICL.01115042/ROV | 11 | 150 | 42 | 42 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01115042/ROV
Build-In Floor | Mini Canal | MICL.01115042/RSS | 11 | 150 | 42 | 42 | 735 | 735 | 735 | 0.0175 | 286 | 0.0068095 | 837 | 0.019929 | 1.362 | A04 | MICL0.01115042/RSS
Build-In Floor | Mini Canal | MICL.01115042/SBL | 11 | 150 | 42 | 42 | 766 | 766 | 766 | 0.018238 | 298 | 0.0070952 | 872 | 0.020762 | 1.362 | A04 | MICL0.01115042/SBL
Build-In Floor | Mini Canal | MICL.01115042/SBR | 11 | 150 | 42 | 42 | 766 | 766 | 766 | 0.018238 | 298 | 0.0070952 | 872 | 0.020762 | 1.362 | A04 | MICL0.01115042/SBR
Build-In Floor | Mini Canal | MICL.01115042/SDB | 11 | 150 | 42 | 42 | 766 | 766 | 766 | 0.018238 | 298 | 0.0070952 | 872 | 0.020762 | 1.362 | A04 | MICL0.01115042/SDB
Build-In Floor | Mini Canal | MICL.01115042/SNA | 11 | 150 | 42 | 42 | 766 | 766 | 766 | 0.018238 | 298 | 0.0070952 | 872 | 0.020762 | 1.362 | A04 | MICL0.01115042/SNA
Build-In Floor | Mini Canal | MICL.01115042/SNC | 11 | 150 | 42 | 42 | 766 | 766 | 766 | 0.018238 | 298 | 0.0070952 | 872 | 0.020762 | 1.362 | A04 | MICL0.01115042/SNC
Build-In Floor | Mini Canal | MICL.01117014/ANA | 11 | 170 | 14 | 14 | 230 | 230 | 230 | 0.0054762 | 89 | 0.002119 | 262 | 0.0062381 | 1.362 | A04 | MICL0.01117014/ANA
Build-In Floor | Mini Canal | MICL.01117014/DBL | 11 | 170 | 14 | 14 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01117014/DBL
Build-In Floor | Mini Canal | MICL.01117014/DBN | 11 | 170 | 14 | 14 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01117014/DBN
Build-In Floor | Mini Canal | MICL.01117014/DBR | 11 | 170 | 14 | 14 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01117014/DBR
Build-In Floor | Mini Canal | MICL.01117014/DBV | 11 | 170 | 14 | 14 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01117014/DBV
Build-In Floor | Mini Canal | MICL.01117014/DDB | 11 | 170 | 14 | 14 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01117014/DDB
Build-In Floor | Mini Canal | MICL.01117014/DMN | 11 | 170 | 14 | 14 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01117014/DMN
Build-In Floor | Mini Canal | MICL.01117014/DMV | 11 | 170 | 14 | 14 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01117014/DMV
Build-In Floor | Mini Canal | MICL.01117014/DNA | 11 | 170 | 14 | 14 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01117014/DNA
Build-In Floor | Mini Canal | MICL.01117014/DNC | 11 | 170 | 14 | 14 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01117014/DNC
Build-In Floor | Mini Canal | MICL.01117014/DON | 11 | 170 | 14 | 14 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01117014/DON
Build-In Floor | Mini Canal | MICL.01117014/DOV | 11 | 170 | 14 | 14 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01117014/DOV
Build-In Floor | Mini Canal | MICL.01117014/RBL | 11 | 170 | 14 | 14 | 306 | 306 | 306 | 0.0072857 | 119 | 0.0028333 | 349 | 0.0083095 | 1.362 | A04 | MICL0.01117014/RBL
Build-In Floor | Mini Canal | MICL.01117014/RBN | 11 | 170 | 14 | 14 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01117014/RBN
Build-In Floor | Mini Canal | MICL.01117014/RBR | 11 | 170 | 14 | 14 | 306 | 306 | 306 | 0.0072857 | 119 | 0.0028333 | 349 | 0.0083095 | 1.362 | A04 | MICL0.01117014/RBR
Build-In Floor | Mini Canal | MICL.01117014/RBV | 11 | 170 | 14 | 14 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01117014/RBV
Build-In Floor | Mini Canal | MICL.01117014/RDB | 11 | 170 | 14 | 14 | 306 | 306 | 306 | 0.0072857 | 119 | 0.0028333 | 349 | 0.0083095 | 1.362 | A04 | MICL0.01117014/RDB
Build-In Floor | Mini Canal | MICL.01117014/RMN | 11 | 170 | 14 | 14 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01117014/RMN
Build-In Floor | Mini Canal | MICL.01117014/RMV | 11 | 170 | 14 | 14 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01117014/RMV
Build-In Floor | Mini Canal | MICL.01117014/RNA | 11 | 170 | 14 | 14 | 306 | 306 | 306 | 0.0072857 | 119 | 0.0028333 | 349 | 0.0083095 | 1.362 | A04 | MICL0.01117014/RNA
Build-In Floor | Mini Canal | MICL.01117014/RON | 11 | 170 | 14 | 14 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01117014/RON
Build-In Floor | Mini Canal | MICL.01117014/ROV | 11 | 170 | 14 | 14 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01117014/ROV
Build-In Floor | Mini Canal | MICL.01117014/RSS | 11 | 170 | 14 | 14 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.01117014/RSS
Build-In Floor | Mini Canal | MICL.01117014/SBL | 11 | 170 | 14 | 14 | 306 | 306 | 306 | 0.0072857 | 119 | 0.0028333 | 349 | 0.0083095 | 1.362 | A04 | MICL0.01117014/SBL
Build-In Floor | Mini Canal | MICL.01117014/SBR | 11 | 170 | 14 | 14 | 306 | 306 | 306 | 0.0072857 | 119 | 0.0028333 | 349 | 0.0083095 | 1.362 | A04 | MICL0.01117014/SBR
Build-In Floor | Mini Canal | MICL.01117014/SDB | 11 | 170 | 14 | 14 | 306 | 306 | 306 | 0.0072857 | 119 | 0.0028333 | 349 | 0.0083095 | 1.362 | A04 | MICL0.01117014/SDB
Build-In Floor | Mini Canal | MICL.01117014/SNA | 11 | 170 | 14 | 14 | 306 | 306 | 306 | 0.0072857 | 119 | 0.0028333 | 349 | 0.0083095 | 1.362 | A04 | MICL0.01117014/SNA
Build-In Floor | Mini Canal | MICL.01117014/SNC | 11 | 170 | 14 | 14 | 306 | 306 | 306 | 0.0072857 | 119 | 0.0028333 | 349 | 0.0083095 | 1.362 | A04 | MICL0.01117014/SNC
Build-In Floor | Mini Canal | MICL.01117018/ANA | 11 | 170 | 18 | 18 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01117018/ANA
Build-In Floor | Mini Canal | MICL.01117018/DBL | 11 | 170 | 18 | 18 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01117018/DBL
Build-In Floor | Mini Canal | MICL.01117018/DBN | 11 | 170 | 18 | 18 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01117018/DBN
Build-In Floor | Mini Canal | MICL.01117018/DBR | 11 | 170 | 18 | 18 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01117018/DBR
Build-In Floor | Mini Canal | MICL.01117018/DBV | 11 | 170 | 18 | 18 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01117018/DBV
Build-In Floor | Mini Canal | MICL.01117018/DDB | 11 | 170 | 18 | 18 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01117018/DDB
Build-In Floor | Mini Canal | MICL.01117018/DMN | 11 | 170 | 18 | 18 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01117018/DMN
Build-In Floor | Mini Canal | MICL.01117018/DMV | 11 | 170 | 18 | 18 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01117018/DMV
Build-In Floor | Mini Canal | MICL.01117018/DNA | 11 | 170 | 18 | 18 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01117018/DNA
Build-In Floor | Mini Canal | MICL.01117018/DNC | 11 | 170 | 18 | 18 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01117018/DNC
Build-In Floor | Mini Canal | MICL.01117018/DON | 11 | 170 | 18 | 18 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01117018/DON
Build-In Floor | Mini Canal | MICL.01117018/DOV | 11 | 170 | 18 | 18 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01117018/DOV
Build-In Floor | Mini Canal | MICL.01117018/RBL | 11 | 170 | 18 | 18 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01117018/RBL
Build-In Floor | Mini Canal | MICL.01117018/RBN | 11 | 170 | 18 | 18 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01117018/RBN
Build-In Floor | Mini Canal | MICL.01117018/RBR | 11 | 170 | 18 | 18 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01117018/RBR
Build-In Floor | Mini Canal | MICL.01117018/RBV | 11 | 170 | 18 | 18 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01117018/RBV
Build-In Floor | Mini Canal | MICL.01117018/RDB | 11 | 170 | 18 | 18 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01117018/RDB
Build-In Floor | Mini Canal | MICL.01117018/RMN | 11 | 170 | 18 | 18 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01117018/RMN
Build-In Floor | Mini Canal | MICL.01117018/RMV | 11 | 170 | 18 | 18 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01117018/RMV
Build-In Floor | Mini Canal | MICL.01117018/RNA | 11 | 170 | 18 | 18 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01117018/RNA
Build-In Floor | Mini Canal | MICL.01117018/RON | 11 | 170 | 18 | 18 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01117018/RON
Build-In Floor | Mini Canal | MICL.01117018/ROV | 11 | 170 | 18 | 18 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01117018/ROV
Build-In Floor | Mini Canal | MICL.01117018/RSS | 11 | 170 | 18 | 18 | 348 | 348 | 348 | 0.0082857 | 135 | 0.0032143 | 396 | 0.0094286 | 1.362 | A04 | MICL0.01117018/RSS
Build-In Floor | Mini Canal | MICL.01117018/SBL | 11 | 170 | 18 | 18 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01117018/SBL
Build-In Floor | Mini Canal | MICL.01117018/SBR | 11 | 170 | 18 | 18 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01117018/SBR
Build-In Floor | Mini Canal | MICL.01117018/SDB | 11 | 170 | 18 | 18 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01117018/SDB
Build-In Floor | Mini Canal | MICL.01117018/SNA | 11 | 170 | 18 | 18 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01117018/SNA
Build-In Floor | Mini Canal | MICL.01117018/SNC | 11 | 170 | 18 | 18 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01117018/SNC
Build-In Floor | Mini Canal | MICL.01117026/ANA | 11 | 170 | 26 | 26 | 367 | 367 | 367 | 0.0087381 | 143 | 0.0034048 | 418 | 0.0099524 | 1.362 | A04 | MICL0.01117026/ANA
Build-In Floor | Mini Canal | MICL.01117026/DBL | 11 | 170 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01117026/DBL
Build-In Floor | Mini Canal | MICL.01117026/DBN | 11 | 170 | 26 | 26 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01117026/DBN
Build-In Floor | Mini Canal | MICL.01117026/DBR | 11 | 170 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01117026/DBR
Build-In Floor | Mini Canal | MICL.01117026/DBV | 11 | 170 | 26 | 26 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01117026/DBV
Build-In Floor | Mini Canal | MICL.01117026/DDB | 11 | 170 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01117026/DDB
Build-In Floor | Mini Canal | MICL.01117026/DMN | 11 | 170 | 26 | 26 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01117026/DMN
Build-In Floor | Mini Canal | MICL.01117026/DMV | 11 | 170 | 26 | 26 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01117026/DMV
Build-In Floor | Mini Canal | MICL.01117026/DNA | 11 | 170 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01117026/DNA
Build-In Floor | Mini Canal | MICL.01117026/DNC | 11 | 170 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01117026/DNC
Build-In Floor | Mini Canal | MICL.01117026/DON | 11 | 170 | 26 | 26 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01117026/DON
Build-In Floor | Mini Canal | MICL.01117026/DOV | 11 | 170 | 26 | 26 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01117026/DOV
Build-In Floor | Mini Canal | MICL.01117026/PNC | 11 | 170 | 26 | 26 | 416 | 416 | 416 | 0.0099048 | 162 | 0.0038571 | 474 | 0.011286 | 1.362 | A04 | MICL0.01117026/PNC
Build-In Floor | Mini Canal | MICL.01117026/RBL | 11 | 170 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01117026/RBL
Build-In Floor | Mini Canal | MICL.01117026/RBN | 11 | 170 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01117026/RBN
Build-In Floor | Mini Canal | MICL.01117026/RBR | 11 | 170 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01117026/RBR
Build-In Floor | Mini Canal | MICL.01117026/RBV | 11 | 170 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01117026/RBV
Build-In Floor | Mini Canal | MICL.01117026/RDB | 11 | 170 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01117026/RDB
Build-In Floor | Mini Canal | MICL.01117026/RMN | 11 | 170 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01117026/RMN
Build-In Floor | Mini Canal | MICL.01117026/RMV | 11 | 170 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01117026/RMV
Build-In Floor | Mini Canal | MICL.01117026/RNA | 11 | 170 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01117026/RNA
Build-In Floor | Mini Canal | MICL.01117026/RON | 11 | 170 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01117026/RON
Build-In Floor | Mini Canal | MICL.01117026/ROV | 11 | 170 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01117026/ROV
Build-In Floor | Mini Canal | MICL.01117026/RSS | 11 | 170 | 26 | 26 | 469 | 469 | 469 | 0.011167 | 182 | 0.0043333 | 534 | 0.012714 | 1.362 | A04 | MICL0.01117026/RSS
Build-In Floor | Mini Canal | MICL.01117026/SBL | 11 | 170 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01117026/SBL
Build-In Floor | Mini Canal | MICL.01117026/SBR | 11 | 170 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01117026/SBR
Build-In Floor | Mini Canal | MICL.01117026/SDB | 11 | 170 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01117026/SDB
Build-In Floor | Mini Canal | MICL.01117026/SNA | 11 | 170 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01117026/SNA
Build-In Floor | Mini Canal | MICL.01117026/SNC | 11 | 170 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01117026/SNC
Build-In Floor | Mini Canal | MICL.01117034/ANA | 11 | 170 | 34 | 34 | 477 | 477 | 477 | 0.011357 | 186 | 0.0044286 | 543 | 0.012929 | 1.362 | A04 | MICL0.01117034/ANA
Build-In Floor | Mini Canal | MICL.01117034/DBL | 11 | 170 | 34 | 34 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01117034/DBL
Build-In Floor | Mini Canal | MICL.01117034/DBN | 11 | 170 | 34 | 34 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.01117034/DBN
Build-In Floor | Mini Canal | MICL.01117034/DBR | 11 | 170 | 34 | 34 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01117034/DBR
Build-In Floor | Mini Canal | MICL.01117034/DBV | 11 | 170 | 34 | 34 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.01117034/DBV
Build-In Floor | Mini Canal | MICL.01117034/DDB | 11 | 170 | 34 | 34 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01117034/DDB
Build-In Floor | Mini Canal | MICL.01117034/DMN | 11 | 170 | 34 | 34 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.01117034/DMN
Build-In Floor | Mini Canal | MICL.01117034/DMV | 11 | 170 | 34 | 34 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.01117034/DMV
Build-In Floor | Mini Canal | MICL.01117034/DNA | 11 | 170 | 34 | 34 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01117034/DNA
Build-In Floor | Mini Canal | MICL.01117034/DNC | 11 | 170 | 34 | 34 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01117034/DNC
Build-In Floor | Mini Canal | MICL.01117034/DON | 11 | 170 | 34 | 34 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.01117034/DON
Build-In Floor | Mini Canal | MICL.01117034/DOV | 11 | 170 | 34 | 34 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.01117034/DOV
Build-In Floor | Mini Canal | MICL.01117034/PNC | 11 | 170 | 34 | 34 | 541 | 541 | 541 | 0.012881 | 210 | 0.005 | 616 | 0.014667 | 1.362 | A04 | MICL0.01117034/PNC
Build-In Floor | Mini Canal | MICL.01117034/RBL | 11 | 170 | 34 | 34 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01117034/RBL
Build-In Floor | Mini Canal | MICL.01117034/RBN | 11 | 170 | 34 | 34 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01117034/RBN
Build-In Floor | Mini Canal | MICL.01117034/RBR | 11 | 170 | 34 | 34 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01117034/RBR
Build-In Floor | Mini Canal | MICL.01117034/RBV | 11 | 170 | 34 | 34 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01117034/RBV
Build-In Floor | Mini Canal | MICL.01117034/RDB | 11 | 170 | 34 | 34 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01117034/RDB
Build-In Floor | Mini Canal | MICL.01117034/RMN | 11 | 170 | 34 | 34 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01117034/RMN
Build-In Floor | Mini Canal | MICL.01117034/RMV | 11 | 170 | 34 | 34 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01117034/RMV
Build-In Floor | Mini Canal | MICL.01117034/RNA | 11 | 170 | 34 | 34 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01117034/RNA
Build-In Floor | Mini Canal | MICL.01117034/RON | 11 | 170 | 34 | 34 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01117034/RON
Build-In Floor | Mini Canal | MICL.01117034/ROV | 11 | 170 | 34 | 34 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01117034/ROV
Build-In Floor | Mini Canal | MICL.01117034/RSS | 11 | 170 | 34 | 34 | 611 | 611 | 611 | 0.014548 | 238 | 0.0056667 | 696 | 0.016571 | 1.362 | A04 | MICL0.01117034/RSS
Build-In Floor | Mini Canal | MICL.01117034/SBL | 11 | 170 | 34 | 34 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01117034/SBL
Build-In Floor | Mini Canal | MICL.01117034/SBR | 11 | 170 | 34 | 34 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01117034/SBR
Build-In Floor | Mini Canal | MICL.01117034/SDB | 11 | 170 | 34 | 34 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01117034/SDB
Build-In Floor | Mini Canal | MICL.01117034/SNA | 11 | 170 | 34 | 34 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01117034/SNA
Build-In Floor | Mini Canal | MICL.01117034/SNC | 11 | 170 | 34 | 34 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01117034/SNC
Build-In Floor | Mini Canal | MICL.01117042/ANA | 11 | 170 | 42 | 42 | 670 | 670 | 670 | 0.015952 | 261 | 0.0062143 | 763 | 0.018167 | 1.362 | A04 | MICL0.01117042/ANA
Build-In Floor | Mini Canal | MICL.01117042/DBL | 11 | 170 | 42 | 42 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01117042/DBL
Build-In Floor | Mini Canal | MICL.01117042/DBN | 11 | 170 | 42 | 42 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01117042/DBN
Build-In Floor | Mini Canal | MICL.01117042/DBR | 11 | 170 | 42 | 42 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01117042/DBR
Build-In Floor | Mini Canal | MICL.01117042/DBV | 11 | 170 | 42 | 42 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01117042/DBV
Build-In Floor | Mini Canal | MICL.01117042/DDB | 11 | 170 | 42 | 42 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01117042/DDB
Build-In Floor | Mini Canal | MICL.01117042/DMN | 11 | 170 | 42 | 42 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01117042/DMN
Build-In Floor | Mini Canal | MICL.01117042/DMV | 11 | 170 | 42 | 42 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01117042/DMV
Build-In Floor | Mini Canal | MICL.01117042/DNA | 11 | 170 | 42 | 42 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01117042/DNA
Build-In Floor | Mini Canal | MICL.01117042/DNC | 11 | 170 | 42 | 42 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01117042/DNC
Build-In Floor | Mini Canal | MICL.01117042/DON | 11 | 170 | 42 | 42 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01117042/DON
Build-In Floor | Mini Canal | MICL.01117042/DOV | 11 | 170 | 42 | 42 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01117042/DOV
Build-In Floor | Mini Canal | MICL.01117042/PNC | 11 | 170 | 42 | 42 | 759 | 759 | 759 | 0.018071 | 295 | 0.0070238 | 865 | 0.020595 | 1.362 | A04 | MICL0.01117042/PNC
Build-In Floor | Mini Canal | MICL.01117042/RBL | 11 | 170 | 42 | 42 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01117042/RBL
Build-In Floor | Mini Canal | MICL.01117042/RBN | 11 | 170 | 42 | 42 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01117042/RBN
Build-In Floor | Mini Canal | MICL.01117042/RBR | 11 | 170 | 42 | 42 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01117042/RBR
Build-In Floor | Mini Canal | MICL.01117042/RBV | 11 | 170 | 42 | 42 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01117042/RBV
Build-In Floor | Mini Canal | MICL.01117042/RDB | 11 | 170 | 42 | 42 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01117042/RDB
Build-In Floor | Mini Canal | MICL.01117042/RMN | 11 | 170 | 42 | 42 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01117042/RMN
Build-In Floor | Mini Canal | MICL.01117042/RMV | 11 | 170 | 42 | 42 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01117042/RMV
Build-In Floor | Mini Canal | MICL.01117042/RNA | 11 | 170 | 42 | 42 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01117042/RNA
Build-In Floor | Mini Canal | MICL.01117042/RON | 11 | 170 | 42 | 42 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01117042/RON
Build-In Floor | Mini Canal | MICL.01117042/ROV | 11 | 170 | 42 | 42 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01117042/ROV
Build-In Floor | Mini Canal | MICL.01117042/RSS | 11 | 170 | 42 | 42 | 857 | 857 | 857 | 0.020405 | 333 | 0.0079286 | 976 | 0.023238 | 1.362 | A04 | MICL0.01117042/RSS
Build-In Floor | Mini Canal | MICL.01117042/SBL | 11 | 170 | 42 | 42 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01117042/SBL
Build-In Floor | Mini Canal | MICL.01117042/SBR | 11 | 170 | 42 | 42 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01117042/SBR
Build-In Floor | Mini Canal | MICL.01117042/SDB | 11 | 170 | 42 | 42 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01117042/SDB
Build-In Floor | Mini Canal | MICL.01117042/SNA | 11 | 170 | 42 | 42 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01117042/SNA
Build-In Floor | Mini Canal | MICL.01117042/SNC | 11 | 170 | 42 | 42 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01117042/SNC
Build-In Floor | Mini Canal | MICL.01119014/ANA | 11 | 190 | 14 | 14 | 262 | 262 | 262 | 0.0062381 | 102 | 0.0024286 | 298 | 0.0070952 | 1.362 | A04 | MICL0.01119014/ANA
Build-In Floor | Mini Canal | MICL.01119014/DBL | 11 | 190 | 14 | 14 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01119014/DBL
Build-In Floor | Mini Canal | MICL.01119014/DBN | 11 | 190 | 14 | 14 | 325 | 325 | 325 | 0.0077381 | 126 | 0.003 | 370 | 0.0088095 | 1.362 | A04 | MICL0.01119014/DBN
Build-In Floor | Mini Canal | MICL.01119014/DBR | 11 | 190 | 14 | 14 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01119014/DBR
Build-In Floor | Mini Canal | MICL.01119014/DBV | 11 | 190 | 14 | 14 | 325 | 325 | 325 | 0.0077381 | 126 | 0.003 | 370 | 0.0088095 | 1.362 | A04 | MICL0.01119014/DBV
Build-In Floor | Mini Canal | MICL.01119014/DDB | 11 | 190 | 14 | 14 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01119014/DDB
Build-In Floor | Mini Canal | MICL.01119014/DMN | 11 | 190 | 14 | 14 | 325 | 325 | 325 | 0.0077381 | 126 | 0.003 | 370 | 0.0088095 | 1.362 | A04 | MICL0.01119014/DMN
Build-In Floor | Mini Canal | MICL.01119014/DMV | 11 | 190 | 14 | 14 | 325 | 325 | 325 | 0.0077381 | 126 | 0.003 | 370 | 0.0088095 | 1.362 | A04 | MICL0.01119014/DMV
Build-In Floor | Mini Canal | MICL.01119014/DNA | 11 | 190 | 14 | 14 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01119014/DNA
Build-In Floor | Mini Canal | MICL.01119014/DNC | 11 | 190 | 14 | 14 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01119014/DNC
Build-In Floor | Mini Canal | MICL.01119014/DON | 11 | 190 | 14 | 14 | 325 | 325 | 325 | 0.0077381 | 126 | 0.003 | 370 | 0.0088095 | 1.362 | A04 | MICL0.01119014/DON
Build-In Floor | Mini Canal | MICL.01119014/DOV | 11 | 190 | 14 | 14 | 325 | 325 | 325 | 0.0077381 | 126 | 0.003 | 370 | 0.0088095 | 1.362 | A04 | MICL0.01119014/DOV
Build-In Floor | Mini Canal | MICL.01119014/RBL | 11 | 190 | 14 | 14 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01119014/RBL
Build-In Floor | Mini Canal | MICL.01119014/RBN | 11 | 190 | 14 | 14 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01119014/RBN
Build-In Floor | Mini Canal | MICL.01119014/RBR | 11 | 190 | 14 | 14 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01119014/RBR
Build-In Floor | Mini Canal | MICL.01119014/RBV | 11 | 190 | 14 | 14 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01119014/RBV
Build-In Floor | Mini Canal | MICL.01119014/RDB | 11 | 190 | 14 | 14 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01119014/RDB
Build-In Floor | Mini Canal | MICL.01119014/RMN | 11 | 190 | 14 | 14 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01119014/RMN
Build-In Floor | Mini Canal | MICL.01119014/RMV | 11 | 190 | 14 | 14 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01119014/RMV
Build-In Floor | Mini Canal | MICL.01119014/RNA | 11 | 190 | 14 | 14 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01119014/RNA
Build-In Floor | Mini Canal | MICL.01119014/RON | 11 | 190 | 14 | 14 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01119014/RON
Build-In Floor | Mini Canal | MICL.01119014/ROV | 11 | 190 | 14 | 14 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01119014/ROV
Build-In Floor | Mini Canal | MICL.01119014/RSS | 11 | 190 | 14 | 14 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01119014/RSS
Build-In Floor | Mini Canal | MICL.01119014/SBL | 11 | 190 | 14 | 14 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01119014/SBL
Build-In Floor | Mini Canal | MICL.01119014/SBR | 11 | 190 | 14 | 14 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01119014/SBR
Build-In Floor | Mini Canal | MICL.01119014/SDB | 11 | 190 | 14 | 14 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01119014/SDB
Build-In Floor | Mini Canal | MICL.01119014/SNA | 11 | 190 | 14 | 14 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01119014/SNA
Build-In Floor | Mini Canal | MICL.01119014/SNC | 11 | 190 | 14 | 14 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01119014/SNC
Build-In Floor | Mini Canal | MICL.01119018/ANA | 11 | 190 | 18 | 18 | 311 | 311 | 311 | 0.0074048 | 121 | 0.002881 | 354 | 0.0084286 | 1.362 | A04 | MICL0.01119018/ANA
Build-In Floor | Mini Canal | MICL.01119018/DBL | 11 | 190 | 18 | 18 | 402 | 402 | 402 | 0.0095714 | 156 | 0.0037143 | 458 | 0.010905 | 1.362 | A04 | MICL0.01119018/DBL
Build-In Floor | Mini Canal | MICL.01119018/DBN | 11 | 190 | 18 | 18 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01119018/DBN
Build-In Floor | Mini Canal | MICL.01119018/DBR | 11 | 190 | 18 | 18 | 402 | 402 | 402 | 0.0095714 | 156 | 0.0037143 | 458 | 0.010905 | 1.362 | A04 | MICL0.01119018/DBR
Build-In Floor | Mini Canal | MICL.01119018/DBV | 11 | 190 | 18 | 18 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01119018/DBV
Build-In Floor | Mini Canal | MICL.01119018/DDB | 11 | 190 | 18 | 18 | 402 | 402 | 402 | 0.0095714 | 156 | 0.0037143 | 458 | 0.010905 | 1.362 | A04 | MICL0.01119018/DDB
Build-In Floor | Mini Canal | MICL.01119018/DMN | 11 | 190 | 18 | 18 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01119018/DMN
Build-In Floor | Mini Canal | MICL.01119018/DMV | 11 | 190 | 18 | 18 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01119018/DMV
Build-In Floor | Mini Canal | MICL.01119018/DNA | 11 | 190 | 18 | 18 | 402 | 402 | 402 | 0.0095714 | 156 | 0.0037143 | 458 | 0.010905 | 1.362 | A04 | MICL0.01119018/DNA
Build-In Floor | Mini Canal | MICL.01119018/DNC | 11 | 190 | 18 | 18 | 402 | 402 | 402 | 0.0095714 | 156 | 0.0037143 | 458 | 0.010905 | 1.362 | A04 | MICL0.01119018/DNC
Build-In Floor | Mini Canal | MICL.01119018/DON | 11 | 190 | 18 | 18 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01119018/DON
Build-In Floor | Mini Canal | MICL.01119018/DOV | 11 | 190 | 18 | 18 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01119018/DOV
Build-In Floor | Mini Canal | MICL.01119018/RBL | 11 | 190 | 18 | 18 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.01119018/RBL
Build-In Floor | Mini Canal | MICL.01119018/RBN | 11 | 190 | 18 | 18 | 402 | 402 | 402 | 0.0095714 | 156 | 0.0037143 | 458 | 0.010905 | 1.362 | A04 | MICL0.01119018/RBN
Build-In Floor | Mini Canal | MICL.01119018/RBR | 11 | 190 | 18 | 18 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.01119018/RBR
Build-In Floor | Mini Canal | MICL.01119018/RBV | 11 | 190 | 18 | 18 | 402 | 402 | 402 | 0.0095714 | 156 | 0.0037143 | 458 | 0.010905 | 1.362 | A04 | MICL0.01119018/RBV
Build-In Floor | Mini Canal | MICL.01119018/RDB | 11 | 190 | 18 | 18 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.01119018/RDB
Build-In Floor | Mini Canal | MICL.01119018/RMN | 11 | 190 | 18 | 18 | 402 | 402 | 402 | 0.0095714 | 156 | 0.0037143 | 458 | 0.010905 | 1.362 | A04 | MICL0.01119018/RMN
Build-In Floor | Mini Canal | MICL.01119018/RMV | 11 | 190 | 18 | 18 | 402 | 402 | 402 | 0.0095714 | 156 | 0.0037143 | 458 | 0.010905 | 1.362 | A04 | MICL0.01119018/RMV
Build-In Floor | Mini Canal | MICL.01119018/RNA | 11 | 190 | 18 | 18 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.01119018/RNA
Build-In Floor | Mini Canal | MICL.01119018/RON | 11 | 190 | 18 | 18 | 402 | 402 | 402 | 0.0095714 | 156 | 0.0037143 | 458 | 0.010905 | 1.362 | A04 | MICL0.01119018/RON
Build-In Floor | Mini Canal | MICL.01119018/ROV | 11 | 190 | 18 | 18 | 402 | 402 | 402 | 0.0095714 | 156 | 0.0037143 | 458 | 0.010905 | 1.362 | A04 | MICL0.01119018/ROV
Build-In Floor | Mini Canal | MICL.01119018/RSS | 11 | 190 | 18 | 18 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01119018/RSS
Build-In Floor | Mini Canal | MICL.01119018/SBL | 11 | 190 | 18 | 18 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.01119018/SBL
Build-In Floor | Mini Canal | MICL.01119018/SBR | 11 | 190 | 18 | 18 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.01119018/SBR
Build-In Floor | Mini Canal | MICL.01119018/SDB | 11 | 190 | 18 | 18 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.01119018/SDB
Build-In Floor | Mini Canal | MICL.01119018/SNA | 11 | 190 | 18 | 18 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.01119018/SNA
Build-In Floor | Mini Canal | MICL.01119018/SNC | 11 | 190 | 18 | 18 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.01119018/SNC
Build-In Floor | Mini Canal | MICL.01119026/ANA | 11 | 190 | 26 | 26 | 419 | 419 | 419 | 0.0099762 | 163 | 0.003881 | 477 | 0.011357 | 1.362 | A04 | MICL0.01119026/ANA
Build-In Floor | Mini Canal | MICL.01119026/DBL | 11 | 190 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 211 | 0.0050238 | 617 | 0.01469 | 1.362 | A04 | MICL0.01119026/DBL
Build-In Floor | Mini Canal | MICL.01119026/DBN | 11 | 190 | 26 | 26 | 520 | 520 | 520 | 0.012381 | 202 | 0.0048095 | 592 | 0.014095 | 1.362 | A04 | MICL0.01119026/DBN
Build-In Floor | Mini Canal | MICL.01119026/DBR | 11 | 190 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 211 | 0.0050238 | 617 | 0.01469 | 1.362 | A04 | MICL0.01119026/DBR
Build-In Floor | Mini Canal | MICL.01119026/DBV | 11 | 190 | 26 | 26 | 520 | 520 | 520 | 0.012381 | 202 | 0.0048095 | 592 | 0.014095 | 1.362 | A04 | MICL0.01119026/DBV
Build-In Floor | Mini Canal | MICL.01119026/DDB | 11 | 190 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 211 | 0.0050238 | 617 | 0.01469 | 1.362 | A04 | MICL0.01119026/DDB
Build-In Floor | Mini Canal | MICL.01119026/DMN | 11 | 190 | 26 | 26 | 520 | 520 | 520 | 0.012381 | 202 | 0.0048095 | 592 | 0.014095 | 1.362 | A04 | MICL0.01119026/DMN
Build-In Floor | Mini Canal | MICL.01119026/DMV | 11 | 190 | 26 | 26 | 520 | 520 | 520 | 0.012381 | 202 | 0.0048095 | 592 | 0.014095 | 1.362 | A04 | MICL0.01119026/DMV
Build-In Floor | Mini Canal | MICL.01119026/DNA | 11 | 190 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 211 | 0.0050238 | 617 | 0.01469 | 1.362 | A04 | MICL0.01119026/DNA
Build-In Floor | Mini Canal | MICL.01119026/DNC | 11 | 190 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 211 | 0.0050238 | 617 | 0.01469 | 1.362 | A04 | MICL0.01119026/DNC
Build-In Floor | Mini Canal | MICL.01119026/DON | 11 | 190 | 26 | 26 | 520 | 520 | 520 | 0.012381 | 202 | 0.0048095 | 592 | 0.014095 | 1.362 | A04 | MICL0.01119026/DON
Build-In Floor | Mini Canal | MICL.01119026/DOV | 11 | 190 | 26 | 26 | 520 | 520 | 520 | 0.012381 | 202 | 0.0048095 | 592 | 0.014095 | 1.362 | A04 | MICL0.01119026/DOV
Build-In Floor | Mini Canal | MICL.01119026/PNC | 11 | 190 | 26 | 26 | 475 | 475 | 475 | 0.01131 | 185 | 0.0044048 | 541 | 0.012881 | 1.362 | A04 | MICL0.01119026/PNC
Build-In Floor | Mini Canal | MICL.01119026/RBL | 11 | 190 | 26 | 26 | 559 | 559 | 559 | 0.01331 | 217 | 0.0051667 | 637 | 0.015167 | 1.362 | A04 | MICL0.01119026/RBL
Build-In Floor | Mini Canal | MICL.01119026/RBN | 11 | 190 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 211 | 0.0050238 | 617 | 0.01469 | 1.362 | A04 | MICL0.01119026/RBN
Build-In Floor | Mini Canal | MICL.01119026/RBR | 11 | 190 | 26 | 26 | 559 | 559 | 559 | 0.01331 | 217 | 0.0051667 | 637 | 0.015167 | 1.362 | A04 | MICL0.01119026/RBR
Build-In Floor | Mini Canal | MICL.01119026/RBV | 11 | 190 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 211 | 0.0050238 | 617 | 0.01469 | 1.362 | A04 | MICL0.01119026/RBV
Build-In Floor | Mini Canal | MICL.01119026/RDB | 11 | 190 | 26 | 26 | 559 | 559 | 559 | 0.01331 | 217 | 0.0051667 | 637 | 0.015167 | 1.362 | A04 | MICL0.01119026/RDB
Build-In Floor | Mini Canal | MICL.01119026/RMN | 11 | 190 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 211 | 0.0050238 | 617 | 0.01469 | 1.362 | A04 | MICL0.01119026/RMN
Build-In Floor | Mini Canal | MICL.01119026/RMV | 11 | 190 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 211 | 0.0050238 | 617 | 0.01469 | 1.362 | A04 | MICL0.01119026/RMV
Build-In Floor | Mini Canal | MICL.01119026/RNA | 11 | 190 | 26 | 26 | 559 | 559 | 559 | 0.01331 | 217 | 0.0051667 | 637 | 0.015167 | 1.362 | A04 | MICL0.01119026/RNA
Build-In Floor | Mini Canal | MICL.01119026/RON | 11 | 190 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 211 | 0.0050238 | 617 | 0.01469 | 1.362 | A04 | MICL0.01119026/RON
Build-In Floor | Mini Canal | MICL.01119026/ROV | 11 | 190 | 26 | 26 | 542 | 542 | 542 | 0.012905 | 211 | 0.0050238 | 617 | 0.01469 | 1.362 | A04 | MICL0.01119026/ROV
Build-In Floor | Mini Canal | MICL.01119026/RSS | 11 | 190 | 26 | 26 | 537 | 537 | 537 | 0.012786 | 209 | 0.0049762 | 612 | 0.014571 | 1.362 | A04 | MICL0.01119026/RSS
Build-In Floor | Mini Canal | MICL.01119026/SBL | 11 | 190 | 26 | 26 | 559 | 559 | 559 | 0.01331 | 217 | 0.0051667 | 637 | 0.015167 | 1.362 | A04 | MICL0.01119026/SBL
Build-In Floor | Mini Canal | MICL.01119026/SBR | 11 | 190 | 26 | 26 | 559 | 559 | 559 | 0.01331 | 217 | 0.0051667 | 637 | 0.015167 | 1.362 | A04 | MICL0.01119026/SBR
Build-In Floor | Mini Canal | MICL.01119026/SDB | 11 | 190 | 26 | 26 | 559 | 559 | 559 | 0.01331 | 217 | 0.0051667 | 637 | 0.015167 | 1.362 | A04 | MICL0.01119026/SDB
Build-In Floor | Mini Canal | MICL.01119026/SNA | 11 | 190 | 26 | 26 | 559 | 559 | 559 | 0.01331 | 217 | 0.0051667 | 637 | 0.015167 | 1.362 | A04 | MICL0.01119026/SNA
Build-In Floor | Mini Canal | MICL.01119026/SNC | 11 | 190 | 26 | 26 | 559 | 559 | 559 | 0.01331 | 217 | 0.0051667 | 637 | 0.015167 | 1.362 | A04 | MICL0.01119026/SNC
Build-In Floor | Mini Canal | MICL.01119034/ANA | 11 | 190 | 34 | 34 | 545 | 545 | 545 | 0.012976 | 212 | 0.0050476 | 621 | 0.014786 | 1.362 | A04 | MICL0.01119034/ANA
Build-In Floor | Mini Canal | MICL.01119034/DBL | 11 | 190 | 34 | 34 | 704 | 704 | 704 | 0.016762 | 274 | 0.0065238 | 802 | 0.019095 | 1.362 | A04 | MICL0.01119034/DBL
Build-In Floor | Mini Canal | MICL.01119034/DBN | 11 | 190 | 34 | 34 | 675 | 675 | 675 | 0.016071 | 263 | 0.0062619 | 769 | 0.01831 | 1.362 | A04 | MICL0.01119034/DBN
Build-In Floor | Mini Canal | MICL.01119034/DBR | 11 | 190 | 34 | 34 | 704 | 704 | 704 | 0.016762 | 274 | 0.0065238 | 802 | 0.019095 | 1.362 | A04 | MICL0.01119034/DBR
Build-In Floor | Mini Canal | MICL.01119034/DBV | 11 | 190 | 34 | 34 | 675 | 675 | 675 | 0.016071 | 263 | 0.0062619 | 769 | 0.01831 | 1.362 | A04 | MICL0.01119034/DBV
Build-In Floor | Mini Canal | MICL.01119034/DDB | 11 | 190 | 34 | 34 | 704 | 704 | 704 | 0.016762 | 274 | 0.0065238 | 802 | 0.019095 | 1.362 | A04 | MICL0.01119034/DDB
Build-In Floor | Mini Canal | MICL.01119034/DMN | 11 | 190 | 34 | 34 | 675 | 675 | 675 | 0.016071 | 263 | 0.0062619 | 769 | 0.01831 | 1.362 | A04 | MICL0.01119034/DMN
Build-In Floor | Mini Canal | MICL.01119034/DMV | 11 | 190 | 34 | 34 | 675 | 675 | 675 | 0.016071 | 263 | 0.0062619 | 769 | 0.01831 | 1.362 | A04 | MICL0.01119034/DMV
Build-In Floor | Mini Canal | MICL.01119034/DNA | 11 | 190 | 34 | 34 | 704 | 704 | 704 | 0.016762 | 274 | 0.0065238 | 802 | 0.019095 | 1.362 | A04 | MICL0.01119034/DNA
Build-In Floor | Mini Canal | MICL.01119034/DNC | 11 | 190 | 34 | 34 | 704 | 704 | 704 | 0.016762 | 274 | 0.0065238 | 802 | 0.019095 | 1.362 | A04 | MICL0.01119034/DNC
Build-In Floor | Mini Canal | MICL.01119034/DON | 11 | 190 | 34 | 34 | 675 | 675 | 675 | 0.016071 | 263 | 0.0062619 | 769 | 0.01831 | 1.362 | A04 | MICL0.01119034/DON
Build-In Floor | Mini Canal | MICL.01119034/DOV | 11 | 190 | 34 | 34 | 675 | 675 | 675 | 0.016071 | 263 | 0.0062619 | 769 | 0.01831 | 1.362 | A04 | MICL0.01119034/DOV
Build-In Floor | Mini Canal | MICL.01119034/PNC | 11 | 190 | 34 | 34 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01119034/PNC
Build-In Floor | Mini Canal | MICL.01119034/RBL | 11 | 190 | 34 | 34 | 726 | 726 | 726 | 0.017286 | 282 | 0.0067143 | 827 | 0.01969 | 1.362 | A04 | MICL0.01119034/RBL
Build-In Floor | Mini Canal | MICL.01119034/RBN | 11 | 190 | 34 | 34 | 704 | 704 | 704 | 0.016762 | 274 | 0.0065238 | 802 | 0.019095 | 1.362 | A04 | MICL0.01119034/RBN
Build-In Floor | Mini Canal | MICL.01119034/RBR | 11 | 190 | 34 | 34 | 726 | 726 | 726 | 0.017286 | 282 | 0.0067143 | 827 | 0.01969 | 1.362 | A04 | MICL0.01119034/RBR
Build-In Floor | Mini Canal | MICL.01119034/RBV | 11 | 190 | 34 | 34 | 704 | 704 | 704 | 0.016762 | 274 | 0.0065238 | 802 | 0.019095 | 1.362 | A04 | MICL0.01119034/RBV
Build-In Floor | Mini Canal | MICL.01119034/RDB | 11 | 190 | 34 | 34 | 726 | 726 | 726 | 0.017286 | 282 | 0.0067143 | 827 | 0.01969 | 1.362 | A04 | MICL0.01119034/RDB
Build-In Floor | Mini Canal | MICL.01119034/RMN | 11 | 190 | 34 | 34 | 704 | 704 | 704 | 0.016762 | 274 | 0.0065238 | 802 | 0.019095 | 1.362 | A04 | MICL0.01119034/RMN
Build-In Floor | Mini Canal | MICL.01119034/RMV | 11 | 190 | 34 | 34 | 704 | 704 | 704 | 0.016762 | 274 | 0.0065238 | 802 | 0.019095 | 1.362 | A04 | MICL0.01119034/RMV
Build-In Floor | Mini Canal | MICL.01119034/RNA | 11 | 190 | 34 | 34 | 726 | 726 | 726 | 0.017286 | 282 | 0.0067143 | 827 | 0.01969 | 1.362 | A04 | MICL0.01119034/RNA
Build-In Floor | Mini Canal | MICL.01119034/RON | 11 | 190 | 34 | 34 | 704 | 704 | 704 | 0.016762 | 274 | 0.0065238 | 802 | 0.019095 | 1.362 | A04 | MICL0.01119034/RON
Build-In Floor | Mini Canal | MICL.01119034/ROV | 11 | 190 | 34 | 34 | 704 | 704 | 704 | 0.016762 | 274 | 0.0065238 | 802 | 0.019095 | 1.362 | A04 | MICL0.01119034/ROV
Build-In Floor | Mini Canal | MICL.01119034/RSS | 11 | 190 | 34 | 34 | 697 | 697 | 697 | 0.016595 | 271 | 0.0064524 | 794 | 0.018905 | 1.362 | A04 | MICL0.01119034/RSS
Build-In Floor | Mini Canal | MICL.01119034/SBL | 11 | 190 | 34 | 34 | 726 | 726 | 726 | 0.017286 | 282 | 0.0067143 | 827 | 0.01969 | 1.362 | A04 | MICL0.01119034/SBL
Build-In Floor | Mini Canal | MICL.01119034/SBR | 11 | 190 | 34 | 34 | 726 | 726 | 726 | 0.017286 | 282 | 0.0067143 | 827 | 0.01969 | 1.362 | A04 | MICL0.01119034/SBR
Build-In Floor | Mini Canal | MICL.01119034/SDB | 11 | 190 | 34 | 34 | 726 | 726 | 726 | 0.017286 | 282 | 0.0067143 | 827 | 0.01969 | 1.362 | A04 | MICL0.01119034/SDB
Build-In Floor | Mini Canal | MICL.01119034/SNA | 11 | 190 | 34 | 34 | 726 | 726 | 726 | 0.017286 | 282 | 0.0067143 | 827 | 0.01969 | 1.362 | A04 | MICL0.01119034/SNA
Build-In Floor | Mini Canal | MICL.01119034/SNC | 11 | 190 | 34 | 34 | 726 | 726 | 726 | 0.017286 | 282 | 0.0067143 | 827 | 0.01969 | 1.362 | A04 | MICL0.01119034/SNC
Build-In Floor | Mini Canal | MICL.01119042/ANA | 11 | 190 | 42 | 42 | 766 | 766 | 766 | 0.018238 | 298 | 0.0070952 | 872 | 0.020762 | 1.362 | A04 | MICL0.01119042/ANA
Build-In Floor | Mini Canal | MICL.01119042/DBL | 11 | 190 | 42 | 42 | 990 | 990 | 990 | 0.023571 | 385 | 0.0091667 | 1128 | 0.026857 | 1.362 | A04 | MICL0.01119042/DBL
Build-In Floor | Mini Canal | MICL.01119042/DBN | 11 | 190 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01119042/DBN
Build-In Floor | Mini Canal | MICL.01119042/DBR | 11 | 190 | 42 | 42 | 990 | 990 | 990 | 0.023571 | 385 | 0.0091667 | 1128 | 0.026857 | 1.362 | A04 | MICL0.01119042/DBR
Build-In Floor | Mini Canal | MICL.01119042/DBV | 11 | 190 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01119042/DBV
Build-In Floor | Mini Canal | MICL.01119042/DDB | 11 | 190 | 42 | 42 | 990 | 990 | 990 | 0.023571 | 385 | 0.0091667 | 1128 | 0.026857 | 1.362 | A04 | MICL0.01119042/DDB
Build-In Floor | Mini Canal | MICL.01119042/DMN | 11 | 190 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01119042/DMN
Build-In Floor | Mini Canal | MICL.01119042/DMV | 11 | 190 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01119042/DMV
Build-In Floor | Mini Canal | MICL.01119042/DNA | 11 | 190 | 42 | 42 | 990 | 990 | 990 | 0.023571 | 385 | 0.0091667 | 1128 | 0.026857 | 1.362 | A04 | MICL0.01119042/DNA
Build-In Floor | Mini Canal | MICL.01119042/DNC | 11 | 190 | 42 | 42 | 990 | 990 | 990 | 0.023571 | 385 | 0.0091667 | 1128 | 0.026857 | 1.362 | A04 | MICL0.01119042/DNC
Build-In Floor | Mini Canal | MICL.01119042/DON | 11 | 190 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01119042/DON
Build-In Floor | Mini Canal | MICL.01119042/DOV | 11 | 190 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01119042/DOV
Build-In Floor | Mini Canal | MICL.01119042/PNC | 11 | 190 | 42 | 42 | 868 | 868 | 868 | 0.020667 | 338 | 0.0080476 | 989 | 0.023548 | 1.362 | A04 | MICL0.01119042/PNC
Build-In Floor | Mini Canal | MICL.01119042/RBL | 11 | 190 | 42 | 42 | 1021 | 1021 | 1021 | 0.02431 | 397 | 0.0094524 | 1163 | 0.02769 | 1.362 | A04 | MICL0.01119042/RBL
Build-In Floor | Mini Canal | MICL.01119042/RBN | 11 | 190 | 42 | 42 | 990 | 990 | 990 | 0.023571 | 385 | 0.0091667 | 1128 | 0.026857 | 1.362 | A04 | MICL0.01119042/RBN
Build-In Floor | Mini Canal | MICL.01119042/RBR | 11 | 190 | 42 | 42 | 1021 | 1021 | 1021 | 0.02431 | 397 | 0.0094524 | 1163 | 0.02769 | 1.362 | A04 | MICL0.01119042/RBR
Build-In Floor | Mini Canal | MICL.01119042/RBV | 11 | 190 | 42 | 42 | 990 | 990 | 990 | 0.023571 | 385 | 0.0091667 | 1128 | 0.026857 | 1.362 | A04 | MICL0.01119042/RBV
Build-In Floor | Mini Canal | MICL.01119042/RDB | 11 | 190 | 42 | 42 | 1021 | 1021 | 1021 | 0.02431 | 397 | 0.0094524 | 1163 | 0.02769 | 1.362 | A04 | MICL0.01119042/RDB
Build-In Floor | Mini Canal | MICL.01119042/RMN | 11 | 190 | 42 | 42 | 990 | 990 | 990 | 0.023571 | 385 | 0.0091667 | 1128 | 0.026857 | 1.362 | A04 | MICL0.01119042/RMN
Build-In Floor | Mini Canal | MICL.01119042/RMV | 11 | 190 | 42 | 42 | 990 | 990 | 990 | 0.023571 | 385 | 0.0091667 | 1128 | 0.026857 | 1.362 | A04 | MICL0.01119042/RMV
Build-In Floor | Mini Canal | MICL.01119042/RNA | 11 | 190 | 42 | 42 | 1021 | 1021 | 1021 | 0.02431 | 397 | 0.0094524 | 1163 | 0.02769 | 1.362 | A04 | MICL0.01119042/RNA
Build-In Floor | Mini Canal | MICL.01119042/RON | 11 | 190 | 42 | 42 | 990 | 990 | 990 | 0.023571 | 385 | 0.0091667 | 1128 | 0.026857 | 1.362 | A04 | MICL0.01119042/RON
Build-In Floor | Mini Canal | MICL.01119042/ROV | 11 | 190 | 42 | 42 | 990 | 990 | 990 | 0.023571 | 385 | 0.0091667 | 1128 | 0.026857 | 1.362 | A04 | MICL0.01119042/ROV
Build-In Floor | Mini Canal | MICL.01119042/RSS | 11 | 190 | 42 | 42 | 980 | 980 | 980 | 0.023333 | 381 | 0.0090714 | 1116 | 0.026571 | 1.362 | A04 | MICL0.01119042/RSS
Build-In Floor | Mini Canal | MICL.01119042/SBL | 11 | 190 | 42 | 42 | 1021 | 1021 | 1021 | 0.02431 | 397 | 0.0094524 | 1163 | 0.02769 | 1.362 | A04 | MICL0.01119042/SBL
Build-In Floor | Mini Canal | MICL.01119042/SBR | 11 | 190 | 42 | 42 | 1021 | 1021 | 1021 | 0.02431 | 397 | 0.0094524 | 1163 | 0.02769 | 1.362 | A04 | MICL0.01119042/SBR
Build-In Floor | Mini Canal | MICL.01119042/SDB | 11 | 190 | 42 | 42 | 1021 | 1021 | 1021 | 0.02431 | 397 | 0.0094524 | 1163 | 0.02769 | 1.362 | A04 | MICL0.01119042/SDB
Build-In Floor | Mini Canal | MICL.01119042/SNA | 11 | 190 | 42 | 42 | 1021 | 1021 | 1021 | 0.02431 | 397 | 0.0094524 | 1163 | 0.02769 | 1.362 | A04 | MICL0.01119042/SNA
Build-In Floor | Mini Canal | MICL.01119042/SNC | 11 | 190 | 42 | 42 | 1021 | 1021 | 1021 | 0.02431 | 397 | 0.0094524 | 1163 | 0.02769 | 1.362 | A04 | MICL0.01119042/SNC
Build-In Floor | Mini Canal | MICL.01121014/ANA | 11 | 210 | 14 | 14 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.01121014/ANA
Build-In Floor | Mini Canal | MICL.01121014/DBL | 11 | 210 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.01121014/DBL
Build-In Floor | Mini Canal | MICL.01121014/DBN | 11 | 210 | 14 | 14 | 365 | 365 | 365 | 0.0086905 | 142 | 0.003381 | 416 | 0.0099048 | 1.362 | A04 | MICL0.01121014/DBN
Build-In Floor | Mini Canal | MICL.01121014/DBR | 11 | 210 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.01121014/DBR
Build-In Floor | Mini Canal | MICL.01121014/DBV | 11 | 210 | 14 | 14 | 365 | 365 | 365 | 0.0086905 | 142 | 0.003381 | 416 | 0.0099048 | 1.362 | A04 | MICL0.01121014/DBV
Build-In Floor | Mini Canal | MICL.01121014/DDB | 11 | 210 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.01121014/DDB
Build-In Floor | Mini Canal | MICL.01121014/DMN | 11 | 210 | 14 | 14 | 365 | 365 | 365 | 0.0086905 | 142 | 0.003381 | 416 | 0.0099048 | 1.362 | A04 | MICL0.01121014/DMN
Build-In Floor | Mini Canal | MICL.01121014/DMV | 11 | 210 | 14 | 14 | 365 | 365 | 365 | 0.0086905 | 142 | 0.003381 | 416 | 0.0099048 | 1.362 | A04 | MICL0.01121014/DMV
Build-In Floor | Mini Canal | MICL.01121014/DNA | 11 | 210 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.01121014/DNA
Build-In Floor | Mini Canal | MICL.01121014/DNC | 11 | 210 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.01121014/DNC
Build-In Floor | Mini Canal | MICL.01121014/DON | 11 | 210 | 14 | 14 | 365 | 365 | 365 | 0.0086905 | 142 | 0.003381 | 416 | 0.0099048 | 1.362 | A04 | MICL0.01121014/DON
Build-In Floor | Mini Canal | MICL.01121014/DOV | 11 | 210 | 14 | 14 | 365 | 365 | 365 | 0.0086905 | 142 | 0.003381 | 416 | 0.0099048 | 1.362 | A04 | MICL0.01121014/DOV
Build-In Floor | Mini Canal | MICL.01121014/RBL | 11 | 210 | 14 | 14 | 393 | 393 | 393 | 0.0093571 | 153 | 0.0036429 | 448 | 0.010667 | 1.362 | A04 | MICL0.01121014/RBL
Build-In Floor | Mini Canal | MICL.01121014/RBN | 11 | 210 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.01121014/RBN
Build-In Floor | Mini Canal | MICL.01121014/RBR | 11 | 210 | 14 | 14 | 393 | 393 | 393 | 0.0093571 | 153 | 0.0036429 | 448 | 0.010667 | 1.362 | A04 | MICL0.01121014/RBR
Build-In Floor | Mini Canal | MICL.01121014/RBV | 11 | 210 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.01121014/RBV
Build-In Floor | Mini Canal | MICL.01121014/RDB | 11 | 210 | 14 | 14 | 393 | 393 | 393 | 0.0093571 | 153 | 0.0036429 | 448 | 0.010667 | 1.362 | A04 | MICL0.01121014/RDB
Build-In Floor | Mini Canal | MICL.01121014/RMN | 11 | 210 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.01121014/RMN
Build-In Floor | Mini Canal | MICL.01121014/RMV | 11 | 210 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.01121014/RMV
Build-In Floor | Mini Canal | MICL.01121014/RNA | 11 | 210 | 14 | 14 | 393 | 393 | 393 | 0.0093571 | 153 | 0.0036429 | 448 | 0.010667 | 1.362 | A04 | MICL0.01121014/RNA
Build-In Floor | Mini Canal | MICL.01121014/RON | 11 | 210 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.01121014/RON
Build-In Floor | Mini Canal | MICL.01121014/ROV | 11 | 210 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.01121014/ROV
Build-In Floor | Mini Canal | MICL.01121014/RSS | 11 | 210 | 14 | 14 | 377 | 377 | 377 | 0.0089762 | 147 | 0.0035 | 429 | 0.010214 | 1.362 | A04 | MICL0.01121014/RSS
Build-In Floor | Mini Canal | MICL.01121014/SBL | 11 | 210 | 14 | 14 | 393 | 393 | 393 | 0.0093571 | 153 | 0.0036429 | 448 | 0.010667 | 1.362 | A04 | MICL0.01121014/SBL
Build-In Floor | Mini Canal | MICL.01121014/SBR | 11 | 210 | 14 | 14 | 393 | 393 | 393 | 0.0093571 | 153 | 0.0036429 | 448 | 0.010667 | 1.362 | A04 | MICL0.01121014/SBR
Build-In Floor | Mini Canal | MICL.01121014/SDB | 11 | 210 | 14 | 14 | 393 | 393 | 393 | 0.0093571 | 153 | 0.0036429 | 448 | 0.010667 | 1.362 | A04 | MICL0.01121014/SDB
Build-In Floor | Mini Canal | MICL.01121014/SNA | 11 | 210 | 14 | 14 | 393 | 393 | 393 | 0.0093571 | 153 | 0.0036429 | 448 | 0.010667 | 1.362 | A04 | MICL0.01121014/SNA
Build-In Floor | Mini Canal | MICL.01121014/SNC | 11 | 210 | 14 | 14 | 393 | 393 | 393 | 0.0093571 | 153 | 0.0036429 | 448 | 0.010667 | 1.362 | A04 | MICL0.01121014/SNC
Build-In Floor | Mini Canal | MICL.01121018/ANA | 11 | 210 | 18 | 18 | 350 | 350 | 350 | 0.0083333 | 136 | 0.0032381 | 399 | 0.0095 | 1.362 | A04 | MICL0.01121018/ANA
Build-In Floor | Mini Canal | MICL.01121018/DBL | 11 | 210 | 18 | 18 | 452 | 452 | 452 | 0.010762 | 176 | 0.0041905 | 515 | 0.012262 | 1.362 | A04 | MICL0.01121018/DBL
Build-In Floor | Mini Canal | MICL.01121018/DBN | 11 | 210 | 18 | 18 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01121018/DBN
Build-In Floor | Mini Canal | MICL.01121018/DBR | 11 | 210 | 18 | 18 | 452 | 452 | 452 | 0.010762 | 176 | 0.0041905 | 515 | 0.012262 | 1.362 | A04 | MICL0.01121018/DBR
Build-In Floor | Mini Canal | MICL.01121018/DBV | 11 | 210 | 18 | 18 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01121018/DBV
Build-In Floor | Mini Canal | MICL.01121018/DDB | 11 | 210 | 18 | 18 | 452 | 452 | 452 | 0.010762 | 176 | 0.0041905 | 515 | 0.012262 | 1.362 | A04 | MICL0.01121018/DDB
Build-In Floor | Mini Canal | MICL.01121018/DMN | 11 | 210 | 18 | 18 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01121018/DMN
Build-In Floor | Mini Canal | MICL.01121018/DMV | 11 | 210 | 18 | 18 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01121018/DMV
Build-In Floor | Mini Canal | MICL.01121018/DNA | 11 | 210 | 18 | 18 | 452 | 452 | 452 | 0.010762 | 176 | 0.0041905 | 515 | 0.012262 | 1.362 | A04 | MICL0.01121018/DNA
Build-In Floor | Mini Canal | MICL.01121018/DNC | 11 | 210 | 18 | 18 | 452 | 452 | 452 | 0.010762 | 176 | 0.0041905 | 515 | 0.012262 | 1.362 | A04 | MICL0.01121018/DNC
Build-In Floor | Mini Canal | MICL.01121018/DON | 11 | 210 | 18 | 18 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01121018/DON
Build-In Floor | Mini Canal | MICL.01121018/DOV | 11 | 210 | 18 | 18 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01121018/DOV
Build-In Floor | Mini Canal | MICL.01121018/RBL | 11 | 210 | 18 | 18 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01121018/RBL
Build-In Floor | Mini Canal | MICL.01121018/RBN | 11 | 210 | 18 | 18 | 452 | 452 | 452 | 0.010762 | 176 | 0.0041905 | 515 | 0.012262 | 1.362 | A04 | MICL0.01121018/RBN
Build-In Floor | Mini Canal | MICL.01121018/RBR | 11 | 210 | 18 | 18 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01121018/RBR
Build-In Floor | Mini Canal | MICL.01121018/RBV | 11 | 210 | 18 | 18 | 452 | 452 | 452 | 0.010762 | 176 | 0.0041905 | 515 | 0.012262 | 1.362 | A04 | MICL0.01121018/RBV
Build-In Floor | Mini Canal | MICL.01121018/RDB | 11 | 210 | 18 | 18 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01121018/RDB
Build-In Floor | Mini Canal | MICL.01121018/RMN | 11 | 210 | 18 | 18 | 452 | 452 | 452 | 0.010762 | 176 | 0.0041905 | 515 | 0.012262 | 1.362 | A04 | MICL0.01121018/RMN
Build-In Floor | Mini Canal | MICL.01121018/RMV | 11 | 210 | 18 | 18 | 452 | 452 | 452 | 0.010762 | 176 | 0.0041905 | 515 | 0.012262 | 1.362 | A04 | MICL0.01121018/RMV
Build-In Floor | Mini Canal | MICL.01121018/RNA | 11 | 210 | 18 | 18 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01121018/RNA
Build-In Floor | Mini Canal | MICL.01121018/RON | 11 | 210 | 18 | 18 | 452 | 452 | 452 | 0.010762 | 176 | 0.0041905 | 515 | 0.012262 | 1.362 | A04 | MICL0.01121018/RON
Build-In Floor | Mini Canal | MICL.01121018/ROV | 11 | 210 | 18 | 18 | 452 | 452 | 452 | 0.010762 | 176 | 0.0041905 | 515 | 0.012262 | 1.362 | A04 | MICL0.01121018/ROV
Build-In Floor | Mini Canal | MICL.01121018/RSS | 11 | 210 | 18 | 18 | 447 | 447 | 447 | 0.010643 | 174 | 0.0041429 | 509 | 0.012119 | 1.362 | A04 | MICL0.01121018/RSS
Build-In Floor | Mini Canal | MICL.01121018/SBL | 11 | 210 | 18 | 18 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01121018/SBL
Build-In Floor | Mini Canal | MICL.01121018/SBR | 11 | 210 | 18 | 18 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01121018/SBR
Build-In Floor | Mini Canal | MICL.01121018/SDB | 11 | 210 | 18 | 18 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01121018/SDB
Build-In Floor | Mini Canal | MICL.01121018/SNA | 11 | 210 | 18 | 18 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01121018/SNA
Build-In Floor | Mini Canal | MICL.01121018/SNC | 11 | 210 | 18 | 18 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01121018/SNC
Build-In Floor | Mini Canal | MICL.01121026/ANA | 11 | 210 | 26 | 26 | 472 | 472 | 472 | 0.011238 | 184 | 0.004381 | 538 | 0.01281 | 1.362 | A04 | MICL0.01121026/ANA
Build-In Floor | Mini Canal | MICL.01121026/DBL | 11 | 210 | 26 | 26 | 610 | 610 | 610 | 0.014524 | 237 | 0.0056429 | 695 | 0.016548 | 1.362 | A04 | MICL0.01121026/DBL
Build-In Floor | Mini Canal | MICL.01121026/DBN | 11 | 210 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01121026/DBN
Build-In Floor | Mini Canal | MICL.01121026/DBR | 11 | 210 | 26 | 26 | 610 | 610 | 610 | 0.014524 | 237 | 0.0056429 | 695 | 0.016548 | 1.362 | A04 | MICL0.01121026/DBR
Build-In Floor | Mini Canal | MICL.01121026/DBV | 11 | 210 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01121026/DBV
Build-In Floor | Mini Canal | MICL.01121026/DDB | 11 | 210 | 26 | 26 | 610 | 610 | 610 | 0.014524 | 237 | 0.0056429 | 695 | 0.016548 | 1.362 | A04 | MICL0.01121026/DDB
Build-In Floor | Mini Canal | MICL.01121026/DMN | 11 | 210 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01121026/DMN
Build-In Floor | Mini Canal | MICL.01121026/DMV | 11 | 210 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01121026/DMV
Build-In Floor | Mini Canal | MICL.01121026/DNA | 11 | 210 | 26 | 26 | 610 | 610 | 610 | 0.014524 | 237 | 0.0056429 | 695 | 0.016548 | 1.362 | A04 | MICL0.01121026/DNA
Build-In Floor | Mini Canal | MICL.01121026/DNC | 11 | 210 | 26 | 26 | 610 | 610 | 610 | 0.014524 | 237 | 0.0056429 | 695 | 0.016548 | 1.362 | A04 | MICL0.01121026/DNC
Build-In Floor | Mini Canal | MICL.01121026/DON | 11 | 210 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01121026/DON
Build-In Floor | Mini Canal | MICL.01121026/DOV | 11 | 210 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01121026/DOV
Build-In Floor | Mini Canal | MICL.01121026/PNC | 11 | 210 | 26 | 26 | 535 | 535 | 535 | 0.012738 | 208 | 0.0049524 | 609 | 0.0145 | 1.362 | A04 | MICL0.01121026/PNC
Build-In Floor | Mini Canal | MICL.01121026/RBL | 11 | 210 | 26 | 26 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.01121026/RBL
Build-In Floor | Mini Canal | MICL.01121026/RBN | 11 | 210 | 26 | 26 | 610 | 610 | 610 | 0.014524 | 237 | 0.0056429 | 695 | 0.016548 | 1.362 | A04 | MICL0.01121026/RBN
Build-In Floor | Mini Canal | MICL.01121026/RBR | 11 | 210 | 26 | 26 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.01121026/RBR
Build-In Floor | Mini Canal | MICL.01121026/RBV | 11 | 210 | 26 | 26 | 610 | 610 | 610 | 0.014524 | 237 | 0.0056429 | 695 | 0.016548 | 1.362 | A04 | MICL0.01121026/RBV
Build-In Floor | Mini Canal | MICL.01121026/RDB | 11 | 210 | 26 | 26 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.01121026/RDB
Build-In Floor | Mini Canal | MICL.01121026/RMN | 11 | 210 | 26 | 26 | 610 | 610 | 610 | 0.014524 | 237 | 0.0056429 | 695 | 0.016548 | 1.362 | A04 | MICL0.01121026/RMN
Build-In Floor | Mini Canal | MICL.01121026/RMV | 11 | 210 | 26 | 26 | 610 | 610 | 610 | 0.014524 | 237 | 0.0056429 | 695 | 0.016548 | 1.362 | A04 | MICL0.01121026/RMV
Build-In Floor | Mini Canal | MICL.01121026/RNA | 11 | 210 | 26 | 26 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.01121026/RNA
Build-In Floor | Mini Canal | MICL.01121026/RON | 11 | 210 | 26 | 26 | 610 | 610 | 610 | 0.014524 | 237 | 0.0056429 | 695 | 0.016548 | 1.362 | A04 | MICL0.01121026/RON
Build-In Floor | Mini Canal | MICL.01121026/ROV | 11 | 210 | 26 | 26 | 610 | 610 | 610 | 0.014524 | 237 | 0.0056429 | 695 | 0.016548 | 1.362 | A04 | MICL0.01121026/ROV
Build-In Floor | Mini Canal | MICL.01121026/RSS | 11 | 210 | 26 | 26 | 604 | 604 | 604 | 0.014381 | 235 | 0.0055952 | 688 | 0.016381 | 1.362 | A04 | MICL0.01121026/RSS
Build-In Floor | Mini Canal | MICL.01121026/SBL | 11 | 210 | 26 | 26 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.01121026/SBL
Build-In Floor | Mini Canal | MICL.01121026/SBR | 11 | 210 | 26 | 26 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.01121026/SBR
Build-In Floor | Mini Canal | MICL.01121026/SDB | 11 | 210 | 26 | 26 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.01121026/SDB
Build-In Floor | Mini Canal | MICL.01121026/SNA | 11 | 210 | 26 | 26 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.01121026/SNA
Build-In Floor | Mini Canal | MICL.01121026/SNC | 11 | 210 | 26 | 26 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.01121026/SNC
Build-In Floor | Mini Canal | MICL.01121034/ANA | 11 | 210 | 34 | 34 | 613 | 613 | 613 | 0.014595 | 238 | 0.0056667 | 698 | 0.016619 | 1.362 | A04 | MICL0.01121034/ANA
Build-In Floor | Mini Canal | MICL.01121034/DBL | 11 | 210 | 34 | 34 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01121034/DBL
Build-In Floor | Mini Canal | MICL.01121034/DBN | 11 | 210 | 34 | 34 | 760 | 760 | 760 | 0.018095 | 296 | 0.0070476 | 866 | 0.020619 | 1.362 | A04 | MICL0.01121034/DBN
Build-In Floor | Mini Canal | MICL.01121034/DBR | 11 | 210 | 34 | 34 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01121034/DBR
Build-In Floor | Mini Canal | MICL.01121034/DBV | 11 | 210 | 34 | 34 | 760 | 760 | 760 | 0.018095 | 296 | 0.0070476 | 866 | 0.020619 | 1.362 | A04 | MICL0.01121034/DBV
Build-In Floor | Mini Canal | MICL.01121034/DDB | 11 | 210 | 34 | 34 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01121034/DDB
Build-In Floor | Mini Canal | MICL.01121034/DMN | 11 | 210 | 34 | 34 | 760 | 760 | 760 | 0.018095 | 296 | 0.0070476 | 866 | 0.020619 | 1.362 | A04 | MICL0.01121034/DMN
Build-In Floor | Mini Canal | MICL.01121034/DMV | 11 | 210 | 34 | 34 | 760 | 760 | 760 | 0.018095 | 296 | 0.0070476 | 866 | 0.020619 | 1.362 | A04 | MICL0.01121034/DMV
Build-In Floor | Mini Canal | MICL.01121034/DNA | 11 | 210 | 34 | 34 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01121034/DNA
Build-In Floor | Mini Canal | MICL.01121034/DNC | 11 | 210 | 34 | 34 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01121034/DNC
Build-In Floor | Mini Canal | MICL.01121034/DON | 11 | 210 | 34 | 34 | 760 | 760 | 760 | 0.018095 | 296 | 0.0070476 | 866 | 0.020619 | 1.362 | A04 | MICL0.01121034/DON
Build-In Floor | Mini Canal | MICL.01121034/DOV | 11 | 210 | 34 | 34 | 760 | 760 | 760 | 0.018095 | 296 | 0.0070476 | 866 | 0.020619 | 1.362 | A04 | MICL0.01121034/DOV
Build-In Floor | Mini Canal | MICL.01121034/PNC | 11 | 210 | 34 | 34 | 694 | 694 | 694 | 0.016524 | 270 | 0.0064286 | 790 | 0.01881 | 1.362 | A04 | MICL0.01121034/PNC
Build-In Floor | Mini Canal | MICL.01121034/RBL | 11 | 210 | 34 | 34 | 817 | 817 | 817 | 0.019452 | 318 | 0.0075714 | 931 | 0.022167 | 1.362 | A04 | MICL0.01121034/RBL
Build-In Floor | Mini Canal | MICL.01121034/RBN | 11 | 210 | 34 | 34 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01121034/RBN
Build-In Floor | Mini Canal | MICL.01121034/RBR | 11 | 210 | 34 | 34 | 817 | 817 | 817 | 0.019452 | 318 | 0.0075714 | 931 | 0.022167 | 1.362 | A04 | MICL0.01121034/RBR
Build-In Floor | Mini Canal | MICL.01121034/RBV | 11 | 210 | 34 | 34 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01121034/RBV
Build-In Floor | Mini Canal | MICL.01121034/RDB | 11 | 210 | 34 | 34 | 817 | 817 | 817 | 0.019452 | 318 | 0.0075714 | 931 | 0.022167 | 1.362 | A04 | MICL0.01121034/RDB
Build-In Floor | Mini Canal | MICL.01121034/RMN | 11 | 210 | 34 | 34 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01121034/RMN
Build-In Floor | Mini Canal | MICL.01121034/RMV | 11 | 210 | 34 | 34 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01121034/RMV
Build-In Floor | Mini Canal | MICL.01121034/RNA | 11 | 210 | 34 | 34 | 817 | 817 | 817 | 0.019452 | 318 | 0.0075714 | 931 | 0.022167 | 1.362 | A04 | MICL0.01121034/RNA
Build-In Floor | Mini Canal | MICL.01121034/RON | 11 | 210 | 34 | 34 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01121034/RON
Build-In Floor | Mini Canal | MICL.01121034/ROV | 11 | 210 | 34 | 34 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01121034/ROV
Build-In Floor | Mini Canal | MICL.01121034/RSS | 11 | 210 | 34 | 34 | 784 | 784 | 784 | 0.018667 | 305 | 0.0072619 | 893 | 0.021262 | 1.362 | A04 | MICL0.01121034/RSS
Build-In Floor | Mini Canal | MICL.01121034/SBL | 11 | 210 | 34 | 34 | 817 | 817 | 817 | 0.019452 | 318 | 0.0075714 | 931 | 0.022167 | 1.362 | A04 | MICL0.01121034/SBL
Build-In Floor | Mini Canal | MICL.01121034/SBR | 11 | 210 | 34 | 34 | 817 | 817 | 817 | 0.019452 | 318 | 0.0075714 | 931 | 0.022167 | 1.362 | A04 | MICL0.01121034/SBR
Build-In Floor | Mini Canal | MICL.01121034/SDB | 11 | 210 | 34 | 34 | 817 | 817 | 817 | 0.019452 | 318 | 0.0075714 | 931 | 0.022167 | 1.362 | A04 | MICL0.01121034/SDB
Build-In Floor | Mini Canal | MICL.01121034/SNA | 11 | 210 | 34 | 34 | 817 | 817 | 817 | 0.019452 | 318 | 0.0075714 | 931 | 0.022167 | 1.362 | A04 | MICL0.01121034/SNA
Build-In Floor | Mini Canal | MICL.01121034/SNC | 11 | 210 | 34 | 34 | 817 | 817 | 817 | 0.019452 | 318 | 0.0075714 | 931 | 0.022167 | 1.362 | A04 | MICL0.01121034/SNC
Build-In Floor | Mini Canal | MICL.01121042/ANA | 11 | 210 | 42 | 42 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.01121042/ANA
Build-In Floor | Mini Canal | MICL.01121042/DBL | 11 | 210 | 42 | 42 | 1114 | 1114 | 1114 | 0.026524 | 433 | 0.01031 | 1269 | 0.030214 | 1.362 | A04 | MICL0.01121042/DBL
Build-In Floor | Mini Canal | MICL.01121042/DBN | 11 | 210 | 42 | 42 | 1068 | 1068 | 1068 | 0.025429 | 415 | 0.009881 | 1216 | 0.028952 | 1.362 | A04 | MICL0.01121042/DBN
Build-In Floor | Mini Canal | MICL.01121042/DBR | 11 | 210 | 42 | 42 | 1114 | 1114 | 1114 | 0.026524 | 433 | 0.01031 | 1269 | 0.030214 | 1.362 | A04 | MICL0.01121042/DBR
Build-In Floor | Mini Canal | MICL.01121042/DBV | 11 | 210 | 42 | 42 | 1068 | 1068 | 1068 | 0.025429 | 415 | 0.009881 | 1216 | 0.028952 | 1.362 | A04 | MICL0.01121042/DBV
Build-In Floor | Mini Canal | MICL.01121042/DDB | 11 | 210 | 42 | 42 | 1114 | 1114 | 1114 | 0.026524 | 433 | 0.01031 | 1269 | 0.030214 | 1.362 | A04 | MICL0.01121042/DDB
Build-In Floor | Mini Canal | MICL.01121042/DMN | 11 | 210 | 42 | 42 | 1068 | 1068 | 1068 | 0.025429 | 415 | 0.009881 | 1216 | 0.028952 | 1.362 | A04 | MICL0.01121042/DMN
Build-In Floor | Mini Canal | MICL.01121042/DMV | 11 | 210 | 42 | 42 | 1068 | 1068 | 1068 | 0.025429 | 415 | 0.009881 | 1216 | 0.028952 | 1.362 | A04 | MICL0.01121042/DMV
Build-In Floor | Mini Canal | MICL.01121042/DNA | 11 | 210 | 42 | 42 | 1114 | 1114 | 1114 | 0.026524 | 433 | 0.01031 | 1269 | 0.030214 | 1.362 | A04 | MICL0.01121042/DNA
Build-In Floor | Mini Canal | MICL.01121042/DNC | 11 | 210 | 42 | 42 | 1114 | 1114 | 1114 | 0.026524 | 433 | 0.01031 | 1269 | 0.030214 | 1.362 | A04 | MICL0.01121042/DNC
Build-In Floor | Mini Canal | MICL.01121042/DON | 11 | 210 | 42 | 42 | 1068 | 1068 | 1068 | 0.025429 | 415 | 0.009881 | 1216 | 0.028952 | 1.362 | A04 | MICL0.01121042/DON
Build-In Floor | Mini Canal | MICL.01121042/DOV | 11 | 210 | 42 | 42 | 1068 | 1068 | 1068 | 0.025429 | 415 | 0.009881 | 1216 | 0.028952 | 1.362 | A04 | MICL0.01121042/DOV
Build-In Floor | Mini Canal | MICL.01121042/PNC | 11 | 210 | 42 | 42 | 976 | 976 | 976 | 0.023238 | 380 | 0.0090476 | 1112 | 0.026476 | 1.362 | A04 | MICL0.01121042/PNC
Build-In Floor | Mini Canal | MICL.01121042/RBL | 11 | 210 | 42 | 42 | 1148 | 1148 | 1148 | 0.027333 | 447 | 0.010643 | 1308 | 0.031143 | 1.362 | A04 | MICL0.01121042/RBL
Build-In Floor | Mini Canal | MICL.01121042/RBN | 11 | 210 | 42 | 42 | 1114 | 1114 | 1114 | 0.026524 | 433 | 0.01031 | 1269 | 0.030214 | 1.362 | A04 | MICL0.01121042/RBN
Build-In Floor | Mini Canal | MICL.01121042/RBR | 11 | 210 | 42 | 42 | 1148 | 1148 | 1148 | 0.027333 | 447 | 0.010643 | 1308 | 0.031143 | 1.362 | A04 | MICL0.01121042/RBR
Build-In Floor | Mini Canal | MICL.01121042/RBV | 11 | 210 | 42 | 42 | 1114 | 1114 | 1114 | 0.026524 | 433 | 0.01031 | 1269 | 0.030214 | 1.362 | A04 | MICL0.01121042/RBV
Build-In Floor | Mini Canal | MICL.01121042/RDB | 11 | 210 | 42 | 42 | 1148 | 1148 | 1148 | 0.027333 | 447 | 0.010643 | 1308 | 0.031143 | 1.362 | A04 | MICL0.01121042/RDB
Build-In Floor | Mini Canal | MICL.01121042/RMN | 11 | 210 | 42 | 42 | 1114 | 1114 | 1114 | 0.026524 | 433 | 0.01031 | 1269 | 0.030214 | 1.362 | A04 | MICL0.01121042/RMN
Build-In Floor | Mini Canal | MICL.01121042/RMV | 11 | 210 | 42 | 42 | 1114 | 1114 | 1114 | 0.026524 | 433 | 0.01031 | 1269 | 0.030214 | 1.362 | A04 | MICL0.01121042/RMV
Build-In Floor | Mini Canal | MICL.01121042/RNA | 11 | 210 | 42 | 42 | 1148 | 1148 | 1148 | 0.027333 | 447 | 0.010643 | 1308 | 0.031143 | 1.362 | A04 | MICL0.01121042/RNA
Build-In Floor | Mini Canal | MICL.01121042/RON | 11 | 210 | 42 | 42 | 1114 | 1114 | 1114 | 0.026524 | 433 | 0.01031 | 1269 | 0.030214 | 1.362 | A04 | MICL0.01121042/RON
Build-In Floor | Mini Canal | MICL.01121042/ROV | 11 | 210 | 42 | 42 | 1114 | 1114 | 1114 | 0.026524 | 433 | 0.01031 | 1269 | 0.030214 | 1.362 | A04 | MICL0.01121042/ROV
Build-In Floor | Mini Canal | MICL.01121042/RSS | 11 | 210 | 42 | 42 | 1102 | 1102 | 1102 | 0.026238 | 429 | 0.010214 | 1255 | 0.029881 | 1.362 | A04 | MICL0.01121042/RSS
Build-In Floor | Mini Canal | MICL.01121042/SBL | 11 | 210 | 42 | 42 | 1148 | 1148 | 1148 | 0.027333 | 447 | 0.010643 | 1308 | 0.031143 | 1.362 | A04 | MICL0.01121042/SBL
Build-In Floor | Mini Canal | MICL.01121042/SBR | 11 | 210 | 42 | 42 | 1148 | 1148 | 1148 | 0.027333 | 447 | 0.010643 | 1308 | 0.031143 | 1.362 | A04 | MICL0.01121042/SBR
Build-In Floor | Mini Canal | MICL.01121042/SDB | 11 | 210 | 42 | 42 | 1148 | 1148 | 1148 | 0.027333 | 447 | 0.010643 | 1308 | 0.031143 | 1.362 | A04 | MICL0.01121042/SDB
Build-In Floor | Mini Canal | MICL.01121042/SNA | 11 | 210 | 42 | 42 | 1148 | 1148 | 1148 | 0.027333 | 447 | 0.010643 | 1308 | 0.031143 | 1.362 | A04 | MICL0.01121042/SNA
Build-In Floor | Mini Canal | MICL.01121042/SNC | 11 | 210 | 42 | 42 | 1148 | 1148 | 1148 | 0.027333 | 447 | 0.010643 | 1308 | 0.031143 | 1.362 | A04 | MICL0.01121042/SNC
Build-In Floor | Mini Canal | MICL.01123014/ANA | 11 | 230 | 14 | 14 | 328 | 328 | 328 | 0.0078095 | 128 | 0.0030476 | 374 | 0.0089048 | 1.362 | A04 | MICL0.01123014/ANA
Build-In Floor | Mini Canal | MICL.01123014/DBL | 11 | 230 | 14 | 14 | 424 | 424 | 424 | 0.010095 | 165 | 0.0039286 | 483 | 0.0115 | 1.362 | A04 | MICL0.01123014/DBL
Build-In Floor | Mini Canal | MICL.01123014/DBN | 11 | 230 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.01123014/DBN
Build-In Floor | Mini Canal | MICL.01123014/DBR | 11 | 230 | 14 | 14 | 424 | 424 | 424 | 0.010095 | 165 | 0.0039286 | 483 | 0.0115 | 1.362 | A04 | MICL0.01123014/DBR
Build-In Floor | Mini Canal | MICL.01123014/DBV | 11 | 230 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.01123014/DBV
Build-In Floor | Mini Canal | MICL.01123014/DDB | 11 | 230 | 14 | 14 | 424 | 424 | 424 | 0.010095 | 165 | 0.0039286 | 483 | 0.0115 | 1.362 | A04 | MICL0.01123014/DDB
Build-In Floor | Mini Canal | MICL.01123014/DMN | 11 | 230 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.01123014/DMN
Build-In Floor | Mini Canal | MICL.01123014/DMV | 11 | 230 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.01123014/DMV
Build-In Floor | Mini Canal | MICL.01123014/DNA | 11 | 230 | 14 | 14 | 424 | 424 | 424 | 0.010095 | 165 | 0.0039286 | 483 | 0.0115 | 1.362 | A04 | MICL0.01123014/DNA
Build-In Floor | Mini Canal | MICL.01123014/DNC | 11 | 230 | 14 | 14 | 424 | 424 | 424 | 0.010095 | 165 | 0.0039286 | 483 | 0.0115 | 1.362 | A04 | MICL0.01123014/DNC
Build-In Floor | Mini Canal | MICL.01123014/DON | 11 | 230 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.01123014/DON
Build-In Floor | Mini Canal | MICL.01123014/DOV | 11 | 230 | 14 | 14 | 406 | 406 | 406 | 0.0096667 | 158 | 0.0037619 | 462 | 0.011 | 1.362 | A04 | MICL0.01123014/DOV
Build-In Floor | Mini Canal | MICL.01123014/RBL | 11 | 230 | 14 | 14 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01123014/RBL
Build-In Floor | Mini Canal | MICL.01123014/RBN | 11 | 230 | 14 | 14 | 424 | 424 | 424 | 0.010095 | 165 | 0.0039286 | 483 | 0.0115 | 1.362 | A04 | MICL0.01123014/RBN
Build-In Floor | Mini Canal | MICL.01123014/RBR | 11 | 230 | 14 | 14 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01123014/RBR
Build-In Floor | Mini Canal | MICL.01123014/RBV | 11 | 230 | 14 | 14 | 424 | 424 | 424 | 0.010095 | 165 | 0.0039286 | 483 | 0.0115 | 1.362 | A04 | MICL0.01123014/RBV
Build-In Floor | Mini Canal | MICL.01123014/RDB | 11 | 230 | 14 | 14 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01123014/RDB
Build-In Floor | Mini Canal | MICL.01123014/RMN | 11 | 230 | 14 | 14 | 424 | 424 | 424 | 0.010095 | 165 | 0.0039286 | 483 | 0.0115 | 1.362 | A04 | MICL0.01123014/RMN
Build-In Floor | Mini Canal | MICL.01123014/RMV | 11 | 230 | 14 | 14 | 424 | 424 | 424 | 0.010095 | 165 | 0.0039286 | 483 | 0.0115 | 1.362 | A04 | MICL0.01123014/RMV
Build-In Floor | Mini Canal | MICL.01123014/RNA | 11 | 230 | 14 | 14 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01123014/RNA
Build-In Floor | Mini Canal | MICL.01123014/RON | 11 | 230 | 14 | 14 | 424 | 424 | 424 | 0.010095 | 165 | 0.0039286 | 483 | 0.0115 | 1.362 | A04 | MICL0.01123014/RON
Build-In Floor | Mini Canal | MICL.01123014/ROV | 11 | 230 | 14 | 14 | 424 | 424 | 424 | 0.010095 | 165 | 0.0039286 | 483 | 0.0115 | 1.362 | A04 | MICL0.01123014/ROV
Build-In Floor | Mini Canal | MICL.01123014/RSS | 11 | 230 | 14 | 14 | 420 | 420 | 420 | 0.01 | 163 | 0.003881 | 478 | 0.011381 | 1.362 | A04 | MICL0.01123014/RSS
Build-In Floor | Mini Canal | MICL.01123014/SBL | 11 | 230 | 14 | 14 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01123014/SBL
Build-In Floor | Mini Canal | MICL.01123014/SBR | 11 | 230 | 14 | 14 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01123014/SBR
Build-In Floor | Mini Canal | MICL.01123014/SDB | 11 | 230 | 14 | 14 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01123014/SDB
Build-In Floor | Mini Canal | MICL.01123014/SNA | 11 | 230 | 14 | 14 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01123014/SNA
Build-In Floor | Mini Canal | MICL.01123014/SNC | 11 | 230 | 14 | 14 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01123014/SNC
Build-In Floor | Mini Canal | MICL.01123018/ANA | 11 | 230 | 18 | 18 | 389 | 389 | 389 | 0.0092619 | 151 | 0.0035952 | 443 | 0.010548 | 1.362 | A04 | MICL0.01123018/ANA
Build-In Floor | Mini Canal | MICL.01123018/DBL | 11 | 230 | 18 | 18 | 502 | 502 | 502 | 0.011952 | 195 | 0.0046429 | 572 | 0.013619 | 1.362 | A04 | MICL0.01123018/DBL
Build-In Floor | Mini Canal | MICL.01123018/DBN | 11 | 230 | 18 | 18 | 482 | 482 | 482 | 0.011476 | 187 | 0.0044524 | 549 | 0.013071 | 1.362 | A04 | MICL0.01123018/DBN
Build-In Floor | Mini Canal | MICL.01123018/DBR | 11 | 230 | 18 | 18 | 502 | 502 | 502 | 0.011952 | 195 | 0.0046429 | 572 | 0.013619 | 1.362 | A04 | MICL0.01123018/DBR
Build-In Floor | Mini Canal | MICL.01123018/DBV | 11 | 230 | 18 | 18 | 482 | 482 | 482 | 0.011476 | 187 | 0.0044524 | 549 | 0.013071 | 1.362 | A04 | MICL0.01123018/DBV
Build-In Floor | Mini Canal | MICL.01123018/DDB | 11 | 230 | 18 | 18 | 502 | 502 | 502 | 0.011952 | 195 | 0.0046429 | 572 | 0.013619 | 1.362 | A04 | MICL0.01123018/DDB
Build-In Floor | Mini Canal | MICL.01123018/DMN | 11 | 230 | 18 | 18 | 482 | 482 | 482 | 0.011476 | 187 | 0.0044524 | 549 | 0.013071 | 1.362 | A04 | MICL0.01123018/DMN
Build-In Floor | Mini Canal | MICL.01123018/DMV | 11 | 230 | 18 | 18 | 482 | 482 | 482 | 0.011476 | 187 | 0.0044524 | 549 | 0.013071 | 1.362 | A04 | MICL0.01123018/DMV
Build-In Floor | Mini Canal | MICL.01123018/DNA | 11 | 230 | 18 | 18 | 502 | 502 | 502 | 0.011952 | 195 | 0.0046429 | 572 | 0.013619 | 1.362 | A04 | MICL0.01123018/DNA
Build-In Floor | Mini Canal | MICL.01123018/DNC | 11 | 230 | 18 | 18 | 502 | 502 | 502 | 0.011952 | 195 | 0.0046429 | 572 | 0.013619 | 1.362 | A04 | MICL0.01123018/DNC
Build-In Floor | Mini Canal | MICL.01123018/DON | 11 | 230 | 18 | 18 | 482 | 482 | 482 | 0.011476 | 187 | 0.0044524 | 549 | 0.013071 | 1.362 | A04 | MICL0.01123018/DON
Build-In Floor | Mini Canal | MICL.01123018/DOV | 11 | 230 | 18 | 18 | 482 | 482 | 482 | 0.011476 | 187 | 0.0044524 | 549 | 0.013071 | 1.362 | A04 | MICL0.01123018/DOV
Build-In Floor | Mini Canal | MICL.01123018/RBL | 11 | 230 | 18 | 18 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.01123018/RBL
Build-In Floor | Mini Canal | MICL.01123018/RBN | 11 | 230 | 18 | 18 | 502 | 502 | 502 | 0.011952 | 195 | 0.0046429 | 572 | 0.013619 | 1.362 | A04 | MICL0.01123018/RBN
Build-In Floor | Mini Canal | MICL.01123018/RBR | 11 | 230 | 18 | 18 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.01123018/RBR
Build-In Floor | Mini Canal | MICL.01123018/RBV | 11 | 230 | 18 | 18 | 502 | 502 | 502 | 0.011952 | 195 | 0.0046429 | 572 | 0.013619 | 1.362 | A04 | MICL0.01123018/RBV
Build-In Floor | Mini Canal | MICL.01123018/RDB | 11 | 230 | 18 | 18 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.01123018/RDB
Build-In Floor | Mini Canal | MICL.01123018/RMN | 11 | 230 | 18 | 18 | 502 | 502 | 502 | 0.011952 | 195 | 0.0046429 | 572 | 0.013619 | 1.362 | A04 | MICL0.01123018/RMN
Build-In Floor | Mini Canal | MICL.01123018/RMV | 11 | 230 | 18 | 18 | 502 | 502 | 502 | 0.011952 | 195 | 0.0046429 | 572 | 0.013619 | 1.362 | A04 | MICL0.01123018/RMV
Build-In Floor | Mini Canal | MICL.01123018/RNA | 11 | 230 | 18 | 18 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.01123018/RNA
Build-In Floor | Mini Canal | MICL.01123018/RON | 11 | 230 | 18 | 18 | 502 | 502 | 502 | 0.011952 | 195 | 0.0046429 | 572 | 0.013619 | 1.362 | A04 | MICL0.01123018/RON
Build-In Floor | Mini Canal | MICL.01123018/ROV | 11 | 230 | 18 | 18 | 502 | 502 | 502 | 0.011952 | 195 | 0.0046429 | 572 | 0.013619 | 1.362 | A04 | MICL0.01123018/ROV
Build-In Floor | Mini Canal | MICL.01123018/RSS | 11 | 230 | 18 | 18 | 497 | 497 | 497 | 0.011833 | 193 | 0.0045952 | 566 | 0.013476 | 1.362 | A04 | MICL0.01123018/RSS
Build-In Floor | Mini Canal | MICL.01123018/SBL | 11 | 230 | 18 | 18 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.01123018/SBL
Build-In Floor | Mini Canal | MICL.01123018/SBR | 11 | 230 | 18 | 18 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.01123018/SBR
Build-In Floor | Mini Canal | MICL.01123018/SDB | 11 | 230 | 18 | 18 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.01123018/SDB
Build-In Floor | Mini Canal | MICL.01123018/SNA | 11 | 230 | 18 | 18 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.01123018/SNA
Build-In Floor | Mini Canal | MICL.01123018/SNC | 11 | 230 | 18 | 18 | 518 | 518 | 518 | 0.012333 | 202 | 0.0048095 | 590 | 0.014048 | 1.362 | A04 | MICL0.01123018/SNC
Build-In Floor | Mini Canal | MICL.01123026/ANA | 11 | 230 | 26 | 26 | 524 | 524 | 524 | 0.012476 | 204 | 0.0048571 | 597 | 0.014214 | 1.362 | A04 | MICL0.01123026/ANA
Build-In Floor | Mini Canal | MICL.01123026/DBL | 11 | 230 | 26 | 26 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01123026/DBL
Build-In Floor | Mini Canal | MICL.01123026/DBN | 11 | 230 | 26 | 26 | 650 | 650 | 650 | 0.015476 | 253 | 0.0060238 | 740 | 0.017619 | 1.362 | A04 | MICL0.01123026/DBN
Build-In Floor | Mini Canal | MICL.01123026/DBR | 11 | 230 | 26 | 26 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01123026/DBR
Build-In Floor | Mini Canal | MICL.01123026/DBV | 11 | 230 | 26 | 26 | 650 | 650 | 650 | 0.015476 | 253 | 0.0060238 | 740 | 0.017619 | 1.362 | A04 | MICL0.01123026/DBV
Build-In Floor | Mini Canal | MICL.01123026/DDB | 11 | 230 | 26 | 26 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01123026/DDB
Build-In Floor | Mini Canal | MICL.01123026/DMN | 11 | 230 | 26 | 26 | 650 | 650 | 650 | 0.015476 | 253 | 0.0060238 | 740 | 0.017619 | 1.362 | A04 | MICL0.01123026/DMN
Build-In Floor | Mini Canal | MICL.01123026/DMV | 11 | 230 | 26 | 26 | 650 | 650 | 650 | 0.015476 | 253 | 0.0060238 | 740 | 0.017619 | 1.362 | A04 | MICL0.01123026/DMV
Build-In Floor | Mini Canal | MICL.01123026/DNA | 11 | 230 | 26 | 26 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01123026/DNA
Build-In Floor | Mini Canal | MICL.01123026/DNC | 11 | 230 | 26 | 26 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01123026/DNC
Build-In Floor | Mini Canal | MICL.01123026/DON | 11 | 230 | 26 | 26 | 650 | 650 | 650 | 0.015476 | 253 | 0.0060238 | 740 | 0.017619 | 1.362 | A04 | MICL0.01123026/DON
Build-In Floor | Mini Canal | MICL.01123026/DOV | 11 | 230 | 26 | 26 | 650 | 650 | 650 | 0.015476 | 253 | 0.0060238 | 740 | 0.017619 | 1.362 | A04 | MICL0.01123026/DOV
Build-In Floor | Mini Canal | MICL.01123026/PNC | 11 | 230 | 26 | 26 | 594 | 594 | 594 | 0.014143 | 231 | 0.0055 | 677 | 0.016119 | 1.362 | A04 | MICL0.01123026/PNC
Build-In Floor | Mini Canal | MICL.01123026/RBL | 11 | 230 | 26 | 26 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01123026/RBL
Build-In Floor | Mini Canal | MICL.01123026/RBN | 11 | 230 | 26 | 26 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01123026/RBN
Build-In Floor | Mini Canal | MICL.01123026/RBR | 11 | 230 | 26 | 26 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01123026/RBR
Build-In Floor | Mini Canal | MICL.01123026/RBV | 11 | 230 | 26 | 26 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01123026/RBV
Build-In Floor | Mini Canal | MICL.01123026/RDB | 11 | 230 | 26 | 26 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01123026/RDB
Build-In Floor | Mini Canal | MICL.01123026/RMN | 11 | 230 | 26 | 26 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01123026/RMN
Build-In Floor | Mini Canal | MICL.01123026/RMV | 11 | 230 | 26 | 26 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01123026/RMV
Build-In Floor | Mini Canal | MICL.01123026/RNA | 11 | 230 | 26 | 26 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01123026/RNA
Build-In Floor | Mini Canal | MICL.01123026/RON | 11 | 230 | 26 | 26 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01123026/RON
Build-In Floor | Mini Canal | MICL.01123026/ROV | 11 | 230 | 26 | 26 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01123026/ROV
Build-In Floor | Mini Canal | MICL.01123026/RSS | 11 | 230 | 26 | 26 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.01123026/RSS
Build-In Floor | Mini Canal | MICL.01123026/SBL | 11 | 230 | 26 | 26 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01123026/SBL
Build-In Floor | Mini Canal | MICL.01123026/SBR | 11 | 230 | 26 | 26 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01123026/SBR
Build-In Floor | Mini Canal | MICL.01123026/SDB | 11 | 230 | 26 | 26 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01123026/SDB
Build-In Floor | Mini Canal | MICL.01123026/SNA | 11 | 230 | 26 | 26 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01123026/SNA
Build-In Floor | Mini Canal | MICL.01123026/SNC | 11 | 230 | 26 | 26 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01123026/SNC
Build-In Floor | Mini Canal | MICL.01123034/ANA | 11 | 230 | 34 | 34 | 681 | 681 | 681 | 0.016214 | 265 | 0.0063095 | 776 | 0.018476 | 1.362 | A04 | MICL0.01123034/ANA
Build-In Floor | Mini Canal | MICL.01123034/DBL | 11 | 230 | 34 | 34 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01123034/DBL
Build-In Floor | Mini Canal | MICL.01123034/DBN | 11 | 230 | 34 | 34 | 844 | 844 | 844 | 0.020095 | 328 | 0.0078095 | 961 | 0.022881 | 1.362 | A04 | MICL0.01123034/DBN
Build-In Floor | Mini Canal | MICL.01123034/DBR | 11 | 230 | 34 | 34 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01123034/DBR
Build-In Floor | Mini Canal | MICL.01123034/DBV | 11 | 230 | 34 | 34 | 844 | 844 | 844 | 0.020095 | 328 | 0.0078095 | 961 | 0.022881 | 1.362 | A04 | MICL0.01123034/DBV
Build-In Floor | Mini Canal | MICL.01123034/DDB | 11 | 230 | 34 | 34 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01123034/DDB
Build-In Floor | Mini Canal | MICL.01123034/DMN | 11 | 230 | 34 | 34 | 844 | 844 | 844 | 0.020095 | 328 | 0.0078095 | 961 | 0.022881 | 1.362 | A04 | MICL0.01123034/DMN
Build-In Floor | Mini Canal | MICL.01123034/DMV | 11 | 230 | 34 | 34 | 844 | 844 | 844 | 0.020095 | 328 | 0.0078095 | 961 | 0.022881 | 1.362 | A04 | MICL0.01123034/DMV
Build-In Floor | Mini Canal | MICL.01123034/DNA | 11 | 230 | 34 | 34 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01123034/DNA
Build-In Floor | Mini Canal | MICL.01123034/DNC | 11 | 230 | 34 | 34 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01123034/DNC
Build-In Floor | Mini Canal | MICL.01123034/DON | 11 | 230 | 34 | 34 | 844 | 844 | 844 | 0.020095 | 328 | 0.0078095 | 961 | 0.022881 | 1.362 | A04 | MICL0.01123034/DON
Build-In Floor | Mini Canal | MICL.01123034/DOV | 11 | 230 | 34 | 34 | 844 | 844 | 844 | 0.020095 | 328 | 0.0078095 | 961 | 0.022881 | 1.362 | A04 | MICL0.01123034/DOV
Build-In Floor | Mini Canal | MICL.01123034/PNC | 11 | 230 | 34 | 34 | 772 | 772 | 772 | 0.018381 | 300 | 0.0071429 | 879 | 0.020929 | 1.362 | A04 | MICL0.01123034/PNC
Build-In Floor | Mini Canal | MICL.01123034/RBL | 11 | 230 | 34 | 34 | 908 | 908 | 908 | 0.021619 | 353 | 0.0084048 | 1034 | 0.024619 | 1.362 | A04 | MICL0.01123034/RBL
Build-In Floor | Mini Canal | MICL.01123034/RBN | 11 | 230 | 34 | 34 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01123034/RBN
Build-In Floor | Mini Canal | MICL.01123034/RBR | 11 | 230 | 34 | 34 | 908 | 908 | 908 | 0.021619 | 353 | 0.0084048 | 1034 | 0.024619 | 1.362 | A04 | MICL0.01123034/RBR
Build-In Floor | Mini Canal | MICL.01123034/RBV | 11 | 230 | 34 | 34 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01123034/RBV
Build-In Floor | Mini Canal | MICL.01123034/RDB | 11 | 230 | 34 | 34 | 908 | 908 | 908 | 0.021619 | 353 | 0.0084048 | 1034 | 0.024619 | 1.362 | A04 | MICL0.01123034/RDB
Build-In Floor | Mini Canal | MICL.01123034/RMN | 11 | 230 | 34 | 34 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01123034/RMN
Build-In Floor | Mini Canal | MICL.01123034/RMV | 11 | 230 | 34 | 34 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01123034/RMV
Build-In Floor | Mini Canal | MICL.01123034/RNA | 11 | 230 | 34 | 34 | 908 | 908 | 908 | 0.021619 | 353 | 0.0084048 | 1034 | 0.024619 | 1.362 | A04 | MICL0.01123034/RNA
Build-In Floor | Mini Canal | MICL.01123034/RON | 11 | 230 | 34 | 34 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01123034/RON
Build-In Floor | Mini Canal | MICL.01123034/ROV | 11 | 230 | 34 | 34 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01123034/ROV
Build-In Floor | Mini Canal | MICL.01123034/RSS | 11 | 230 | 34 | 34 | 872 | 872 | 872 | 0.020762 | 339 | 0.0080714 | 993 | 0.023643 | 1.362 | A04 | MICL0.01123034/RSS
Build-In Floor | Mini Canal | MICL.01123034/SBL | 11 | 230 | 34 | 34 | 908 | 908 | 908 | 0.021619 | 353 | 0.0084048 | 1034 | 0.024619 | 1.362 | A04 | MICL0.01123034/SBL
Build-In Floor | Mini Canal | MICL.01123034/SBR | 11 | 230 | 34 | 34 | 908 | 908 | 908 | 0.021619 | 353 | 0.0084048 | 1034 | 0.024619 | 1.362 | A04 | MICL0.01123034/SBR
Build-In Floor | Mini Canal | MICL.01123034/SDB | 11 | 230 | 34 | 34 | 908 | 908 | 908 | 0.021619 | 353 | 0.0084048 | 1034 | 0.024619 | 1.362 | A04 | MICL0.01123034/SDB
Build-In Floor | Mini Canal | MICL.01123034/SNA | 11 | 230 | 34 | 34 | 908 | 908 | 908 | 0.021619 | 353 | 0.0084048 | 1034 | 0.024619 | 1.362 | A04 | MICL0.01123034/SNA
Build-In Floor | Mini Canal | MICL.01123034/SNC | 11 | 230 | 34 | 34 | 908 | 908 | 908 | 0.021619 | 353 | 0.0084048 | 1034 | 0.024619 | 1.362 | A04 | MICL0.01123034/SNC
Build-In Floor | Mini Canal | MICL.01123042/ANA | 11 | 230 | 42 | 42 | 957 | 957 | 957 | 0.022786 | 372 | 0.0088571 | 1090 | 0.025952 | 1.362 | A04 | MICL0.01123042/ANA
Build-In Floor | Mini Canal | MICL.01123042/DBL | 11 | 230 | 42 | 42 | 1238 | 1238 | 1238 | 0.029476 | 482 | 0.011476 | 1410 | 0.033571 | 1.362 | A04 | MICL0.01123042/DBL
Build-In Floor | Mini Canal | MICL.01123042/DBN | 11 | 230 | 42 | 42 | 1187 | 1187 | 1187 | 0.028262 | 462 | 0.011 | 1352 | 0.03219 | 1.362 | A04 | MICL0.01123042/DBN
Build-In Floor | Mini Canal | MICL.01123042/DBR | 11 | 230 | 42 | 42 | 1238 | 1238 | 1238 | 0.029476 | 482 | 0.011476 | 1410 | 0.033571 | 1.362 | A04 | MICL0.01123042/DBR
Build-In Floor | Mini Canal | MICL.01123042/DBV | 11 | 230 | 42 | 42 | 1187 | 1187 | 1187 | 0.028262 | 462 | 0.011 | 1352 | 0.03219 | 1.362 | A04 | MICL0.01123042/DBV
Build-In Floor | Mini Canal | MICL.01123042/DDB | 11 | 230 | 42 | 42 | 1238 | 1238 | 1238 | 0.029476 | 482 | 0.011476 | 1410 | 0.033571 | 1.362 | A04 | MICL0.01123042/DDB
Build-In Floor | Mini Canal | MICL.01123042/DMN | 11 | 230 | 42 | 42 | 1187 | 1187 | 1187 | 0.028262 | 462 | 0.011 | 1352 | 0.03219 | 1.362 | A04 | MICL0.01123042/DMN
Build-In Floor | Mini Canal | MICL.01123042/DMV | 11 | 230 | 42 | 42 | 1187 | 1187 | 1187 | 0.028262 | 462 | 0.011 | 1352 | 0.03219 | 1.362 | A04 | MICL0.01123042/DMV
Build-In Floor | Mini Canal | MICL.01123042/DNA | 11 | 230 | 42 | 42 | 1238 | 1238 | 1238 | 0.029476 | 482 | 0.011476 | 1410 | 0.033571 | 1.362 | A04 | MICL0.01123042/DNA
Build-In Floor | Mini Canal | MICL.01123042/DNC | 11 | 230 | 42 | 42 | 1238 | 1238 | 1238 | 0.029476 | 482 | 0.011476 | 1410 | 0.033571 | 1.362 | A04 | MICL0.01123042/DNC
Build-In Floor | Mini Canal | MICL.01123042/DON | 11 | 230 | 42 | 42 | 1187 | 1187 | 1187 | 0.028262 | 462 | 0.011 | 1352 | 0.03219 | 1.362 | A04 | MICL0.01123042/DON
Build-In Floor | Mini Canal | MICL.01123042/DOV | 11 | 230 | 42 | 42 | 1187 | 1187 | 1187 | 0.028262 | 462 | 0.011 | 1352 | 0.03219 | 1.362 | A04 | MICL0.01123042/DOV
Build-In Floor | Mini Canal | MICL.01123042/PNC | 11 | 230 | 42 | 42 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01123042/PNC
Build-In Floor | Mini Canal | MICL.01123042/RBL | 11 | 230 | 42 | 42 | 1276 | 1276 | 1276 | 0.030381 | 496 | 0.01181 | 1453 | 0.034595 | 1.362 | A04 | MICL0.01123042/RBL
Build-In Floor | Mini Canal | MICL.01123042/RBN | 11 | 230 | 42 | 42 | 1238 | 1238 | 1238 | 0.029476 | 482 | 0.011476 | 1410 | 0.033571 | 1.362 | A04 | MICL0.01123042/RBN
Build-In Floor | Mini Canal | MICL.01123042/RBR | 11 | 230 | 42 | 42 | 1276 | 1276 | 1276 | 0.030381 | 496 | 0.01181 | 1453 | 0.034595 | 1.362 | A04 | MICL0.01123042/RBR
Build-In Floor | Mini Canal | MICL.01123042/RBV | 11 | 230 | 42 | 42 | 1238 | 1238 | 1238 | 0.029476 | 482 | 0.011476 | 1410 | 0.033571 | 1.362 | A04 | MICL0.01123042/RBV
Build-In Floor | Mini Canal | MICL.01123042/RDB | 11 | 230 | 42 | 42 | 1276 | 1276 | 1276 | 0.030381 | 496 | 0.01181 | 1453 | 0.034595 | 1.362 | A04 | MICL0.01123042/RDB
Build-In Floor | Mini Canal | MICL.01123042/RMN | 11 | 230 | 42 | 42 | 1238 | 1238 | 1238 | 0.029476 | 482 | 0.011476 | 1410 | 0.033571 | 1.362 | A04 | MICL0.01123042/RMN
Build-In Floor | Mini Canal | MICL.01123042/RMV | 11 | 230 | 42 | 42 | 1238 | 1238 | 1238 | 0.029476 | 482 | 0.011476 | 1410 | 0.033571 | 1.362 | A04 | MICL0.01123042/RMV
Build-In Floor | Mini Canal | MICL.01123042/RNA | 11 | 230 | 42 | 42 | 1276 | 1276 | 1276 | 0.030381 | 496 | 0.01181 | 1453 | 0.034595 | 1.362 | A04 | MICL0.01123042/RNA
Build-In Floor | Mini Canal | MICL.01123042/RON | 11 | 230 | 42 | 42 | 1238 | 1238 | 1238 | 0.029476 | 482 | 0.011476 | 1410 | 0.033571 | 1.362 | A04 | MICL0.01123042/RON
Build-In Floor | Mini Canal | MICL.01123042/ROV | 11 | 230 | 42 | 42 | 1238 | 1238 | 1238 | 0.029476 | 482 | 0.011476 | 1410 | 0.033571 | 1.362 | A04 | MICL0.01123042/ROV
Build-In Floor | Mini Canal | MICL.01123042/RSS | 11 | 230 | 42 | 42 | 1225 | 1225 | 1225 | 0.029167 | 477 | 0.011357 | 1395 | 0.033214 | 1.362 | A04 | MICL0.01123042/RSS
Build-In Floor | Mini Canal | MICL.01123042/SBL | 11 | 230 | 42 | 42 | 1276 | 1276 | 1276 | 0.030381 | 496 | 0.01181 | 1453 | 0.034595 | 1.362 | A04 | MICL0.01123042/SBL
Build-In Floor | Mini Canal | MICL.01123042/SBR | 11 | 230 | 42 | 42 | 1276 | 1276 | 1276 | 0.030381 | 496 | 0.01181 | 1453 | 0.034595 | 1.362 | A04 | MICL0.01123042/SBR
Build-In Floor | Mini Canal | MICL.01123042/SDB | 11 | 230 | 42 | 42 | 1276 | 1276 | 1276 | 0.030381 | 496 | 0.01181 | 1453 | 0.034595 | 1.362 | A04 | MICL0.01123042/SDB
Build-In Floor | Mini Canal | MICL.01123042/SNA | 11 | 230 | 42 | 42 | 1276 | 1276 | 1276 | 0.030381 | 496 | 0.01181 | 1453 | 0.034595 | 1.362 | A04 | MICL0.01123042/SNA
Build-In Floor | Mini Canal | MICL.01123042/SNC | 11 | 230 | 42 | 42 | 1276 | 1276 | 1276 | 0.030381 | 496 | 0.01181 | 1453 | 0.034595 | 1.362 | A04 | MICL0.01123042/SNC
Build-In Floor | Mini Canal | MICL.01125014/ANA | 11 | 250 | 14 | 14 | 360 | 360 | 360 | 0.0085714 | 140 | 0.0033333 | 410 | 0.0097619 | 1.362 | A04 | MICL0.01125014/ANA
Build-In Floor | Mini Canal | MICL.01125014/DBL | 11 | 250 | 14 | 14 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01125014/DBL
Build-In Floor | Mini Canal | MICL.01125014/DBN | 11 | 250 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01125014/DBN
Build-In Floor | Mini Canal | MICL.01125014/DBR | 11 | 250 | 14 | 14 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01125014/DBR
Build-In Floor | Mini Canal | MICL.01125014/DBV | 11 | 250 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01125014/DBV
Build-In Floor | Mini Canal | MICL.01125014/DDB | 11 | 250 | 14 | 14 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01125014/DDB
Build-In Floor | Mini Canal | MICL.01125014/DMN | 11 | 250 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01125014/DMN
Build-In Floor | Mini Canal | MICL.01125014/DMV | 11 | 250 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01125014/DMV
Build-In Floor | Mini Canal | MICL.01125014/DNA | 11 | 250 | 14 | 14 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01125014/DNA
Build-In Floor | Mini Canal | MICL.01125014/DNC | 11 | 250 | 14 | 14 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01125014/DNC
Build-In Floor | Mini Canal | MICL.01125014/DON | 11 | 250 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01125014/DON
Build-In Floor | Mini Canal | MICL.01125014/DOV | 11 | 250 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01125014/DOV
Build-In Floor | Mini Canal | MICL.01125014/RBL | 11 | 250 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01125014/RBL
Build-In Floor | Mini Canal | MICL.01125014/RBN | 11 | 250 | 14 | 14 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01125014/RBN
Build-In Floor | Mini Canal | MICL.01125014/RBR | 11 | 250 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01125014/RBR
Build-In Floor | Mini Canal | MICL.01125014/RBV | 11 | 250 | 14 | 14 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01125014/RBV
Build-In Floor | Mini Canal | MICL.01125014/RDB | 11 | 250 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01125014/RDB
Build-In Floor | Mini Canal | MICL.01125014/RMN | 11 | 250 | 14 | 14 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01125014/RMN
Build-In Floor | Mini Canal | MICL.01125014/RMV | 11 | 250 | 14 | 14 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01125014/RMV
Build-In Floor | Mini Canal | MICL.01125014/RNA | 11 | 250 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01125014/RNA
Build-In Floor | Mini Canal | MICL.01125014/RON | 11 | 250 | 14 | 14 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01125014/RON
Build-In Floor | Mini Canal | MICL.01125014/ROV | 11 | 250 | 14 | 14 | 466 | 466 | 466 | 0.011095 | 181 | 0.0043095 | 531 | 0.012643 | 1.362 | A04 | MICL0.01125014/ROV
Build-In Floor | Mini Canal | MICL.01125014/RSS | 11 | 250 | 14 | 14 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01125014/RSS
Build-In Floor | Mini Canal | MICL.01125014/SBL | 11 | 250 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01125014/SBL
Build-In Floor | Mini Canal | MICL.01125014/SBR | 11 | 250 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01125014/SBR
Build-In Floor | Mini Canal | MICL.01125014/SDB | 11 | 250 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01125014/SDB
Build-In Floor | Mini Canal | MICL.01125014/SNA | 11 | 250 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01125014/SNA
Build-In Floor | Mini Canal | MICL.01125014/SNC | 11 | 250 | 14 | 14 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01125014/SNC
Build-In Floor | Mini Canal | MICL.01125018/ANA | 11 | 250 | 18 | 18 | 427 | 427 | 427 | 0.010167 | 166 | 0.0039524 | 486 | 0.011571 | 1.362 | A04 | MICL0.01125018/ANA
Build-In Floor | Mini Canal | MICL.01125018/DBL | 11 | 250 | 18 | 18 | 552 | 552 | 552 | 0.013143 | 215 | 0.005119 | 629 | 0.014976 | 1.362 | A04 | MICL0.01125018/DBL
Build-In Floor | Mini Canal | MICL.01125018/DBN | 11 | 250 | 18 | 18 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01125018/DBN
Build-In Floor | Mini Canal | MICL.01125018/DBR | 11 | 250 | 18 | 18 | 552 | 552 | 552 | 0.013143 | 215 | 0.005119 | 629 | 0.014976 | 1.362 | A04 | MICL0.01125018/DBR
Build-In Floor | Mini Canal | MICL.01125018/DBV | 11 | 250 | 18 | 18 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01125018/DBV
Build-In Floor | Mini Canal | MICL.01125018/DDB | 11 | 250 | 18 | 18 | 552 | 552 | 552 | 0.013143 | 215 | 0.005119 | 629 | 0.014976 | 1.362 | A04 | MICL0.01125018/DDB
Build-In Floor | Mini Canal | MICL.01125018/DMN | 11 | 250 | 18 | 18 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01125018/DMN
Build-In Floor | Mini Canal | MICL.01125018/DMV | 11 | 250 | 18 | 18 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01125018/DMV
Build-In Floor | Mini Canal | MICL.01125018/DNA | 11 | 250 | 18 | 18 | 552 | 552 | 552 | 0.013143 | 215 | 0.005119 | 629 | 0.014976 | 1.362 | A04 | MICL0.01125018/DNA
Build-In Floor | Mini Canal | MICL.01125018/DNC | 11 | 250 | 18 | 18 | 552 | 552 | 552 | 0.013143 | 215 | 0.005119 | 629 | 0.014976 | 1.362 | A04 | MICL0.01125018/DNC
Build-In Floor | Mini Canal | MICL.01125018/DON | 11 | 250 | 18 | 18 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01125018/DON
Build-In Floor | Mini Canal | MICL.01125018/DOV | 11 | 250 | 18 | 18 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01125018/DOV
Build-In Floor | Mini Canal | MICL.01125018/RBL | 11 | 250 | 18 | 18 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01125018/RBL
Build-In Floor | Mini Canal | MICL.01125018/RBN | 11 | 250 | 18 | 18 | 552 | 552 | 552 | 0.013143 | 215 | 0.005119 | 629 | 0.014976 | 1.362 | A04 | MICL0.01125018/RBN
Build-In Floor | Mini Canal | MICL.01125018/RBR | 11 | 250 | 18 | 18 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01125018/RBR
Build-In Floor | Mini Canal | MICL.01125018/RBV | 11 | 250 | 18 | 18 | 552 | 552 | 552 | 0.013143 | 215 | 0.005119 | 629 | 0.014976 | 1.362 | A04 | MICL0.01125018/RBV
Build-In Floor | Mini Canal | MICL.01125018/RDB | 11 | 250 | 18 | 18 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01125018/RDB
Build-In Floor | Mini Canal | MICL.01125018/RMN | 11 | 250 | 18 | 18 | 552 | 552 | 552 | 0.013143 | 215 | 0.005119 | 629 | 0.014976 | 1.362 | A04 | MICL0.01125018/RMN
Build-In Floor | Mini Canal | MICL.01125018/RMV | 11 | 250 | 18 | 18 | 552 | 552 | 552 | 0.013143 | 215 | 0.005119 | 629 | 0.014976 | 1.362 | A04 | MICL0.01125018/RMV
Build-In Floor | Mini Canal | MICL.01125018/RNA | 11 | 250 | 18 | 18 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01125018/RNA
Build-In Floor | Mini Canal | MICL.01125018/RON | 11 | 250 | 18 | 18 | 552 | 552 | 552 | 0.013143 | 215 | 0.005119 | 629 | 0.014976 | 1.362 | A04 | MICL0.01125018/RON
Build-In Floor | Mini Canal | MICL.01125018/ROV | 11 | 250 | 18 | 18 | 552 | 552 | 552 | 0.013143 | 215 | 0.005119 | 629 | 0.014976 | 1.362 | A04 | MICL0.01125018/ROV
Build-In Floor | Mini Canal | MICL.01125018/RSS | 11 | 250 | 18 | 18 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01125018/RSS
Build-In Floor | Mini Canal | MICL.01125018/SBL | 11 | 250 | 18 | 18 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01125018/SBL
Build-In Floor | Mini Canal | MICL.01125018/SBR | 11 | 250 | 18 | 18 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01125018/SBR
Build-In Floor | Mini Canal | MICL.01125018/SDB | 11 | 250 | 18 | 18 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01125018/SDB
Build-In Floor | Mini Canal | MICL.01125018/SNA | 11 | 250 | 18 | 18 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01125018/SNA
Build-In Floor | Mini Canal | MICL.01125018/SNC | 11 | 250 | 18 | 18 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01125018/SNC
Build-In Floor | Mini Canal | MICL.01125026/ANA | 11 | 250 | 26 | 26 | 577 | 577 | 577 | 0.013738 | 224 | 0.0053333 | 657 | 0.015643 | 1.362 | A04 | MICL0.01125026/ANA
Build-In Floor | Mini Canal | MICL.01125026/DBL | 11 | 250 | 26 | 26 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.01125026/DBL
Build-In Floor | Mini Canal | MICL.01125026/DBN | 11 | 250 | 26 | 26 | 715 | 715 | 715 | 0.017024 | 278 | 0.006619 | 814 | 0.019381 | 1.362 | A04 | MICL0.01125026/DBN
Build-In Floor | Mini Canal | MICL.01125026/DBR | 11 | 250 | 26 | 26 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.01125026/DBR
Build-In Floor | Mini Canal | MICL.01125026/DBV | 11 | 250 | 26 | 26 | 715 | 715 | 715 | 0.017024 | 278 | 0.006619 | 814 | 0.019381 | 1.362 | A04 | MICL0.01125026/DBV
Build-In Floor | Mini Canal | MICL.01125026/DDB | 11 | 250 | 26 | 26 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.01125026/DDB
Build-In Floor | Mini Canal | MICL.01125026/DMN | 11 | 250 | 26 | 26 | 715 | 715 | 715 | 0.017024 | 278 | 0.006619 | 814 | 0.019381 | 1.362 | A04 | MICL0.01125026/DMN
Build-In Floor | Mini Canal | MICL.01125026/DMV | 11 | 250 | 26 | 26 | 715 | 715 | 715 | 0.017024 | 278 | 0.006619 | 814 | 0.019381 | 1.362 | A04 | MICL0.01125026/DMV
Build-In Floor | Mini Canal | MICL.01125026/DNA | 11 | 250 | 26 | 26 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.01125026/DNA
Build-In Floor | Mini Canal | MICL.01125026/DNC | 11 | 250 | 26 | 26 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.01125026/DNC
Build-In Floor | Mini Canal | MICL.01125026/DON | 11 | 250 | 26 | 26 | 715 | 715 | 715 | 0.017024 | 278 | 0.006619 | 814 | 0.019381 | 1.362 | A04 | MICL0.01125026/DON
Build-In Floor | Mini Canal | MICL.01125026/DOV | 11 | 250 | 26 | 26 | 715 | 715 | 715 | 0.017024 | 278 | 0.006619 | 814 | 0.019381 | 1.362 | A04 | MICL0.01125026/DOV
Build-In Floor | Mini Canal | MICL.01125026/PNC | 11 | 250 | 26 | 26 | 654 | 654 | 654 | 0.015571 | 254 | 0.0060476 | 745 | 0.017738 | 1.362 | A04 | MICL0.01125026/PNC
Build-In Floor | Mini Canal | MICL.01125026/RBL | 11 | 250 | 26 | 26 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.01125026/RBL
Build-In Floor | Mini Canal | MICL.01125026/RBN | 11 | 250 | 26 | 26 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.01125026/RBN
Build-In Floor | Mini Canal | MICL.01125026/RBR | 11 | 250 | 26 | 26 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.01125026/RBR
Build-In Floor | Mini Canal | MICL.01125026/RBV | 11 | 250 | 26 | 26 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.01125026/RBV
Build-In Floor | Mini Canal | MICL.01125026/RDB | 11 | 250 | 26 | 26 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.01125026/RDB
Build-In Floor | Mini Canal | MICL.01125026/RMN | 11 | 250 | 26 | 26 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.01125026/RMN
Build-In Floor | Mini Canal | MICL.01125026/RMV | 11 | 250 | 26 | 26 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.01125026/RMV
Build-In Floor | Mini Canal | MICL.01125026/RNA | 11 | 250 | 26 | 26 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.01125026/RNA
Build-In Floor | Mini Canal | MICL.01125026/RON | 11 | 250 | 26 | 26 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.01125026/RON
Build-In Floor | Mini Canal | MICL.01125026/ROV | 11 | 250 | 26 | 26 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.01125026/ROV
Build-In Floor | Mini Canal | MICL.01125026/RSS | 11 | 250 | 26 | 26 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.01125026/RSS
Build-In Floor | Mini Canal | MICL.01125026/SBL | 11 | 250 | 26 | 26 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.01125026/SBL
Build-In Floor | Mini Canal | MICL.01125026/SBR | 11 | 250 | 26 | 26 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.01125026/SBR
Build-In Floor | Mini Canal | MICL.01125026/SDB | 11 | 250 | 26 | 26 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.01125026/SDB
Build-In Floor | Mini Canal | MICL.01125026/SNA | 11 | 250 | 26 | 26 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.01125026/SNA
Build-In Floor | Mini Canal | MICL.01125026/SNC | 11 | 250 | 26 | 26 | 769 | 769 | 769 | 0.01831 | 299 | 0.007119 | 876 | 0.020857 | 1.362 | A04 | MICL0.01125026/SNC
Build-In Floor | Mini Canal | MICL.01125034/ANA | 11 | 250 | 34 | 34 | 749 | 749 | 749 | 0.017833 | 291 | 0.0069286 | 853 | 0.02031 | 1.362 | A04 | MICL0.01125034/ANA
Build-In Floor | Mini Canal | MICL.01125034/DBL | 11 | 250 | 34 | 34 | 968 | 968 | 968 | 0.023048 | 377 | 0.0089762 | 1103 | 0.026262 | 1.362 | A04 | MICL0.01125034/DBL
Build-In Floor | Mini Canal | MICL.01125034/DBN | 11 | 250 | 34 | 34 | 928 | 928 | 928 | 0.022095 | 361 | 0.0085952 | 1057 | 0.025167 | 1.362 | A04 | MICL0.01125034/DBN
Build-In Floor | Mini Canal | MICL.01125034/DBR | 11 | 250 | 34 | 34 | 968 | 968 | 968 | 0.023048 | 377 | 0.0089762 | 1103 | 0.026262 | 1.362 | A04 | MICL0.01125034/DBR
Build-In Floor | Mini Canal | MICL.01125034/DBV | 11 | 250 | 34 | 34 | 928 | 928 | 928 | 0.022095 | 361 | 0.0085952 | 1057 | 0.025167 | 1.362 | A04 | MICL0.01125034/DBV
Build-In Floor | Mini Canal | MICL.01125034/DDB | 11 | 250 | 34 | 34 | 968 | 968 | 968 | 0.023048 | 377 | 0.0089762 | 1103 | 0.026262 | 1.362 | A04 | MICL0.01125034/DDB
Build-In Floor | Mini Canal | MICL.01125034/DMN | 11 | 250 | 34 | 34 | 928 | 928 | 928 | 0.022095 | 361 | 0.0085952 | 1057 | 0.025167 | 1.362 | A04 | MICL0.01125034/DMN
Build-In Floor | Mini Canal | MICL.01125034/DMV | 11 | 250 | 34 | 34 | 928 | 928 | 928 | 0.022095 | 361 | 0.0085952 | 1057 | 0.025167 | 1.362 | A04 | MICL0.01125034/DMV
Build-In Floor | Mini Canal | MICL.01125034/DNA | 11 | 250 | 34 | 34 | 968 | 968 | 968 | 0.023048 | 377 | 0.0089762 | 1103 | 0.026262 | 1.362 | A04 | MICL0.01125034/DNA
Build-In Floor | Mini Canal | MICL.01125034/DNC | 11 | 250 | 34 | 34 | 968 | 968 | 968 | 0.023048 | 377 | 0.0089762 | 1103 | 0.026262 | 1.362 | A04 | MICL0.01125034/DNC
Build-In Floor | Mini Canal | MICL.01125034/DON | 11 | 250 | 34 | 34 | 928 | 928 | 928 | 0.022095 | 361 | 0.0085952 | 1057 | 0.025167 | 1.362 | A04 | MICL0.01125034/DON
Build-In Floor | Mini Canal | MICL.01125034/DOV | 11 | 250 | 34 | 34 | 928 | 928 | 928 | 0.022095 | 361 | 0.0085952 | 1057 | 0.025167 | 1.362 | A04 | MICL0.01125034/DOV
Build-In Floor | Mini Canal | MICL.01125034/PNC | 11 | 250 | 34 | 34 | 848 | 848 | 848 | 0.02019 | 330 | 0.0078571 | 966 | 0.023 | 1.362 | A04 | MICL0.01125034/PNC
Build-In Floor | Mini Canal | MICL.01125034/RBL | 11 | 250 | 34 | 34 | 998 | 998 | 998 | 0.023762 | 388 | 0.0092381 | 1137 | 0.027071 | 1.362 | A04 | MICL0.01125034/RBL
Build-In Floor | Mini Canal | MICL.01125034/RBN | 11 | 250 | 34 | 34 | 968 | 968 | 968 | 0.023048 | 377 | 0.0089762 | 1103 | 0.026262 | 1.362 | A04 | MICL0.01125034/RBN
Build-In Floor | Mini Canal | MICL.01125034/RBR | 11 | 250 | 34 | 34 | 998 | 998 | 998 | 0.023762 | 388 | 0.0092381 | 1137 | 0.027071 | 1.362 | A04 | MICL0.01125034/RBR
Build-In Floor | Mini Canal | MICL.01125034/RBV | 11 | 250 | 34 | 34 | 968 | 968 | 968 | 0.023048 | 377 | 0.0089762 | 1103 | 0.026262 | 1.362 | A04 | MICL0.01125034/RBV
Build-In Floor | Mini Canal | MICL.01125034/RDB | 11 | 250 | 34 | 34 | 998 | 998 | 998 | 0.023762 | 388 | 0.0092381 | 1137 | 0.027071 | 1.362 | A04 | MICL0.01125034/RDB
Build-In Floor | Mini Canal | MICL.01125034/RMN | 11 | 250 | 34 | 34 | 968 | 968 | 968 | 0.023048 | 377 | 0.0089762 | 1103 | 0.026262 | 1.362 | A04 | MICL0.01125034/RMN
Build-In Floor | Mini Canal | MICL.01125034/RMV | 11 | 250 | 34 | 34 | 968 | 968 | 968 | 0.023048 | 377 | 0.0089762 | 1103 | 0.026262 | 1.362 | A04 | MICL0.01125034/RMV
Build-In Floor | Mini Canal | MICL.01125034/RNA | 11 | 250 | 34 | 34 | 998 | 998 | 998 | 0.023762 | 388 | 0.0092381 | 1137 | 0.027071 | 1.362 | A04 | MICL0.01125034/RNA
Build-In Floor | Mini Canal | MICL.01125034/RON | 11 | 250 | 34 | 34 | 968 | 968 | 968 | 0.023048 | 377 | 0.0089762 | 1103 | 0.026262 | 1.362 | A04 | MICL0.01125034/RON
Build-In Floor | Mini Canal | MICL.01125034/ROV | 11 | 250 | 34 | 34 | 968 | 968 | 968 | 0.023048 | 377 | 0.0089762 | 1103 | 0.026262 | 1.362 | A04 | MICL0.01125034/ROV
Build-In Floor | Mini Canal | MICL.01125034/RSS | 11 | 250 | 34 | 34 | 958 | 958 | 958 | 0.02281 | 373 | 0.008881 | 1091 | 0.025976 | 1.362 | A04 | MICL0.01125034/RSS
Build-In Floor | Mini Canal | MICL.01125034/SBL | 11 | 250 | 34 | 34 | 998 | 998 | 998 | 0.023762 | 388 | 0.0092381 | 1137 | 0.027071 | 1.362 | A04 | MICL0.01125034/SBL
Build-In Floor | Mini Canal | MICL.01125034/SBR | 11 | 250 | 34 | 34 | 998 | 998 | 998 | 0.023762 | 388 | 0.0092381 | 1137 | 0.027071 | 1.362 | A04 | MICL0.01125034/SBR
Build-In Floor | Mini Canal | MICL.01125034/SDB | 11 | 250 | 34 | 34 | 998 | 998 | 998 | 0.023762 | 388 | 0.0092381 | 1137 | 0.027071 | 1.362 | A04 | MICL0.01125034/SDB
Build-In Floor | Mini Canal | MICL.01125034/SNA | 11 | 250 | 34 | 34 | 998 | 998 | 998 | 0.023762 | 388 | 0.0092381 | 1137 | 0.027071 | 1.362 | A04 | MICL0.01125034/SNA
Build-In Floor | Mini Canal | MICL.01125034/SNC | 11 | 250 | 34 | 34 | 998 | 998 | 998 | 0.023762 | 388 | 0.0092381 | 1137 | 0.027071 | 1.362 | A04 | MICL0.01125034/SNC
Build-In Floor | Mini Canal | MICL.01125042/ANA | 11 | 250 | 42 | 42 | 1053 | 1053 | 1053 | 0.025071 | 410 | 0.0097619 | 1199 | 0.028548 | 1.362 | A04 | MICL0.01125042/ANA
Build-In Floor | Mini Canal | MICL.01125042/DBL | 11 | 250 | 42 | 42 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01125042/DBL
Build-In Floor | Mini Canal | MICL.01125042/DBN | 11 | 250 | 42 | 42 | 1306 | 1306 | 1306 | 0.031095 | 508 | 0.012095 | 1488 | 0.035429 | 1.362 | A04 | MICL0.01125042/DBN
Build-In Floor | Mini Canal | MICL.01125042/DBR | 11 | 250 | 42 | 42 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01125042/DBR
Build-In Floor | Mini Canal | MICL.01125042/DBV | 11 | 250 | 42 | 42 | 1306 | 1306 | 1306 | 0.031095 | 508 | 0.012095 | 1488 | 0.035429 | 1.362 | A04 | MICL0.01125042/DBV
Build-In Floor | Mini Canal | MICL.01125042/DDB | 11 | 250 | 42 | 42 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01125042/DDB
Build-In Floor | Mini Canal | MICL.01125042/DMN | 11 | 250 | 42 | 42 | 1306 | 1306 | 1306 | 0.031095 | 508 | 0.012095 | 1488 | 0.035429 | 1.362 | A04 | MICL0.01125042/DMN
Build-In Floor | Mini Canal | MICL.01125042/DMV | 11 | 250 | 42 | 42 | 1306 | 1306 | 1306 | 0.031095 | 508 | 0.012095 | 1488 | 0.035429 | 1.362 | A04 | MICL0.01125042/DMV
Build-In Floor | Mini Canal | MICL.01125042/DNA | 11 | 250 | 42 | 42 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01125042/DNA
Build-In Floor | Mini Canal | MICL.01125042/DNC | 11 | 250 | 42 | 42 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01125042/DNC
Build-In Floor | Mini Canal | MICL.01125042/DON | 11 | 250 | 42 | 42 | 1306 | 1306 | 1306 | 0.031095 | 508 | 0.012095 | 1488 | 0.035429 | 1.362 | A04 | MICL0.01125042/DON
Build-In Floor | Mini Canal | MICL.01125042/DOV | 11 | 250 | 42 | 42 | 1306 | 1306 | 1306 | 0.031095 | 508 | 0.012095 | 1488 | 0.035429 | 1.362 | A04 | MICL0.01125042/DOV
Build-In Floor | Mini Canal | MICL.01125042/PNC | 11 | 250 | 42 | 42 | 1193 | 1193 | 1193 | 0.028405 | 464 | 0.011048 | 1359 | 0.032357 | 1.362 | A04 | MICL0.01125042/PNC
Build-In Floor | Mini Canal | MICL.01125042/RBL | 11 | 250 | 42 | 42 | 1404 | 1404 | 1404 | 0.033429 | 546 | 0.013 | 1599 | 0.038071 | 1.362 | A04 | MICL0.01125042/RBL
Build-In Floor | Mini Canal | MICL.01125042/RBN | 11 | 250 | 42 | 42 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01125042/RBN
Build-In Floor | Mini Canal | MICL.01125042/RBR | 11 | 250 | 42 | 42 | 1404 | 1404 | 1404 | 0.033429 | 546 | 0.013 | 1599 | 0.038071 | 1.362 | A04 | MICL0.01125042/RBR
Build-In Floor | Mini Canal | MICL.01125042/RBV | 11 | 250 | 42 | 42 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01125042/RBV
Build-In Floor | Mini Canal | MICL.01125042/RDB | 11 | 250 | 42 | 42 | 1404 | 1404 | 1404 | 0.033429 | 546 | 0.013 | 1599 | 0.038071 | 1.362 | A04 | MICL0.01125042/RDB
Build-In Floor | Mini Canal | MICL.01125042/RMN | 11 | 250 | 42 | 42 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01125042/RMN
Build-In Floor | Mini Canal | MICL.01125042/RMV | 11 | 250 | 42 | 42 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01125042/RMV
Build-In Floor | Mini Canal | MICL.01125042/RNA | 11 | 250 | 42 | 42 | 1404 | 1404 | 1404 | 0.033429 | 546 | 0.013 | 1599 | 0.038071 | 1.362 | A04 | MICL0.01125042/RNA
Build-In Floor | Mini Canal | MICL.01125042/RON | 11 | 250 | 42 | 42 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01125042/RON
Build-In Floor | Mini Canal | MICL.01125042/ROV | 11 | 250 | 42 | 42 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01125042/ROV
Build-In Floor | Mini Canal | MICL.01125042/RSS | 11 | 250 | 42 | 42 | 1348 | 1348 | 1348 | 0.032095 | 524 | 0.012476 | 1535 | 0.036548 | 1.362 | A04 | MICL0.01125042/RSS
Build-In Floor | Mini Canal | MICL.01125042/SBL | 11 | 250 | 42 | 42 | 1404 | 1404 | 1404 | 0.033429 | 546 | 0.013 | 1599 | 0.038071 | 1.362 | A04 | MICL0.01125042/SBL
Build-In Floor | Mini Canal | MICL.01125042/SBR | 11 | 250 | 42 | 42 | 1404 | 1404 | 1404 | 0.033429 | 546 | 0.013 | 1599 | 0.038071 | 1.362 | A04 | MICL0.01125042/SBR
Build-In Floor | Mini Canal | MICL.01125042/SDB | 11 | 250 | 42 | 42 | 1404 | 1404 | 1404 | 0.033429 | 546 | 0.013 | 1599 | 0.038071 | 1.362 | A04 | MICL0.01125042/SDB
Build-In Floor | Mini Canal | MICL.01125042/SNA | 11 | 250 | 42 | 42 | 1404 | 1404 | 1404 | 0.033429 | 546 | 0.013 | 1599 | 0.038071 | 1.362 | A04 | MICL0.01125042/SNA
Build-In Floor | Mini Canal | MICL.01125042/SNC | 11 | 250 | 42 | 42 | 1404 | 1404 | 1404 | 0.033429 | 546 | 0.013 | 1599 | 0.038071 | 1.362 | A04 | MICL0.01125042/SNC
Build-In Floor | Mini Canal | MICL.01127014/ANA | 11 | 270 | 14 | 14 | 393 | 393 | 393 | 0.0093571 | 153 | 0.0036429 | 448 | 0.010667 | 1.362 | A04 | MICL0.01127014/ANA
Build-In Floor | Mini Canal | MICL.01127014/DBL | 11 | 270 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01127014/DBL
Build-In Floor | Mini Canal | MICL.01127014/DBN | 11 | 270 | 14 | 14 | 487 | 487 | 487 | 0.011595 | 189 | 0.0045 | 555 | 0.013214 | 1.362 | A04 | MICL0.01127014/DBN
Build-In Floor | Mini Canal | MICL.01127014/DBR | 11 | 270 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01127014/DBR
Build-In Floor | Mini Canal | MICL.01127014/DBV | 11 | 270 | 14 | 14 | 487 | 487 | 487 | 0.011595 | 189 | 0.0045 | 555 | 0.013214 | 1.362 | A04 | MICL0.01127014/DBV
Build-In Floor | Mini Canal | MICL.01127014/DDB | 11 | 270 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01127014/DDB
Build-In Floor | Mini Canal | MICL.01127014/DMN | 11 | 270 | 14 | 14 | 487 | 487 | 487 | 0.011595 | 189 | 0.0045 | 555 | 0.013214 | 1.362 | A04 | MICL0.01127014/DMN
Build-In Floor | Mini Canal | MICL.01127014/DMV | 11 | 270 | 14 | 14 | 487 | 487 | 487 | 0.011595 | 189 | 0.0045 | 555 | 0.013214 | 1.362 | A04 | MICL0.01127014/DMV
Build-In Floor | Mini Canal | MICL.01127014/DNA | 11 | 270 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01127014/DNA
Build-In Floor | Mini Canal | MICL.01127014/DNC | 11 | 270 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01127014/DNC
Build-In Floor | Mini Canal | MICL.01127014/DON | 11 | 270 | 14 | 14 | 487 | 487 | 487 | 0.011595 | 189 | 0.0045 | 555 | 0.013214 | 1.362 | A04 | MICL0.01127014/DON
Build-In Floor | Mini Canal | MICL.01127014/DOV | 11 | 270 | 14 | 14 | 487 | 487 | 487 | 0.011595 | 189 | 0.0045 | 555 | 0.013214 | 1.362 | A04 | MICL0.01127014/DOV
Build-In Floor | Mini Canal | MICL.01127014/RBL | 11 | 270 | 14 | 14 | 524 | 524 | 524 | 0.012476 | 204 | 0.0048571 | 597 | 0.014214 | 1.362 | A04 | MICL0.01127014/RBL
Build-In Floor | Mini Canal | MICL.01127014/RBN | 11 | 270 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01127014/RBN
Build-In Floor | Mini Canal | MICL.01127014/RBR | 11 | 270 | 14 | 14 | 524 | 524 | 524 | 0.012476 | 204 | 0.0048571 | 597 | 0.014214 | 1.362 | A04 | MICL0.01127014/RBR
Build-In Floor | Mini Canal | MICL.01127014/RBV | 11 | 270 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01127014/RBV
Build-In Floor | Mini Canal | MICL.01127014/RDB | 11 | 270 | 14 | 14 | 524 | 524 | 524 | 0.012476 | 204 | 0.0048571 | 597 | 0.014214 | 1.362 | A04 | MICL0.01127014/RDB
Build-In Floor | Mini Canal | MICL.01127014/RMN | 11 | 270 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01127014/RMN
Build-In Floor | Mini Canal | MICL.01127014/RMV | 11 | 270 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01127014/RMV
Build-In Floor | Mini Canal | MICL.01127014/RNA | 11 | 270 | 14 | 14 | 524 | 524 | 524 | 0.012476 | 204 | 0.0048571 | 597 | 0.014214 | 1.362 | A04 | MICL0.01127014/RNA
Build-In Floor | Mini Canal | MICL.01127014/RON | 11 | 270 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01127014/RON
Build-In Floor | Mini Canal | MICL.01127014/ROV | 11 | 270 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01127014/ROV
Build-In Floor | Mini Canal | MICL.01127014/RSS | 11 | 270 | 14 | 14 | 503 | 503 | 503 | 0.011976 | 196 | 0.0046667 | 573 | 0.013643 | 1.362 | A04 | MICL0.01127014/RSS
Build-In Floor | Mini Canal | MICL.01127014/SBL | 11 | 270 | 14 | 14 | 524 | 524 | 524 | 0.012476 | 204 | 0.0048571 | 597 | 0.014214 | 1.362 | A04 | MICL0.01127014/SBL
Build-In Floor | Mini Canal | MICL.01127014/SBR | 11 | 270 | 14 | 14 | 524 | 524 | 524 | 0.012476 | 204 | 0.0048571 | 597 | 0.014214 | 1.362 | A04 | MICL0.01127014/SBR
Build-In Floor | Mini Canal | MICL.01127014/SDB | 11 | 270 | 14 | 14 | 524 | 524 | 524 | 0.012476 | 204 | 0.0048571 | 597 | 0.014214 | 1.362 | A04 | MICL0.01127014/SDB
Build-In Floor | Mini Canal | MICL.01127014/SNA | 11 | 270 | 14 | 14 | 524 | 524 | 524 | 0.012476 | 204 | 0.0048571 | 597 | 0.014214 | 1.362 | A04 | MICL0.01127014/SNA
Build-In Floor | Mini Canal | MICL.01127014/SNC | 11 | 270 | 14 | 14 | 524 | 524 | 524 | 0.012476 | 204 | 0.0048571 | 597 | 0.014214 | 1.362 | A04 | MICL0.01127014/SNC
Build-In Floor | Mini Canal | MICL.01127018/ANA | 11 | 270 | 18 | 18 | 467 | 467 | 467 | 0.011119 | 182 | 0.0043333 | 532 | 0.012667 | 1.362 | A04 | MICL0.01127018/ANA
Build-In Floor | Mini Canal | MICL.01127018/DBL | 11 | 270 | 18 | 18 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01127018/DBL
Build-In Floor | Mini Canal | MICL.01127018/DBN | 11 | 270 | 18 | 18 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01127018/DBN
Build-In Floor | Mini Canal | MICL.01127018/DBR | 11 | 270 | 18 | 18 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01127018/DBR
Build-In Floor | Mini Canal | MICL.01127018/DBV | 11 | 270 | 18 | 18 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01127018/DBV
Build-In Floor | Mini Canal | MICL.01127018/DDB | 11 | 270 | 18 | 18 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01127018/DDB
Build-In Floor | Mini Canal | MICL.01127018/DMN | 11 | 270 | 18 | 18 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01127018/DMN
Build-In Floor | Mini Canal | MICL.01127018/DMV | 11 | 270 | 18 | 18 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01127018/DMV
Build-In Floor | Mini Canal | MICL.01127018/DNA | 11 | 270 | 18 | 18 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01127018/DNA
Build-In Floor | Mini Canal | MICL.01127018/DNC | 11 | 270 | 18 | 18 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01127018/DNC
Build-In Floor | Mini Canal | MICL.01127018/DON | 11 | 270 | 18 | 18 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01127018/DON
Build-In Floor | Mini Canal | MICL.01127018/DOV | 11 | 270 | 18 | 18 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01127018/DOV
Build-In Floor | Mini Canal | MICL.01127018/RBL | 11 | 270 | 18 | 18 | 622 | 622 | 622 | 0.01481 | 242 | 0.0057619 | 708 | 0.016857 | 1.362 | A04 | MICL0.01127018/RBL
Build-In Floor | Mini Canal | MICL.01127018/RBN | 11 | 270 | 18 | 18 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01127018/RBN
Build-In Floor | Mini Canal | MICL.01127018/RBR | 11 | 270 | 18 | 18 | 622 | 622 | 622 | 0.01481 | 242 | 0.0057619 | 708 | 0.016857 | 1.362 | A04 | MICL0.01127018/RBR
Build-In Floor | Mini Canal | MICL.01127018/RBV | 11 | 270 | 18 | 18 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01127018/RBV
Build-In Floor | Mini Canal | MICL.01127018/RDB | 11 | 270 | 18 | 18 | 622 | 622 | 622 | 0.01481 | 242 | 0.0057619 | 708 | 0.016857 | 1.362 | A04 | MICL0.01127018/RDB
Build-In Floor | Mini Canal | MICL.01127018/RMN | 11 | 270 | 18 | 18 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01127018/RMN
Build-In Floor | Mini Canal | MICL.01127018/RMV | 11 | 270 | 18 | 18 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01127018/RMV
Build-In Floor | Mini Canal | MICL.01127018/RNA | 11 | 270 | 18 | 18 | 622 | 622 | 622 | 0.01481 | 242 | 0.0057619 | 708 | 0.016857 | 1.362 | A04 | MICL0.01127018/RNA
Build-In Floor | Mini Canal | MICL.01127018/RON | 11 | 270 | 18 | 18 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01127018/RON
Build-In Floor | Mini Canal | MICL.01127018/ROV | 11 | 270 | 18 | 18 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01127018/ROV
Build-In Floor | Mini Canal | MICL.01127018/RSS | 11 | 270 | 18 | 18 | 597 | 597 | 597 | 0.014214 | 232 | 0.0055238 | 680 | 0.01619 | 1.362 | A04 | MICL0.01127018/RSS
Build-In Floor | Mini Canal | MICL.01127018/SBL | 11 | 270 | 18 | 18 | 622 | 622 | 622 | 0.01481 | 242 | 0.0057619 | 708 | 0.016857 | 1.362 | A04 | MICL0.01127018/SBL
Build-In Floor | Mini Canal | MICL.01127018/SBR | 11 | 270 | 18 | 18 | 622 | 622 | 622 | 0.01481 | 242 | 0.0057619 | 708 | 0.016857 | 1.362 | A04 | MICL0.01127018/SBR
Build-In Floor | Mini Canal | MICL.01127018/SDB | 11 | 270 | 18 | 18 | 622 | 622 | 622 | 0.01481 | 242 | 0.0057619 | 708 | 0.016857 | 1.362 | A04 | MICL0.01127018/SDB
Build-In Floor | Mini Canal | MICL.01127018/SNA | 11 | 270 | 18 | 18 | 622 | 622 | 622 | 0.01481 | 242 | 0.0057619 | 708 | 0.016857 | 1.362 | A04 | MICL0.01127018/SNA
Build-In Floor | Mini Canal | MICL.01127018/SNC | 11 | 270 | 18 | 18 | 622 | 622 | 622 | 0.01481 | 242 | 0.0057619 | 708 | 0.016857 | 1.362 | A04 | MICL0.01127018/SNC
Build-In Floor | Mini Canal | MICL.01127026/ANA | 11 | 270 | 26 | 26 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.01127026/ANA
Build-In Floor | Mini Canal | MICL.01127026/DBL | 11 | 270 | 26 | 26 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.01127026/DBL
Build-In Floor | Mini Canal | MICL.01127026/DBN | 11 | 270 | 26 | 26 | 780 | 780 | 780 | 0.018571 | 303 | 0.0072143 | 888 | 0.021143 | 1.362 | A04 | MICL0.01127026/DBN
Build-In Floor | Mini Canal | MICL.01127026/DBR | 11 | 270 | 26 | 26 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.01127026/DBR
Build-In Floor | Mini Canal | MICL.01127026/DBV | 11 | 270 | 26 | 26 | 780 | 780 | 780 | 0.018571 | 303 | 0.0072143 | 888 | 0.021143 | 1.362 | A04 | MICL0.01127026/DBV
Build-In Floor | Mini Canal | MICL.01127026/DDB | 11 | 270 | 26 | 26 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.01127026/DDB
Build-In Floor | Mini Canal | MICL.01127026/DMN | 11 | 270 | 26 | 26 | 780 | 780 | 780 | 0.018571 | 303 | 0.0072143 | 888 | 0.021143 | 1.362 | A04 | MICL0.01127026/DMN
Build-In Floor | Mini Canal | MICL.01127026/DMV | 11 | 270 | 26 | 26 | 780 | 780 | 780 | 0.018571 | 303 | 0.0072143 | 888 | 0.021143 | 1.362 | A04 | MICL0.01127026/DMV
Build-In Floor | Mini Canal | MICL.01127026/DNA | 11 | 270 | 26 | 26 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.01127026/DNA
Build-In Floor | Mini Canal | MICL.01127026/DNC | 11 | 270 | 26 | 26 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.01127026/DNC
Build-In Floor | Mini Canal | MICL.01127026/DON | 11 | 270 | 26 | 26 | 780 | 780 | 780 | 0.018571 | 303 | 0.0072143 | 888 | 0.021143 | 1.362 | A04 | MICL0.01127026/DON
Build-In Floor | Mini Canal | MICL.01127026/DOV | 11 | 270 | 26 | 26 | 780 | 780 | 780 | 0.018571 | 303 | 0.0072143 | 888 | 0.021143 | 1.362 | A04 | MICL0.01127026/DOV
Build-In Floor | Mini Canal | MICL.01127026/PNC | 11 | 270 | 26 | 26 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.01127026/PNC
Build-In Floor | Mini Canal | MICL.01127026/RBL | 11 | 270 | 26 | 26 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.01127026/RBL
Build-In Floor | Mini Canal | MICL.01127026/RBN | 11 | 270 | 26 | 26 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.01127026/RBN
Build-In Floor | Mini Canal | MICL.01127026/RBR | 11 | 270 | 26 | 26 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.01127026/RBR
Build-In Floor | Mini Canal | MICL.01127026/RBV | 11 | 270 | 26 | 26 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.01127026/RBV
Build-In Floor | Mini Canal | MICL.01127026/RDB | 11 | 270 | 26 | 26 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.01127026/RDB
Build-In Floor | Mini Canal | MICL.01127026/RMN | 11 | 270 | 26 | 26 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.01127026/RMN
Build-In Floor | Mini Canal | MICL.01127026/RMV | 11 | 270 | 26 | 26 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.01127026/RMV
Build-In Floor | Mini Canal | MICL.01127026/RNA | 11 | 270 | 26 | 26 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.01127026/RNA
Build-In Floor | Mini Canal | MICL.01127026/RON | 11 | 270 | 26 | 26 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.01127026/RON
Build-In Floor | Mini Canal | MICL.01127026/ROV | 11 | 270 | 26 | 26 | 814 | 814 | 814 | 0.019381 | 317 | 0.0075476 | 927 | 0.022071 | 1.362 | A04 | MICL0.01127026/ROV
Build-In Floor | Mini Canal | MICL.01127026/RSS | 11 | 270 | 26 | 26 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.01127026/RSS
Build-In Floor | Mini Canal | MICL.01127026/SBL | 11 | 270 | 26 | 26 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.01127026/SBL
Build-In Floor | Mini Canal | MICL.01127026/SBR | 11 | 270 | 26 | 26 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.01127026/SBR
Build-In Floor | Mini Canal | MICL.01127026/SDB | 11 | 270 | 26 | 26 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.01127026/SDB
Build-In Floor | Mini Canal | MICL.01127026/SNA | 11 | 270 | 26 | 26 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.01127026/SNA
Build-In Floor | Mini Canal | MICL.01127026/SNC | 11 | 270 | 26 | 26 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.01127026/SNC
Build-In Floor | Mini Canal | MICL.01127034/ANA | 11 | 270 | 34 | 34 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01127034/ANA
Build-In Floor | Mini Canal | MICL.01127034/DBL | 11 | 270 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01127034/DBL
Build-In Floor | Mini Canal | MICL.01127034/DBN | 11 | 270 | 34 | 34 | 1014 | 1014 | 1014 | 0.024143 | 394 | 0.009381 | 1155 | 0.0275 | 1.362 | A04 | MICL0.01127034/DBN
Build-In Floor | Mini Canal | MICL.01127034/DBR | 11 | 270 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01127034/DBR
Build-In Floor | Mini Canal | MICL.01127034/DBV | 11 | 270 | 34 | 34 | 1014 | 1014 | 1014 | 0.024143 | 394 | 0.009381 | 1155 | 0.0275 | 1.362 | A04 | MICL0.01127034/DBV
Build-In Floor | Mini Canal | MICL.01127034/DDB | 11 | 270 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01127034/DDB
Build-In Floor | Mini Canal | MICL.01127034/DMN | 11 | 270 | 34 | 34 | 1014 | 1014 | 1014 | 0.024143 | 394 | 0.009381 | 1155 | 0.0275 | 1.362 | A04 | MICL0.01127034/DMN
Build-In Floor | Mini Canal | MICL.01127034/DMV | 11 | 270 | 34 | 34 | 1014 | 1014 | 1014 | 0.024143 | 394 | 0.009381 | 1155 | 0.0275 | 1.362 | A04 | MICL0.01127034/DMV
Build-In Floor | Mini Canal | MICL.01127034/DNA | 11 | 270 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01127034/DNA
Build-In Floor | Mini Canal | MICL.01127034/DNC | 11 | 270 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01127034/DNC
Build-In Floor | Mini Canal | MICL.01127034/DON | 11 | 270 | 34 | 34 | 1014 | 1014 | 1014 | 0.024143 | 394 | 0.009381 | 1155 | 0.0275 | 1.362 | A04 | MICL0.01127034/DON
Build-In Floor | Mini Canal | MICL.01127034/DOV | 11 | 270 | 34 | 34 | 1014 | 1014 | 1014 | 0.024143 | 394 | 0.009381 | 1155 | 0.0275 | 1.362 | A04 | MICL0.01127034/DOV
Build-In Floor | Mini Canal | MICL.01127034/PNC | 11 | 270 | 34 | 34 | 927 | 927 | 927 | 0.022071 | 361 | 0.0085952 | 1056 | 0.025143 | 1.362 | A04 | MICL0.01127034/PNC
Build-In Floor | Mini Canal | MICL.01127034/RBL | 11 | 270 | 34 | 34 | 1090 | 1090 | 1090 | 0.025952 | 424 | 0.010095 | 1242 | 0.029571 | 1.362 | A04 | MICL0.01127034/RBL
Build-In Floor | Mini Canal | MICL.01127034/RBN | 11 | 270 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01127034/RBN
Build-In Floor | Mini Canal | MICL.01127034/RBR | 11 | 270 | 34 | 34 | 1090 | 1090 | 1090 | 0.025952 | 424 | 0.010095 | 1242 | 0.029571 | 1.362 | A04 | MICL0.01127034/RBR
Build-In Floor | Mini Canal | MICL.01127034/RBV | 11 | 270 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01127034/RBV
Build-In Floor | Mini Canal | MICL.01127034/RDB | 11 | 270 | 34 | 34 | 1090 | 1090 | 1090 | 0.025952 | 424 | 0.010095 | 1242 | 0.029571 | 1.362 | A04 | MICL0.01127034/RDB
Build-In Floor | Mini Canal | MICL.01127034/RMN | 11 | 270 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01127034/RMN
Build-In Floor | Mini Canal | MICL.01127034/RMV | 11 | 270 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01127034/RMV
Build-In Floor | Mini Canal | MICL.01127034/RNA | 11 | 270 | 34 | 34 | 1090 | 1090 | 1090 | 0.025952 | 424 | 0.010095 | 1242 | 0.029571 | 1.362 | A04 | MICL0.01127034/RNA
Build-In Floor | Mini Canal | MICL.01127034/RON | 11 | 270 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01127034/RON
Build-In Floor | Mini Canal | MICL.01127034/ROV | 11 | 270 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01127034/ROV
Build-In Floor | Mini Canal | MICL.01127034/RSS | 11 | 270 | 34 | 34 | 1046 | 1046 | 1046 | 0.024905 | 407 | 0.0096905 | 1191 | 0.028357 | 1.362 | A04 | MICL0.01127034/RSS
Build-In Floor | Mini Canal | MICL.01127034/SBL | 11 | 270 | 34 | 34 | 1090 | 1090 | 1090 | 0.025952 | 424 | 0.010095 | 1242 | 0.029571 | 1.362 | A04 | MICL0.01127034/SBL
Build-In Floor | Mini Canal | MICL.01127034/SBR | 11 | 270 | 34 | 34 | 1090 | 1090 | 1090 | 0.025952 | 424 | 0.010095 | 1242 | 0.029571 | 1.362 | A04 | MICL0.01127034/SBR
Build-In Floor | Mini Canal | MICL.01127034/SDB | 11 | 270 | 34 | 34 | 1090 | 1090 | 1090 | 0.025952 | 424 | 0.010095 | 1242 | 0.029571 | 1.362 | A04 | MICL0.01127034/SDB
Build-In Floor | Mini Canal | MICL.01127034/SNA | 11 | 270 | 34 | 34 | 1090 | 1090 | 1090 | 0.025952 | 424 | 0.010095 | 1242 | 0.029571 | 1.362 | A04 | MICL0.01127034/SNA
Build-In Floor | Mini Canal | MICL.01127034/SNC | 11 | 270 | 34 | 34 | 1090 | 1090 | 1090 | 0.025952 | 424 | 0.010095 | 1242 | 0.029571 | 1.362 | A04 | MICL0.01127034/SNC
Build-In Floor | Mini Canal | MICL.01127042/ANA | 11 | 270 | 42 | 42 | 1148 | 1148 | 1148 | 0.027333 | 447 | 0.010643 | 1308 | 0.031143 | 1.362 | A04 | MICL0.01127042/ANA
Build-In Floor | Mini Canal | MICL.01127042/DBL | 11 | 270 | 42 | 42 | 1485 | 1485 | 1485 | 0.035357 | 578 | 0.013762 | 1691 | 0.040262 | 1.362 | A04 | MICL0.01127042/DBL
Build-In Floor | Mini Canal | MICL.01127042/DBN | 11 | 270 | 42 | 42 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01127042/DBN
Build-In Floor | Mini Canal | MICL.01127042/DBR | 11 | 270 | 42 | 42 | 1485 | 1485 | 1485 | 0.035357 | 578 | 0.013762 | 1691 | 0.040262 | 1.362 | A04 | MICL0.01127042/DBR
Build-In Floor | Mini Canal | MICL.01127042/DBV | 11 | 270 | 42 | 42 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01127042/DBV
Build-In Floor | Mini Canal | MICL.01127042/DDB | 11 | 270 | 42 | 42 | 1485 | 1485 | 1485 | 0.035357 | 578 | 0.013762 | 1691 | 0.040262 | 1.362 | A04 | MICL0.01127042/DDB
Build-In Floor | Mini Canal | MICL.01127042/DMN | 11 | 270 | 42 | 42 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01127042/DMN
Build-In Floor | Mini Canal | MICL.01127042/DMV | 11 | 270 | 42 | 42 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01127042/DMV
Build-In Floor | Mini Canal | MICL.01127042/DNA | 11 | 270 | 42 | 42 | 1485 | 1485 | 1485 | 0.035357 | 578 | 0.013762 | 1691 | 0.040262 | 1.362 | A04 | MICL0.01127042/DNA
Build-In Floor | Mini Canal | MICL.01127042/DNC | 11 | 270 | 42 | 42 | 1485 | 1485 | 1485 | 0.035357 | 578 | 0.013762 | 1691 | 0.040262 | 1.362 | A04 | MICL0.01127042/DNC
Build-In Floor | Mini Canal | MICL.01127042/DON | 11 | 270 | 42 | 42 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01127042/DON
Build-In Floor | Mini Canal | MICL.01127042/DOV | 11 | 270 | 42 | 42 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01127042/DOV
Build-In Floor | Mini Canal | MICL.01127042/PNC | 11 | 270 | 42 | 42 | 1301 | 1301 | 1301 | 0.030976 | 506 | 0.012048 | 1482 | 0.035286 | 1.362 | A04 | MICL0.01127042/PNC
Build-In Floor | Mini Canal | MICL.01127042/RBL | 11 | 270 | 42 | 42 | 1531 | 1531 | 1531 | 0.036452 | 596 | 0.01419 | 1744 | 0.041524 | 1.362 | A04 | MICL0.01127042/RBL
Build-In Floor | Mini Canal | MICL.01127042/RBN | 11 | 270 | 42 | 42 | 1485 | 1485 | 1485 | 0.035357 | 578 | 0.013762 | 1691 | 0.040262 | 1.362 | A04 | MICL0.01127042/RBN
Build-In Floor | Mini Canal | MICL.01127042/RBR | 11 | 270 | 42 | 42 | 1531 | 1531 | 1531 | 0.036452 | 596 | 0.01419 | 1744 | 0.041524 | 1.362 | A04 | MICL0.01127042/RBR
Build-In Floor | Mini Canal | MICL.01127042/RBV | 11 | 270 | 42 | 42 | 1485 | 1485 | 1485 | 0.035357 | 578 | 0.013762 | 1691 | 0.040262 | 1.362 | A04 | MICL0.01127042/RBV
Build-In Floor | Mini Canal | MICL.01127042/RDB | 11 | 270 | 42 | 42 | 1531 | 1531 | 1531 | 0.036452 | 596 | 0.01419 | 1744 | 0.041524 | 1.362 | A04 | MICL0.01127042/RDB
Build-In Floor | Mini Canal | MICL.01127042/RMN | 11 | 270 | 42 | 42 | 1485 | 1485 | 1485 | 0.035357 | 578 | 0.013762 | 1691 | 0.040262 | 1.362 | A04 | MICL0.01127042/RMN
Build-In Floor | Mini Canal | MICL.01127042/RMV | 11 | 270 | 42 | 42 | 1485 | 1485 | 1485 | 0.035357 | 578 | 0.013762 | 1691 | 0.040262 | 1.362 | A04 | MICL0.01127042/RMV
Build-In Floor | Mini Canal | MICL.01127042/RNA | 11 | 270 | 42 | 42 | 1531 | 1531 | 1531 | 0.036452 | 596 | 0.01419 | 1744 | 0.041524 | 1.362 | A04 | MICL0.01127042/RNA
Build-In Floor | Mini Canal | MICL.01127042/RON | 11 | 270 | 42 | 42 | 1485 | 1485 | 1485 | 0.035357 | 578 | 0.013762 | 1691 | 0.040262 | 1.362 | A04 | MICL0.01127042/RON
Build-In Floor | Mini Canal | MICL.01127042/ROV | 11 | 270 | 42 | 42 | 1485 | 1485 | 1485 | 0.035357 | 578 | 0.013762 | 1691 | 0.040262 | 1.362 | A04 | MICL0.01127042/ROV
Build-In Floor | Mini Canal | MICL.01127042/RSS | 11 | 270 | 42 | 42 | 1470 | 1470 | 1470 | 0.035 | 572 | 0.013619 | 1674 | 0.039857 | 1.362 | A04 | MICL0.01127042/RSS
Build-In Floor | Mini Canal | MICL.01127042/SBL | 11 | 270 | 42 | 42 | 1531 | 1531 | 1531 | 0.036452 | 596 | 0.01419 | 1744 | 0.041524 | 1.362 | A04 | MICL0.01127042/SBL
Build-In Floor | Mini Canal | MICL.01127042/SBR | 11 | 270 | 42 | 42 | 1531 | 1531 | 1531 | 0.036452 | 596 | 0.01419 | 1744 | 0.041524 | 1.362 | A04 | MICL0.01127042/SBR
Build-In Floor | Mini Canal | MICL.01127042/SDB | 11 | 270 | 42 | 42 | 1531 | 1531 | 1531 | 0.036452 | 596 | 0.01419 | 1744 | 0.041524 | 1.362 | A04 | MICL0.01127042/SDB
Build-In Floor | Mini Canal | MICL.01127042/SNA | 11 | 270 | 42 | 42 | 1531 | 1531 | 1531 | 0.036452 | 596 | 0.01419 | 1744 | 0.041524 | 1.362 | A04 | MICL0.01127042/SNA
Build-In Floor | Mini Canal | MICL.01127042/SNC | 11 | 270 | 42 | 42 | 1531 | 1531 | 1531 | 0.036452 | 596 | 0.01419 | 1744 | 0.041524 | 1.362 | A04 | MICL0.01127042/SNC
Build-In Floor | Mini Canal | MICL.01129014/ANA | 11 | 290 | 14 | 14 | 426 | 426 | 426 | 0.010143 | 166 | 0.0039524 | 485 | 0.011548 | 1.362 | A04 | MICL0.01129014/ANA
Build-In Floor | Mini Canal | MICL.01129014/DBL | 11 | 290 | 14 | 14 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.01129014/DBL
Build-In Floor | Mini Canal | MICL.01129014/DBN | 11 | 290 | 14 | 14 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01129014/DBN
Build-In Floor | Mini Canal | MICL.01129014/DBR | 11 | 290 | 14 | 14 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.01129014/DBR
Build-In Floor | Mini Canal | MICL.01129014/DBV | 11 | 290 | 14 | 14 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01129014/DBV
Build-In Floor | Mini Canal | MICL.01129014/DDB | 11 | 290 | 14 | 14 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.01129014/DDB
Build-In Floor | Mini Canal | MICL.01129014/DMN | 11 | 290 | 14 | 14 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01129014/DMN
Build-In Floor | Mini Canal | MICL.01129014/DMV | 11 | 290 | 14 | 14 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01129014/DMV
Build-In Floor | Mini Canal | MICL.01129014/DNA | 11 | 290 | 14 | 14 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.01129014/DNA
Build-In Floor | Mini Canal | MICL.01129014/DNC | 11 | 290 | 14 | 14 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.01129014/DNC
Build-In Floor | Mini Canal | MICL.01129014/DON | 11 | 290 | 14 | 14 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01129014/DON
Build-In Floor | Mini Canal | MICL.01129014/DOV | 11 | 290 | 14 | 14 | 528 | 528 | 528 | 0.012571 | 205 | 0.004881 | 601 | 0.01431 | 1.362 | A04 | MICL0.01129014/DOV
Build-In Floor | Mini Canal | MICL.01129014/RBL | 11 | 290 | 14 | 14 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.01129014/RBL
Build-In Floor | Mini Canal | MICL.01129014/RBN | 11 | 290 | 14 | 14 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.01129014/RBN
Build-In Floor | Mini Canal | MICL.01129014/RBR | 11 | 290 | 14 | 14 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.01129014/RBR
Build-In Floor | Mini Canal | MICL.01129014/RBV | 11 | 290 | 14 | 14 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.01129014/RBV
Build-In Floor | Mini Canal | MICL.01129014/RDB | 11 | 290 | 14 | 14 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.01129014/RDB
Build-In Floor | Mini Canal | MICL.01129014/RMN | 11 | 290 | 14 | 14 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.01129014/RMN
Build-In Floor | Mini Canal | MICL.01129014/RMV | 11 | 290 | 14 | 14 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.01129014/RMV
Build-In Floor | Mini Canal | MICL.01129014/RNA | 11 | 290 | 14 | 14 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.01129014/RNA
Build-In Floor | Mini Canal | MICL.01129014/RON | 11 | 290 | 14 | 14 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.01129014/RON
Build-In Floor | Mini Canal | MICL.01129014/ROV | 11 | 290 | 14 | 14 | 551 | 551 | 551 | 0.013119 | 214 | 0.0050952 | 628 | 0.014952 | 1.362 | A04 | MICL0.01129014/ROV
Build-In Floor | Mini Canal | MICL.01129014/RSS | 11 | 290 | 14 | 14 | 545 | 545 | 545 | 0.012976 | 212 | 0.0050476 | 621 | 0.014786 | 1.362 | A04 | MICL0.01129014/RSS
Build-In Floor | Mini Canal | MICL.01129014/SBL | 11 | 290 | 14 | 14 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.01129014/SBL
Build-In Floor | Mini Canal | MICL.01129014/SBR | 11 | 290 | 14 | 14 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.01129014/SBR
Build-In Floor | Mini Canal | MICL.01129014/SDB | 11 | 290 | 14 | 14 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.01129014/SDB
Build-In Floor | Mini Canal | MICL.01129014/SNA | 11 | 290 | 14 | 14 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.01129014/SNA
Build-In Floor | Mini Canal | MICL.01129014/SNC | 11 | 290 | 14 | 14 | 568 | 568 | 568 | 0.013524 | 221 | 0.0052619 | 647 | 0.015405 | 1.362 | A04 | MICL0.01129014/SNC
Build-In Floor | Mini Canal | MICL.01129018/ANA | 11 | 290 | 18 | 18 | 505 | 505 | 505 | 0.012024 | 196 | 0.0046667 | 575 | 0.01369 | 1.362 | A04 | MICL0.01129018/ANA
Build-In Floor | Mini Canal | MICL.01129018/DBL | 11 | 290 | 18 | 18 | 653 | 653 | 653 | 0.015548 | 254 | 0.0060476 | 744 | 0.017714 | 1.362 | A04 | MICL0.01129018/DBL
Build-In Floor | Mini Canal | MICL.01129018/DBN | 11 | 290 | 18 | 18 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01129018/DBN
Build-In Floor | Mini Canal | MICL.01129018/DBR | 11 | 290 | 18 | 18 | 653 | 653 | 653 | 0.015548 | 254 | 0.0060476 | 744 | 0.017714 | 1.362 | A04 | MICL0.01129018/DBR
Build-In Floor | Mini Canal | MICL.01129018/DBV | 11 | 290 | 18 | 18 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01129018/DBV
Build-In Floor | Mini Canal | MICL.01129018/DDB | 11 | 290 | 18 | 18 | 653 | 653 | 653 | 0.015548 | 254 | 0.0060476 | 744 | 0.017714 | 1.362 | A04 | MICL0.01129018/DDB
Build-In Floor | Mini Canal | MICL.01129018/DMN | 11 | 290 | 18 | 18 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01129018/DMN
Build-In Floor | Mini Canal | MICL.01129018/DMV | 11 | 290 | 18 | 18 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01129018/DMV
Build-In Floor | Mini Canal | MICL.01129018/DNA | 11 | 290 | 18 | 18 | 653 | 653 | 653 | 0.015548 | 254 | 0.0060476 | 744 | 0.017714 | 1.362 | A04 | MICL0.01129018/DNA
Build-In Floor | Mini Canal | MICL.01129018/DNC | 11 | 290 | 18 | 18 | 653 | 653 | 653 | 0.015548 | 254 | 0.0060476 | 744 | 0.017714 | 1.362 | A04 | MICL0.01129018/DNC
Build-In Floor | Mini Canal | MICL.01129018/DON | 11 | 290 | 18 | 18 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01129018/DON
Build-In Floor | Mini Canal | MICL.01129018/DOV | 11 | 290 | 18 | 18 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01129018/DOV
Build-In Floor | Mini Canal | MICL.01129018/RBL | 11 | 290 | 18 | 18 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01129018/RBL
Build-In Floor | Mini Canal | MICL.01129018/RBN | 11 | 290 | 18 | 18 | 653 | 653 | 653 | 0.015548 | 254 | 0.0060476 | 744 | 0.017714 | 1.362 | A04 | MICL0.01129018/RBN
Build-In Floor | Mini Canal | MICL.01129018/RBR | 11 | 290 | 18 | 18 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01129018/RBR
Build-In Floor | Mini Canal | MICL.01129018/RBV | 11 | 290 | 18 | 18 | 653 | 653 | 653 | 0.015548 | 254 | 0.0060476 | 744 | 0.017714 | 1.362 | A04 | MICL0.01129018/RBV
Build-In Floor | Mini Canal | MICL.01129018/RDB | 11 | 290 | 18 | 18 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01129018/RDB
Build-In Floor | Mini Canal | MICL.01129018/RMN | 11 | 290 | 18 | 18 | 653 | 653 | 653 | 0.015548 | 254 | 0.0060476 | 744 | 0.017714 | 1.362 | A04 | MICL0.01129018/RMN
Build-In Floor | Mini Canal | MICL.01129018/RMV | 11 | 290 | 18 | 18 | 653 | 653 | 653 | 0.015548 | 254 | 0.0060476 | 744 | 0.017714 | 1.362 | A04 | MICL0.01129018/RMV
Build-In Floor | Mini Canal | MICL.01129018/RNA | 11 | 290 | 18 | 18 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01129018/RNA
Build-In Floor | Mini Canal | MICL.01129018/RON | 11 | 290 | 18 | 18 | 653 | 653 | 653 | 0.015548 | 254 | 0.0060476 | 744 | 0.017714 | 1.362 | A04 | MICL0.01129018/RON
Build-In Floor | Mini Canal | MICL.01129018/ROV | 11 | 290 | 18 | 18 | 653 | 653 | 653 | 0.015548 | 254 | 0.0060476 | 744 | 0.017714 | 1.362 | A04 | MICL0.01129018/ROV
Build-In Floor | Mini Canal | MICL.01129018/RSS | 11 | 290 | 18 | 18 | 646 | 646 | 646 | 0.015381 | 251 | 0.0059762 | 736 | 0.017524 | 1.362 | A04 | MICL0.01129018/RSS
Build-In Floor | Mini Canal | MICL.01129018/SBL | 11 | 290 | 18 | 18 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01129018/SBL
Build-In Floor | Mini Canal | MICL.01129018/SBR | 11 | 290 | 18 | 18 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01129018/SBR
Build-In Floor | Mini Canal | MICL.01129018/SDB | 11 | 290 | 18 | 18 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01129018/SDB
Build-In Floor | Mini Canal | MICL.01129018/SNA | 11 | 290 | 18 | 18 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01129018/SNA
Build-In Floor | Mini Canal | MICL.01129018/SNC | 11 | 290 | 18 | 18 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01129018/SNC
Build-In Floor | Mini Canal | MICL.01129026/ANA | 11 | 290 | 26 | 26 | 682 | 682 | 682 | 0.016238 | 265 | 0.0063095 | 777 | 0.0185 | 1.362 | A04 | MICL0.01129026/ANA
Build-In Floor | Mini Canal | MICL.01129026/DBL | 11 | 290 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01129026/DBL
Build-In Floor | Mini Canal | MICL.01129026/DBN | 11 | 290 | 26 | 26 | 845 | 845 | 845 | 0.020119 | 329 | 0.0078333 | 962 | 0.022905 | 1.362 | A04 | MICL0.01129026/DBN
Build-In Floor | Mini Canal | MICL.01129026/DBR | 11 | 290 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01129026/DBR
Build-In Floor | Mini Canal | MICL.01129026/DBV | 11 | 290 | 26 | 26 | 845 | 845 | 845 | 0.020119 | 329 | 0.0078333 | 962 | 0.022905 | 1.362 | A04 | MICL0.01129026/DBV
Build-In Floor | Mini Canal | MICL.01129026/DDB | 11 | 290 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01129026/DDB
Build-In Floor | Mini Canal | MICL.01129026/DMN | 11 | 290 | 26 | 26 | 845 | 845 | 845 | 0.020119 | 329 | 0.0078333 | 962 | 0.022905 | 1.362 | A04 | MICL0.01129026/DMN
Build-In Floor | Mini Canal | MICL.01129026/DMV | 11 | 290 | 26 | 26 | 845 | 845 | 845 | 0.020119 | 329 | 0.0078333 | 962 | 0.022905 | 1.362 | A04 | MICL0.01129026/DMV
Build-In Floor | Mini Canal | MICL.01129026/DNA | 11 | 290 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01129026/DNA
Build-In Floor | Mini Canal | MICL.01129026/DNC | 11 | 290 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01129026/DNC
Build-In Floor | Mini Canal | MICL.01129026/DON | 11 | 290 | 26 | 26 | 845 | 845 | 845 | 0.020119 | 329 | 0.0078333 | 962 | 0.022905 | 1.362 | A04 | MICL0.01129026/DON
Build-In Floor | Mini Canal | MICL.01129026/DOV | 11 | 290 | 26 | 26 | 845 | 845 | 845 | 0.020119 | 329 | 0.0078333 | 962 | 0.022905 | 1.362 | A04 | MICL0.01129026/DOV
Build-In Floor | Mini Canal | MICL.01129026/PNC | 11 | 290 | 26 | 26 | 773 | 773 | 773 | 0.018405 | 301 | 0.0071667 | 880 | 0.020952 | 1.362 | A04 | MICL0.01129026/PNC
Build-In Floor | Mini Canal | MICL.01129026/RBL | 11 | 290 | 26 | 26 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01129026/RBL
Build-In Floor | Mini Canal | MICL.01129026/RBN | 11 | 290 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01129026/RBN
Build-In Floor | Mini Canal | MICL.01129026/RBR | 11 | 290 | 26 | 26 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01129026/RBR
Build-In Floor | Mini Canal | MICL.01129026/RBV | 11 | 290 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01129026/RBV
Build-In Floor | Mini Canal | MICL.01129026/RDB | 11 | 290 | 26 | 26 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01129026/RDB
Build-In Floor | Mini Canal | MICL.01129026/RMN | 11 | 290 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01129026/RMN
Build-In Floor | Mini Canal | MICL.01129026/RMV | 11 | 290 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01129026/RMV
Build-In Floor | Mini Canal | MICL.01129026/RNA | 11 | 290 | 26 | 26 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01129026/RNA
Build-In Floor | Mini Canal | MICL.01129026/RON | 11 | 290 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01129026/RON
Build-In Floor | Mini Canal | MICL.01129026/ROV | 11 | 290 | 26 | 26 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01129026/ROV
Build-In Floor | Mini Canal | MICL.01129026/RSS | 11 | 290 | 26 | 26 | 873 | 873 | 873 | 0.020786 | 340 | 0.0080952 | 994 | 0.023667 | 1.362 | A04 | MICL0.01129026/RSS
Build-In Floor | Mini Canal | MICL.01129026/SBL | 11 | 290 | 26 | 26 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01129026/SBL
Build-In Floor | Mini Canal | MICL.01129026/SBR | 11 | 290 | 26 | 26 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01129026/SBR
Build-In Floor | Mini Canal | MICL.01129026/SDB | 11 | 290 | 26 | 26 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01129026/SDB
Build-In Floor | Mini Canal | MICL.01129026/SNA | 11 | 290 | 26 | 26 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01129026/SNA
Build-In Floor | Mini Canal | MICL.01129026/SNC | 11 | 290 | 26 | 26 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01129026/SNC
Build-In Floor | Mini Canal | MICL.01129034/ANA | 11 | 290 | 34 | 34 | 885 | 885 | 885 | 0.021071 | 344 | 0.0081905 | 1008 | 0.024 | 1.362 | A04 | MICL0.01129034/ANA
Build-In Floor | Mini Canal | MICL.01129034/DBL | 11 | 290 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.01129034/DBL
Build-In Floor | Mini Canal | MICL.01129034/DBN | 11 | 290 | 34 | 34 | 1097 | 1097 | 1097 | 0.026119 | 427 | 0.010167 | 1249 | 0.029738 | 1.362 | A04 | MICL0.01129034/DBN
Build-In Floor | Mini Canal | MICL.01129034/DBR | 11 | 290 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.01129034/DBR
Build-In Floor | Mini Canal | MICL.01129034/DBV | 11 | 290 | 34 | 34 | 1097 | 1097 | 1097 | 0.026119 | 427 | 0.010167 | 1249 | 0.029738 | 1.362 | A04 | MICL0.01129034/DBV
Build-In Floor | Mini Canal | MICL.01129034/DDB | 11 | 290 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.01129034/DDB
Build-In Floor | Mini Canal | MICL.01129034/DMN | 11 | 290 | 34 | 34 | 1097 | 1097 | 1097 | 0.026119 | 427 | 0.010167 | 1249 | 0.029738 | 1.362 | A04 | MICL0.01129034/DMN
Build-In Floor | Mini Canal | MICL.01129034/DMV | 11 | 290 | 34 | 34 | 1097 | 1097 | 1097 | 0.026119 | 427 | 0.010167 | 1249 | 0.029738 | 1.362 | A04 | MICL0.01129034/DMV
Build-In Floor | Mini Canal | MICL.01129034/DNA | 11 | 290 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.01129034/DNA
Build-In Floor | Mini Canal | MICL.01129034/DNC | 11 | 290 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.01129034/DNC
Build-In Floor | Mini Canal | MICL.01129034/DON | 11 | 290 | 34 | 34 | 1097 | 1097 | 1097 | 0.026119 | 427 | 0.010167 | 1249 | 0.029738 | 1.362 | A04 | MICL0.01129034/DON
Build-In Floor | Mini Canal | MICL.01129034/DOV | 11 | 290 | 34 | 34 | 1097 | 1097 | 1097 | 0.026119 | 427 | 0.010167 | 1249 | 0.029738 | 1.362 | A04 | MICL0.01129034/DOV
Build-In Floor | Mini Canal | MICL.01129034/PNC | 11 | 290 | 34 | 34 | 1003 | 1003 | 1003 | 0.023881 | 390 | 0.0092857 | 1142 | 0.02719 | 1.362 | A04 | MICL0.01129034/PNC
Build-In Floor | Mini Canal | MICL.01129034/RBL | 11 | 290 | 34 | 34 | 1180 | 1180 | 1180 | 0.028095 | 459 | 0.010929 | 1344 | 0.032 | 1.362 | A04 | MICL0.01129034/RBL
Build-In Floor | Mini Canal | MICL.01129034/RBN | 11 | 290 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.01129034/RBN
Build-In Floor | Mini Canal | MICL.01129034/RBR | 11 | 290 | 34 | 34 | 1180 | 1180 | 1180 | 0.028095 | 459 | 0.010929 | 1344 | 0.032 | 1.362 | A04 | MICL0.01129034/RBR
Build-In Floor | Mini Canal | MICL.01129034/RBV | 11 | 290 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.01129034/RBV
Build-In Floor | Mini Canal | MICL.01129034/RDB | 11 | 290 | 34 | 34 | 1180 | 1180 | 1180 | 0.028095 | 459 | 0.010929 | 1344 | 0.032 | 1.362 | A04 | MICL0.01129034/RDB
Build-In Floor | Mini Canal | MICL.01129034/RMN | 11 | 290 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.01129034/RMN
Build-In Floor | Mini Canal | MICL.01129034/RMV | 11 | 290 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.01129034/RMV
Build-In Floor | Mini Canal | MICL.01129034/RNA | 11 | 290 | 34 | 34 | 1180 | 1180 | 1180 | 0.028095 | 459 | 0.010929 | 1344 | 0.032 | 1.362 | A04 | MICL0.01129034/RNA
Build-In Floor | Mini Canal | MICL.01129034/RON | 11 | 290 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.01129034/RON
Build-In Floor | Mini Canal | MICL.01129034/ROV | 11 | 290 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.01129034/ROV
Build-In Floor | Mini Canal | MICL.01129034/RSS | 11 | 290 | 34 | 34 | 1133 | 1133 | 1133 | 0.026976 | 441 | 0.0105 | 1290 | 0.030714 | 1.362 | A04 | MICL0.01129034/RSS
Build-In Floor | Mini Canal | MICL.01129034/SBL | 11 | 290 | 34 | 34 | 1180 | 1180 | 1180 | 0.028095 | 459 | 0.010929 | 1344 | 0.032 | 1.362 | A04 | MICL0.01129034/SBL
Build-In Floor | Mini Canal | MICL.01129034/SBR | 11 | 290 | 34 | 34 | 1180 | 1180 | 1180 | 0.028095 | 459 | 0.010929 | 1344 | 0.032 | 1.362 | A04 | MICL0.01129034/SBR
Build-In Floor | Mini Canal | MICL.01129034/SDB | 11 | 290 | 34 | 34 | 1180 | 1180 | 1180 | 0.028095 | 459 | 0.010929 | 1344 | 0.032 | 1.362 | A04 | MICL0.01129034/SDB
Build-In Floor | Mini Canal | MICL.01129034/SNA | 11 | 290 | 34 | 34 | 1180 | 1180 | 1180 | 0.028095 | 459 | 0.010929 | 1344 | 0.032 | 1.362 | A04 | MICL0.01129034/SNA
Build-In Floor | Mini Canal | MICL.01129034/SNC | 11 | 290 | 34 | 34 | 1180 | 1180 | 1180 | 0.028095 | 459 | 0.010929 | 1344 | 0.032 | 1.362 | A04 | MICL0.01129034/SNC
Build-In Floor | Mini Canal | MICL.01129042/ANA | 11 | 290 | 42 | 42 | 1244 | 1244 | 1244 | 0.029619 | 484 | 0.011524 | 1417 | 0.033738 | 1.362 | A04 | MICL0.01129042/ANA
Build-In Floor | Mini Canal | MICL.01129042/DBL | 11 | 290 | 42 | 42 | 1609 | 1609 | 1609 | 0.03831 | 626 | 0.014905 | 1833 | 0.043643 | 1.362 | A04 | MICL0.01129042/DBL
Build-In Floor | Mini Canal | MICL.01129042/DBN | 11 | 290 | 42 | 42 | 1543 | 1543 | 1543 | 0.036738 | 600 | 0.014286 | 1757 | 0.041833 | 1.362 | A04 | MICL0.01129042/DBN
Build-In Floor | Mini Canal | MICL.01129042/DBR | 11 | 290 | 42 | 42 | 1609 | 1609 | 1609 | 0.03831 | 626 | 0.014905 | 1833 | 0.043643 | 1.362 | A04 | MICL0.01129042/DBR
Build-In Floor | Mini Canal | MICL.01129042/DBV | 11 | 290 | 42 | 42 | 1543 | 1543 | 1543 | 0.036738 | 600 | 0.014286 | 1757 | 0.041833 | 1.362 | A04 | MICL0.01129042/DBV
Build-In Floor | Mini Canal | MICL.01129042/DDB | 11 | 290 | 42 | 42 | 1609 | 1609 | 1609 | 0.03831 | 626 | 0.014905 | 1833 | 0.043643 | 1.362 | A04 | MICL0.01129042/DDB
Build-In Floor | Mini Canal | MICL.01129042/DMN | 11 | 290 | 42 | 42 | 1543 | 1543 | 1543 | 0.036738 | 600 | 0.014286 | 1757 | 0.041833 | 1.362 | A04 | MICL0.01129042/DMN
Build-In Floor | Mini Canal | MICL.01129042/DMV | 11 | 290 | 42 | 42 | 1543 | 1543 | 1543 | 0.036738 | 600 | 0.014286 | 1757 | 0.041833 | 1.362 | A04 | MICL0.01129042/DMV
Build-In Floor | Mini Canal | MICL.01129042/DNA | 11 | 290 | 42 | 42 | 1609 | 1609 | 1609 | 0.03831 | 626 | 0.014905 | 1833 | 0.043643 | 1.362 | A04 | MICL0.01129042/DNA
Build-In Floor | Mini Canal | MICL.01129042/DNC | 11 | 290 | 42 | 42 | 1609 | 1609 | 1609 | 0.03831 | 626 | 0.014905 | 1833 | 0.043643 | 1.362 | A04 | MICL0.01129042/DNC
Build-In Floor | Mini Canal | MICL.01129042/DON | 11 | 290 | 42 | 42 | 1543 | 1543 | 1543 | 0.036738 | 600 | 0.014286 | 1757 | 0.041833 | 1.362 | A04 | MICL0.01129042/DON
Build-In Floor | Mini Canal | MICL.01129042/DOV | 11 | 290 | 42 | 42 | 1543 | 1543 | 1543 | 0.036738 | 600 | 0.014286 | 1757 | 0.041833 | 1.362 | A04 | MICL0.01129042/DOV
Build-In Floor | Mini Canal | MICL.01129042/PNC | 11 | 290 | 42 | 42 | 1410 | 1410 | 1410 | 0.033571 | 548 | 0.013048 | 1606 | 0.038238 | 1.362 | A04 | MICL0.01129042/PNC
Build-In Floor | Mini Canal | MICL.01129042/RBL | 11 | 290 | 42 | 42 | 1659 | 1659 | 1659 | 0.0395 | 645 | 0.015357 | 1890 | 0.045 | 1.362 | A04 | MICL0.01129042/RBL
Build-In Floor | Mini Canal | MICL.01129042/RBN | 11 | 290 | 42 | 42 | 1609 | 1609 | 1609 | 0.03831 | 626 | 0.014905 | 1833 | 0.043643 | 1.362 | A04 | MICL0.01129042/RBN
Build-In Floor | Mini Canal | MICL.01129042/RBR | 11 | 290 | 42 | 42 | 1659 | 1659 | 1659 | 0.0395 | 645 | 0.015357 | 1890 | 0.045 | 1.362 | A04 | MICL0.01129042/RBR
Build-In Floor | Mini Canal | MICL.01129042/RBV | 11 | 290 | 42 | 42 | 1609 | 1609 | 1609 | 0.03831 | 626 | 0.014905 | 1833 | 0.043643 | 1.362 | A04 | MICL0.01129042/RBV
Build-In Floor | Mini Canal | MICL.01129042/RDB | 11 | 290 | 42 | 42 | 1659 | 1659 | 1659 | 0.0395 | 645 | 0.015357 | 1890 | 0.045 | 1.362 | A04 | MICL0.01129042/RDB
Build-In Floor | Mini Canal | MICL.01129042/RMN | 11 | 290 | 42 | 42 | 1609 | 1609 | 1609 | 0.03831 | 626 | 0.014905 | 1833 | 0.043643 | 1.362 | A04 | MICL0.01129042/RMN
Build-In Floor | Mini Canal | MICL.01129042/RMV | 11 | 290 | 42 | 42 | 1609 | 1609 | 1609 | 0.03831 | 626 | 0.014905 | 1833 | 0.043643 | 1.362 | A04 | MICL0.01129042/RMV
Build-In Floor | Mini Canal | MICL.01129042/RNA | 11 | 290 | 42 | 42 | 1659 | 1659 | 1659 | 0.0395 | 645 | 0.015357 | 1890 | 0.045 | 1.362 | A04 | MICL0.01129042/RNA
Build-In Floor | Mini Canal | MICL.01129042/RON | 11 | 290 | 42 | 42 | 1609 | 1609 | 1609 | 0.03831 | 626 | 0.014905 | 1833 | 0.043643 | 1.362 | A04 | MICL0.01129042/RON
Build-In Floor | Mini Canal | MICL.01129042/ROV | 11 | 290 | 42 | 42 | 1609 | 1609 | 1609 | 0.03831 | 626 | 0.014905 | 1833 | 0.043643 | 1.362 | A04 | MICL0.01129042/ROV
Build-In Floor | Mini Canal | MICL.01129042/RSS | 11 | 290 | 42 | 42 | 1593 | 1593 | 1593 | 0.037929 | 620 | 0.014762 | 1814 | 0.04319 | 1.362 | A04 | MICL0.01129042/RSS
Build-In Floor | Mini Canal | MICL.01129042/SBL | 11 | 290 | 42 | 42 | 1659 | 1659 | 1659 | 0.0395 | 645 | 0.015357 | 1890 | 0.045 | 1.362 | A04 | MICL0.01129042/SBL
Build-In Floor | Mini Canal | MICL.01129042/SBR | 11 | 290 | 42 | 42 | 1659 | 1659 | 1659 | 0.0395 | 645 | 0.015357 | 1890 | 0.045 | 1.362 | A04 | MICL0.01129042/SBR
Build-In Floor | Mini Canal | MICL.01129042/SDB | 11 | 290 | 42 | 42 | 1659 | 1659 | 1659 | 0.0395 | 645 | 0.015357 | 1890 | 0.045 | 1.362 | A04 | MICL0.01129042/SDB
Build-In Floor | Mini Canal | MICL.01129042/SNA | 11 | 290 | 42 | 42 | 1659 | 1659 | 1659 | 0.0395 | 645 | 0.015357 | 1890 | 0.045 | 1.362 | A04 | MICL0.01129042/SNA
Build-In Floor | Mini Canal | MICL.01129042/SNC | 11 | 290 | 42 | 42 | 1659 | 1659 | 1659 | 0.0395 | 645 | 0.015357 | 1890 | 0.045 | 1.362 | A04 | MICL0.01129042/SNC
Build-In Floor | Mini Canal | MICL.01131014/ANA | 11 | 310 | 14 | 14 | 459 | 459 | 459 | 0.010929 | 179 | 0.0042619 | 523 | 0.012452 | 1.362 | A04 | MICL0.01131014/ANA
Build-In Floor | Mini Canal | MICL.01131014/DBL | 11 | 310 | 14 | 14 | 594 | 594 | 594 | 0.014143 | 231 | 0.0055 | 677 | 0.016119 | 1.362 | A04 | MICL0.01131014/DBL
Build-In Floor | Mini Canal | MICL.01131014/DBN | 11 | 310 | 14 | 14 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01131014/DBN
Build-In Floor | Mini Canal | MICL.01131014/DBR | 11 | 310 | 14 | 14 | 594 | 594 | 594 | 0.014143 | 231 | 0.0055 | 677 | 0.016119 | 1.362 | A04 | MICL0.01131014/DBR
Build-In Floor | Mini Canal | MICL.01131014/DBV | 11 | 310 | 14 | 14 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01131014/DBV
Build-In Floor | Mini Canal | MICL.01131014/DDB | 11 | 310 | 14 | 14 | 594 | 594 | 594 | 0.014143 | 231 | 0.0055 | 677 | 0.016119 | 1.362 | A04 | MICL0.01131014/DDB
Build-In Floor | Mini Canal | MICL.01131014/DMN | 11 | 310 | 14 | 14 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01131014/DMN
Build-In Floor | Mini Canal | MICL.01131014/DMV | 11 | 310 | 14 | 14 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01131014/DMV
Build-In Floor | Mini Canal | MICL.01131014/DNA | 11 | 310 | 14 | 14 | 594 | 594 | 594 | 0.014143 | 231 | 0.0055 | 677 | 0.016119 | 1.362 | A04 | MICL0.01131014/DNA
Build-In Floor | Mini Canal | MICL.01131014/DNC | 11 | 310 | 14 | 14 | 594 | 594 | 594 | 0.014143 | 231 | 0.0055 | 677 | 0.016119 | 1.362 | A04 | MICL0.01131014/DNC
Build-In Floor | Mini Canal | MICL.01131014/DON | 11 | 310 | 14 | 14 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01131014/DON
Build-In Floor | Mini Canal | MICL.01131014/DOV | 11 | 310 | 14 | 14 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01131014/DOV
Build-In Floor | Mini Canal | MICL.01131014/RBL | 11 | 310 | 14 | 14 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.01131014/RBL
Build-In Floor | Mini Canal | MICL.01131014/RBN | 11 | 310 | 14 | 14 | 594 | 594 | 594 | 0.014143 | 231 | 0.0055 | 677 | 0.016119 | 1.362 | A04 | MICL0.01131014/RBN
Build-In Floor | Mini Canal | MICL.01131014/RBR | 11 | 310 | 14 | 14 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.01131014/RBR
Build-In Floor | Mini Canal | MICL.01131014/RBV | 11 | 310 | 14 | 14 | 594 | 594 | 594 | 0.014143 | 231 | 0.0055 | 677 | 0.016119 | 1.362 | A04 | MICL0.01131014/RBV
Build-In Floor | Mini Canal | MICL.01131014/RDB | 11 | 310 | 14 | 14 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.01131014/RDB
Build-In Floor | Mini Canal | MICL.01131014/RMN | 11 | 310 | 14 | 14 | 594 | 594 | 594 | 0.014143 | 231 | 0.0055 | 677 | 0.016119 | 1.362 | A04 | MICL0.01131014/RMN
Build-In Floor | Mini Canal | MICL.01131014/RMV | 11 | 310 | 14 | 14 | 594 | 594 | 594 | 0.014143 | 231 | 0.0055 | 677 | 0.016119 | 1.362 | A04 | MICL0.01131014/RMV
Build-In Floor | Mini Canal | MICL.01131014/RNA | 11 | 310 | 14 | 14 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.01131014/RNA
Build-In Floor | Mini Canal | MICL.01131014/RON | 11 | 310 | 14 | 14 | 594 | 594 | 594 | 0.014143 | 231 | 0.0055 | 677 | 0.016119 | 1.362 | A04 | MICL0.01131014/RON
Build-In Floor | Mini Canal | MICL.01131014/ROV | 11 | 310 | 14 | 14 | 594 | 594 | 594 | 0.014143 | 231 | 0.0055 | 677 | 0.016119 | 1.362 | A04 | MICL0.01131014/ROV
Build-In Floor | Mini Canal | MICL.01131014/RSS | 11 | 310 | 14 | 14 | 588 | 588 | 588 | 0.014 | 229 | 0.0054524 | 670 | 0.015952 | 1.362 | A04 | MICL0.01131014/RSS
Build-In Floor | Mini Canal | MICL.01131014/SBL | 11 | 310 | 14 | 14 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.01131014/SBL
Build-In Floor | Mini Canal | MICL.01131014/SBR | 11 | 310 | 14 | 14 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.01131014/SBR
Build-In Floor | Mini Canal | MICL.01131014/SDB | 11 | 310 | 14 | 14 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.01131014/SDB
Build-In Floor | Mini Canal | MICL.01131014/SNA | 11 | 310 | 14 | 14 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.01131014/SNA
Build-In Floor | Mini Canal | MICL.01131014/SNC | 11 | 310 | 14 | 14 | 612 | 612 | 612 | 0.014571 | 238 | 0.0056667 | 697 | 0.016595 | 1.362 | A04 | MICL0.01131014/SNC
Build-In Floor | Mini Canal | MICL.01131018/ANA | 11 | 310 | 18 | 18 | 544 | 544 | 544 | 0.012952 | 212 | 0.0050476 | 620 | 0.014762 | 1.362 | A04 | MICL0.01131018/ANA
Build-In Floor | Mini Canal | MICL.01131018/DBL | 11 | 310 | 18 | 18 | 703 | 703 | 703 | 0.016738 | 273 | 0.0065 | 801 | 0.019071 | 1.362 | A04 | MICL0.01131018/DBL
Build-In Floor | Mini Canal | MICL.01131018/DBN | 11 | 310 | 18 | 18 | 674 | 674 | 674 | 0.016048 | 262 | 0.0062381 | 768 | 0.018286 | 1.362 | A04 | MICL0.01131018/DBN
Build-In Floor | Mini Canal | MICL.01131018/DBR | 11 | 310 | 18 | 18 | 703 | 703 | 703 | 0.016738 | 273 | 0.0065 | 801 | 0.019071 | 1.362 | A04 | MICL0.01131018/DBR
Build-In Floor | Mini Canal | MICL.01131018/DBV | 11 | 310 | 18 | 18 | 674 | 674 | 674 | 0.016048 | 262 | 0.0062381 | 768 | 0.018286 | 1.362 | A04 | MICL0.01131018/DBV
Build-In Floor | Mini Canal | MICL.01131018/DDB | 11 | 310 | 18 | 18 | 703 | 703 | 703 | 0.016738 | 273 | 0.0065 | 801 | 0.019071 | 1.362 | A04 | MICL0.01131018/DDB
Build-In Floor | Mini Canal | MICL.01131018/DMN | 11 | 310 | 18 | 18 | 674 | 674 | 674 | 0.016048 | 262 | 0.0062381 | 768 | 0.018286 | 1.362 | A04 | MICL0.01131018/DMN
Build-In Floor | Mini Canal | MICL.01131018/DMV | 11 | 310 | 18 | 18 | 674 | 674 | 674 | 0.016048 | 262 | 0.0062381 | 768 | 0.018286 | 1.362 | A04 | MICL0.01131018/DMV
Build-In Floor | Mini Canal | MICL.01131018/DNA | 11 | 310 | 18 | 18 | 703 | 703 | 703 | 0.016738 | 273 | 0.0065 | 801 | 0.019071 | 1.362 | A04 | MICL0.01131018/DNA
Build-In Floor | Mini Canal | MICL.01131018/DNC | 11 | 310 | 18 | 18 | 703 | 703 | 703 | 0.016738 | 273 | 0.0065 | 801 | 0.019071 | 1.362 | A04 | MICL0.01131018/DNC
Build-In Floor | Mini Canal | MICL.01131018/DON | 11 | 310 | 18 | 18 | 674 | 674 | 674 | 0.016048 | 262 | 0.0062381 | 768 | 0.018286 | 1.362 | A04 | MICL0.01131018/DON
Build-In Floor | Mini Canal | MICL.01131018/DOV | 11 | 310 | 18 | 18 | 674 | 674 | 674 | 0.016048 | 262 | 0.0062381 | 768 | 0.018286 | 1.362 | A04 | MICL0.01131018/DOV
Build-In Floor | Mini Canal | MICL.01131018/RBL | 11 | 310 | 18 | 18 | 725 | 725 | 725 | 0.017262 | 282 | 0.0067143 | 826 | 0.019667 | 1.362 | A04 | MICL0.01131018/RBL
Build-In Floor | Mini Canal | MICL.01131018/RBN | 11 | 310 | 18 | 18 | 703 | 703 | 703 | 0.016738 | 273 | 0.0065 | 801 | 0.019071 | 1.362 | A04 | MICL0.01131018/RBN
Build-In Floor | Mini Canal | MICL.01131018/RBR | 11 | 310 | 18 | 18 | 725 | 725 | 725 | 0.017262 | 282 | 0.0067143 | 826 | 0.019667 | 1.362 | A04 | MICL0.01131018/RBR
Build-In Floor | Mini Canal | MICL.01131018/RBV | 11 | 310 | 18 | 18 | 703 | 703 | 703 | 0.016738 | 273 | 0.0065 | 801 | 0.019071 | 1.362 | A04 | MICL0.01131018/RBV
Build-In Floor | Mini Canal | MICL.01131018/RDB | 11 | 310 | 18 | 18 | 725 | 725 | 725 | 0.017262 | 282 | 0.0067143 | 826 | 0.019667 | 1.362 | A04 | MICL0.01131018/RDB
Build-In Floor | Mini Canal | MICL.01131018/RMN | 11 | 310 | 18 | 18 | 703 | 703 | 703 | 0.016738 | 273 | 0.0065 | 801 | 0.019071 | 1.362 | A04 | MICL0.01131018/RMN
Build-In Floor | Mini Canal | MICL.01131018/RMV | 11 | 310 | 18 | 18 | 703 | 703 | 703 | 0.016738 | 273 | 0.0065 | 801 | 0.019071 | 1.362 | A04 | MICL0.01131018/RMV
Build-In Floor | Mini Canal | MICL.01131018/RNA | 11 | 310 | 18 | 18 | 725 | 725 | 725 | 0.017262 | 282 | 0.0067143 | 826 | 0.019667 | 1.362 | A04 | MICL0.01131018/RNA
Build-In Floor | Mini Canal | MICL.01131018/RON | 11 | 310 | 18 | 18 | 703 | 703 | 703 | 0.016738 | 273 | 0.0065 | 801 | 0.019071 | 1.362 | A04 | MICL0.01131018/RON
Build-In Floor | Mini Canal | MICL.01131018/ROV | 11 | 310 | 18 | 18 | 703 | 703 | 703 | 0.016738 | 273 | 0.0065 | 801 | 0.019071 | 1.362 | A04 | MICL0.01131018/ROV
Build-In Floor | Mini Canal | MICL.01131018/RSS | 11 | 310 | 18 | 18 | 696 | 696 | 696 | 0.016571 | 271 | 0.0064524 | 793 | 0.018881 | 1.362 | A04 | MICL0.01131018/RSS
Build-In Floor | Mini Canal | MICL.01131018/SBL | 11 | 310 | 18 | 18 | 725 | 725 | 725 | 0.017262 | 282 | 0.0067143 | 826 | 0.019667 | 1.362 | A04 | MICL0.01131018/SBL
Build-In Floor | Mini Canal | MICL.01131018/SBR | 11 | 310 | 18 | 18 | 725 | 725 | 725 | 0.017262 | 282 | 0.0067143 | 826 | 0.019667 | 1.362 | A04 | MICL0.01131018/SBR
Build-In Floor | Mini Canal | MICL.01131018/SDB | 11 | 310 | 18 | 18 | 725 | 725 | 725 | 0.017262 | 282 | 0.0067143 | 826 | 0.019667 | 1.362 | A04 | MICL0.01131018/SDB
Build-In Floor | Mini Canal | MICL.01131018/SNA | 11 | 310 | 18 | 18 | 725 | 725 | 725 | 0.017262 | 282 | 0.0067143 | 826 | 0.019667 | 1.362 | A04 | MICL0.01131018/SNA
Build-In Floor | Mini Canal | MICL.01131018/SNC | 11 | 310 | 18 | 18 | 725 | 725 | 725 | 0.017262 | 282 | 0.0067143 | 826 | 0.019667 | 1.362 | A04 | MICL0.01131018/SNC
Build-In Floor | Mini Canal | MICL.01131026/ANA | 11 | 310 | 26 | 26 | 734 | 734 | 734 | 0.017476 | 286 | 0.0068095 | 836 | 0.019905 | 1.362 | A04 | MICL0.01131026/ANA
Build-In Floor | Mini Canal | MICL.01131026/DBL | 11 | 310 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01131026/DBL
Build-In Floor | Mini Canal | MICL.01131026/DBN | 11 | 310 | 26 | 26 | 910 | 910 | 910 | 0.021667 | 354 | 0.0084286 | 1036 | 0.024667 | 1.362 | A04 | MICL0.01131026/DBN
Build-In Floor | Mini Canal | MICL.01131026/DBR | 11 | 310 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01131026/DBR
Build-In Floor | Mini Canal | MICL.01131026/DBV | 11 | 310 | 26 | 26 | 910 | 910 | 910 | 0.021667 | 354 | 0.0084286 | 1036 | 0.024667 | 1.362 | A04 | MICL0.01131026/DBV
Build-In Floor | Mini Canal | MICL.01131026/DDB | 11 | 310 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01131026/DDB
Build-In Floor | Mini Canal | MICL.01131026/DMN | 11 | 310 | 26 | 26 | 910 | 910 | 910 | 0.021667 | 354 | 0.0084286 | 1036 | 0.024667 | 1.362 | A04 | MICL0.01131026/DMN
Build-In Floor | Mini Canal | MICL.01131026/DMV | 11 | 310 | 26 | 26 | 910 | 910 | 910 | 0.021667 | 354 | 0.0084286 | 1036 | 0.024667 | 1.362 | A04 | MICL0.01131026/DMV
Build-In Floor | Mini Canal | MICL.01131026/DNA | 11 | 310 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01131026/DNA
Build-In Floor | Mini Canal | MICL.01131026/DNC | 11 | 310 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01131026/DNC
Build-In Floor | Mini Canal | MICL.01131026/DON | 11 | 310 | 26 | 26 | 910 | 910 | 910 | 0.021667 | 354 | 0.0084286 | 1036 | 0.024667 | 1.362 | A04 | MICL0.01131026/DON
Build-In Floor | Mini Canal | MICL.01131026/DOV | 11 | 310 | 26 | 26 | 910 | 910 | 910 | 0.021667 | 354 | 0.0084286 | 1036 | 0.024667 | 1.362 | A04 | MICL0.01131026/DOV
Build-In Floor | Mini Canal | MICL.01131026/PNC | 11 | 310 | 26 | 26 | 831 | 831 | 831 | 0.019786 | 323 | 0.0076905 | 947 | 0.022548 | 1.362 | A04 | MICL0.01131026/PNC
Build-In Floor | Mini Canal | MICL.01131026/RBL | 11 | 310 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01131026/RBL
Build-In Floor | Mini Canal | MICL.01131026/RBN | 11 | 310 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01131026/RBN
Build-In Floor | Mini Canal | MICL.01131026/RBR | 11 | 310 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01131026/RBR
Build-In Floor | Mini Canal | MICL.01131026/RBV | 11 | 310 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01131026/RBV
Build-In Floor | Mini Canal | MICL.01131026/RDB | 11 | 310 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01131026/RDB
Build-In Floor | Mini Canal | MICL.01131026/RMN | 11 | 310 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01131026/RMN
Build-In Floor | Mini Canal | MICL.01131026/RMV | 11 | 310 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01131026/RMV
Build-In Floor | Mini Canal | MICL.01131026/RNA | 11 | 310 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01131026/RNA
Build-In Floor | Mini Canal | MICL.01131026/RON | 11 | 310 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01131026/RON
Build-In Floor | Mini Canal | MICL.01131026/ROV | 11 | 310 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01131026/ROV
Build-In Floor | Mini Canal | MICL.01131026/RSS | 11 | 310 | 26 | 26 | 939 | 939 | 939 | 0.022357 | 365 | 0.0086905 | 1070 | 0.025476 | 1.362 | A04 | MICL0.01131026/RSS
Build-In Floor | Mini Canal | MICL.01131026/SBL | 11 | 310 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01131026/SBL
Build-In Floor | Mini Canal | MICL.01131026/SBR | 11 | 310 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01131026/SBR
Build-In Floor | Mini Canal | MICL.01131026/SDB | 11 | 310 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01131026/SDB
Build-In Floor | Mini Canal | MICL.01131026/SNA | 11 | 310 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01131026/SNA
Build-In Floor | Mini Canal | MICL.01131026/SNC | 11 | 310 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01131026/SNC
Build-In Floor | Mini Canal | MICL.01131034/ANA | 11 | 310 | 34 | 34 | 953 | 953 | 953 | 0.02269 | 371 | 0.0088333 | 1085 | 0.025833 | 1.362 | A04 | MICL0.01131034/ANA
Build-In Floor | Mini Canal | MICL.01131034/DBL | 11 | 310 | 34 | 34 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01131034/DBL
Build-In Floor | Mini Canal | MICL.01131034/DBN | 11 | 310 | 34 | 34 | 1182 | 1182 | 1182 | 0.028143 | 460 | 0.010952 | 1346 | 0.032048 | 1.362 | A04 | MICL0.01131034/DBN
Build-In Floor | Mini Canal | MICL.01131034/DBR | 11 | 310 | 34 | 34 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01131034/DBR
Build-In Floor | Mini Canal | MICL.01131034/DBV | 11 | 310 | 34 | 34 | 1182 | 1182 | 1182 | 0.028143 | 460 | 0.010952 | 1346 | 0.032048 | 1.362 | A04 | MICL0.01131034/DBV
Build-In Floor | Mini Canal | MICL.01131034/DDB | 11 | 310 | 34 | 34 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01131034/DDB
Build-In Floor | Mini Canal | MICL.01131034/DMN | 11 | 310 | 34 | 34 | 1182 | 1182 | 1182 | 0.028143 | 460 | 0.010952 | 1346 | 0.032048 | 1.362 | A04 | MICL0.01131034/DMN
Build-In Floor | Mini Canal | MICL.01131034/DMV | 11 | 310 | 34 | 34 | 1182 | 1182 | 1182 | 0.028143 | 460 | 0.010952 | 1346 | 0.032048 | 1.362 | A04 | MICL0.01131034/DMV
Build-In Floor | Mini Canal | MICL.01131034/DNA | 11 | 310 | 34 | 34 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01131034/DNA
Build-In Floor | Mini Canal | MICL.01131034/DNC | 11 | 310 | 34 | 34 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01131034/DNC
Build-In Floor | Mini Canal | MICL.01131034/DON | 11 | 310 | 34 | 34 | 1182 | 1182 | 1182 | 0.028143 | 460 | 0.010952 | 1346 | 0.032048 | 1.362 | A04 | MICL0.01131034/DON
Build-In Floor | Mini Canal | MICL.01131034/DOV | 11 | 310 | 34 | 34 | 1182 | 1182 | 1182 | 0.028143 | 460 | 0.010952 | 1346 | 0.032048 | 1.362 | A04 | MICL0.01131034/DOV
Build-In Floor | Mini Canal | MICL.01131034/PNC | 11 | 310 | 34 | 34 | 1080 | 1080 | 1080 | 0.025714 | 420 | 0.01 | 1230 | 0.029286 | 1.362 | A04 | MICL0.01131034/PNC
Build-In Floor | Mini Canal | MICL.01131034/RBL | 11 | 310 | 34 | 34 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01131034/RBL
Build-In Floor | Mini Canal | MICL.01131034/RBN | 11 | 310 | 34 | 34 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01131034/RBN
Build-In Floor | Mini Canal | MICL.01131034/RBR | 11 | 310 | 34 | 34 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01131034/RBR
Build-In Floor | Mini Canal | MICL.01131034/RBV | 11 | 310 | 34 | 34 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01131034/RBV
Build-In Floor | Mini Canal | MICL.01131034/RDB | 11 | 310 | 34 | 34 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01131034/RDB
Build-In Floor | Mini Canal | MICL.01131034/RMN | 11 | 310 | 34 | 34 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01131034/RMN
Build-In Floor | Mini Canal | MICL.01131034/RMV | 11 | 310 | 34 | 34 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01131034/RMV
Build-In Floor | Mini Canal | MICL.01131034/RNA | 11 | 310 | 34 | 34 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01131034/RNA
Build-In Floor | Mini Canal | MICL.01131034/RON | 11 | 310 | 34 | 34 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01131034/RON
Build-In Floor | Mini Canal | MICL.01131034/ROV | 11 | 310 | 34 | 34 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01131034/ROV
Build-In Floor | Mini Canal | MICL.01131034/RSS | 11 | 310 | 34 | 34 | 1220 | 1220 | 1220 | 0.029048 | 475 | 0.01131 | 1390 | 0.033095 | 1.362 | A04 | MICL0.01131034/RSS
Build-In Floor | Mini Canal | MICL.01131034/SBL | 11 | 310 | 34 | 34 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01131034/SBL
Build-In Floor | Mini Canal | MICL.01131034/SBR | 11 | 310 | 34 | 34 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01131034/SBR
Build-In Floor | Mini Canal | MICL.01131034/SDB | 11 | 310 | 34 | 34 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01131034/SDB
Build-In Floor | Mini Canal | MICL.01131034/SNA | 11 | 310 | 34 | 34 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01131034/SNA
Build-In Floor | Mini Canal | MICL.01131034/SNC | 11 | 310 | 34 | 34 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01131034/SNC
Build-In Floor | Mini Canal | MICL.01131042/ANA | 11 | 310 | 42 | 42 | 1340 | 1340 | 1340 | 0.031905 | 521 | 0.012405 | 1526 | 0.036333 | 1.362 | A04 | MICL0.01131042/ANA
Build-In Floor | Mini Canal | MICL.01131042/DBL | 11 | 310 | 42 | 42 | 1732 | 1732 | 1732 | 0.041238 | 674 | 0.016048 | 1973 | 0.046976 | 1.362 | A04 | MICL0.01131042/DBL
Build-In Floor | Mini Canal | MICL.01131042/DBN | 11 | 310 | 42 | 42 | 1661 | 1661 | 1661 | 0.039548 | 646 | 0.015381 | 1892 | 0.045048 | 1.362 | A04 | MICL0.01131042/DBN
Build-In Floor | Mini Canal | MICL.01131042/DBR | 11 | 310 | 42 | 42 | 1732 | 1732 | 1732 | 0.041238 | 674 | 0.016048 | 1973 | 0.046976 | 1.362 | A04 | MICL0.01131042/DBR
Build-In Floor | Mini Canal | MICL.01131042/DBV | 11 | 310 | 42 | 42 | 1661 | 1661 | 1661 | 0.039548 | 646 | 0.015381 | 1892 | 0.045048 | 1.362 | A04 | MICL0.01131042/DBV
Build-In Floor | Mini Canal | MICL.01131042/DDB | 11 | 310 | 42 | 42 | 1732 | 1732 | 1732 | 0.041238 | 674 | 0.016048 | 1973 | 0.046976 | 1.362 | A04 | MICL0.01131042/DDB
Build-In Floor | Mini Canal | MICL.01131042/DMN | 11 | 310 | 42 | 42 | 1661 | 1661 | 1661 | 0.039548 | 646 | 0.015381 | 1892 | 0.045048 | 1.362 | A04 | MICL0.01131042/DMN
Build-In Floor | Mini Canal | MICL.01131042/DMV | 11 | 310 | 42 | 42 | 1661 | 1661 | 1661 | 0.039548 | 646 | 0.015381 | 1892 | 0.045048 | 1.362 | A04 | MICL0.01131042/DMV
Build-In Floor | Mini Canal | MICL.01131042/DNA | 11 | 310 | 42 | 42 | 1732 | 1732 | 1732 | 0.041238 | 674 | 0.016048 | 1973 | 0.046976 | 1.362 | A04 | MICL0.01131042/DNA
Build-In Floor | Mini Canal | MICL.01131042/DNC | 11 | 310 | 42 | 42 | 1732 | 1732 | 1732 | 0.041238 | 674 | 0.016048 | 1973 | 0.046976 | 1.362 | A04 | MICL0.01131042/DNC
Build-In Floor | Mini Canal | MICL.01131042/DON | 11 | 310 | 42 | 42 | 1661 | 1661 | 1661 | 0.039548 | 646 | 0.015381 | 1892 | 0.045048 | 1.362 | A04 | MICL0.01131042/DON
Build-In Floor | Mini Canal | MICL.01131042/DOV | 11 | 310 | 42 | 42 | 1661 | 1661 | 1661 | 0.039548 | 646 | 0.015381 | 1892 | 0.045048 | 1.362 | A04 | MICL0.01131042/DOV
Build-In Floor | Mini Canal | MICL.01131042/PNC | 11 | 310 | 42 | 42 | 1518 | 1518 | 1518 | 0.036143 | 591 | 0.014071 | 1729 | 0.041167 | 1.362 | A04 | MICL0.01131042/PNC
Build-In Floor | Mini Canal | MICL.01131042/RBL | 11 | 310 | 42 | 42 | 1786 | 1786 | 1786 | 0.042524 | 695 | 0.016548 | 2034 | 0.048429 | 1.362 | A04 | MICL0.01131042/RBL
Build-In Floor | Mini Canal | MICL.01131042/RBN | 11 | 310 | 42 | 42 | 1732 | 1732 | 1732 | 0.041238 | 674 | 0.016048 | 1973 | 0.046976 | 1.362 | A04 | MICL0.01131042/RBN
Build-In Floor | Mini Canal | MICL.01131042/RBR | 11 | 310 | 42 | 42 | 1786 | 1786 | 1786 | 0.042524 | 695 | 0.016548 | 2034 | 0.048429 | 1.362 | A04 | MICL0.01131042/RBR
Build-In Floor | Mini Canal | MICL.01131042/RBV | 11 | 310 | 42 | 42 | 1732 | 1732 | 1732 | 0.041238 | 674 | 0.016048 | 1973 | 0.046976 | 1.362 | A04 | MICL0.01131042/RBV
Build-In Floor | Mini Canal | MICL.01131042/RDB | 11 | 310 | 42 | 42 | 1786 | 1786 | 1786 | 0.042524 | 695 | 0.016548 | 2034 | 0.048429 | 1.362 | A04 | MICL0.01131042/RDB
Build-In Floor | Mini Canal | MICL.01131042/RMN | 11 | 310 | 42 | 42 | 1732 | 1732 | 1732 | 0.041238 | 674 | 0.016048 | 1973 | 0.046976 | 1.362 | A04 | MICL0.01131042/RMN
Build-In Floor | Mini Canal | MICL.01131042/RMV | 11 | 310 | 42 | 42 | 1732 | 1732 | 1732 | 0.041238 | 674 | 0.016048 | 1973 | 0.046976 | 1.362 | A04 | MICL0.01131042/RMV
Build-In Floor | Mini Canal | MICL.01131042/RNA | 11 | 310 | 42 | 42 | 1786 | 1786 | 1786 | 0.042524 | 695 | 0.016548 | 2034 | 0.048429 | 1.362 | A04 | MICL0.01131042/RNA
Build-In Floor | Mini Canal | MICL.01131042/RON | 11 | 310 | 42 | 42 | 1732 | 1732 | 1732 | 0.041238 | 674 | 0.016048 | 1973 | 0.046976 | 1.362 | A04 | MICL0.01131042/RON
Build-In Floor | Mini Canal | MICL.01131042/ROV | 11 | 310 | 42 | 42 | 1732 | 1732 | 1732 | 0.041238 | 674 | 0.016048 | 1973 | 0.046976 | 1.362 | A04 | MICL0.01131042/ROV
Build-In Floor | Mini Canal | MICL.01131042/RSS | 11 | 310 | 42 | 42 | 1715 | 1715 | 1715 | 0.040833 | 667 | 0.015881 | 1953 | 0.0465 | 1.362 | A04 | MICL0.01131042/RSS
Build-In Floor | Mini Canal | MICL.01131042/SBL | 11 | 310 | 42 | 42 | 1786 | 1786 | 1786 | 0.042524 | 695 | 0.016548 | 2034 | 0.048429 | 1.362 | A04 | MICL0.01131042/SBL
Build-In Floor | Mini Canal | MICL.01131042/SBR | 11 | 310 | 42 | 42 | 1786 | 1786 | 1786 | 0.042524 | 695 | 0.016548 | 2034 | 0.048429 | 1.362 | A04 | MICL0.01131042/SBR
Build-In Floor | Mini Canal | MICL.01131042/SDB | 11 | 310 | 42 | 42 | 1786 | 1786 | 1786 | 0.042524 | 695 | 0.016548 | 2034 | 0.048429 | 1.362 | A04 | MICL0.01131042/SDB
Build-In Floor | Mini Canal | MICL.01131042/SNA | 11 | 310 | 42 | 42 | 1786 | 1786 | 1786 | 0.042524 | 695 | 0.016548 | 2034 | 0.048429 | 1.362 | A04 | MICL0.01131042/SNA
Build-In Floor | Mini Canal | MICL.01131042/SNC | 11 | 310 | 42 | 42 | 1786 | 1786 | 1786 | 0.042524 | 695 | 0.016548 | 2034 | 0.048429 | 1.362 | A04 | MICL0.01131042/SNC
Build-In Floor | Mini Canal | MICL.01133014/ANA | 11 | 330 | 14 | 14 | 491 | 491 | 491 | 0.01169 | 191 | 0.0045476 | 559 | 0.01331 | 1.362 | A04 | MICL0.01133014/ANA
Build-In Floor | Mini Canal | MICL.01133014/DBL | 11 | 330 | 14 | 14 | 635 | 635 | 635 | 0.015119 | 247 | 0.005881 | 723 | 0.017214 | 1.362 | A04 | MICL0.01133014/DBL
Build-In Floor | Mini Canal | MICL.01133014/DBN | 11 | 330 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.01133014/DBN
Build-In Floor | Mini Canal | MICL.01133014/DBR | 11 | 330 | 14 | 14 | 635 | 635 | 635 | 0.015119 | 247 | 0.005881 | 723 | 0.017214 | 1.362 | A04 | MICL0.01133014/DBR
Build-In Floor | Mini Canal | MICL.01133014/DBV | 11 | 330 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.01133014/DBV
Build-In Floor | Mini Canal | MICL.01133014/DDB | 11 | 330 | 14 | 14 | 635 | 635 | 635 | 0.015119 | 247 | 0.005881 | 723 | 0.017214 | 1.362 | A04 | MICL0.01133014/DDB
Build-In Floor | Mini Canal | MICL.01133014/DMN | 11 | 330 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.01133014/DMN
Build-In Floor | Mini Canal | MICL.01133014/DMV | 11 | 330 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.01133014/DMV
Build-In Floor | Mini Canal | MICL.01133014/DNA | 11 | 330 | 14 | 14 | 635 | 635 | 635 | 0.015119 | 247 | 0.005881 | 723 | 0.017214 | 1.362 | A04 | MICL0.01133014/DNA
Build-In Floor | Mini Canal | MICL.01133014/DNC | 11 | 330 | 14 | 14 | 635 | 635 | 635 | 0.015119 | 247 | 0.005881 | 723 | 0.017214 | 1.362 | A04 | MICL0.01133014/DNC
Build-In Floor | Mini Canal | MICL.01133014/DON | 11 | 330 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.01133014/DON
Build-In Floor | Mini Canal | MICL.01133014/DOV | 11 | 330 | 14 | 14 | 609 | 609 | 609 | 0.0145 | 237 | 0.0056429 | 694 | 0.016524 | 1.362 | A04 | MICL0.01133014/DOV
Build-In Floor | Mini Canal | MICL.01133014/RBL | 11 | 330 | 14 | 14 | 655 | 655 | 655 | 0.015595 | 255 | 0.0060714 | 746 | 0.017762 | 1.362 | A04 | MICL0.01133014/RBL
Build-In Floor | Mini Canal | MICL.01133014/RBN | 11 | 330 | 14 | 14 | 635 | 635 | 635 | 0.015119 | 247 | 0.005881 | 723 | 0.017214 | 1.362 | A04 | MICL0.01133014/RBN
Build-In Floor | Mini Canal | MICL.01133014/RBR | 11 | 330 | 14 | 14 | 655 | 655 | 655 | 0.015595 | 255 | 0.0060714 | 746 | 0.017762 | 1.362 | A04 | MICL0.01133014/RBR
Build-In Floor | Mini Canal | MICL.01133014/RBV | 11 | 330 | 14 | 14 | 635 | 635 | 635 | 0.015119 | 247 | 0.005881 | 723 | 0.017214 | 1.362 | A04 | MICL0.01133014/RBV
Build-In Floor | Mini Canal | MICL.01133014/RDB | 11 | 330 | 14 | 14 | 655 | 655 | 655 | 0.015595 | 255 | 0.0060714 | 746 | 0.017762 | 1.362 | A04 | MICL0.01133014/RDB
Build-In Floor | Mini Canal | MICL.01133014/RMN | 11 | 330 | 14 | 14 | 635 | 635 | 635 | 0.015119 | 247 | 0.005881 | 723 | 0.017214 | 1.362 | A04 | MICL0.01133014/RMN
Build-In Floor | Mini Canal | MICL.01133014/RMV | 11 | 330 | 14 | 14 | 635 | 635 | 635 | 0.015119 | 247 | 0.005881 | 723 | 0.017214 | 1.362 | A04 | MICL0.01133014/RMV
Build-In Floor | Mini Canal | MICL.01133014/RNA | 11 | 330 | 14 | 14 | 655 | 655 | 655 | 0.015595 | 255 | 0.0060714 | 746 | 0.017762 | 1.362 | A04 | MICL0.01133014/RNA
Build-In Floor | Mini Canal | MICL.01133014/RON | 11 | 330 | 14 | 14 | 635 | 635 | 635 | 0.015119 | 247 | 0.005881 | 723 | 0.017214 | 1.362 | A04 | MICL0.01133014/RON
Build-In Floor | Mini Canal | MICL.01133014/ROV | 11 | 330 | 14 | 14 | 635 | 635 | 635 | 0.015119 | 247 | 0.005881 | 723 | 0.017214 | 1.362 | A04 | MICL0.01133014/ROV
Build-In Floor | Mini Canal | MICL.01133014/RSS | 11 | 330 | 14 | 14 | 629 | 629 | 629 | 0.014976 | 245 | 0.0058333 | 716 | 0.017048 | 1.362 | A04 | MICL0.01133014/RSS
Build-In Floor | Mini Canal | MICL.01133014/SBL | 11 | 330 | 14 | 14 | 655 | 655 | 655 | 0.015595 | 255 | 0.0060714 | 746 | 0.017762 | 1.362 | A04 | MICL0.01133014/SBL
Build-In Floor | Mini Canal | MICL.01133014/SBR | 11 | 330 | 14 | 14 | 655 | 655 | 655 | 0.015595 | 255 | 0.0060714 | 746 | 0.017762 | 1.362 | A04 | MICL0.01133014/SBR
Build-In Floor | Mini Canal | MICL.01133014/SDB | 11 | 330 | 14 | 14 | 655 | 655 | 655 | 0.015595 | 255 | 0.0060714 | 746 | 0.017762 | 1.362 | A04 | MICL0.01133014/SDB
Build-In Floor | Mini Canal | MICL.01133014/SNA | 11 | 330 | 14 | 14 | 655 | 655 | 655 | 0.015595 | 255 | 0.0060714 | 746 | 0.017762 | 1.362 | A04 | MICL0.01133014/SNA
Build-In Floor | Mini Canal | MICL.01133014/SNC | 11 | 330 | 14 | 14 | 655 | 655 | 655 | 0.015595 | 255 | 0.0060714 | 746 | 0.017762 | 1.362 | A04 | MICL0.01133014/SNC
Build-In Floor | Mini Canal | MICL.01133018/ANA | 11 | 330 | 18 | 18 | 583 | 583 | 583 | 0.013881 | 227 | 0.0054048 | 664 | 0.01581 | 1.362 | A04 | MICL0.01133018/ANA
Build-In Floor | Mini Canal | MICL.01133018/DBL | 11 | 330 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.01133018/DBL
Build-In Floor | Mini Canal | MICL.01133018/DBN | 11 | 330 | 18 | 18 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.01133018/DBN
Build-In Floor | Mini Canal | MICL.01133018/DBR | 11 | 330 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.01133018/DBR
Build-In Floor | Mini Canal | MICL.01133018/DBV | 11 | 330 | 18 | 18 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.01133018/DBV
Build-In Floor | Mini Canal | MICL.01133018/DDB | 11 | 330 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.01133018/DDB
Build-In Floor | Mini Canal | MICL.01133018/DMN | 11 | 330 | 18 | 18 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.01133018/DMN
Build-In Floor | Mini Canal | MICL.01133018/DMV | 11 | 330 | 18 | 18 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.01133018/DMV
Build-In Floor | Mini Canal | MICL.01133018/DNA | 11 | 330 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.01133018/DNA
Build-In Floor | Mini Canal | MICL.01133018/DNC | 11 | 330 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.01133018/DNC
Build-In Floor | Mini Canal | MICL.01133018/DON | 11 | 330 | 18 | 18 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.01133018/DON
Build-In Floor | Mini Canal | MICL.01133018/DOV | 11 | 330 | 18 | 18 | 723 | 723 | 723 | 0.017214 | 281 | 0.0066905 | 823 | 0.019595 | 1.362 | A04 | MICL0.01133018/DOV
Build-In Floor | Mini Canal | MICL.01133018/RBL | 11 | 330 | 18 | 18 | 777 | 777 | 777 | 0.0185 | 302 | 0.0071905 | 885 | 0.021071 | 1.362 | A04 | MICL0.01133018/RBL
Build-In Floor | Mini Canal | MICL.01133018/RBN | 11 | 330 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.01133018/RBN
Build-In Floor | Mini Canal | MICL.01133018/RBR | 11 | 330 | 18 | 18 | 777 | 777 | 777 | 0.0185 | 302 | 0.0071905 | 885 | 0.021071 | 1.362 | A04 | MICL0.01133018/RBR
Build-In Floor | Mini Canal | MICL.01133018/RBV | 11 | 330 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.01133018/RBV
Build-In Floor | Mini Canal | MICL.01133018/RDB | 11 | 330 | 18 | 18 | 777 | 777 | 777 | 0.0185 | 302 | 0.0071905 | 885 | 0.021071 | 1.362 | A04 | MICL0.01133018/RDB
Build-In Floor | Mini Canal | MICL.01133018/RMN | 11 | 330 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.01133018/RMN
Build-In Floor | Mini Canal | MICL.01133018/RMV | 11 | 330 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.01133018/RMV
Build-In Floor | Mini Canal | MICL.01133018/RNA | 11 | 330 | 18 | 18 | 777 | 777 | 777 | 0.0185 | 302 | 0.0071905 | 885 | 0.021071 | 1.362 | A04 | MICL0.01133018/RNA
Build-In Floor | Mini Canal | MICL.01133018/RON | 11 | 330 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.01133018/RON
Build-In Floor | Mini Canal | MICL.01133018/ROV | 11 | 330 | 18 | 18 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.01133018/ROV
Build-In Floor | Mini Canal | MICL.01133018/RSS | 11 | 330 | 18 | 18 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.362 | A04 | MICL0.01133018/RSS
Build-In Floor | Mini Canal | MICL.01133018/SBL | 11 | 330 | 18 | 18 | 777 | 777 | 777 | 0.0185 | 302 | 0.0071905 | 885 | 0.021071 | 1.362 | A04 | MICL0.01133018/SBL
Build-In Floor | Mini Canal | MICL.01133018/SBR | 11 | 330 | 18 | 18 | 777 | 777 | 777 | 0.0185 | 302 | 0.0071905 | 885 | 0.021071 | 1.362 | A04 | MICL0.01133018/SBR
Build-In Floor | Mini Canal | MICL.01133018/SDB | 11 | 330 | 18 | 18 | 777 | 777 | 777 | 0.0185 | 302 | 0.0071905 | 885 | 0.021071 | 1.362 | A04 | MICL0.01133018/SDB
Build-In Floor | Mini Canal | MICL.01133018/SNA | 11 | 330 | 18 | 18 | 777 | 777 | 777 | 0.0185 | 302 | 0.0071905 | 885 | 0.021071 | 1.362 | A04 | MICL0.01133018/SNA
Build-In Floor | Mini Canal | MICL.01133018/SNC | 11 | 330 | 18 | 18 | 777 | 777 | 777 | 0.0185 | 302 | 0.0071905 | 885 | 0.021071 | 1.362 | A04 | MICL0.01133018/SNC
Build-In Floor | Mini Canal | MICL.01133026/ANA | 11 | 330 | 26 | 26 | 786 | 786 | 786 | 0.018714 | 306 | 0.0072857 | 895 | 0.02131 | 1.362 | A04 | MICL0.01133026/ANA
Build-In Floor | Mini Canal | MICL.01133026/DBL | 11 | 330 | 26 | 26 | 1017 | 1017 | 1017 | 0.024214 | 396 | 0.0094286 | 1158 | 0.027571 | 1.362 | A04 | MICL0.01133026/DBL
Build-In Floor | Mini Canal | MICL.01133026/DBN | 11 | 330 | 26 | 26 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01133026/DBN
Build-In Floor | Mini Canal | MICL.01133026/DBR | 11 | 330 | 26 | 26 | 1017 | 1017 | 1017 | 0.024214 | 396 | 0.0094286 | 1158 | 0.027571 | 1.362 | A04 | MICL0.01133026/DBR
Build-In Floor | Mini Canal | MICL.01133026/DBV | 11 | 330 | 26 | 26 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01133026/DBV
Build-In Floor | Mini Canal | MICL.01133026/DDB | 11 | 330 | 26 | 26 | 1017 | 1017 | 1017 | 0.024214 | 396 | 0.0094286 | 1158 | 0.027571 | 1.362 | A04 | MICL0.01133026/DDB
Build-In Floor | Mini Canal | MICL.01133026/DMN | 11 | 330 | 26 | 26 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01133026/DMN
Build-In Floor | Mini Canal | MICL.01133026/DMV | 11 | 330 | 26 | 26 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01133026/DMV
Build-In Floor | Mini Canal | MICL.01133026/DNA | 11 | 330 | 26 | 26 | 1017 | 1017 | 1017 | 0.024214 | 396 | 0.0094286 | 1158 | 0.027571 | 1.362 | A04 | MICL0.01133026/DNA
Build-In Floor | Mini Canal | MICL.01133026/DNC | 11 | 330 | 26 | 26 | 1017 | 1017 | 1017 | 0.024214 | 396 | 0.0094286 | 1158 | 0.027571 | 1.362 | A04 | MICL0.01133026/DNC
Build-In Floor | Mini Canal | MICL.01133026/DON | 11 | 330 | 26 | 26 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01133026/DON
Build-In Floor | Mini Canal | MICL.01133026/DOV | 11 | 330 | 26 | 26 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01133026/DOV
Build-In Floor | Mini Canal | MICL.01133026/PNC | 11 | 330 | 26 | 26 | 891 | 891 | 891 | 0.021214 | 347 | 0.0082619 | 1015 | 0.024167 | 1.362 | A04 | MICL0.01133026/PNC
Build-In Floor | Mini Canal | MICL.01133026/RBL | 11 | 330 | 26 | 26 | 1048 | 1048 | 1048 | 0.024952 | 408 | 0.0097143 | 1194 | 0.028429 | 1.362 | A04 | MICL0.01133026/RBL
Build-In Floor | Mini Canal | MICL.01133026/RBN | 11 | 330 | 26 | 26 | 1017 | 1017 | 1017 | 0.024214 | 396 | 0.0094286 | 1158 | 0.027571 | 1.362 | A04 | MICL0.01133026/RBN
Build-In Floor | Mini Canal | MICL.01133026/RBR | 11 | 330 | 26 | 26 | 1048 | 1048 | 1048 | 0.024952 | 408 | 0.0097143 | 1194 | 0.028429 | 1.362 | A04 | MICL0.01133026/RBR
Build-In Floor | Mini Canal | MICL.01133026/RBV | 11 | 330 | 26 | 26 | 1017 | 1017 | 1017 | 0.024214 | 396 | 0.0094286 | 1158 | 0.027571 | 1.362 | A04 | MICL0.01133026/RBV
Build-In Floor | Mini Canal | MICL.01133026/RDB | 11 | 330 | 26 | 26 | 1048 | 1048 | 1048 | 0.024952 | 408 | 0.0097143 | 1194 | 0.028429 | 1.362 | A04 | MICL0.01133026/RDB
Build-In Floor | Mini Canal | MICL.01133026/RMN | 11 | 330 | 26 | 26 | 1017 | 1017 | 1017 | 0.024214 | 396 | 0.0094286 | 1158 | 0.027571 | 1.362 | A04 | MICL0.01133026/RMN
Build-In Floor | Mini Canal | MICL.01133026/RMV | 11 | 330 | 26 | 26 | 1017 | 1017 | 1017 | 0.024214 | 396 | 0.0094286 | 1158 | 0.027571 | 1.362 | A04 | MICL0.01133026/RMV
Build-In Floor | Mini Canal | MICL.01133026/RNA | 11 | 330 | 26 | 26 | 1048 | 1048 | 1048 | 0.024952 | 408 | 0.0097143 | 1194 | 0.028429 | 1.362 | A04 | MICL0.01133026/RNA
Build-In Floor | Mini Canal | MICL.01133026/RON | 11 | 330 | 26 | 26 | 1017 | 1017 | 1017 | 0.024214 | 396 | 0.0094286 | 1158 | 0.027571 | 1.362 | A04 | MICL0.01133026/RON
Build-In Floor | Mini Canal | MICL.01133026/ROV | 11 | 330 | 26 | 26 | 1017 | 1017 | 1017 | 0.024214 | 396 | 0.0094286 | 1158 | 0.027571 | 1.362 | A04 | MICL0.01133026/ROV
Build-In Floor | Mini Canal | MICL.01133026/RSS | 11 | 330 | 26 | 26 | 1006 | 1006 | 1006 | 0.023952 | 391 | 0.0093095 | 1146 | 0.027286 | 1.362 | A04 | MICL0.01133026/RSS
Build-In Floor | Mini Canal | MICL.01133026/SBL | 11 | 330 | 26 | 26 | 1048 | 1048 | 1048 | 0.024952 | 408 | 0.0097143 | 1194 | 0.028429 | 1.362 | A04 | MICL0.01133026/SBL
Build-In Floor | Mini Canal | MICL.01133026/SBR | 11 | 330 | 26 | 26 | 1048 | 1048 | 1048 | 0.024952 | 408 | 0.0097143 | 1194 | 0.028429 | 1.362 | A04 | MICL0.01133026/SBR
Build-In Floor | Mini Canal | MICL.01133026/SDB | 11 | 330 | 26 | 26 | 1048 | 1048 | 1048 | 0.024952 | 408 | 0.0097143 | 1194 | 0.028429 | 1.362 | A04 | MICL0.01133026/SDB
Build-In Floor | Mini Canal | MICL.01133026/SNA | 11 | 330 | 26 | 26 | 1048 | 1048 | 1048 | 0.024952 | 408 | 0.0097143 | 1194 | 0.028429 | 1.362 | A04 | MICL0.01133026/SNA
Build-In Floor | Mini Canal | MICL.01133026/SNC | 11 | 330 | 26 | 26 | 1048 | 1048 | 1048 | 0.024952 | 408 | 0.0097143 | 1194 | 0.028429 | 1.362 | A04 | MICL0.01133026/SNC
Build-In Floor | Mini Canal | MICL.01133034/ANA | 11 | 330 | 34 | 34 | 1022 | 1022 | 1022 | 0.024333 | 398 | 0.0094762 | 1164 | 0.027714 | 1.362 | A04 | MICL0.01133034/ANA
Build-In Floor | Mini Canal | MICL.01133034/DBL | 11 | 330 | 34 | 34 | 1321 | 1321 | 1321 | 0.031452 | 514 | 0.012238 | 1505 | 0.035833 | 1.362 | A04 | MICL0.01133034/DBL
Build-In Floor | Mini Canal | MICL.01133034/DBN | 11 | 330 | 34 | 34 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01133034/DBN
Build-In Floor | Mini Canal | MICL.01133034/DBR | 11 | 330 | 34 | 34 | 1321 | 1321 | 1321 | 0.031452 | 514 | 0.012238 | 1505 | 0.035833 | 1.362 | A04 | MICL0.01133034/DBR
Build-In Floor | Mini Canal | MICL.01133034/DBV | 11 | 330 | 34 | 34 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01133034/DBV
Build-In Floor | Mini Canal | MICL.01133034/DDB | 11 | 330 | 34 | 34 | 1321 | 1321 | 1321 | 0.031452 | 514 | 0.012238 | 1505 | 0.035833 | 1.362 | A04 | MICL0.01133034/DDB
Build-In Floor | Mini Canal | MICL.01133034/DMN | 11 | 330 | 34 | 34 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01133034/DMN
Build-In Floor | Mini Canal | MICL.01133034/DMV | 11 | 330 | 34 | 34 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01133034/DMV
Build-In Floor | Mini Canal | MICL.01133034/DNA | 11 | 330 | 34 | 34 | 1321 | 1321 | 1321 | 0.031452 | 514 | 0.012238 | 1505 | 0.035833 | 1.362 | A04 | MICL0.01133034/DNA
Build-In Floor | Mini Canal | MICL.01133034/DNC | 11 | 330 | 34 | 34 | 1321 | 1321 | 1321 | 0.031452 | 514 | 0.012238 | 1505 | 0.035833 | 1.362 | A04 | MICL0.01133034/DNC
Build-In Floor | Mini Canal | MICL.01133034/DON | 11 | 330 | 34 | 34 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01133034/DON
Build-In Floor | Mini Canal | MICL.01133034/DOV | 11 | 330 | 34 | 34 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01133034/DOV
Build-In Floor | Mini Canal | MICL.01133034/PNC | 11 | 330 | 34 | 34 | 1158 | 1158 | 1158 | 0.027571 | 450 | 0.010714 | 1319 | 0.031405 | 1.362 | A04 | MICL0.01133034/PNC
Build-In Floor | Mini Canal | MICL.01133034/RBL | 11 | 330 | 34 | 34 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01133034/RBL
Build-In Floor | Mini Canal | MICL.01133034/RBN | 11 | 330 | 34 | 34 | 1321 | 1321 | 1321 | 0.031452 | 514 | 0.012238 | 1505 | 0.035833 | 1.362 | A04 | MICL0.01133034/RBN
Build-In Floor | Mini Canal | MICL.01133034/RBR | 11 | 330 | 34 | 34 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01133034/RBR
Build-In Floor | Mini Canal | MICL.01133034/RBV | 11 | 330 | 34 | 34 | 1321 | 1321 | 1321 | 0.031452 | 514 | 0.012238 | 1505 | 0.035833 | 1.362 | A04 | MICL0.01133034/RBV
Build-In Floor | Mini Canal | MICL.01133034/RDB | 11 | 330 | 34 | 34 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01133034/RDB
Build-In Floor | Mini Canal | MICL.01133034/RMN | 11 | 330 | 34 | 34 | 1321 | 1321 | 1321 | 0.031452 | 514 | 0.012238 | 1505 | 0.035833 | 1.362 | A04 | MICL0.01133034/RMN
Build-In Floor | Mini Canal | MICL.01133034/RMV | 11 | 330 | 34 | 34 | 1321 | 1321 | 1321 | 0.031452 | 514 | 0.012238 | 1505 | 0.035833 | 1.362 | A04 | MICL0.01133034/RMV
Build-In Floor | Mini Canal | MICL.01133034/RNA | 11 | 330 | 34 | 34 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01133034/RNA
Build-In Floor | Mini Canal | MICL.01133034/RON | 11 | 330 | 34 | 34 | 1321 | 1321 | 1321 | 0.031452 | 514 | 0.012238 | 1505 | 0.035833 | 1.362 | A04 | MICL0.01133034/RON
Build-In Floor | Mini Canal | MICL.01133034/ROV | 11 | 330 | 34 | 34 | 1321 | 1321 | 1321 | 0.031452 | 514 | 0.012238 | 1505 | 0.035833 | 1.362 | A04 | MICL0.01133034/ROV
Build-In Floor | Mini Canal | MICL.01133034/RSS | 11 | 330 | 34 | 34 | 1308 | 1308 | 1308 | 0.031143 | 509 | 0.012119 | 1490 | 0.035476 | 1.362 | A04 | MICL0.01133034/RSS
Build-In Floor | Mini Canal | MICL.01133034/SBL | 11 | 330 | 34 | 34 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01133034/SBL
Build-In Floor | Mini Canal | MICL.01133034/SBR | 11 | 330 | 34 | 34 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01133034/SBR
Build-In Floor | Mini Canal | MICL.01133034/SDB | 11 | 330 | 34 | 34 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01133034/SDB
Build-In Floor | Mini Canal | MICL.01133034/SNA | 11 | 330 | 34 | 34 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01133034/SNA
Build-In Floor | Mini Canal | MICL.01133034/SNC | 11 | 330 | 34 | 34 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01133034/SNC
Build-In Floor | Mini Canal | MICL.01133042/ANA | 11 | 330 | 42 | 42 | 1436 | 1436 | 1436 | 0.03419 | 559 | 0.01331 | 1636 | 0.038952 | 1.362 | A04 | MICL0.01133042/ANA
Build-In Floor | Mini Canal | MICL.01133042/DBL | 11 | 330 | 42 | 42 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01133042/DBL
Build-In Floor | Mini Canal | MICL.01133042/DBN | 11 | 330 | 42 | 42 | 1780 | 1780 | 1780 | 0.042381 | 692 | 0.016476 | 2027 | 0.048262 | 1.362 | A04 | MICL0.01133042/DBN
Build-In Floor | Mini Canal | MICL.01133042/DBR | 11 | 330 | 42 | 42 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01133042/DBR
Build-In Floor | Mini Canal | MICL.01133042/DBV | 11 | 330 | 42 | 42 | 1780 | 1780 | 1780 | 0.042381 | 692 | 0.016476 | 2027 | 0.048262 | 1.362 | A04 | MICL0.01133042/DBV
Build-In Floor | Mini Canal | MICL.01133042/DDB | 11 | 330 | 42 | 42 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01133042/DDB
Build-In Floor | Mini Canal | MICL.01133042/DMN | 11 | 330 | 42 | 42 | 1780 | 1780 | 1780 | 0.042381 | 692 | 0.016476 | 2027 | 0.048262 | 1.362 | A04 | MICL0.01133042/DMN
Build-In Floor | Mini Canal | MICL.01133042/DMV | 11 | 330 | 42 | 42 | 1780 | 1780 | 1780 | 0.042381 | 692 | 0.016476 | 2027 | 0.048262 | 1.362 | A04 | MICL0.01133042/DMV
Build-In Floor | Mini Canal | MICL.01133042/DNA | 11 | 330 | 42 | 42 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01133042/DNA
Build-In Floor | Mini Canal | MICL.01133042/DNC | 11 | 330 | 42 | 42 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01133042/DNC
Build-In Floor | Mini Canal | MICL.01133042/DON | 11 | 330 | 42 | 42 | 1780 | 1780 | 1780 | 0.042381 | 692 | 0.016476 | 2027 | 0.048262 | 1.362 | A04 | MICL0.01133042/DON
Build-In Floor | Mini Canal | MICL.01133042/DOV | 11 | 330 | 42 | 42 | 1780 | 1780 | 1780 | 0.042381 | 692 | 0.016476 | 2027 | 0.048262 | 1.362 | A04 | MICL0.01133042/DOV
Build-In Floor | Mini Canal | MICL.01133042/PNC | 11 | 330 | 42 | 42 | 1627 | 1627 | 1627 | 0.038738 | 633 | 0.015071 | 1853 | 0.044119 | 1.362 | A04 | MICL0.01133042/PNC
Build-In Floor | Mini Canal | MICL.01133042/RBL | 11 | 330 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01133042/RBL
Build-In Floor | Mini Canal | MICL.01133042/RBN | 11 | 330 | 42 | 42 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01133042/RBN
Build-In Floor | Mini Canal | MICL.01133042/RBR | 11 | 330 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01133042/RBR
Build-In Floor | Mini Canal | MICL.01133042/RBV | 11 | 330 | 42 | 42 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01133042/RBV
Build-In Floor | Mini Canal | MICL.01133042/RDB | 11 | 330 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01133042/RDB
Build-In Floor | Mini Canal | MICL.01133042/RMN | 11 | 330 | 42 | 42 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01133042/RMN
Build-In Floor | Mini Canal | MICL.01133042/RMV | 11 | 330 | 42 | 42 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01133042/RMV
Build-In Floor | Mini Canal | MICL.01133042/RNA | 11 | 330 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01133042/RNA
Build-In Floor | Mini Canal | MICL.01133042/RON | 11 | 330 | 42 | 42 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01133042/RON
Build-In Floor | Mini Canal | MICL.01133042/ROV | 11 | 330 | 42 | 42 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01133042/ROV
Build-In Floor | Mini Canal | MICL.01133042/RSS | 11 | 330 | 42 | 42 | 1837 | 1837 | 1837 | 0.043738 | 715 | 0.017024 | 2092 | 0.04981 | 1.362 | A04 | MICL0.01133042/RSS
Build-In Floor | Mini Canal | MICL.01133042/SBL | 11 | 330 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01133042/SBL
Build-In Floor | Mini Canal | MICL.01133042/SBR | 11 | 330 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01133042/SBR
Build-In Floor | Mini Canal | MICL.01133042/SDB | 11 | 330 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01133042/SDB
Build-In Floor | Mini Canal | MICL.01133042/SNA | 11 | 330 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01133042/SNA
Build-In Floor | Mini Canal | MICL.01133042/SNC | 11 | 330 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01133042/SNC
Build-In Floor | Mini Canal | MICL.01135014/ANA | 11 | 350 | 14 | 14 | 524 | 524 | 524 | 0.012476 | 204 | 0.0048571 | 597 | 0.014214 | 1.362 | A04 | MICL0.01135014/ANA
Build-In Floor | Mini Canal | MICL.01135014/DBL | 11 | 350 | 14 | 14 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01135014/DBL
Build-In Floor | Mini Canal | MICL.01135014/DBN | 11 | 350 | 14 | 14 | 650 | 650 | 650 | 0.015476 | 253 | 0.0060238 | 740 | 0.017619 | 1.362 | A04 | MICL0.01135014/DBN
Build-In Floor | Mini Canal | MICL.01135014/DBR | 11 | 350 | 14 | 14 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01135014/DBR
Build-In Floor | Mini Canal | MICL.01135014/DBV | 11 | 350 | 14 | 14 | 650 | 650 | 650 | 0.015476 | 253 | 0.0060238 | 740 | 0.017619 | 1.362 | A04 | MICL0.01135014/DBV
Build-In Floor | Mini Canal | MICL.01135014/DDB | 11 | 350 | 14 | 14 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01135014/DDB
Build-In Floor | Mini Canal | MICL.01135014/DMN | 11 | 350 | 14 | 14 | 650 | 650 | 650 | 0.015476 | 253 | 0.0060238 | 740 | 0.017619 | 1.362 | A04 | MICL0.01135014/DMN
Build-In Floor | Mini Canal | MICL.01135014/DMV | 11 | 350 | 14 | 14 | 650 | 650 | 650 | 0.015476 | 253 | 0.0060238 | 740 | 0.017619 | 1.362 | A04 | MICL0.01135014/DMV
Build-In Floor | Mini Canal | MICL.01135014/DNA | 11 | 350 | 14 | 14 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01135014/DNA
Build-In Floor | Mini Canal | MICL.01135014/DNC | 11 | 350 | 14 | 14 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01135014/DNC
Build-In Floor | Mini Canal | MICL.01135014/DON | 11 | 350 | 14 | 14 | 650 | 650 | 650 | 0.015476 | 253 | 0.0060238 | 740 | 0.017619 | 1.362 | A04 | MICL0.01135014/DON
Build-In Floor | Mini Canal | MICL.01135014/DOV | 11 | 350 | 14 | 14 | 650 | 650 | 650 | 0.015476 | 253 | 0.0060238 | 740 | 0.017619 | 1.362 | A04 | MICL0.01135014/DOV
Build-In Floor | Mini Canal | MICL.01135014/RBL | 11 | 350 | 14 | 14 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01135014/RBL
Build-In Floor | Mini Canal | MICL.01135014/RBN | 11 | 350 | 14 | 14 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01135014/RBN
Build-In Floor | Mini Canal | MICL.01135014/RBR | 11 | 350 | 14 | 14 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01135014/RBR
Build-In Floor | Mini Canal | MICL.01135014/RBV | 11 | 350 | 14 | 14 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01135014/RBV
Build-In Floor | Mini Canal | MICL.01135014/RDB | 11 | 350 | 14 | 14 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01135014/RDB
Build-In Floor | Mini Canal | MICL.01135014/RMN | 11 | 350 | 14 | 14 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01135014/RMN
Build-In Floor | Mini Canal | MICL.01135014/RMV | 11 | 350 | 14 | 14 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01135014/RMV
Build-In Floor | Mini Canal | MICL.01135014/RNA | 11 | 350 | 14 | 14 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01135014/RNA
Build-In Floor | Mini Canal | MICL.01135014/RON | 11 | 350 | 14 | 14 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01135014/RON
Build-In Floor | Mini Canal | MICL.01135014/ROV | 11 | 350 | 14 | 14 | 678 | 678 | 678 | 0.016143 | 264 | 0.0062857 | 772 | 0.018381 | 1.362 | A04 | MICL0.01135014/ROV
Build-In Floor | Mini Canal | MICL.01135014/RSS | 11 | 350 | 14 | 14 | 671 | 671 | 671 | 0.015976 | 261 | 0.0062143 | 764 | 0.01819 | 1.362 | A04 | MICL0.01135014/RSS
Build-In Floor | Mini Canal | MICL.01135014/SBL | 11 | 350 | 14 | 14 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01135014/SBL
Build-In Floor | Mini Canal | MICL.01135014/SBR | 11 | 350 | 14 | 14 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01135014/SBR
Build-In Floor | Mini Canal | MICL.01135014/SDB | 11 | 350 | 14 | 14 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01135014/SDB
Build-In Floor | Mini Canal | MICL.01135014/SNA | 11 | 350 | 14 | 14 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01135014/SNA
Build-In Floor | Mini Canal | MICL.01135014/SNC | 11 | 350 | 14 | 14 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01135014/SNC
Build-In Floor | Mini Canal | MICL.01135018/ANA | 11 | 350 | 18 | 18 | 621 | 621 | 621 | 0.014786 | 242 | 0.0057619 | 707 | 0.016833 | 1.362 | A04 | MICL0.01135018/ANA
Build-In Floor | Mini Canal | MICL.01135018/DBL | 11 | 350 | 18 | 18 | 803 | 803 | 803 | 0.019119 | 312 | 0.0074286 | 915 | 0.021786 | 1.362 | A04 | MICL0.01135018/DBL
Build-In Floor | Mini Canal | MICL.01135018/DBN | 11 | 350 | 18 | 18 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01135018/DBN
Build-In Floor | Mini Canal | MICL.01135018/DBR | 11 | 350 | 18 | 18 | 803 | 803 | 803 | 0.019119 | 312 | 0.0074286 | 915 | 0.021786 | 1.362 | A04 | MICL0.01135018/DBR
Build-In Floor | Mini Canal | MICL.01135018/DBV | 11 | 350 | 18 | 18 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01135018/DBV
Build-In Floor | Mini Canal | MICL.01135018/DDB | 11 | 350 | 18 | 18 | 803 | 803 | 803 | 0.019119 | 312 | 0.0074286 | 915 | 0.021786 | 1.362 | A04 | MICL0.01135018/DDB
Build-In Floor | Mini Canal | MICL.01135018/DMN | 11 | 350 | 18 | 18 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01135018/DMN
Build-In Floor | Mini Canal | MICL.01135018/DMV | 11 | 350 | 18 | 18 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01135018/DMV
Build-In Floor | Mini Canal | MICL.01135018/DNA | 11 | 350 | 18 | 18 | 803 | 803 | 803 | 0.019119 | 312 | 0.0074286 | 915 | 0.021786 | 1.362 | A04 | MICL0.01135018/DNA
Build-In Floor | Mini Canal | MICL.01135018/DNC | 11 | 350 | 18 | 18 | 803 | 803 | 803 | 0.019119 | 312 | 0.0074286 | 915 | 0.021786 | 1.362 | A04 | MICL0.01135018/DNC
Build-In Floor | Mini Canal | MICL.01135018/DON | 11 | 350 | 18 | 18 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01135018/DON
Build-In Floor | Mini Canal | MICL.01135018/DOV | 11 | 350 | 18 | 18 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01135018/DOV
Build-In Floor | Mini Canal | MICL.01135018/RBL | 11 | 350 | 18 | 18 | 828 | 828 | 828 | 0.019714 | 322 | 0.0076667 | 943 | 0.022452 | 1.362 | A04 | MICL0.01135018/RBL
Build-In Floor | Mini Canal | MICL.01135018/RBN | 11 | 350 | 18 | 18 | 803 | 803 | 803 | 0.019119 | 312 | 0.0074286 | 915 | 0.021786 | 1.362 | A04 | MICL0.01135018/RBN
Build-In Floor | Mini Canal | MICL.01135018/RBR | 11 | 350 | 18 | 18 | 828 | 828 | 828 | 0.019714 | 322 | 0.0076667 | 943 | 0.022452 | 1.362 | A04 | MICL0.01135018/RBR
Build-In Floor | Mini Canal | MICL.01135018/RBV | 11 | 350 | 18 | 18 | 803 | 803 | 803 | 0.019119 | 312 | 0.0074286 | 915 | 0.021786 | 1.362 | A04 | MICL0.01135018/RBV
Build-In Floor | Mini Canal | MICL.01135018/RDB | 11 | 350 | 18 | 18 | 828 | 828 | 828 | 0.019714 | 322 | 0.0076667 | 943 | 0.022452 | 1.362 | A04 | MICL0.01135018/RDB
Build-In Floor | Mini Canal | MICL.01135018/RMN | 11 | 350 | 18 | 18 | 803 | 803 | 803 | 0.019119 | 312 | 0.0074286 | 915 | 0.021786 | 1.362 | A04 | MICL0.01135018/RMN
Build-In Floor | Mini Canal | MICL.01135018/RMV | 11 | 350 | 18 | 18 | 803 | 803 | 803 | 0.019119 | 312 | 0.0074286 | 915 | 0.021786 | 1.362 | A04 | MICL0.01135018/RMV
Build-In Floor | Mini Canal | MICL.01135018/RNA | 11 | 350 | 18 | 18 | 828 | 828 | 828 | 0.019714 | 322 | 0.0076667 | 943 | 0.022452 | 1.362 | A04 | MICL0.01135018/RNA
Build-In Floor | Mini Canal | MICL.01135018/RON | 11 | 350 | 18 | 18 | 803 | 803 | 803 | 0.019119 | 312 | 0.0074286 | 915 | 0.021786 | 1.362 | A04 | MICL0.01135018/RON
Build-In Floor | Mini Canal | MICL.01135018/ROV | 11 | 350 | 18 | 18 | 803 | 803 | 803 | 0.019119 | 312 | 0.0074286 | 915 | 0.021786 | 1.362 | A04 | MICL0.01135018/ROV
Build-In Floor | Mini Canal | MICL.01135018/RSS | 11 | 350 | 18 | 18 | 795 | 795 | 795 | 0.018929 | 309 | 0.0073571 | 906 | 0.021571 | 1.362 | A04 | MICL0.01135018/RSS
Build-In Floor | Mini Canal | MICL.01135018/SBL | 11 | 350 | 18 | 18 | 828 | 828 | 828 | 0.019714 | 322 | 0.0076667 | 943 | 0.022452 | 1.362 | A04 | MICL0.01135018/SBL
Build-In Floor | Mini Canal | MICL.01135018/SBR | 11 | 350 | 18 | 18 | 828 | 828 | 828 | 0.019714 | 322 | 0.0076667 | 943 | 0.022452 | 1.362 | A04 | MICL0.01135018/SBR
Build-In Floor | Mini Canal | MICL.01135018/SDB | 11 | 350 | 18 | 18 | 828 | 828 | 828 | 0.019714 | 322 | 0.0076667 | 943 | 0.022452 | 1.362 | A04 | MICL0.01135018/SDB
Build-In Floor | Mini Canal | MICL.01135018/SNA | 11 | 350 | 18 | 18 | 828 | 828 | 828 | 0.019714 | 322 | 0.0076667 | 943 | 0.022452 | 1.362 | A04 | MICL0.01135018/SNA
Build-In Floor | Mini Canal | MICL.01135018/SNC | 11 | 350 | 18 | 18 | 828 | 828 | 828 | 0.019714 | 322 | 0.0076667 | 943 | 0.022452 | 1.362 | A04 | MICL0.01135018/SNC
Build-In Floor | Mini Canal | MICL.01135026/ANA | 11 | 350 | 26 | 26 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.01135026/ANA
Build-In Floor | Mini Canal | MICL.01135026/DBL | 11 | 350 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01135026/DBL
Build-In Floor | Mini Canal | MICL.01135026/DBN | 11 | 350 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 405 | 0.0096429 | 1186 | 0.028238 | 1.362 | A04 | MICL0.01135026/DBN
Build-In Floor | Mini Canal | MICL.01135026/DBR | 11 | 350 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01135026/DBR
Build-In Floor | Mini Canal | MICL.01135026/DBV | 11 | 350 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 405 | 0.0096429 | 1186 | 0.028238 | 1.362 | A04 | MICL0.01135026/DBV
Build-In Floor | Mini Canal | MICL.01135026/DDB | 11 | 350 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01135026/DDB
Build-In Floor | Mini Canal | MICL.01135026/DMN | 11 | 350 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 405 | 0.0096429 | 1186 | 0.028238 | 1.362 | A04 | MICL0.01135026/DMN
Build-In Floor | Mini Canal | MICL.01135026/DMV | 11 | 350 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 405 | 0.0096429 | 1186 | 0.028238 | 1.362 | A04 | MICL0.01135026/DMV
Build-In Floor | Mini Canal | MICL.01135026/DNA | 11 | 350 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01135026/DNA
Build-In Floor | Mini Canal | MICL.01135026/DNC | 11 | 350 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01135026/DNC
Build-In Floor | Mini Canal | MICL.01135026/DON | 11 | 350 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 405 | 0.0096429 | 1186 | 0.028238 | 1.362 | A04 | MICL0.01135026/DON
Build-In Floor | Mini Canal | MICL.01135026/DOV | 11 | 350 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 405 | 0.0096429 | 1186 | 0.028238 | 1.362 | A04 | MICL0.01135026/DOV
Build-In Floor | Mini Canal | MICL.01135026/PNC | 11 | 350 | 26 | 26 | 951 | 951 | 951 | 0.022643 | 370 | 0.0088095 | 1083 | 0.025786 | 1.362 | A04 | MICL0.01135026/PNC
Build-In Floor | Mini Canal | MICL.01135026/RBL | 11 | 350 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01135026/RBL
Build-In Floor | Mini Canal | MICL.01135026/RBN | 11 | 350 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01135026/RBN
Build-In Floor | Mini Canal | MICL.01135026/RBR | 11 | 350 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01135026/RBR
Build-In Floor | Mini Canal | MICL.01135026/RBV | 11 | 350 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01135026/RBV
Build-In Floor | Mini Canal | MICL.01135026/RDB | 11 | 350 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01135026/RDB
Build-In Floor | Mini Canal | MICL.01135026/RMN | 11 | 350 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01135026/RMN
Build-In Floor | Mini Canal | MICL.01135026/RMV | 11 | 350 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01135026/RMV
Build-In Floor | Mini Canal | MICL.01135026/RNA | 11 | 350 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01135026/RNA
Build-In Floor | Mini Canal | MICL.01135026/RON | 11 | 350 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01135026/RON
Build-In Floor | Mini Canal | MICL.01135026/ROV | 11 | 350 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01135026/ROV
Build-In Floor | Mini Canal | MICL.01135026/RSS | 11 | 350 | 26 | 26 | 1074 | 1074 | 1074 | 0.025571 | 418 | 0.0099524 | 1223 | 0.029119 | 1.362 | A04 | MICL0.01135026/RSS
Build-In Floor | Mini Canal | MICL.01135026/SBL | 11 | 350 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01135026/SBL
Build-In Floor | Mini Canal | MICL.01135026/SBR | 11 | 350 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01135026/SBR
Build-In Floor | Mini Canal | MICL.01135026/SDB | 11 | 350 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01135026/SDB
Build-In Floor | Mini Canal | MICL.01135026/SNA | 11 | 350 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01135026/SNA
Build-In Floor | Mini Canal | MICL.01135026/SNC | 11 | 350 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01135026/SNC
Build-In Floor | Mini Canal | MICL.01135034/ANA | 11 | 350 | 34 | 34 | 1089 | 1089 | 1089 | 0.025929 | 424 | 0.010095 | 1240 | 0.029524 | 1.362 | A04 | MICL0.01135034/ANA
Build-In Floor | Mini Canal | MICL.01135034/DBL | 11 | 350 | 34 | 34 | 1408 | 1408 | 1408 | 0.033524 | 548 | 0.013048 | 1604 | 0.03819 | 1.362 | A04 | MICL0.01135034/DBL
Build-In Floor | Mini Canal | MICL.01135034/DBN | 11 | 350 | 34 | 34 | 1350 | 1350 | 1350 | 0.032143 | 525 | 0.0125 | 1538 | 0.036619 | 1.362 | A04 | MICL0.01135034/DBN
Build-In Floor | Mini Canal | MICL.01135034/DBR | 11 | 350 | 34 | 34 | 1408 | 1408 | 1408 | 0.033524 | 548 | 0.013048 | 1604 | 0.03819 | 1.362 | A04 | MICL0.01135034/DBR
Build-In Floor | Mini Canal | MICL.01135034/DBV | 11 | 350 | 34 | 34 | 1350 | 1350 | 1350 | 0.032143 | 525 | 0.0125 | 1538 | 0.036619 | 1.362 | A04 | MICL0.01135034/DBV
Build-In Floor | Mini Canal | MICL.01135034/DDB | 11 | 350 | 34 | 34 | 1408 | 1408 | 1408 | 0.033524 | 548 | 0.013048 | 1604 | 0.03819 | 1.362 | A04 | MICL0.01135034/DDB
Build-In Floor | Mini Canal | MICL.01135034/DMN | 11 | 350 | 34 | 34 | 1350 | 1350 | 1350 | 0.032143 | 525 | 0.0125 | 1538 | 0.036619 | 1.362 | A04 | MICL0.01135034/DMN
Build-In Floor | Mini Canal | MICL.01135034/DMV | 11 | 350 | 34 | 34 | 1350 | 1350 | 1350 | 0.032143 | 525 | 0.0125 | 1538 | 0.036619 | 1.362 | A04 | MICL0.01135034/DMV
Build-In Floor | Mini Canal | MICL.01135034/DNA | 11 | 350 | 34 | 34 | 1408 | 1408 | 1408 | 0.033524 | 548 | 0.013048 | 1604 | 0.03819 | 1.362 | A04 | MICL0.01135034/DNA
Build-In Floor | Mini Canal | MICL.01135034/DNC | 11 | 350 | 34 | 34 | 1408 | 1408 | 1408 | 0.033524 | 548 | 0.013048 | 1604 | 0.03819 | 1.362 | A04 | MICL0.01135034/DNC
Build-In Floor | Mini Canal | MICL.01135034/DON | 11 | 350 | 34 | 34 | 1350 | 1350 | 1350 | 0.032143 | 525 | 0.0125 | 1538 | 0.036619 | 1.362 | A04 | MICL0.01135034/DON
Build-In Floor | Mini Canal | MICL.01135034/DOV | 11 | 350 | 34 | 34 | 1350 | 1350 | 1350 | 0.032143 | 525 | 0.0125 | 1538 | 0.036619 | 1.362 | A04 | MICL0.01135034/DOV
Build-In Floor | Mini Canal | MICL.01135034/PNC | 11 | 350 | 34 | 34 | 1234 | 1234 | 1234 | 0.029381 | 480 | 0.011429 | 1406 | 0.033476 | 1.362 | A04 | MICL0.01135034/PNC
Build-In Floor | Mini Canal | MICL.01135034/RBL | 11 | 350 | 34 | 34 | 1452 | 1452 | 1452 | 0.034571 | 565 | 0.013452 | 1654 | 0.039381 | 1.362 | A04 | MICL0.01135034/RBL
Build-In Floor | Mini Canal | MICL.01135034/RBN | 11 | 350 | 34 | 34 | 1408 | 1408 | 1408 | 0.033524 | 548 | 0.013048 | 1604 | 0.03819 | 1.362 | A04 | MICL0.01135034/RBN
Build-In Floor | Mini Canal | MICL.01135034/RBR | 11 | 350 | 34 | 34 | 1452 | 1452 | 1452 | 0.034571 | 565 | 0.013452 | 1654 | 0.039381 | 1.362 | A04 | MICL0.01135034/RBR
Build-In Floor | Mini Canal | MICL.01135034/RBV | 11 | 350 | 34 | 34 | 1408 | 1408 | 1408 | 0.033524 | 548 | 0.013048 | 1604 | 0.03819 | 1.362 | A04 | MICL0.01135034/RBV
Build-In Floor | Mini Canal | MICL.01135034/RDB | 11 | 350 | 34 | 34 | 1452 | 1452 | 1452 | 0.034571 | 565 | 0.013452 | 1654 | 0.039381 | 1.362 | A04 | MICL0.01135034/RDB
Build-In Floor | Mini Canal | MICL.01135034/RMN | 11 | 350 | 34 | 34 | 1408 | 1408 | 1408 | 0.033524 | 548 | 0.013048 | 1604 | 0.03819 | 1.362 | A04 | MICL0.01135034/RMN
Build-In Floor | Mini Canal | MICL.01135034/RMV | 11 | 350 | 34 | 34 | 1408 | 1408 | 1408 | 0.033524 | 548 | 0.013048 | 1604 | 0.03819 | 1.362 | A04 | MICL0.01135034/RMV
Build-In Floor | Mini Canal | MICL.01135034/RNA | 11 | 350 | 34 | 34 | 1452 | 1452 | 1452 | 0.034571 | 565 | 0.013452 | 1654 | 0.039381 | 1.362 | A04 | MICL0.01135034/RNA
Build-In Floor | Mini Canal | MICL.01135034/RON | 11 | 350 | 34 | 34 | 1408 | 1408 | 1408 | 0.033524 | 548 | 0.013048 | 1604 | 0.03819 | 1.362 | A04 | MICL0.01135034/RON
Build-In Floor | Mini Canal | MICL.01135034/ROV | 11 | 350 | 34 | 34 | 1408 | 1408 | 1408 | 0.033524 | 548 | 0.013048 | 1604 | 0.03819 | 1.362 | A04 | MICL0.01135034/ROV
Build-In Floor | Mini Canal | MICL.01135034/RSS | 11 | 350 | 34 | 34 | 1394 | 1394 | 1394 | 0.03319 | 542 | 0.012905 | 1588 | 0.03781 | 1.362 | A04 | MICL0.01135034/RSS
Build-In Floor | Mini Canal | MICL.01135034/SBL | 11 | 350 | 34 | 34 | 1452 | 1452 | 1452 | 0.034571 | 565 | 0.013452 | 1654 | 0.039381 | 1.362 | A04 | MICL0.01135034/SBL
Build-In Floor | Mini Canal | MICL.01135034/SBR | 11 | 350 | 34 | 34 | 1452 | 1452 | 1452 | 0.034571 | 565 | 0.013452 | 1654 | 0.039381 | 1.362 | A04 | MICL0.01135034/SBR
Build-In Floor | Mini Canal | MICL.01135034/SDB | 11 | 350 | 34 | 34 | 1452 | 1452 | 1452 | 0.034571 | 565 | 0.013452 | 1654 | 0.039381 | 1.362 | A04 | MICL0.01135034/SDB
Build-In Floor | Mini Canal | MICL.01135034/SNA | 11 | 350 | 34 | 34 | 1452 | 1452 | 1452 | 0.034571 | 565 | 0.013452 | 1654 | 0.039381 | 1.362 | A04 | MICL0.01135034/SNA
Build-In Floor | Mini Canal | MICL.01135034/SNC | 11 | 350 | 34 | 34 | 1452 | 1452 | 1452 | 0.034571 | 565 | 0.013452 | 1654 | 0.039381 | 1.362 | A04 | MICL0.01135034/SNC
Build-In Floor | Mini Canal | MICL.01135042/ANA | 11 | 350 | 42 | 42 | 1532 | 1532 | 1532 | 0.036476 | 596 | 0.01419 | 1745 | 0.041548 | 1.362 | A04 | MICL0.01135042/ANA
Build-In Floor | Mini Canal | MICL.01135042/DBL | 11 | 350 | 42 | 42 | 1981 | 1981 | 1981 | 0.047167 | 771 | 0.018357 | 2256 | 0.053714 | 1.362 | A04 | MICL0.01135042/DBL
Build-In Floor | Mini Canal | MICL.01135042/DBN | 11 | 350 | 42 | 42 | 1899 | 1899 | 1899 | 0.045214 | 739 | 0.017595 | 2163 | 0.0515 | 1.362 | A04 | MICL0.01135042/DBN
Build-In Floor | Mini Canal | MICL.01135042/DBR | 11 | 350 | 42 | 42 | 1981 | 1981 | 1981 | 0.047167 | 771 | 0.018357 | 2256 | 0.053714 | 1.362 | A04 | MICL0.01135042/DBR
Build-In Floor | Mini Canal | MICL.01135042/DBV | 11 | 350 | 42 | 42 | 1899 | 1899 | 1899 | 0.045214 | 739 | 0.017595 | 2163 | 0.0515 | 1.362 | A04 | MICL0.01135042/DBV
Build-In Floor | Mini Canal | MICL.01135042/DDB | 11 | 350 | 42 | 42 | 1981 | 1981 | 1981 | 0.047167 | 771 | 0.018357 | 2256 | 0.053714 | 1.362 | A04 | MICL0.01135042/DDB
Build-In Floor | Mini Canal | MICL.01135042/DMN | 11 | 350 | 42 | 42 | 1899 | 1899 | 1899 | 0.045214 | 739 | 0.017595 | 2163 | 0.0515 | 1.362 | A04 | MICL0.01135042/DMN
Build-In Floor | Mini Canal | MICL.01135042/DMV | 11 | 350 | 42 | 42 | 1899 | 1899 | 1899 | 0.045214 | 739 | 0.017595 | 2163 | 0.0515 | 1.362 | A04 | MICL0.01135042/DMV
Build-In Floor | Mini Canal | MICL.01135042/DNA | 11 | 350 | 42 | 42 | 1981 | 1981 | 1981 | 0.047167 | 771 | 0.018357 | 2256 | 0.053714 | 1.362 | A04 | MICL0.01135042/DNA
Build-In Floor | Mini Canal | MICL.01135042/DNC | 11 | 350 | 42 | 42 | 1981 | 1981 | 1981 | 0.047167 | 771 | 0.018357 | 2256 | 0.053714 | 1.362 | A04 | MICL0.01135042/DNC
Build-In Floor | Mini Canal | MICL.01135042/DON | 11 | 350 | 42 | 42 | 1899 | 1899 | 1899 | 0.045214 | 739 | 0.017595 | 2163 | 0.0515 | 1.362 | A04 | MICL0.01135042/DON
Build-In Floor | Mini Canal | MICL.01135042/DOV | 11 | 350 | 42 | 42 | 1899 | 1899 | 1899 | 0.045214 | 739 | 0.017595 | 2163 | 0.0515 | 1.362 | A04 | MICL0.01135042/DOV
Build-In Floor | Mini Canal | MICL.01135042/PNC | 11 | 350 | 42 | 42 | 1736 | 1736 | 1736 | 0.041333 | 675 | 0.016071 | 1977 | 0.047071 | 1.362 | A04 | MICL0.01135042/PNC
Build-In Floor | Mini Canal | MICL.01135042/RBL | 11 | 350 | 42 | 42 | 2042 | 2042 | 2042 | 0.048619 | 794 | 0.018905 | 2326 | 0.055381 | 1.362 | A04 | MICL0.01135042/RBL
Build-In Floor | Mini Canal | MICL.01135042/RBN | 11 | 350 | 42 | 42 | 1981 | 1981 | 1981 | 0.047167 | 771 | 0.018357 | 2256 | 0.053714 | 1.362 | A04 | MICL0.01135042/RBN
Build-In Floor | Mini Canal | MICL.01135042/RBR | 11 | 350 | 42 | 42 | 2042 | 2042 | 2042 | 0.048619 | 794 | 0.018905 | 2326 | 0.055381 | 1.362 | A04 | MICL0.01135042/RBR
Build-In Floor | Mini Canal | MICL.01135042/RBV | 11 | 350 | 42 | 42 | 1981 | 1981 | 1981 | 0.047167 | 771 | 0.018357 | 2256 | 0.053714 | 1.362 | A04 | MICL0.01135042/RBV
Build-In Floor | Mini Canal | MICL.01135042/RDB | 11 | 350 | 42 | 42 | 2042 | 2042 | 2042 | 0.048619 | 794 | 0.018905 | 2326 | 0.055381 | 1.362 | A04 | MICL0.01135042/RDB
Build-In Floor | Mini Canal | MICL.01135042/RMN | 11 | 350 | 42 | 42 | 1981 | 1981 | 1981 | 0.047167 | 771 | 0.018357 | 2256 | 0.053714 | 1.362 | A04 | MICL0.01135042/RMN
Build-In Floor | Mini Canal | MICL.01135042/RMV | 11 | 350 | 42 | 42 | 1981 | 1981 | 1981 | 0.047167 | 771 | 0.018357 | 2256 | 0.053714 | 1.362 | A04 | MICL0.01135042/RMV
Build-In Floor | Mini Canal | MICL.01135042/RNA | 11 | 350 | 42 | 42 | 2042 | 2042 | 2042 | 0.048619 | 794 | 0.018905 | 2326 | 0.055381 | 1.362 | A04 | MICL0.01135042/RNA
Build-In Floor | Mini Canal | MICL.01135042/RON | 11 | 350 | 42 | 42 | 1981 | 1981 | 1981 | 0.047167 | 771 | 0.018357 | 2256 | 0.053714 | 1.362 | A04 | MICL0.01135042/RON
Build-In Floor | Mini Canal | MICL.01135042/ROV | 11 | 350 | 42 | 42 | 1981 | 1981 | 1981 | 0.047167 | 771 | 0.018357 | 2256 | 0.053714 | 1.362 | A04 | MICL0.01135042/ROV
Build-In Floor | Mini Canal | MICL.01135042/RSS | 11 | 350 | 42 | 42 | 1960 | 1960 | 1960 | 0.046667 | 762 | 0.018143 | 2232 | 0.053143 | 1.362 | A04 | MICL0.01135042/RSS
Build-In Floor | Mini Canal | MICL.01135042/SBL | 11 | 350 | 42 | 42 | 2042 | 2042 | 2042 | 0.048619 | 794 | 0.018905 | 2326 | 0.055381 | 1.362 | A04 | MICL0.01135042/SBL
Build-In Floor | Mini Canal | MICL.01135042/SBR | 11 | 350 | 42 | 42 | 2042 | 2042 | 2042 | 0.048619 | 794 | 0.018905 | 2326 | 0.055381 | 1.362 | A04 | MICL0.01135042/SBR
Build-In Floor | Mini Canal | MICL.01135042/SDB | 11 | 350 | 42 | 42 | 2042 | 2042 | 2042 | 0.048619 | 794 | 0.018905 | 2326 | 0.055381 | 1.362 | A04 | MICL0.01135042/SDB
Build-In Floor | Mini Canal | MICL.01135042/SNA | 11 | 350 | 42 | 42 | 2042 | 2042 | 2042 | 0.048619 | 794 | 0.018905 | 2326 | 0.055381 | 1.362 | A04 | MICL0.01135042/SNA
Build-In Floor | Mini Canal | MICL.01135042/SNC | 11 | 350 | 42 | 42 | 2042 | 2042 | 2042 | 0.048619 | 794 | 0.018905 | 2326 | 0.055381 | 1.362 | A04 | MICL0.01135042/SNC
Build-In Floor | Mini Canal | MICL.01137014/ANA | 11 | 370 | 14 | 14 | 557 | 557 | 557 | 0.013262 | 217 | 0.0051667 | 634 | 0.015095 | 1.362 | A04 | MICL0.01137014/ANA
Build-In Floor | Mini Canal | MICL.01137014/DBL | 11 | 370 | 14 | 14 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01137014/DBL
Build-In Floor | Mini Canal | MICL.01137014/DBN | 11 | 370 | 14 | 14 | 691 | 691 | 691 | 0.016452 | 269 | 0.0064048 | 787 | 0.018738 | 1.362 | A04 | MICL0.01137014/DBN
Build-In Floor | Mini Canal | MICL.01137014/DBR | 11 | 370 | 14 | 14 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01137014/DBR
Build-In Floor | Mini Canal | MICL.01137014/DBV | 11 | 370 | 14 | 14 | 691 | 691 | 691 | 0.016452 | 269 | 0.0064048 | 787 | 0.018738 | 1.362 | A04 | MICL0.01137014/DBV
Build-In Floor | Mini Canal | MICL.01137014/DDB | 11 | 370 | 14 | 14 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01137014/DDB
Build-In Floor | Mini Canal | MICL.01137014/DMN | 11 | 370 | 14 | 14 | 691 | 691 | 691 | 0.016452 | 269 | 0.0064048 | 787 | 0.018738 | 1.362 | A04 | MICL0.01137014/DMN
Build-In Floor | Mini Canal | MICL.01137014/DMV | 11 | 370 | 14 | 14 | 691 | 691 | 691 | 0.016452 | 269 | 0.0064048 | 787 | 0.018738 | 1.362 | A04 | MICL0.01137014/DMV
Build-In Floor | Mini Canal | MICL.01137014/DNA | 11 | 370 | 14 | 14 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01137014/DNA
Build-In Floor | Mini Canal | MICL.01137014/DNC | 11 | 370 | 14 | 14 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01137014/DNC
Build-In Floor | Mini Canal | MICL.01137014/DON | 11 | 370 | 14 | 14 | 691 | 691 | 691 | 0.016452 | 269 | 0.0064048 | 787 | 0.018738 | 1.362 | A04 | MICL0.01137014/DON
Build-In Floor | Mini Canal | MICL.01137014/DOV | 11 | 370 | 14 | 14 | 691 | 691 | 691 | 0.016452 | 269 | 0.0064048 | 787 | 0.018738 | 1.362 | A04 | MICL0.01137014/DOV
Build-In Floor | Mini Canal | MICL.01137014/RBL | 11 | 370 | 14 | 14 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01137014/RBL
Build-In Floor | Mini Canal | MICL.01137014/RBN | 11 | 370 | 14 | 14 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01137014/RBN
Build-In Floor | Mini Canal | MICL.01137014/RBR | 11 | 370 | 14 | 14 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01137014/RBR
Build-In Floor | Mini Canal | MICL.01137014/RBV | 11 | 370 | 14 | 14 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01137014/RBV
Build-In Floor | Mini Canal | MICL.01137014/RDB | 11 | 370 | 14 | 14 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01137014/RDB
Build-In Floor | Mini Canal | MICL.01137014/RMN | 11 | 370 | 14 | 14 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01137014/RMN
Build-In Floor | Mini Canal | MICL.01137014/RMV | 11 | 370 | 14 | 14 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01137014/RMV
Build-In Floor | Mini Canal | MICL.01137014/RNA | 11 | 370 | 14 | 14 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01137014/RNA
Build-In Floor | Mini Canal | MICL.01137014/RON | 11 | 370 | 14 | 14 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01137014/RON
Build-In Floor | Mini Canal | MICL.01137014/ROV | 11 | 370 | 14 | 14 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01137014/ROV
Build-In Floor | Mini Canal | MICL.01137014/RSS | 11 | 370 | 14 | 14 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.01137014/RSS
Build-In Floor | Mini Canal | MICL.01137014/SBL | 11 | 370 | 14 | 14 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01137014/SBL
Build-In Floor | Mini Canal | MICL.01137014/SBR | 11 | 370 | 14 | 14 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01137014/SBR
Build-In Floor | Mini Canal | MICL.01137014/SDB | 11 | 370 | 14 | 14 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01137014/SDB
Build-In Floor | Mini Canal | MICL.01137014/SNA | 11 | 370 | 14 | 14 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01137014/SNA
Build-In Floor | Mini Canal | MICL.01137014/SNC | 11 | 370 | 14 | 14 | 743 | 743 | 743 | 0.01769 | 289 | 0.006881 | 846 | 0.020143 | 1.362 | A04 | MICL0.01137014/SNC
Build-In Floor | Mini Canal | MICL.01137018/ANA | 11 | 370 | 18 | 18 | 661 | 661 | 661 | 0.015738 | 257 | 0.006119 | 753 | 0.017929 | 1.362 | A04 | MICL0.01137018/ANA
Build-In Floor | Mini Canal | MICL.01137018/DBL | 11 | 370 | 18 | 18 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01137018/DBL
Build-In Floor | Mini Canal | MICL.01137018/DBN | 11 | 370 | 18 | 18 | 819 | 819 | 819 | 0.0195 | 319 | 0.0075952 | 933 | 0.022214 | 1.362 | A04 | MICL0.01137018/DBN
Build-In Floor | Mini Canal | MICL.01137018/DBR | 11 | 370 | 18 | 18 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01137018/DBR
Build-In Floor | Mini Canal | MICL.01137018/DBV | 11 | 370 | 18 | 18 | 819 | 819 | 819 | 0.0195 | 319 | 0.0075952 | 933 | 0.022214 | 1.362 | A04 | MICL0.01137018/DBV
Build-In Floor | Mini Canal | MICL.01137018/DDB | 11 | 370 | 18 | 18 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01137018/DDB
Build-In Floor | Mini Canal | MICL.01137018/DMN | 11 | 370 | 18 | 18 | 819 | 819 | 819 | 0.0195 | 319 | 0.0075952 | 933 | 0.022214 | 1.362 | A04 | MICL0.01137018/DMN
Build-In Floor | Mini Canal | MICL.01137018/DMV | 11 | 370 | 18 | 18 | 819 | 819 | 819 | 0.0195 | 319 | 0.0075952 | 933 | 0.022214 | 1.362 | A04 | MICL0.01137018/DMV
Build-In Floor | Mini Canal | MICL.01137018/DNA | 11 | 370 | 18 | 18 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01137018/DNA
Build-In Floor | Mini Canal | MICL.01137018/DNC | 11 | 370 | 18 | 18 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01137018/DNC
Build-In Floor | Mini Canal | MICL.01137018/DON | 11 | 370 | 18 | 18 | 819 | 819 | 819 | 0.0195 | 319 | 0.0075952 | 933 | 0.022214 | 1.362 | A04 | MICL0.01137018/DON
Build-In Floor | Mini Canal | MICL.01137018/DOV | 11 | 370 | 18 | 18 | 819 | 819 | 819 | 0.0195 | 319 | 0.0075952 | 933 | 0.022214 | 1.362 | A04 | MICL0.01137018/DOV
Build-In Floor | Mini Canal | MICL.01137018/RBL | 11 | 370 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01137018/RBL
Build-In Floor | Mini Canal | MICL.01137018/RBN | 11 | 370 | 18 | 18 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01137018/RBN
Build-In Floor | Mini Canal | MICL.01137018/RBR | 11 | 370 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01137018/RBR
Build-In Floor | Mini Canal | MICL.01137018/RBV | 11 | 370 | 18 | 18 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01137018/RBV
Build-In Floor | Mini Canal | MICL.01137018/RDB | 11 | 370 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01137018/RDB
Build-In Floor | Mini Canal | MICL.01137018/RMN | 11 | 370 | 18 | 18 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01137018/RMN
Build-In Floor | Mini Canal | MICL.01137018/RMV | 11 | 370 | 18 | 18 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01137018/RMV
Build-In Floor | Mini Canal | MICL.01137018/RNA | 11 | 370 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01137018/RNA
Build-In Floor | Mini Canal | MICL.01137018/RON | 11 | 370 | 18 | 18 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01137018/RON
Build-In Floor | Mini Canal | MICL.01137018/ROV | 11 | 370 | 18 | 18 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01137018/ROV
Build-In Floor | Mini Canal | MICL.01137018/RSS | 11 | 370 | 18 | 18 | 846 | 846 | 846 | 0.020143 | 329 | 0.0078333 | 964 | 0.022952 | 1.362 | A04 | MICL0.01137018/RSS
Build-In Floor | Mini Canal | MICL.01137018/SBL | 11 | 370 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01137018/SBL
Build-In Floor | Mini Canal | MICL.01137018/SBR | 11 | 370 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01137018/SBR
Build-In Floor | Mini Canal | MICL.01137018/SDB | 11 | 370 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01137018/SDB
Build-In Floor | Mini Canal | MICL.01137018/SNA | 11 | 370 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01137018/SNA
Build-In Floor | Mini Canal | MICL.01137018/SNC | 11 | 370 | 18 | 18 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01137018/SNC
Build-In Floor | Mini Canal | MICL.01137026/ANA | 11 | 370 | 26 | 26 | 891 | 891 | 891 | 0.021214 | 347 | 0.0082619 | 1015 | 0.024167 | 1.362 | A04 | MICL0.01137026/ANA
Build-In Floor | Mini Canal | MICL.01137026/DBL | 11 | 370 | 26 | 26 | 1152 | 1152 | 1152 | 0.027429 | 448 | 0.010667 | 1312 | 0.031238 | 1.362 | A04 | MICL0.01137026/DBL
Build-In Floor | Mini Canal | MICL.01137026/DBN | 11 | 370 | 26 | 26 | 1105 | 1105 | 1105 | 0.02631 | 430 | 0.010238 | 1259 | 0.029976 | 1.362 | A04 | MICL0.01137026/DBN
Build-In Floor | Mini Canal | MICL.01137026/DBR | 11 | 370 | 26 | 26 | 1152 | 1152 | 1152 | 0.027429 | 448 | 0.010667 | 1312 | 0.031238 | 1.362 | A04 | MICL0.01137026/DBR
Build-In Floor | Mini Canal | MICL.01137026/DBV | 11 | 370 | 26 | 26 | 1105 | 1105 | 1105 | 0.02631 | 430 | 0.010238 | 1259 | 0.029976 | 1.362 | A04 | MICL0.01137026/DBV
Build-In Floor | Mini Canal | MICL.01137026/DDB | 11 | 370 | 26 | 26 | 1152 | 1152 | 1152 | 0.027429 | 448 | 0.010667 | 1312 | 0.031238 | 1.362 | A04 | MICL0.01137026/DDB
Build-In Floor | Mini Canal | MICL.01137026/DMN | 11 | 370 | 26 | 26 | 1105 | 1105 | 1105 | 0.02631 | 430 | 0.010238 | 1259 | 0.029976 | 1.362 | A04 | MICL0.01137026/DMN
Build-In Floor | Mini Canal | MICL.01137026/DMV | 11 | 370 | 26 | 26 | 1105 | 1105 | 1105 | 0.02631 | 430 | 0.010238 | 1259 | 0.029976 | 1.362 | A04 | MICL0.01137026/DMV
Build-In Floor | Mini Canal | MICL.01137026/DNA | 11 | 370 | 26 | 26 | 1152 | 1152 | 1152 | 0.027429 | 448 | 0.010667 | 1312 | 0.031238 | 1.362 | A04 | MICL0.01137026/DNA
Build-In Floor | Mini Canal | MICL.01137026/DNC | 11 | 370 | 26 | 26 | 1152 | 1152 | 1152 | 0.027429 | 448 | 0.010667 | 1312 | 0.031238 | 1.362 | A04 | MICL0.01137026/DNC
Build-In Floor | Mini Canal | MICL.01137026/DON | 11 | 370 | 26 | 26 | 1105 | 1105 | 1105 | 0.02631 | 430 | 0.010238 | 1259 | 0.029976 | 1.362 | A04 | MICL0.01137026/DON
Build-In Floor | Mini Canal | MICL.01137026/DOV | 11 | 370 | 26 | 26 | 1105 | 1105 | 1105 | 0.02631 | 430 | 0.010238 | 1259 | 0.029976 | 1.362 | A04 | MICL0.01137026/DOV
Build-In Floor | Mini Canal | MICL.01137026/PNC | 11 | 370 | 26 | 26 | 1010 | 1010 | 1010 | 0.024048 | 393 | 0.0093571 | 1150 | 0.027381 | 1.362 | A04 | MICL0.01137026/PNC
Build-In Floor | Mini Canal | MICL.01137026/RBL | 11 | 370 | 26 | 26 | 1188 | 1188 | 1188 | 0.028286 | 462 | 0.011 | 1353 | 0.032214 | 1.362 | A04 | MICL0.01137026/RBL
Build-In Floor | Mini Canal | MICL.01137026/RBN | 11 | 370 | 26 | 26 | 1152 | 1152 | 1152 | 0.027429 | 448 | 0.010667 | 1312 | 0.031238 | 1.362 | A04 | MICL0.01137026/RBN
Build-In Floor | Mini Canal | MICL.01137026/RBR | 11 | 370 | 26 | 26 | 1188 | 1188 | 1188 | 0.028286 | 462 | 0.011 | 1353 | 0.032214 | 1.362 | A04 | MICL0.01137026/RBR
Build-In Floor | Mini Canal | MICL.01137026/RBV | 11 | 370 | 26 | 26 | 1152 | 1152 | 1152 | 0.027429 | 448 | 0.010667 | 1312 | 0.031238 | 1.362 | A04 | MICL0.01137026/RBV
Build-In Floor | Mini Canal | MICL.01137026/RDB | 11 | 370 | 26 | 26 | 1188 | 1188 | 1188 | 0.028286 | 462 | 0.011 | 1353 | 0.032214 | 1.362 | A04 | MICL0.01137026/RDB
Build-In Floor | Mini Canal | MICL.01137026/RMN | 11 | 370 | 26 | 26 | 1152 | 1152 | 1152 | 0.027429 | 448 | 0.010667 | 1312 | 0.031238 | 1.362 | A04 | MICL0.01137026/RMN
Build-In Floor | Mini Canal | MICL.01137026/RMV | 11 | 370 | 26 | 26 | 1152 | 1152 | 1152 | 0.027429 | 448 | 0.010667 | 1312 | 0.031238 | 1.362 | A04 | MICL0.01137026/RMV
Build-In Floor | Mini Canal | MICL.01137026/RNA | 11 | 370 | 26 | 26 | 1188 | 1188 | 1188 | 0.028286 | 462 | 0.011 | 1353 | 0.032214 | 1.362 | A04 | MICL0.01137026/RNA
Build-In Floor | Mini Canal | MICL.01137026/RON | 11 | 370 | 26 | 26 | 1152 | 1152 | 1152 | 0.027429 | 448 | 0.010667 | 1312 | 0.031238 | 1.362 | A04 | MICL0.01137026/RON
Build-In Floor | Mini Canal | MICL.01137026/ROV | 11 | 370 | 26 | 26 | 1152 | 1152 | 1152 | 0.027429 | 448 | 0.010667 | 1312 | 0.031238 | 1.362 | A04 | MICL0.01137026/ROV
Build-In Floor | Mini Canal | MICL.01137026/RSS | 11 | 370 | 26 | 26 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01137026/RSS
Build-In Floor | Mini Canal | MICL.01137026/SBL | 11 | 370 | 26 | 26 | 1188 | 1188 | 1188 | 0.028286 | 462 | 0.011 | 1353 | 0.032214 | 1.362 | A04 | MICL0.01137026/SBL
Build-In Floor | Mini Canal | MICL.01137026/SBR | 11 | 370 | 26 | 26 | 1188 | 1188 | 1188 | 0.028286 | 462 | 0.011 | 1353 | 0.032214 | 1.362 | A04 | MICL0.01137026/SBR
Build-In Floor | Mini Canal | MICL.01137026/SDB | 11 | 370 | 26 | 26 | 1188 | 1188 | 1188 | 0.028286 | 462 | 0.011 | 1353 | 0.032214 | 1.362 | A04 | MICL0.01137026/SDB
Build-In Floor | Mini Canal | MICL.01137026/SNA | 11 | 370 | 26 | 26 | 1188 | 1188 | 1188 | 0.028286 | 462 | 0.011 | 1353 | 0.032214 | 1.362 | A04 | MICL0.01137026/SNA
Build-In Floor | Mini Canal | MICL.01137026/SNC | 11 | 370 | 26 | 26 | 1188 | 1188 | 1188 | 0.028286 | 462 | 0.011 | 1353 | 0.032214 | 1.362 | A04 | MICL0.01137026/SNC
Build-In Floor | Mini Canal | MICL.01137034/ANA | 11 | 370 | 34 | 34 | 1158 | 1158 | 1158 | 0.027571 | 450 | 0.010714 | 1319 | 0.031405 | 1.362 | A04 | MICL0.01137034/ANA
Build-In Floor | Mini Canal | MICL.01137034/DBL | 11 | 370 | 34 | 34 | 1498 | 1498 | 1498 | 0.035667 | 583 | 0.013881 | 1706 | 0.040619 | 1.362 | A04 | MICL0.01137034/DBL
Build-In Floor | Mini Canal | MICL.01137034/DBN | 11 | 370 | 34 | 34 | 1436 | 1436 | 1436 | 0.03419 | 559 | 0.01331 | 1636 | 0.038952 | 1.362 | A04 | MICL0.01137034/DBN
Build-In Floor | Mini Canal | MICL.01137034/DBR | 11 | 370 | 34 | 34 | 1498 | 1498 | 1498 | 0.035667 | 583 | 0.013881 | 1706 | 0.040619 | 1.362 | A04 | MICL0.01137034/DBR
Build-In Floor | Mini Canal | MICL.01137034/DBV | 11 | 370 | 34 | 34 | 1436 | 1436 | 1436 | 0.03419 | 559 | 0.01331 | 1636 | 0.038952 | 1.362 | A04 | MICL0.01137034/DBV
Build-In Floor | Mini Canal | MICL.01137034/DDB | 11 | 370 | 34 | 34 | 1498 | 1498 | 1498 | 0.035667 | 583 | 0.013881 | 1706 | 0.040619 | 1.362 | A04 | MICL0.01137034/DDB
Build-In Floor | Mini Canal | MICL.01137034/DMN | 11 | 370 | 34 | 34 | 1436 | 1436 | 1436 | 0.03419 | 559 | 0.01331 | 1636 | 0.038952 | 1.362 | A04 | MICL0.01137034/DMN
Build-In Floor | Mini Canal | MICL.01137034/DMV | 11 | 370 | 34 | 34 | 1436 | 1436 | 1436 | 0.03419 | 559 | 0.01331 | 1636 | 0.038952 | 1.362 | A04 | MICL0.01137034/DMV
Build-In Floor | Mini Canal | MICL.01137034/DNA | 11 | 370 | 34 | 34 | 1498 | 1498 | 1498 | 0.035667 | 583 | 0.013881 | 1706 | 0.040619 | 1.362 | A04 | MICL0.01137034/DNA
Build-In Floor | Mini Canal | MICL.01137034/DNC | 11 | 370 | 34 | 34 | 1498 | 1498 | 1498 | 0.035667 | 583 | 0.013881 | 1706 | 0.040619 | 1.362 | A04 | MICL0.01137034/DNC
Build-In Floor | Mini Canal | MICL.01137034/DON | 11 | 370 | 34 | 34 | 1436 | 1436 | 1436 | 0.03419 | 559 | 0.01331 | 1636 | 0.038952 | 1.362 | A04 | MICL0.01137034/DON
Build-In Floor | Mini Canal | MICL.01137034/DOV | 11 | 370 | 34 | 34 | 1436 | 1436 | 1436 | 0.03419 | 559 | 0.01331 | 1636 | 0.038952 | 1.362 | A04 | MICL0.01137034/DOV
Build-In Floor | Mini Canal | MICL.01137034/PNC | 11 | 370 | 34 | 34 | 1312 | 1312 | 1312 | 0.031238 | 510 | 0.012143 | 1494 | 0.035571 | 1.362 | A04 | MICL0.01137034/PNC
Build-In Floor | Mini Canal | MICL.01137034/RBL | 11 | 370 | 34 | 34 | 1544 | 1544 | 1544 | 0.036762 | 601 | 0.01431 | 1759 | 0.041881 | 1.362 | A04 | MICL0.01137034/RBL
Build-In Floor | Mini Canal | MICL.01137034/RBN | 11 | 370 | 34 | 34 | 1498 | 1498 | 1498 | 0.035667 | 583 | 0.013881 | 1706 | 0.040619 | 1.362 | A04 | MICL0.01137034/RBN
Build-In Floor | Mini Canal | MICL.01137034/RBR | 11 | 370 | 34 | 34 | 1544 | 1544 | 1544 | 0.036762 | 601 | 0.01431 | 1759 | 0.041881 | 1.362 | A04 | MICL0.01137034/RBR
Build-In Floor | Mini Canal | MICL.01137034/RBV | 11 | 370 | 34 | 34 | 1498 | 1498 | 1498 | 0.035667 | 583 | 0.013881 | 1706 | 0.040619 | 1.362 | A04 | MICL0.01137034/RBV
Build-In Floor | Mini Canal | MICL.01137034/RDB | 11 | 370 | 34 | 34 | 1544 | 1544 | 1544 | 0.036762 | 601 | 0.01431 | 1759 | 0.041881 | 1.362 | A04 | MICL0.01137034/RDB
Build-In Floor | Mini Canal | MICL.01137034/RMN | 11 | 370 | 34 | 34 | 1498 | 1498 | 1498 | 0.035667 | 583 | 0.013881 | 1706 | 0.040619 | 1.362 | A04 | MICL0.01137034/RMN
Build-In Floor | Mini Canal | MICL.01137034/RMV | 11 | 370 | 34 | 34 | 1498 | 1498 | 1498 | 0.035667 | 583 | 0.013881 | 1706 | 0.040619 | 1.362 | A04 | MICL0.01137034/RMV
Build-In Floor | Mini Canal | MICL.01137034/RNA | 11 | 370 | 34 | 34 | 1544 | 1544 | 1544 | 0.036762 | 601 | 0.01431 | 1759 | 0.041881 | 1.362 | A04 | MICL0.01137034/RNA
Build-In Floor | Mini Canal | MICL.01137034/RON | 11 | 370 | 34 | 34 | 1498 | 1498 | 1498 | 0.035667 | 583 | 0.013881 | 1706 | 0.040619 | 1.362 | A04 | MICL0.01137034/RON
Build-In Floor | Mini Canal | MICL.01137034/ROV | 11 | 370 | 34 | 34 | 1498 | 1498 | 1498 | 0.035667 | 583 | 0.013881 | 1706 | 0.040619 | 1.362 | A04 | MICL0.01137034/ROV
Build-In Floor | Mini Canal | MICL.01137034/RSS | 11 | 370 | 34 | 34 | 1482 | 1482 | 1482 | 0.035286 | 576 | 0.013714 | 1688 | 0.04019 | 1.362 | A04 | MICL0.01137034/RSS
Build-In Floor | Mini Canal | MICL.01137034/SBL | 11 | 370 | 34 | 34 | 1544 | 1544 | 1544 | 0.036762 | 601 | 0.01431 | 1759 | 0.041881 | 1.362 | A04 | MICL0.01137034/SBL
Build-In Floor | Mini Canal | MICL.01137034/SBR | 11 | 370 | 34 | 34 | 1544 | 1544 | 1544 | 0.036762 | 601 | 0.01431 | 1759 | 0.041881 | 1.362 | A04 | MICL0.01137034/SBR
Build-In Floor | Mini Canal | MICL.01137034/SDB | 11 | 370 | 34 | 34 | 1544 | 1544 | 1544 | 0.036762 | 601 | 0.01431 | 1759 | 0.041881 | 1.362 | A04 | MICL0.01137034/SDB
Build-In Floor | Mini Canal | MICL.01137034/SNA | 11 | 370 | 34 | 34 | 1544 | 1544 | 1544 | 0.036762 | 601 | 0.01431 | 1759 | 0.041881 | 1.362 | A04 | MICL0.01137034/SNA
Build-In Floor | Mini Canal | MICL.01137034/SNC | 11 | 370 | 34 | 34 | 1544 | 1544 | 1544 | 0.036762 | 601 | 0.01431 | 1759 | 0.041881 | 1.362 | A04 | MICL0.01137034/SNC
Build-In Floor | Mini Canal | MICL.01137042/ANA | 11 | 370 | 42 | 42 | 1627 | 1627 | 1627 | 0.038738 | 633 | 0.015071 | 1853 | 0.044119 | 1.362 | A04 | MICL0.01137042/ANA
Build-In Floor | Mini Canal | MICL.01137042/DBL | 11 | 370 | 42 | 42 | 2104 | 2104 | 2104 | 0.050095 | 818 | 0.019476 | 2396 | 0.057048 | 1.362 | A04 | MICL0.01137042/DBL
Build-In Floor | Mini Canal | MICL.01137042/DBN | 11 | 370 | 42 | 42 | 2017 | 2017 | 2017 | 0.048024 | 785 | 0.01869 | 2297 | 0.05469 | 1.362 | A04 | MICL0.01137042/DBN
Build-In Floor | Mini Canal | MICL.01137042/DBR | 11 | 370 | 42 | 42 | 2104 | 2104 | 2104 | 0.050095 | 818 | 0.019476 | 2396 | 0.057048 | 1.362 | A04 | MICL0.01137042/DBR
Build-In Floor | Mini Canal | MICL.01137042/DBV | 11 | 370 | 42 | 42 | 2017 | 2017 | 2017 | 0.048024 | 785 | 0.01869 | 2297 | 0.05469 | 1.362 | A04 | MICL0.01137042/DBV
Build-In Floor | Mini Canal | MICL.01137042/DDB | 11 | 370 | 42 | 42 | 2104 | 2104 | 2104 | 0.050095 | 818 | 0.019476 | 2396 | 0.057048 | 1.362 | A04 | MICL0.01137042/DDB
Build-In Floor | Mini Canal | MICL.01137042/DMN | 11 | 370 | 42 | 42 | 2017 | 2017 | 2017 | 0.048024 | 785 | 0.01869 | 2297 | 0.05469 | 1.362 | A04 | MICL0.01137042/DMN
Build-In Floor | Mini Canal | MICL.01137042/DMV | 11 | 370 | 42 | 42 | 2017 | 2017 | 2017 | 0.048024 | 785 | 0.01869 | 2297 | 0.05469 | 1.362 | A04 | MICL0.01137042/DMV
Build-In Floor | Mini Canal | MICL.01137042/DNA | 11 | 370 | 42 | 42 | 2104 | 2104 | 2104 | 0.050095 | 818 | 0.019476 | 2396 | 0.057048 | 1.362 | A04 | MICL0.01137042/DNA
Build-In Floor | Mini Canal | MICL.01137042/DNC | 11 | 370 | 42 | 42 | 2104 | 2104 | 2104 | 0.050095 | 818 | 0.019476 | 2396 | 0.057048 | 1.362 | A04 | MICL0.01137042/DNC
Build-In Floor | Mini Canal | MICL.01137042/DON | 11 | 370 | 42 | 42 | 2017 | 2017 | 2017 | 0.048024 | 785 | 0.01869 | 2297 | 0.05469 | 1.362 | A04 | MICL0.01137042/DON
Build-In Floor | Mini Canal | MICL.01137042/DOV | 11 | 370 | 42 | 42 | 2017 | 2017 | 2017 | 0.048024 | 785 | 0.01869 | 2297 | 0.05469 | 1.362 | A04 | MICL0.01137042/DOV
Build-In Floor | Mini Canal | MICL.01137042/PNC | 11 | 370 | 42 | 42 | 1844 | 1844 | 1844 | 0.043905 | 717 | 0.017071 | 2100 | 0.05 | 1.362 | A04 | MICL0.01137042/PNC
Build-In Floor | Mini Canal | MICL.01137042/RBL | 11 | 370 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.01137042/RBL
Build-In Floor | Mini Canal | MICL.01137042/RBN | 11 | 370 | 42 | 42 | 2104 | 2104 | 2104 | 0.050095 | 818 | 0.019476 | 2396 | 0.057048 | 1.362 | A04 | MICL0.01137042/RBN
Build-In Floor | Mini Canal | MICL.01137042/RBR | 11 | 370 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.01137042/RBR
Build-In Floor | Mini Canal | MICL.01137042/RBV | 11 | 370 | 42 | 42 | 2104 | 2104 | 2104 | 0.050095 | 818 | 0.019476 | 2396 | 0.057048 | 1.362 | A04 | MICL0.01137042/RBV
Build-In Floor | Mini Canal | MICL.01137042/RDB | 11 | 370 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.01137042/RDB
Build-In Floor | Mini Canal | MICL.01137042/RMN | 11 | 370 | 42 | 42 | 2104 | 2104 | 2104 | 0.050095 | 818 | 0.019476 | 2396 | 0.057048 | 1.362 | A04 | MICL0.01137042/RMN
Build-In Floor | Mini Canal | MICL.01137042/RMV | 11 | 370 | 42 | 42 | 2104 | 2104 | 2104 | 0.050095 | 818 | 0.019476 | 2396 | 0.057048 | 1.362 | A04 | MICL0.01137042/RMV
Build-In Floor | Mini Canal | MICL.01137042/RNA | 11 | 370 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.01137042/RNA
Build-In Floor | Mini Canal | MICL.01137042/RON | 11 | 370 | 42 | 42 | 2104 | 2104 | 2104 | 0.050095 | 818 | 0.019476 | 2396 | 0.057048 | 1.362 | A04 | MICL0.01137042/RON
Build-In Floor | Mini Canal | MICL.01137042/ROV | 11 | 370 | 42 | 42 | 2104 | 2104 | 2104 | 0.050095 | 818 | 0.019476 | 2396 | 0.057048 | 1.362 | A04 | MICL0.01137042/ROV
Build-In Floor | Mini Canal | MICL.01137042/RSS | 11 | 370 | 42 | 42 | 2082 | 2082 | 2082 | 0.049571 | 810 | 0.019286 | 2371 | 0.056452 | 1.362 | A04 | MICL0.01137042/RSS
Build-In Floor | Mini Canal | MICL.01137042/SBL | 11 | 370 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.01137042/SBL
Build-In Floor | Mini Canal | MICL.01137042/SBR | 11 | 370 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.01137042/SBR
Build-In Floor | Mini Canal | MICL.01137042/SDB | 11 | 370 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.01137042/SDB
Build-In Floor | Mini Canal | MICL.01137042/SNA | 11 | 370 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.01137042/SNA
Build-In Floor | Mini Canal | MICL.01137042/SNC | 11 | 370 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.01137042/SNC
Build-In Floor | Mini Canal | MICL.01139014/ANA | 11 | 390 | 14 | 14 | 590 | 590 | 590 | 0.014048 | 230 | 0.0054762 | 672 | 0.016 | 1.362 | A04 | MICL0.01139014/ANA
Build-In Floor | Mini Canal | MICL.01139014/DBL | 11 | 390 | 14 | 14 | 762 | 762 | 762 | 0.018143 | 296 | 0.0070476 | 868 | 0.020667 | 1.362 | A04 | MICL0.01139014/DBL
Build-In Floor | Mini Canal | MICL.01139014/DBN | 11 | 390 | 14 | 14 | 731 | 731 | 731 | 0.017405 | 284 | 0.0067619 | 833 | 0.019833 | 1.362 | A04 | MICL0.01139014/DBN
Build-In Floor | Mini Canal | MICL.01139014/DBR | 11 | 390 | 14 | 14 | 762 | 762 | 762 | 0.018143 | 296 | 0.0070476 | 868 | 0.020667 | 1.362 | A04 | MICL0.01139014/DBR
Build-In Floor | Mini Canal | MICL.01139014/DBV | 11 | 390 | 14 | 14 | 731 | 731 | 731 | 0.017405 | 284 | 0.0067619 | 833 | 0.019833 | 1.362 | A04 | MICL0.01139014/DBV
Build-In Floor | Mini Canal | MICL.01139014/DDB | 11 | 390 | 14 | 14 | 762 | 762 | 762 | 0.018143 | 296 | 0.0070476 | 868 | 0.020667 | 1.362 | A04 | MICL0.01139014/DDB
Build-In Floor | Mini Canal | MICL.01139014/DMN | 11 | 390 | 14 | 14 | 731 | 731 | 731 | 0.017405 | 284 | 0.0067619 | 833 | 0.019833 | 1.362 | A04 | MICL0.01139014/DMN
Build-In Floor | Mini Canal | MICL.01139014/DMV | 11 | 390 | 14 | 14 | 731 | 731 | 731 | 0.017405 | 284 | 0.0067619 | 833 | 0.019833 | 1.362 | A04 | MICL0.01139014/DMV
Build-In Floor | Mini Canal | MICL.01139014/DNA | 11 | 390 | 14 | 14 | 762 | 762 | 762 | 0.018143 | 296 | 0.0070476 | 868 | 0.020667 | 1.362 | A04 | MICL0.01139014/DNA
Build-In Floor | Mini Canal | MICL.01139014/DNC | 11 | 390 | 14 | 14 | 762 | 762 | 762 | 0.018143 | 296 | 0.0070476 | 868 | 0.020667 | 1.362 | A04 | MICL0.01139014/DNC
Build-In Floor | Mini Canal | MICL.01139014/DON | 11 | 390 | 14 | 14 | 731 | 731 | 731 | 0.017405 | 284 | 0.0067619 | 833 | 0.019833 | 1.362 | A04 | MICL0.01139014/DON
Build-In Floor | Mini Canal | MICL.01139014/DOV | 11 | 390 | 14 | 14 | 731 | 731 | 731 | 0.017405 | 284 | 0.0067619 | 833 | 0.019833 | 1.362 | A04 | MICL0.01139014/DOV
Build-In Floor | Mini Canal | MICL.01139014/RBL | 11 | 390 | 14 | 14 | 786 | 786 | 786 | 0.018714 | 306 | 0.0072857 | 895 | 0.02131 | 1.362 | A04 | MICL0.01139014/RBL
Build-In Floor | Mini Canal | MICL.01139014/RBN | 11 | 390 | 14 | 14 | 762 | 762 | 762 | 0.018143 | 296 | 0.0070476 | 868 | 0.020667 | 1.362 | A04 | MICL0.01139014/RBN
Build-In Floor | Mini Canal | MICL.01139014/RBR | 11 | 390 | 14 | 14 | 786 | 786 | 786 | 0.018714 | 306 | 0.0072857 | 895 | 0.02131 | 1.362 | A04 | MICL0.01139014/RBR
Build-In Floor | Mini Canal | MICL.01139014/RBV | 11 | 390 | 14 | 14 | 762 | 762 | 762 | 0.018143 | 296 | 0.0070476 | 868 | 0.020667 | 1.362 | A04 | MICL0.01139014/RBV
Build-In Floor | Mini Canal | MICL.01139014/RDB | 11 | 390 | 14 | 14 | 786 | 786 | 786 | 0.018714 | 306 | 0.0072857 | 895 | 0.02131 | 1.362 | A04 | MICL0.01139014/RDB
Build-In Floor | Mini Canal | MICL.01139014/RMN | 11 | 390 | 14 | 14 | 762 | 762 | 762 | 0.018143 | 296 | 0.0070476 | 868 | 0.020667 | 1.362 | A04 | MICL0.01139014/RMN
Build-In Floor | Mini Canal | MICL.01139014/RMV | 11 | 390 | 14 | 14 | 762 | 762 | 762 | 0.018143 | 296 | 0.0070476 | 868 | 0.020667 | 1.362 | A04 | MICL0.01139014/RMV
Build-In Floor | Mini Canal | MICL.01139014/RNA | 11 | 390 | 14 | 14 | 786 | 786 | 786 | 0.018714 | 306 | 0.0072857 | 895 | 0.02131 | 1.362 | A04 | MICL0.01139014/RNA
Build-In Floor | Mini Canal | MICL.01139014/RON | 11 | 390 | 14 | 14 | 762 | 762 | 762 | 0.018143 | 296 | 0.0070476 | 868 | 0.020667 | 1.362 | A04 | MICL0.01139014/RON
Build-In Floor | Mini Canal | MICL.01139014/ROV | 11 | 390 | 14 | 14 | 762 | 762 | 762 | 0.018143 | 296 | 0.0070476 | 868 | 0.020667 | 1.362 | A04 | MICL0.01139014/ROV
Build-In Floor | Mini Canal | MICL.01139014/RSS | 11 | 390 | 14 | 14 | 755 | 755 | 755 | 0.017976 | 294 | 0.007 | 860 | 0.020476 | 1.362 | A04 | MICL0.01139014/RSS
Build-In Floor | Mini Canal | MICL.01139014/SBL | 11 | 390 | 14 | 14 | 786 | 786 | 786 | 0.018714 | 306 | 0.0072857 | 895 | 0.02131 | 1.362 | A04 | MICL0.01139014/SBL
Build-In Floor | Mini Canal | MICL.01139014/SBR | 11 | 390 | 14 | 14 | 786 | 786 | 786 | 0.018714 | 306 | 0.0072857 | 895 | 0.02131 | 1.362 | A04 | MICL0.01139014/SBR
Build-In Floor | Mini Canal | MICL.01139014/SDB | 11 | 390 | 14 | 14 | 786 | 786 | 786 | 0.018714 | 306 | 0.0072857 | 895 | 0.02131 | 1.362 | A04 | MICL0.01139014/SDB
Build-In Floor | Mini Canal | MICL.01139014/SNA | 11 | 390 | 14 | 14 | 786 | 786 | 786 | 0.018714 | 306 | 0.0072857 | 895 | 0.02131 | 1.362 | A04 | MICL0.01139014/SNA
Build-In Floor | Mini Canal | MICL.01139014/SNC | 11 | 390 | 14 | 14 | 786 | 786 | 786 | 0.018714 | 306 | 0.0072857 | 895 | 0.02131 | 1.362 | A04 | MICL0.01139014/SNC
Build-In Floor | Mini Canal | MICL.01139018/ANA | 11 | 390 | 18 | 18 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01139018/ANA
Build-In Floor | Mini Canal | MICL.01139018/DBL | 11 | 390 | 18 | 18 | 904 | 904 | 904 | 0.021524 | 352 | 0.008381 | 1030 | 0.024524 | 1.362 | A04 | MICL0.01139018/DBL
Build-In Floor | Mini Canal | MICL.01139018/DBN | 11 | 390 | 18 | 18 | 867 | 867 | 867 | 0.020643 | 337 | 0.0080238 | 988 | 0.023524 | 1.362 | A04 | MICL0.01139018/DBN
Build-In Floor | Mini Canal | MICL.01139018/DBR | 11 | 390 | 18 | 18 | 904 | 904 | 904 | 0.021524 | 352 | 0.008381 | 1030 | 0.024524 | 1.362 | A04 | MICL0.01139018/DBR
Build-In Floor | Mini Canal | MICL.01139018/DBV | 11 | 390 | 18 | 18 | 867 | 867 | 867 | 0.020643 | 337 | 0.0080238 | 988 | 0.023524 | 1.362 | A04 | MICL0.01139018/DBV
Build-In Floor | Mini Canal | MICL.01139018/DDB | 11 | 390 | 18 | 18 | 904 | 904 | 904 | 0.021524 | 352 | 0.008381 | 1030 | 0.024524 | 1.362 | A04 | MICL0.01139018/DDB
Build-In Floor | Mini Canal | MICL.01139018/DMN | 11 | 390 | 18 | 18 | 867 | 867 | 867 | 0.020643 | 337 | 0.0080238 | 988 | 0.023524 | 1.362 | A04 | MICL0.01139018/DMN
Build-In Floor | Mini Canal | MICL.01139018/DMV | 11 | 390 | 18 | 18 | 867 | 867 | 867 | 0.020643 | 337 | 0.0080238 | 988 | 0.023524 | 1.362 | A04 | MICL0.01139018/DMV
Build-In Floor | Mini Canal | MICL.01139018/DNA | 11 | 390 | 18 | 18 | 904 | 904 | 904 | 0.021524 | 352 | 0.008381 | 1030 | 0.024524 | 1.362 | A04 | MICL0.01139018/DNA
Build-In Floor | Mini Canal | MICL.01139018/DNC | 11 | 390 | 18 | 18 | 904 | 904 | 904 | 0.021524 | 352 | 0.008381 | 1030 | 0.024524 | 1.362 | A04 | MICL0.01139018/DNC
Build-In Floor | Mini Canal | MICL.01139018/DON | 11 | 390 | 18 | 18 | 867 | 867 | 867 | 0.020643 | 337 | 0.0080238 | 988 | 0.023524 | 1.362 | A04 | MICL0.01139018/DON
Build-In Floor | Mini Canal | MICL.01139018/DOV | 11 | 390 | 18 | 18 | 867 | 867 | 867 | 0.020643 | 337 | 0.0080238 | 988 | 0.023524 | 1.362 | A04 | MICL0.01139018/DOV
Build-In Floor | Mini Canal | MICL.01139018/RBL | 11 | 390 | 18 | 18 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01139018/RBL
Build-In Floor | Mini Canal | MICL.01139018/RBN | 11 | 390 | 18 | 18 | 904 | 904 | 904 | 0.021524 | 352 | 0.008381 | 1030 | 0.024524 | 1.362 | A04 | MICL0.01139018/RBN
Build-In Floor | Mini Canal | MICL.01139018/RBR | 11 | 390 | 18 | 18 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01139018/RBR
Build-In Floor | Mini Canal | MICL.01139018/RBV | 11 | 390 | 18 | 18 | 904 | 904 | 904 | 0.021524 | 352 | 0.008381 | 1030 | 0.024524 | 1.362 | A04 | MICL0.01139018/RBV
Build-In Floor | Mini Canal | MICL.01139018/RDB | 11 | 390 | 18 | 18 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01139018/RDB
Build-In Floor | Mini Canal | MICL.01139018/RMN | 11 | 390 | 18 | 18 | 904 | 904 | 904 | 0.021524 | 352 | 0.008381 | 1030 | 0.024524 | 1.362 | A04 | MICL0.01139018/RMN
Build-In Floor | Mini Canal | MICL.01139018/RMV | 11 | 390 | 18 | 18 | 904 | 904 | 904 | 0.021524 | 352 | 0.008381 | 1030 | 0.024524 | 1.362 | A04 | MICL0.01139018/RMV
Build-In Floor | Mini Canal | MICL.01139018/RNA | 11 | 390 | 18 | 18 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01139018/RNA
Build-In Floor | Mini Canal | MICL.01139018/RON | 11 | 390 | 18 | 18 | 904 | 904 | 904 | 0.021524 | 352 | 0.008381 | 1030 | 0.024524 | 1.362 | A04 | MICL0.01139018/RON
Build-In Floor | Mini Canal | MICL.01139018/ROV | 11 | 390 | 18 | 18 | 904 | 904 | 904 | 0.021524 | 352 | 0.008381 | 1030 | 0.024524 | 1.362 | A04 | MICL0.01139018/ROV
Build-In Floor | Mini Canal | MICL.01139018/RSS | 11 | 390 | 18 | 18 | 895 | 895 | 895 | 0.02131 | 348 | 0.0082857 | 1019 | 0.024262 | 1.362 | A04 | MICL0.01139018/RSS
Build-In Floor | Mini Canal | MICL.01139018/SBL | 11 | 390 | 18 | 18 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01139018/SBL
Build-In Floor | Mini Canal | MICL.01139018/SBR | 11 | 390 | 18 | 18 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01139018/SBR
Build-In Floor | Mini Canal | MICL.01139018/SDB | 11 | 390 | 18 | 18 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01139018/SDB
Build-In Floor | Mini Canal | MICL.01139018/SNA | 11 | 390 | 18 | 18 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01139018/SNA
Build-In Floor | Mini Canal | MICL.01139018/SNC | 11 | 390 | 18 | 18 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01139018/SNC
Build-In Floor | Mini Canal | MICL.01139026/ANA | 11 | 390 | 26 | 26 | 944 | 944 | 944 | 0.022476 | 367 | 0.0087381 | 1075 | 0.025595 | 1.362 | A04 | MICL0.01139026/ANA
Build-In Floor | Mini Canal | MICL.01139026/DBL | 11 | 390 | 26 | 26 | 1220 | 1220 | 1220 | 0.029048 | 475 | 0.01131 | 1390 | 0.033095 | 1.362 | A04 | MICL0.01139026/DBL
Build-In Floor | Mini Canal | MICL.01139026/DBN | 11 | 390 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01139026/DBN
Build-In Floor | Mini Canal | MICL.01139026/DBR | 11 | 390 | 26 | 26 | 1220 | 1220 | 1220 | 0.029048 | 475 | 0.01131 | 1390 | 0.033095 | 1.362 | A04 | MICL0.01139026/DBR
Build-In Floor | Mini Canal | MICL.01139026/DBV | 11 | 390 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01139026/DBV
Build-In Floor | Mini Canal | MICL.01139026/DDB | 11 | 390 | 26 | 26 | 1220 | 1220 | 1220 | 0.029048 | 475 | 0.01131 | 1390 | 0.033095 | 1.362 | A04 | MICL0.01139026/DDB
Build-In Floor | Mini Canal | MICL.01139026/DMN | 11 | 390 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01139026/DMN
Build-In Floor | Mini Canal | MICL.01139026/DMV | 11 | 390 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01139026/DMV
Build-In Floor | Mini Canal | MICL.01139026/DNA | 11 | 390 | 26 | 26 | 1220 | 1220 | 1220 | 0.029048 | 475 | 0.01131 | 1390 | 0.033095 | 1.362 | A04 | MICL0.01139026/DNA
Build-In Floor | Mini Canal | MICL.01139026/DNC | 11 | 390 | 26 | 26 | 1220 | 1220 | 1220 | 0.029048 | 475 | 0.01131 | 1390 | 0.033095 | 1.362 | A04 | MICL0.01139026/DNC
Build-In Floor | Mini Canal | MICL.01139026/DON | 11 | 390 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01139026/DON
Build-In Floor | Mini Canal | MICL.01139026/DOV | 11 | 390 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01139026/DOV
Build-In Floor | Mini Canal | MICL.01139026/PNC | 11 | 390 | 26 | 26 | 1069 | 1069 | 1069 | 0.025452 | 416 | 0.0099048 | 1218 | 0.029 | 1.362 | A04 | MICL0.01139026/PNC
Build-In Floor | Mini Canal | MICL.01139026/RBL | 11 | 390 | 26 | 26 | 1258 | 1258 | 1258 | 0.029952 | 489 | 0.011643 | 1433 | 0.034119 | 1.362 | A04 | MICL0.01139026/RBL
Build-In Floor | Mini Canal | MICL.01139026/RBN | 11 | 390 | 26 | 26 | 1220 | 1220 | 1220 | 0.029048 | 475 | 0.01131 | 1390 | 0.033095 | 1.362 | A04 | MICL0.01139026/RBN
Build-In Floor | Mini Canal | MICL.01139026/RBR | 11 | 390 | 26 | 26 | 1258 | 1258 | 1258 | 0.029952 | 489 | 0.011643 | 1433 | 0.034119 | 1.362 | A04 | MICL0.01139026/RBR
Build-In Floor | Mini Canal | MICL.01139026/RBV | 11 | 390 | 26 | 26 | 1220 | 1220 | 1220 | 0.029048 | 475 | 0.01131 | 1390 | 0.033095 | 1.362 | A04 | MICL0.01139026/RBV
Build-In Floor | Mini Canal | MICL.01139026/RDB | 11 | 390 | 26 | 26 | 1258 | 1258 | 1258 | 0.029952 | 489 | 0.011643 | 1433 | 0.034119 | 1.362 | A04 | MICL0.01139026/RDB
Build-In Floor | Mini Canal | MICL.01139026/RMN | 11 | 390 | 26 | 26 | 1220 | 1220 | 1220 | 0.029048 | 475 | 0.01131 | 1390 | 0.033095 | 1.362 | A04 | MICL0.01139026/RMN
Build-In Floor | Mini Canal | MICL.01139026/RMV | 11 | 390 | 26 | 26 | 1220 | 1220 | 1220 | 0.029048 | 475 | 0.01131 | 1390 | 0.033095 | 1.362 | A04 | MICL0.01139026/RMV
Build-In Floor | Mini Canal | MICL.01139026/RNA | 11 | 390 | 26 | 26 | 1258 | 1258 | 1258 | 0.029952 | 489 | 0.011643 | 1433 | 0.034119 | 1.362 | A04 | MICL0.01139026/RNA
Build-In Floor | Mini Canal | MICL.01139026/RON | 11 | 390 | 26 | 26 | 1220 | 1220 | 1220 | 0.029048 | 475 | 0.01131 | 1390 | 0.033095 | 1.362 | A04 | MICL0.01139026/RON
Build-In Floor | Mini Canal | MICL.01139026/ROV | 11 | 390 | 26 | 26 | 1220 | 1220 | 1220 | 0.029048 | 475 | 0.01131 | 1390 | 0.033095 | 1.362 | A04 | MICL0.01139026/ROV
Build-In Floor | Mini Canal | MICL.01139026/RSS | 11 | 390 | 26 | 26 | 1208 | 1208 | 1208 | 0.028762 | 470 | 0.01119 | 1376 | 0.032762 | 1.362 | A04 | MICL0.01139026/RSS
Build-In Floor | Mini Canal | MICL.01139026/SBL | 11 | 390 | 26 | 26 | 1258 | 1258 | 1258 | 0.029952 | 489 | 0.011643 | 1433 | 0.034119 | 1.362 | A04 | MICL0.01139026/SBL
Build-In Floor | Mini Canal | MICL.01139026/SBR | 11 | 390 | 26 | 26 | 1258 | 1258 | 1258 | 0.029952 | 489 | 0.011643 | 1433 | 0.034119 | 1.362 | A04 | MICL0.01139026/SBR
Build-In Floor | Mini Canal | MICL.01139026/SDB | 11 | 390 | 26 | 26 | 1258 | 1258 | 1258 | 0.029952 | 489 | 0.011643 | 1433 | 0.034119 | 1.362 | A04 | MICL0.01139026/SDB
Build-In Floor | Mini Canal | MICL.01139026/SNA | 11 | 390 | 26 | 26 | 1258 | 1258 | 1258 | 0.029952 | 489 | 0.011643 | 1433 | 0.034119 | 1.362 | A04 | MICL0.01139026/SNA
Build-In Floor | Mini Canal | MICL.01139026/SNC | 11 | 390 | 26 | 26 | 1258 | 1258 | 1258 | 0.029952 | 489 | 0.011643 | 1433 | 0.034119 | 1.362 | A04 | MICL0.01139026/SNC
Build-In Floor | Mini Canal | MICL.01139034/ANA | 11 | 390 | 34 | 34 | 1226 | 1226 | 1226 | 0.02919 | 477 | 0.011357 | 1396 | 0.033238 | 1.362 | A04 | MICL0.01139034/ANA
Build-In Floor | Mini Canal | MICL.01139034/DBL | 11 | 390 | 34 | 34 | 1585 | 1585 | 1585 | 0.037738 | 617 | 0.01469 | 1805 | 0.042976 | 1.362 | A04 | MICL0.01139034/DBL
Build-In Floor | Mini Canal | MICL.01139034/DBN | 11 | 390 | 34 | 34 | 1520 | 1520 | 1520 | 0.03619 | 591 | 0.014071 | 1731 | 0.041214 | 1.362 | A04 | MICL0.01139034/DBN
Build-In Floor | Mini Canal | MICL.01139034/DBR | 11 | 390 | 34 | 34 | 1585 | 1585 | 1585 | 0.037738 | 617 | 0.01469 | 1805 | 0.042976 | 1.362 | A04 | MICL0.01139034/DBR
Build-In Floor | Mini Canal | MICL.01139034/DBV | 11 | 390 | 34 | 34 | 1520 | 1520 | 1520 | 0.03619 | 591 | 0.014071 | 1731 | 0.041214 | 1.362 | A04 | MICL0.01139034/DBV
Build-In Floor | Mini Canal | MICL.01139034/DDB | 11 | 390 | 34 | 34 | 1585 | 1585 | 1585 | 0.037738 | 617 | 0.01469 | 1805 | 0.042976 | 1.362 | A04 | MICL0.01139034/DDB
Build-In Floor | Mini Canal | MICL.01139034/DMN | 11 | 390 | 34 | 34 | 1520 | 1520 | 1520 | 0.03619 | 591 | 0.014071 | 1731 | 0.041214 | 1.362 | A04 | MICL0.01139034/DMN
Build-In Floor | Mini Canal | MICL.01139034/DMV | 11 | 390 | 34 | 34 | 1520 | 1520 | 1520 | 0.03619 | 591 | 0.014071 | 1731 | 0.041214 | 1.362 | A04 | MICL0.01139034/DMV
Build-In Floor | Mini Canal | MICL.01139034/DNA | 11 | 390 | 34 | 34 | 1585 | 1585 | 1585 | 0.037738 | 617 | 0.01469 | 1805 | 0.042976 | 1.362 | A04 | MICL0.01139034/DNA
Build-In Floor | Mini Canal | MICL.01139034/DNC | 11 | 390 | 34 | 34 | 1585 | 1585 | 1585 | 0.037738 | 617 | 0.01469 | 1805 | 0.042976 | 1.362 | A04 | MICL0.01139034/DNC
Build-In Floor | Mini Canal | MICL.01139034/DON | 11 | 390 | 34 | 34 | 1520 | 1520 | 1520 | 0.03619 | 591 | 0.014071 | 1731 | 0.041214 | 1.362 | A04 | MICL0.01139034/DON
Build-In Floor | Mini Canal | MICL.01139034/DOV | 11 | 390 | 34 | 34 | 1520 | 1520 | 1520 | 0.03619 | 591 | 0.014071 | 1731 | 0.041214 | 1.362 | A04 | MICL0.01139034/DOV
Build-In Floor | Mini Canal | MICL.01139034/PNC | 11 | 390 | 34 | 34 | 1389 | 1389 | 1389 | 0.033071 | 540 | 0.012857 | 1582 | 0.037667 | 1.362 | A04 | MICL0.01139034/PNC
Build-In Floor | Mini Canal | MICL.01139034/RBL | 11 | 390 | 34 | 34 | 1634 | 1634 | 1634 | 0.038905 | 636 | 0.015143 | 1861 | 0.04431 | 1.362 | A04 | MICL0.01139034/RBL
Build-In Floor | Mini Canal | MICL.01139034/RBN | 11 | 390 | 34 | 34 | 1585 | 1585 | 1585 | 0.037738 | 617 | 0.01469 | 1805 | 0.042976 | 1.362 | A04 | MICL0.01139034/RBN
Build-In Floor | Mini Canal | MICL.01139034/RBR | 11 | 390 | 34 | 34 | 1634 | 1634 | 1634 | 0.038905 | 636 | 0.015143 | 1861 | 0.04431 | 1.362 | A04 | MICL0.01139034/RBR
Build-In Floor | Mini Canal | MICL.01139034/RBV | 11 | 390 | 34 | 34 | 1585 | 1585 | 1585 | 0.037738 | 617 | 0.01469 | 1805 | 0.042976 | 1.362 | A04 | MICL0.01139034/RBV
Build-In Floor | Mini Canal | MICL.01139034/RDB | 11 | 390 | 34 | 34 | 1634 | 1634 | 1634 | 0.038905 | 636 | 0.015143 | 1861 | 0.04431 | 1.362 | A04 | MICL0.01139034/RDB
Build-In Floor | Mini Canal | MICL.01139034/RMN | 11 | 390 | 34 | 34 | 1585 | 1585 | 1585 | 0.037738 | 617 | 0.01469 | 1805 | 0.042976 | 1.362 | A04 | MICL0.01139034/RMN
Build-In Floor | Mini Canal | MICL.01139034/RMV | 11 | 390 | 34 | 34 | 1585 | 1585 | 1585 | 0.037738 | 617 | 0.01469 | 1805 | 0.042976 | 1.362 | A04 | MICL0.01139034/RMV
Build-In Floor | Mini Canal | MICL.01139034/RNA | 11 | 390 | 34 | 34 | 1634 | 1634 | 1634 | 0.038905 | 636 | 0.015143 | 1861 | 0.04431 | 1.362 | A04 | MICL0.01139034/RNA
Build-In Floor | Mini Canal | MICL.01139034/RON | 11 | 390 | 34 | 34 | 1585 | 1585 | 1585 | 0.037738 | 617 | 0.01469 | 1805 | 0.042976 | 1.362 | A04 | MICL0.01139034/RON
Build-In Floor | Mini Canal | MICL.01139034/ROV | 11 | 390 | 34 | 34 | 1585 | 1585 | 1585 | 0.037738 | 617 | 0.01469 | 1805 | 0.042976 | 1.362 | A04 | MICL0.01139034/ROV
Build-In Floor | Mini Canal | MICL.01139034/RSS | 11 | 390 | 34 | 34 | 1569 | 1569 | 1569 | 0.037357 | 610 | 0.014524 | 1787 | 0.042548 | 1.362 | A04 | MICL0.01139034/RSS
Build-In Floor | Mini Canal | MICL.01139034/SBL | 11 | 390 | 34 | 34 | 1634 | 1634 | 1634 | 0.038905 | 636 | 0.015143 | 1861 | 0.04431 | 1.362 | A04 | MICL0.01139034/SBL
Build-In Floor | Mini Canal | MICL.01139034/SBR | 11 | 390 | 34 | 34 | 1634 | 1634 | 1634 | 0.038905 | 636 | 0.015143 | 1861 | 0.04431 | 1.362 | A04 | MICL0.01139034/SBR
Build-In Floor | Mini Canal | MICL.01139034/SDB | 11 | 390 | 34 | 34 | 1634 | 1634 | 1634 | 0.038905 | 636 | 0.015143 | 1861 | 0.04431 | 1.362 | A04 | MICL0.01139034/SDB
Build-In Floor | Mini Canal | MICL.01139034/SNA | 11 | 390 | 34 | 34 | 1634 | 1634 | 1634 | 0.038905 | 636 | 0.015143 | 1861 | 0.04431 | 1.362 | A04 | MICL0.01139034/SNA
Build-In Floor | Mini Canal | MICL.01139034/SNC | 11 | 390 | 34 | 34 | 1634 | 1634 | 1634 | 0.038905 | 636 | 0.015143 | 1861 | 0.04431 | 1.362 | A04 | MICL0.01139034/SNC
Build-In Floor | Mini Canal | MICL.01139042/ANA | 11 | 390 | 42 | 42 | 1723 | 1723 | 1723 | 0.041024 | 670 | 0.015952 | 1962 | 0.046714 | 1.362 | A04 | MICL0.01139042/ANA
Build-In Floor | Mini Canal | MICL.01139042/DBL | 11 | 390 | 42 | 42 | 2228 | 2228 | 2228 | 0.053048 | 867 | 0.020643 | 2538 | 0.060429 | 1.362 | A04 | MICL0.01139042/DBL
Build-In Floor | Mini Canal | MICL.01139042/DBN | 11 | 390 | 42 | 42 | 2136 | 2136 | 2136 | 0.050857 | 831 | 0.019786 | 2433 | 0.057929 | 1.362 | A04 | MICL0.01139042/DBN
Build-In Floor | Mini Canal | MICL.01139042/DBR | 11 | 390 | 42 | 42 | 2228 | 2228 | 2228 | 0.053048 | 867 | 0.020643 | 2538 | 0.060429 | 1.362 | A04 | MICL0.01139042/DBR
Build-In Floor | Mini Canal | MICL.01139042/DBV | 11 | 390 | 42 | 42 | 2136 | 2136 | 2136 | 0.050857 | 831 | 0.019786 | 2433 | 0.057929 | 1.362 | A04 | MICL0.01139042/DBV
Build-In Floor | Mini Canal | MICL.01139042/DDB | 11 | 390 | 42 | 42 | 2228 | 2228 | 2228 | 0.053048 | 867 | 0.020643 | 2538 | 0.060429 | 1.362 | A04 | MICL0.01139042/DDB
Build-In Floor | Mini Canal | MICL.01139042/DMN | 11 | 390 | 42 | 42 | 2136 | 2136 | 2136 | 0.050857 | 831 | 0.019786 | 2433 | 0.057929 | 1.362 | A04 | MICL0.01139042/DMN
Build-In Floor | Mini Canal | MICL.01139042/DMV | 11 | 390 | 42 | 42 | 2136 | 2136 | 2136 | 0.050857 | 831 | 0.019786 | 2433 | 0.057929 | 1.362 | A04 | MICL0.01139042/DMV
Build-In Floor | Mini Canal | MICL.01139042/DNA | 11 | 390 | 42 | 42 | 2228 | 2228 | 2228 | 0.053048 | 867 | 0.020643 | 2538 | 0.060429 | 1.362 | A04 | MICL0.01139042/DNA
Build-In Floor | Mini Canal | MICL.01139042/DNC | 11 | 390 | 42 | 42 | 2228 | 2228 | 2228 | 0.053048 | 867 | 0.020643 | 2538 | 0.060429 | 1.362 | A04 | MICL0.01139042/DNC
Build-In Floor | Mini Canal | MICL.01139042/DON | 11 | 390 | 42 | 42 | 2136 | 2136 | 2136 | 0.050857 | 831 | 0.019786 | 2433 | 0.057929 | 1.362 | A04 | MICL0.01139042/DON
Build-In Floor | Mini Canal | MICL.01139042/DOV | 11 | 390 | 42 | 42 | 2136 | 2136 | 2136 | 0.050857 | 831 | 0.019786 | 2433 | 0.057929 | 1.362 | A04 | MICL0.01139042/DOV
Build-In Floor | Mini Canal | MICL.01139042/PNC | 11 | 390 | 42 | 42 | 1952 | 1952 | 1952 | 0.046476 | 759 | 0.018071 | 2223 | 0.052929 | 1.362 | A04 | MICL0.01139042/PNC
Build-In Floor | Mini Canal | MICL.01139042/RBL | 11 | 390 | 42 | 42 | 2297 | 2297 | 2297 | 0.05469 | 894 | 0.021286 | 2616 | 0.062286 | 1.362 | A04 | MICL0.01139042/RBL
Build-In Floor | Mini Canal | MICL.01139042/RBN | 11 | 390 | 42 | 42 | 2228 | 2228 | 2228 | 0.053048 | 867 | 0.020643 | 2538 | 0.060429 | 1.362 | A04 | MICL0.01139042/RBN
Build-In Floor | Mini Canal | MICL.01139042/RBR | 11 | 390 | 42 | 42 | 2297 | 2297 | 2297 | 0.05469 | 894 | 0.021286 | 2616 | 0.062286 | 1.362 | A04 | MICL0.01139042/RBR
Build-In Floor | Mini Canal | MICL.01139042/RBV | 11 | 390 | 42 | 42 | 2228 | 2228 | 2228 | 0.053048 | 867 | 0.020643 | 2538 | 0.060429 | 1.362 | A04 | MICL0.01139042/RBV
Build-In Floor | Mini Canal | MICL.01139042/RDB | 11 | 390 | 42 | 42 | 2297 | 2297 | 2297 | 0.05469 | 894 | 0.021286 | 2616 | 0.062286 | 1.362 | A04 | MICL0.01139042/RDB
Build-In Floor | Mini Canal | MICL.01139042/RMN | 11 | 390 | 42 | 42 | 2228 | 2228 | 2228 | 0.053048 | 867 | 0.020643 | 2538 | 0.060429 | 1.362 | A04 | MICL0.01139042/RMN
Build-In Floor | Mini Canal | MICL.01139042/RMV | 11 | 390 | 42 | 42 | 2228 | 2228 | 2228 | 0.053048 | 867 | 0.020643 | 2538 | 0.060429 | 1.362 | A04 | MICL0.01139042/RMV
Build-In Floor | Mini Canal | MICL.01139042/RNA | 11 | 390 | 42 | 42 | 2297 | 2297 | 2297 | 0.05469 | 894 | 0.021286 | 2616 | 0.062286 | 1.362 | A04 | MICL0.01139042/RNA
Build-In Floor | Mini Canal | MICL.01139042/RON | 11 | 390 | 42 | 42 | 2228 | 2228 | 2228 | 0.053048 | 867 | 0.020643 | 2538 | 0.060429 | 1.362 | A04 | MICL0.01139042/RON
Build-In Floor | Mini Canal | MICL.01139042/ROV | 11 | 390 | 42 | 42 | 2228 | 2228 | 2228 | 0.053048 | 867 | 0.020643 | 2538 | 0.060429 | 1.362 | A04 | MICL0.01139042/ROV
Build-In Floor | Mini Canal | MICL.01139042/RSS | 11 | 390 | 42 | 42 | 2205 | 2205 | 2205 | 0.0525 | 858 | 0.020429 | 2511 | 0.059786 | 1.362 | A04 | MICL0.01139042/RSS
Build-In Floor | Mini Canal | MICL.01139042/SBL | 11 | 390 | 42 | 42 | 2297 | 2297 | 2297 | 0.05469 | 894 | 0.021286 | 2616 | 0.062286 | 1.362 | A04 | MICL0.01139042/SBL
Build-In Floor | Mini Canal | MICL.01139042/SBR | 11 | 390 | 42 | 42 | 2297 | 2297 | 2297 | 0.05469 | 894 | 0.021286 | 2616 | 0.062286 | 1.362 | A04 | MICL0.01139042/SBR
Build-In Floor | Mini Canal | MICL.01139042/SDB | 11 | 390 | 42 | 42 | 2297 | 2297 | 2297 | 0.05469 | 894 | 0.021286 | 2616 | 0.062286 | 1.362 | A04 | MICL0.01139042/SDB
Build-In Floor | Mini Canal | MICL.01139042/SNA | 11 | 390 | 42 | 42 | 2297 | 2297 | 2297 | 0.05469 | 894 | 0.021286 | 2616 | 0.062286 | 1.362 | A04 | MICL0.01139042/SNA
Build-In Floor | Mini Canal | MICL.01139042/SNC | 11 | 390 | 42 | 42 | 2297 | 2297 | 2297 | 0.05469 | 894 | 0.021286 | 2616 | 0.062286 | 1.362 | A04 | MICL0.01139042/SNC
Build-In Floor | Mini Canal | MICL.01141014/ANA | 11 | 410 | 14 | 14 | 623 | 623 | 623 | 0.014833 | 242 | 0.0057619 | 710 | 0.016905 | 1.362 | A04 | MICL0.01141014/ANA
Build-In Floor | Mini Canal | MICL.01141014/DBL | 11 | 410 | 14 | 14 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.01141014/DBL
Build-In Floor | Mini Canal | MICL.01141014/DBN | 11 | 410 | 14 | 14 | 772 | 772 | 772 | 0.018381 | 300 | 0.0071429 | 879 | 0.020929 | 1.362 | A04 | MICL0.01141014/DBN
Build-In Floor | Mini Canal | MICL.01141014/DBR | 11 | 410 | 14 | 14 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.01141014/DBR
Build-In Floor | Mini Canal | MICL.01141014/DBV | 11 | 410 | 14 | 14 | 772 | 772 | 772 | 0.018381 | 300 | 0.0071429 | 879 | 0.020929 | 1.362 | A04 | MICL0.01141014/DBV
Build-In Floor | Mini Canal | MICL.01141014/DDB | 11 | 410 | 14 | 14 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.01141014/DDB
Build-In Floor | Mini Canal | MICL.01141014/DMN | 11 | 410 | 14 | 14 | 772 | 772 | 772 | 0.018381 | 300 | 0.0071429 | 879 | 0.020929 | 1.362 | A04 | MICL0.01141014/DMN
Build-In Floor | Mini Canal | MICL.01141014/DMV | 11 | 410 | 14 | 14 | 772 | 772 | 772 | 0.018381 | 300 | 0.0071429 | 879 | 0.020929 | 1.362 | A04 | MICL0.01141014/DMV
Build-In Floor | Mini Canal | MICL.01141014/DNA | 11 | 410 | 14 | 14 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.01141014/DNA
Build-In Floor | Mini Canal | MICL.01141014/DNC | 11 | 410 | 14 | 14 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.01141014/DNC
Build-In Floor | Mini Canal | MICL.01141014/DON | 11 | 410 | 14 | 14 | 772 | 772 | 772 | 0.018381 | 300 | 0.0071429 | 879 | 0.020929 | 1.362 | A04 | MICL0.01141014/DON
Build-In Floor | Mini Canal | MICL.01141014/DOV | 11 | 410 | 14 | 14 | 772 | 772 | 772 | 0.018381 | 300 | 0.0071429 | 879 | 0.020929 | 1.362 | A04 | MICL0.01141014/DOV
Build-In Floor | Mini Canal | MICL.01141014/RBL | 11 | 410 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01141014/RBL
Build-In Floor | Mini Canal | MICL.01141014/RBN | 11 | 410 | 14 | 14 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.01141014/RBN
Build-In Floor | Mini Canal | MICL.01141014/RBR | 11 | 410 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01141014/RBR
Build-In Floor | Mini Canal | MICL.01141014/RBV | 11 | 410 | 14 | 14 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.01141014/RBV
Build-In Floor | Mini Canal | MICL.01141014/RDB | 11 | 410 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01141014/RDB
Build-In Floor | Mini Canal | MICL.01141014/RMN | 11 | 410 | 14 | 14 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.01141014/RMN
Build-In Floor | Mini Canal | MICL.01141014/RMV | 11 | 410 | 14 | 14 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.01141014/RMV
Build-In Floor | Mini Canal | MICL.01141014/RNA | 11 | 410 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01141014/RNA
Build-In Floor | Mini Canal | MICL.01141014/RON | 11 | 410 | 14 | 14 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.01141014/RON
Build-In Floor | Mini Canal | MICL.01141014/ROV | 11 | 410 | 14 | 14 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.01141014/ROV
Build-In Floor | Mini Canal | MICL.01141014/RSS | 11 | 410 | 14 | 14 | 797 | 797 | 797 | 0.018976 | 310 | 0.007381 | 908 | 0.021619 | 1.362 | A04 | MICL0.01141014/RSS
Build-In Floor | Mini Canal | MICL.01141014/SBL | 11 | 410 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01141014/SBL
Build-In Floor | Mini Canal | MICL.01141014/SBR | 11 | 410 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01141014/SBR
Build-In Floor | Mini Canal | MICL.01141014/SDB | 11 | 410 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01141014/SDB
Build-In Floor | Mini Canal | MICL.01141014/SNA | 11 | 410 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01141014/SNA
Build-In Floor | Mini Canal | MICL.01141014/SNC | 11 | 410 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01141014/SNC
Build-In Floor | Mini Canal | MICL.01141018/ANA | 11 | 410 | 18 | 18 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.01141018/ANA
Build-In Floor | Mini Canal | MICL.01141018/DBL | 11 | 410 | 18 | 18 | 954 | 954 | 954 | 0.022714 | 371 | 0.0088333 | 1087 | 0.025881 | 1.362 | A04 | MICL0.01141018/DBL
Build-In Floor | Mini Canal | MICL.01141018/DBN | 11 | 410 | 18 | 18 | 915 | 915 | 915 | 0.021786 | 356 | 0.0084762 | 1042 | 0.02481 | 1.362 | A04 | MICL0.01141018/DBN
Build-In Floor | Mini Canal | MICL.01141018/DBR | 11 | 410 | 18 | 18 | 954 | 954 | 954 | 0.022714 | 371 | 0.0088333 | 1087 | 0.025881 | 1.362 | A04 | MICL0.01141018/DBR
Build-In Floor | Mini Canal | MICL.01141018/DBV | 11 | 410 | 18 | 18 | 915 | 915 | 915 | 0.021786 | 356 | 0.0084762 | 1042 | 0.02481 | 1.362 | A04 | MICL0.01141018/DBV
Build-In Floor | Mini Canal | MICL.01141018/DDB | 11 | 410 | 18 | 18 | 954 | 954 | 954 | 0.022714 | 371 | 0.0088333 | 1087 | 0.025881 | 1.362 | A04 | MICL0.01141018/DDB
Build-In Floor | Mini Canal | MICL.01141018/DMN | 11 | 410 | 18 | 18 | 915 | 915 | 915 | 0.021786 | 356 | 0.0084762 | 1042 | 0.02481 | 1.362 | A04 | MICL0.01141018/DMN
Build-In Floor | Mini Canal | MICL.01141018/DMV | 11 | 410 | 18 | 18 | 915 | 915 | 915 | 0.021786 | 356 | 0.0084762 | 1042 | 0.02481 | 1.362 | A04 | MICL0.01141018/DMV
Build-In Floor | Mini Canal | MICL.01141018/DNA | 11 | 410 | 18 | 18 | 954 | 954 | 954 | 0.022714 | 371 | 0.0088333 | 1087 | 0.025881 | 1.362 | A04 | MICL0.01141018/DNA
Build-In Floor | Mini Canal | MICL.01141018/DNC | 11 | 410 | 18 | 18 | 954 | 954 | 954 | 0.022714 | 371 | 0.0088333 | 1087 | 0.025881 | 1.362 | A04 | MICL0.01141018/DNC
Build-In Floor | Mini Canal | MICL.01141018/DON | 11 | 410 | 18 | 18 | 915 | 915 | 915 | 0.021786 | 356 | 0.0084762 | 1042 | 0.02481 | 1.362 | A04 | MICL0.01141018/DON
Build-In Floor | Mini Canal | MICL.01141018/DOV | 11 | 410 | 18 | 18 | 915 | 915 | 915 | 0.021786 | 356 | 0.0084762 | 1042 | 0.02481 | 1.362 | A04 | MICL0.01141018/DOV
Build-In Floor | Mini Canal | MICL.01141018/RBL | 11 | 410 | 18 | 18 | 984 | 984 | 984 | 0.023429 | 383 | 0.009119 | 1121 | 0.02669 | 1.362 | A04 | MICL0.01141018/RBL
Build-In Floor | Mini Canal | MICL.01141018/RBN | 11 | 410 | 18 | 18 | 954 | 954 | 954 | 0.022714 | 371 | 0.0088333 | 1087 | 0.025881 | 1.362 | A04 | MICL0.01141018/RBN
Build-In Floor | Mini Canal | MICL.01141018/RBR | 11 | 410 | 18 | 18 | 984 | 984 | 984 | 0.023429 | 383 | 0.009119 | 1121 | 0.02669 | 1.362 | A04 | MICL0.01141018/RBR
Build-In Floor | Mini Canal | MICL.01141018/RBV | 11 | 410 | 18 | 18 | 954 | 954 | 954 | 0.022714 | 371 | 0.0088333 | 1087 | 0.025881 | 1.362 | A04 | MICL0.01141018/RBV
Build-In Floor | Mini Canal | MICL.01141018/RDB | 11 | 410 | 18 | 18 | 984 | 984 | 984 | 0.023429 | 383 | 0.009119 | 1121 | 0.02669 | 1.362 | A04 | MICL0.01141018/RDB
Build-In Floor | Mini Canal | MICL.01141018/RMN | 11 | 410 | 18 | 18 | 954 | 954 | 954 | 0.022714 | 371 | 0.0088333 | 1087 | 0.025881 | 1.362 | A04 | MICL0.01141018/RMN
Build-In Floor | Mini Canal | MICL.01141018/RMV | 11 | 410 | 18 | 18 | 954 | 954 | 954 | 0.022714 | 371 | 0.0088333 | 1087 | 0.025881 | 1.362 | A04 | MICL0.01141018/RMV
Build-In Floor | Mini Canal | MICL.01141018/RNA | 11 | 410 | 18 | 18 | 984 | 984 | 984 | 0.023429 | 383 | 0.009119 | 1121 | 0.02669 | 1.362 | A04 | MICL0.01141018/RNA
Build-In Floor | Mini Canal | MICL.01141018/RON | 11 | 410 | 18 | 18 | 954 | 954 | 954 | 0.022714 | 371 | 0.0088333 | 1087 | 0.025881 | 1.362 | A04 | MICL0.01141018/RON
Build-In Floor | Mini Canal | MICL.01141018/ROV | 11 | 410 | 18 | 18 | 954 | 954 | 954 | 0.022714 | 371 | 0.0088333 | 1087 | 0.025881 | 1.362 | A04 | MICL0.01141018/ROV
Build-In Floor | Mini Canal | MICL.01141018/RSS | 11 | 410 | 18 | 18 | 945 | 945 | 945 | 0.0225 | 368 | 0.0087619 | 1076 | 0.025619 | 1.362 | A04 | MICL0.01141018/RSS
Build-In Floor | Mini Canal | MICL.01141018/SBL | 11 | 410 | 18 | 18 | 984 | 984 | 984 | 0.023429 | 383 | 0.009119 | 1121 | 0.02669 | 1.362 | A04 | MICL0.01141018/SBL
Build-In Floor | Mini Canal | MICL.01141018/SBR | 11 | 410 | 18 | 18 | 984 | 984 | 984 | 0.023429 | 383 | 0.009119 | 1121 | 0.02669 | 1.362 | A04 | MICL0.01141018/SBR
Build-In Floor | Mini Canal | MICL.01141018/SDB | 11 | 410 | 18 | 18 | 984 | 984 | 984 | 0.023429 | 383 | 0.009119 | 1121 | 0.02669 | 1.362 | A04 | MICL0.01141018/SDB
Build-In Floor | Mini Canal | MICL.01141018/SNA | 11 | 410 | 18 | 18 | 984 | 984 | 984 | 0.023429 | 383 | 0.009119 | 1121 | 0.02669 | 1.362 | A04 | MICL0.01141018/SNA
Build-In Floor | Mini Canal | MICL.01141018/SNC | 11 | 410 | 18 | 18 | 984 | 984 | 984 | 0.023429 | 383 | 0.009119 | 1121 | 0.02669 | 1.362 | A04 | MICL0.01141018/SNC
Build-In Floor | Mini Canal | MICL.01141026/ANA | 11 | 410 | 26 | 26 | 996 | 996 | 996 | 0.023714 | 387 | 0.0092143 | 1134 | 0.027 | 1.362 | A04 | MICL0.01141026/ANA
Build-In Floor | Mini Canal | MICL.01141026/DBL | 11 | 410 | 26 | 26 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.01141026/DBL
Build-In Floor | Mini Canal | MICL.01141026/DBN | 11 | 410 | 26 | 26 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01141026/DBN
Build-In Floor | Mini Canal | MICL.01141026/DBR | 11 | 410 | 26 | 26 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.01141026/DBR
Build-In Floor | Mini Canal | MICL.01141026/DBV | 11 | 410 | 26 | 26 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01141026/DBV
Build-In Floor | Mini Canal | MICL.01141026/DDB | 11 | 410 | 26 | 26 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.01141026/DDB
Build-In Floor | Mini Canal | MICL.01141026/DMN | 11 | 410 | 26 | 26 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01141026/DMN
Build-In Floor | Mini Canal | MICL.01141026/DMV | 11 | 410 | 26 | 26 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01141026/DMV
Build-In Floor | Mini Canal | MICL.01141026/DNA | 11 | 410 | 26 | 26 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.01141026/DNA
Build-In Floor | Mini Canal | MICL.01141026/DNC | 11 | 410 | 26 | 26 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.01141026/DNC
Build-In Floor | Mini Canal | MICL.01141026/DON | 11 | 410 | 26 | 26 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01141026/DON
Build-In Floor | Mini Canal | MICL.01141026/DOV | 11 | 410 | 26 | 26 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01141026/DOV
Build-In Floor | Mini Canal | MICL.01141026/PNC | 11 | 410 | 26 | 26 | 1129 | 1129 | 1129 | 0.026881 | 439 | 0.010452 | 1286 | 0.030619 | 1.362 | A04 | MICL0.01141026/PNC
Build-In Floor | Mini Canal | MICL.01141026/RBL | 11 | 410 | 26 | 26 | 1328 | 1328 | 1328 | 0.031619 | 517 | 0.01231 | 1513 | 0.036024 | 1.362 | A04 | MICL0.01141026/RBL
Build-In Floor | Mini Canal | MICL.01141026/RBN | 11 | 410 | 26 | 26 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.01141026/RBN
Build-In Floor | Mini Canal | MICL.01141026/RBR | 11 | 410 | 26 | 26 | 1328 | 1328 | 1328 | 0.031619 | 517 | 0.01231 | 1513 | 0.036024 | 1.362 | A04 | MICL0.01141026/RBR
Build-In Floor | Mini Canal | MICL.01141026/RBV | 11 | 410 | 26 | 26 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.01141026/RBV
Build-In Floor | Mini Canal | MICL.01141026/RDB | 11 | 410 | 26 | 26 | 1328 | 1328 | 1328 | 0.031619 | 517 | 0.01231 | 1513 | 0.036024 | 1.362 | A04 | MICL0.01141026/RDB
Build-In Floor | Mini Canal | MICL.01141026/RMN | 11 | 410 | 26 | 26 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.01141026/RMN
Build-In Floor | Mini Canal | MICL.01141026/RMV | 11 | 410 | 26 | 26 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.01141026/RMV
Build-In Floor | Mini Canal | MICL.01141026/RNA | 11 | 410 | 26 | 26 | 1328 | 1328 | 1328 | 0.031619 | 517 | 0.01231 | 1513 | 0.036024 | 1.362 | A04 | MICL0.01141026/RNA
Build-In Floor | Mini Canal | MICL.01141026/RON | 11 | 410 | 26 | 26 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.01141026/RON
Build-In Floor | Mini Canal | MICL.01141026/ROV | 11 | 410 | 26 | 26 | 1288 | 1288 | 1288 | 0.030667 | 501 | 0.011929 | 1467 | 0.034929 | 1.362 | A04 | MICL0.01141026/ROV
Build-In Floor | Mini Canal | MICL.01141026/RSS | 11 | 410 | 26 | 26 | 1275 | 1275 | 1275 | 0.030357 | 496 | 0.01181 | 1452 | 0.034571 | 1.362 | A04 | MICL0.01141026/RSS
Build-In Floor | Mini Canal | MICL.01141026/SBL | 11 | 410 | 26 | 26 | 1328 | 1328 | 1328 | 0.031619 | 517 | 0.01231 | 1513 | 0.036024 | 1.362 | A04 | MICL0.01141026/SBL
Build-In Floor | Mini Canal | MICL.01141026/SBR | 11 | 410 | 26 | 26 | 1328 | 1328 | 1328 | 0.031619 | 517 | 0.01231 | 1513 | 0.036024 | 1.362 | A04 | MICL0.01141026/SBR
Build-In Floor | Mini Canal | MICL.01141026/SDB | 11 | 410 | 26 | 26 | 1328 | 1328 | 1328 | 0.031619 | 517 | 0.01231 | 1513 | 0.036024 | 1.362 | A04 | MICL0.01141026/SDB
Build-In Floor | Mini Canal | MICL.01141026/SNA | 11 | 410 | 26 | 26 | 1328 | 1328 | 1328 | 0.031619 | 517 | 0.01231 | 1513 | 0.036024 | 1.362 | A04 | MICL0.01141026/SNA
Build-In Floor | Mini Canal | MICL.01141026/SNC | 11 | 410 | 26 | 26 | 1328 | 1328 | 1328 | 0.031619 | 517 | 0.01231 | 1513 | 0.036024 | 1.362 | A04 | MICL0.01141026/SNC
Build-In Floor | Mini Canal | MICL.01141034/ANA | 11 | 410 | 34 | 34 | 1294 | 1294 | 1294 | 0.03081 | 503 | 0.011976 | 1474 | 0.035095 | 1.362 | A04 | MICL0.01141034/ANA
Build-In Floor | Mini Canal | MICL.01141034/DBL | 11 | 410 | 34 | 34 | 1673 | 1673 | 1673 | 0.039833 | 651 | 0.0155 | 1906 | 0.045381 | 1.362 | A04 | MICL0.01141034/DBL
Build-In Floor | Mini Canal | MICL.01141034/DBN | 11 | 410 | 34 | 34 | 1604 | 1604 | 1604 | 0.03819 | 624 | 0.014857 | 1827 | 0.0435 | 1.362 | A04 | MICL0.01141034/DBN
Build-In Floor | Mini Canal | MICL.01141034/DBR | 11 | 410 | 34 | 34 | 1673 | 1673 | 1673 | 0.039833 | 651 | 0.0155 | 1906 | 0.045381 | 1.362 | A04 | MICL0.01141034/DBR
Build-In Floor | Mini Canal | MICL.01141034/DBV | 11 | 410 | 34 | 34 | 1604 | 1604 | 1604 | 0.03819 | 624 | 0.014857 | 1827 | 0.0435 | 1.362 | A04 | MICL0.01141034/DBV
Build-In Floor | Mini Canal | MICL.01141034/DDB | 11 | 410 | 34 | 34 | 1673 | 1673 | 1673 | 0.039833 | 651 | 0.0155 | 1906 | 0.045381 | 1.362 | A04 | MICL0.01141034/DDB
Build-In Floor | Mini Canal | MICL.01141034/DMN | 11 | 410 | 34 | 34 | 1604 | 1604 | 1604 | 0.03819 | 624 | 0.014857 | 1827 | 0.0435 | 1.362 | A04 | MICL0.01141034/DMN
Build-In Floor | Mini Canal | MICL.01141034/DMV | 11 | 410 | 34 | 34 | 1604 | 1604 | 1604 | 0.03819 | 624 | 0.014857 | 1827 | 0.0435 | 1.362 | A04 | MICL0.01141034/DMV
Build-In Floor | Mini Canal | MICL.01141034/DNA | 11 | 410 | 34 | 34 | 1673 | 1673 | 1673 | 0.039833 | 651 | 0.0155 | 1906 | 0.045381 | 1.362 | A04 | MICL0.01141034/DNA
Build-In Floor | Mini Canal | MICL.01141034/DNC | 11 | 410 | 34 | 34 | 1673 | 1673 | 1673 | 0.039833 | 651 | 0.0155 | 1906 | 0.045381 | 1.362 | A04 | MICL0.01141034/DNC
Build-In Floor | Mini Canal | MICL.01141034/DON | 11 | 410 | 34 | 34 | 1604 | 1604 | 1604 | 0.03819 | 624 | 0.014857 | 1827 | 0.0435 | 1.362 | A04 | MICL0.01141034/DON
Build-In Floor | Mini Canal | MICL.01141034/DOV | 11 | 410 | 34 | 34 | 1604 | 1604 | 1604 | 0.03819 | 624 | 0.014857 | 1827 | 0.0435 | 1.362 | A04 | MICL0.01141034/DOV
Build-In Floor | Mini Canal | MICL.01141034/PNC | 11 | 410 | 34 | 34 | 1466 | 1466 | 1466 | 0.034905 | 570 | 0.013571 | 1670 | 0.039762 | 1.362 | A04 | MICL0.01141034/PNC
Build-In Floor | Mini Canal | MICL.01141034/RBL | 11 | 410 | 34 | 34 | 1725 | 1725 | 1725 | 0.041071 | 671 | 0.015976 | 1965 | 0.046786 | 1.362 | A04 | MICL0.01141034/RBL
Build-In Floor | Mini Canal | MICL.01141034/RBN | 11 | 410 | 34 | 34 | 1673 | 1673 | 1673 | 0.039833 | 651 | 0.0155 | 1906 | 0.045381 | 1.362 | A04 | MICL0.01141034/RBN
Build-In Floor | Mini Canal | MICL.01141034/RBR | 11 | 410 | 34 | 34 | 1725 | 1725 | 1725 | 0.041071 | 671 | 0.015976 | 1965 | 0.046786 | 1.362 | A04 | MICL0.01141034/RBR
Build-In Floor | Mini Canal | MICL.01141034/RBV | 11 | 410 | 34 | 34 | 1673 | 1673 | 1673 | 0.039833 | 651 | 0.0155 | 1906 | 0.045381 | 1.362 | A04 | MICL0.01141034/RBV
Build-In Floor | Mini Canal | MICL.01141034/RDB | 11 | 410 | 34 | 34 | 1725 | 1725 | 1725 | 0.041071 | 671 | 0.015976 | 1965 | 0.046786 | 1.362 | A04 | MICL0.01141034/RDB
Build-In Floor | Mini Canal | MICL.01141034/RMN | 11 | 410 | 34 | 34 | 1673 | 1673 | 1673 | 0.039833 | 651 | 0.0155 | 1906 | 0.045381 | 1.362 | A04 | MICL0.01141034/RMN
Build-In Floor | Mini Canal | MICL.01141034/RMV | 11 | 410 | 34 | 34 | 1673 | 1673 | 1673 | 0.039833 | 651 | 0.0155 | 1906 | 0.045381 | 1.362 | A04 | MICL0.01141034/RMV
Build-In Floor | Mini Canal | MICL.01141034/RNA | 11 | 410 | 34 | 34 | 1725 | 1725 | 1725 | 0.041071 | 671 | 0.015976 | 1965 | 0.046786 | 1.362 | A04 | MICL0.01141034/RNA
Build-In Floor | Mini Canal | MICL.01141034/RON | 11 | 410 | 34 | 34 | 1673 | 1673 | 1673 | 0.039833 | 651 | 0.0155 | 1906 | 0.045381 | 1.362 | A04 | MICL0.01141034/RON
Build-In Floor | Mini Canal | MICL.01141034/ROV | 11 | 410 | 34 | 34 | 1673 | 1673 | 1673 | 0.039833 | 651 | 0.0155 | 1906 | 0.045381 | 1.362 | A04 | MICL0.01141034/ROV
Build-In Floor | Mini Canal | MICL.01141034/RSS | 11 | 410 | 34 | 34 | 1656 | 1656 | 1656 | 0.039429 | 644 | 0.015333 | 1886 | 0.044905 | 1.362 | A04 | MICL0.01141034/RSS
Build-In Floor | Mini Canal | MICL.01141034/SBL | 11 | 410 | 34 | 34 | 1725 | 1725 | 1725 | 0.041071 | 671 | 0.015976 | 1965 | 0.046786 | 1.362 | A04 | MICL0.01141034/SBL
Build-In Floor | Mini Canal | MICL.01141034/SBR | 11 | 410 | 34 | 34 | 1725 | 1725 | 1725 | 0.041071 | 671 | 0.015976 | 1965 | 0.046786 | 1.362 | A04 | MICL0.01141034/SBR
Build-In Floor | Mini Canal | MICL.01141034/SDB | 11 | 410 | 34 | 34 | 1725 | 1725 | 1725 | 0.041071 | 671 | 0.015976 | 1965 | 0.046786 | 1.362 | A04 | MICL0.01141034/SDB
Build-In Floor | Mini Canal | MICL.01141034/SNA | 11 | 410 | 34 | 34 | 1725 | 1725 | 1725 | 0.041071 | 671 | 0.015976 | 1965 | 0.046786 | 1.362 | A04 | MICL0.01141034/SNA
Build-In Floor | Mini Canal | MICL.01141034/SNC | 11 | 410 | 34 | 34 | 1725 | 1725 | 1725 | 0.041071 | 671 | 0.015976 | 1965 | 0.046786 | 1.362 | A04 | MICL0.01141034/SNC
Build-In Floor | Mini Canal | MICL.01141042/ANA | 11 | 410 | 42 | 42 | 1818 | 1818 | 1818 | 0.043286 | 707 | 0.016833 | 2071 | 0.04931 | 1.362 | A04 | MICL0.01141042/ANA
Build-In Floor | Mini Canal | MICL.01141042/DBL | 11 | 410 | 42 | 42 | 2351 | 2351 | 2351 | 0.055976 | 915 | 0.021786 | 2678 | 0.063762 | 1.362 | A04 | MICL0.01141042/DBL
Build-In Floor | Mini Canal | MICL.01141042/DBN | 11 | 410 | 42 | 42 | 2254 | 2254 | 2254 | 0.053667 | 877 | 0.020881 | 2567 | 0.061119 | 1.362 | A04 | MICL0.01141042/DBN
Build-In Floor | Mini Canal | MICL.01141042/DBR | 11 | 410 | 42 | 42 | 2351 | 2351 | 2351 | 0.055976 | 915 | 0.021786 | 2678 | 0.063762 | 1.362 | A04 | MICL0.01141042/DBR
Build-In Floor | Mini Canal | MICL.01141042/DBV | 11 | 410 | 42 | 42 | 2254 | 2254 | 2254 | 0.053667 | 877 | 0.020881 | 2567 | 0.061119 | 1.362 | A04 | MICL0.01141042/DBV
Build-In Floor | Mini Canal | MICL.01141042/DDB | 11 | 410 | 42 | 42 | 2351 | 2351 | 2351 | 0.055976 | 915 | 0.021786 | 2678 | 0.063762 | 1.362 | A04 | MICL0.01141042/DDB
Build-In Floor | Mini Canal | MICL.01141042/DMN | 11 | 410 | 42 | 42 | 2254 | 2254 | 2254 | 0.053667 | 877 | 0.020881 | 2567 | 0.061119 | 1.362 | A04 | MICL0.01141042/DMN
Build-In Floor | Mini Canal | MICL.01141042/DMV | 11 | 410 | 42 | 42 | 2254 | 2254 | 2254 | 0.053667 | 877 | 0.020881 | 2567 | 0.061119 | 1.362 | A04 | MICL0.01141042/DMV
Build-In Floor | Mini Canal | MICL.01141042/DNA | 11 | 410 | 42 | 42 | 2351 | 2351 | 2351 | 0.055976 | 915 | 0.021786 | 2678 | 0.063762 | 1.362 | A04 | MICL0.01141042/DNA
Build-In Floor | Mini Canal | MICL.01141042/DNC | 11 | 410 | 42 | 42 | 2351 | 2351 | 2351 | 0.055976 | 915 | 0.021786 | 2678 | 0.063762 | 1.362 | A04 | MICL0.01141042/DNC
Build-In Floor | Mini Canal | MICL.01141042/DON | 11 | 410 | 42 | 42 | 2254 | 2254 | 2254 | 0.053667 | 877 | 0.020881 | 2567 | 0.061119 | 1.362 | A04 | MICL0.01141042/DON
Build-In Floor | Mini Canal | MICL.01141042/DOV | 11 | 410 | 42 | 42 | 2254 | 2254 | 2254 | 0.053667 | 877 | 0.020881 | 2567 | 0.061119 | 1.362 | A04 | MICL0.01141042/DOV
Build-In Floor | Mini Canal | MICL.01141042/PNC | 11 | 410 | 42 | 42 | 2060 | 2060 | 2060 | 0.049048 | 801 | 0.019071 | 2346 | 0.055857 | 1.362 | A04 | MICL0.01141042/PNC
Build-In Floor | Mini Canal | MICL.01141042/RBL | 11 | 410 | 42 | 42 | 2424 | 2424 | 2424 | 0.057714 | 943 | 0.022452 | 2761 | 0.065738 | 1.362 | A04 | MICL0.01141042/RBL
Build-In Floor | Mini Canal | MICL.01141042/RBN | 11 | 410 | 42 | 42 | 2351 | 2351 | 2351 | 0.055976 | 915 | 0.021786 | 2678 | 0.063762 | 1.362 | A04 | MICL0.01141042/RBN
Build-In Floor | Mini Canal | MICL.01141042/RBR | 11 | 410 | 42 | 42 | 2424 | 2424 | 2424 | 0.057714 | 943 | 0.022452 | 2761 | 0.065738 | 1.362 | A04 | MICL0.01141042/RBR
Build-In Floor | Mini Canal | MICL.01141042/RBV | 11 | 410 | 42 | 42 | 2351 | 2351 | 2351 | 0.055976 | 915 | 0.021786 | 2678 | 0.063762 | 1.362 | A04 | MICL0.01141042/RBV
Build-In Floor | Mini Canal | MICL.01141042/RDB | 11 | 410 | 42 | 42 | 2424 | 2424 | 2424 | 0.057714 | 943 | 0.022452 | 2761 | 0.065738 | 1.362 | A04 | MICL0.01141042/RDB
Build-In Floor | Mini Canal | MICL.01141042/RMN | 11 | 410 | 42 | 42 | 2351 | 2351 | 2351 | 0.055976 | 915 | 0.021786 | 2678 | 0.063762 | 1.362 | A04 | MICL0.01141042/RMN
Build-In Floor | Mini Canal | MICL.01141042/RMV | 11 | 410 | 42 | 42 | 2351 | 2351 | 2351 | 0.055976 | 915 | 0.021786 | 2678 | 0.063762 | 1.362 | A04 | MICL0.01141042/RMV
Build-In Floor | Mini Canal | MICL.01141042/RNA | 11 | 410 | 42 | 42 | 2424 | 2424 | 2424 | 0.057714 | 943 | 0.022452 | 2761 | 0.065738 | 1.362 | A04 | MICL0.01141042/RNA
Build-In Floor | Mini Canal | MICL.01141042/RON | 11 | 410 | 42 | 42 | 2351 | 2351 | 2351 | 0.055976 | 915 | 0.021786 | 2678 | 0.063762 | 1.362 | A04 | MICL0.01141042/RON
Build-In Floor | Mini Canal | MICL.01141042/ROV | 11 | 410 | 42 | 42 | 2351 | 2351 | 2351 | 0.055976 | 915 | 0.021786 | 2678 | 0.063762 | 1.362 | A04 | MICL0.01141042/ROV
Build-In Floor | Mini Canal | MICL.01141042/RSS | 11 | 410 | 42 | 42 | 2327 | 2327 | 2327 | 0.055405 | 905 | 0.021548 | 2650 | 0.063095 | 1.362 | A04 | MICL0.01141042/RSS
Build-In Floor | Mini Canal | MICL.01141042/SBL | 11 | 410 | 42 | 42 | 2424 | 2424 | 2424 | 0.057714 | 943 | 0.022452 | 2761 | 0.065738 | 1.362 | A04 | MICL0.01141042/SBL
Build-In Floor | Mini Canal | MICL.01141042/SBR | 11 | 410 | 42 | 42 | 2424 | 2424 | 2424 | 0.057714 | 943 | 0.022452 | 2761 | 0.065738 | 1.362 | A04 | MICL0.01141042/SBR
Build-In Floor | Mini Canal | MICL.01141042/SDB | 11 | 410 | 42 | 42 | 2424 | 2424 | 2424 | 0.057714 | 943 | 0.022452 | 2761 | 0.065738 | 1.362 | A04 | MICL0.01141042/SDB
Build-In Floor | Mini Canal | MICL.01141042/SNA | 11 | 410 | 42 | 42 | 2424 | 2424 | 2424 | 0.057714 | 943 | 0.022452 | 2761 | 0.065738 | 1.362 | A04 | MICL0.01141042/SNA
Build-In Floor | Mini Canal | MICL.01141042/SNC | 11 | 410 | 42 | 42 | 2424 | 2424 | 2424 | 0.057714 | 943 | 0.022452 | 2761 | 0.065738 | 1.362 | A04 | MICL0.01141042/SNC
Build-In Floor | Mini Canal | MICL.01143014/ANA | 11 | 430 | 14 | 14 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.01143014/ANA
Build-In Floor | Mini Canal | MICL.01143014/DBL | 11 | 430 | 14 | 14 | 848 | 848 | 848 | 0.02019 | 330 | 0.0078571 | 966 | 0.023 | 1.362 | A04 | MICL0.01143014/DBL
Build-In Floor | Mini Canal | MICL.01143014/DBN | 11 | 430 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.01143014/DBN
Build-In Floor | Mini Canal | MICL.01143014/DBR | 11 | 430 | 14 | 14 | 848 | 848 | 848 | 0.02019 | 330 | 0.0078571 | 966 | 0.023 | 1.362 | A04 | MICL0.01143014/DBR
Build-In Floor | Mini Canal | MICL.01143014/DBV | 11 | 430 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.01143014/DBV
Build-In Floor | Mini Canal | MICL.01143014/DDB | 11 | 430 | 14 | 14 | 848 | 848 | 848 | 0.02019 | 330 | 0.0078571 | 966 | 0.023 | 1.362 | A04 | MICL0.01143014/DDB
Build-In Floor | Mini Canal | MICL.01143014/DMN | 11 | 430 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.01143014/DMN
Build-In Floor | Mini Canal | MICL.01143014/DMV | 11 | 430 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.01143014/DMV
Build-In Floor | Mini Canal | MICL.01143014/DNA | 11 | 430 | 14 | 14 | 848 | 848 | 848 | 0.02019 | 330 | 0.0078571 | 966 | 0.023 | 1.362 | A04 | MICL0.01143014/DNA
Build-In Floor | Mini Canal | MICL.01143014/DNC | 11 | 430 | 14 | 14 | 848 | 848 | 848 | 0.02019 | 330 | 0.0078571 | 966 | 0.023 | 1.362 | A04 | MICL0.01143014/DNC
Build-In Floor | Mini Canal | MICL.01143014/DON | 11 | 430 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.01143014/DON
Build-In Floor | Mini Canal | MICL.01143014/DOV | 11 | 430 | 14 | 14 | 813 | 813 | 813 | 0.019357 | 316 | 0.0075238 | 926 | 0.022048 | 1.362 | A04 | MICL0.01143014/DOV
Build-In Floor | Mini Canal | MICL.01143014/RBL | 11 | 430 | 14 | 14 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01143014/RBL
Build-In Floor | Mini Canal | MICL.01143014/RBN | 11 | 430 | 14 | 14 | 848 | 848 | 848 | 0.02019 | 330 | 0.0078571 | 966 | 0.023 | 1.362 | A04 | MICL0.01143014/RBN
Build-In Floor | Mini Canal | MICL.01143014/RBR | 11 | 430 | 14 | 14 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01143014/RBR
Build-In Floor | Mini Canal | MICL.01143014/RBV | 11 | 430 | 14 | 14 | 848 | 848 | 848 | 0.02019 | 330 | 0.0078571 | 966 | 0.023 | 1.362 | A04 | MICL0.01143014/RBV
Build-In Floor | Mini Canal | MICL.01143014/RDB | 11 | 430 | 14 | 14 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01143014/RDB
Build-In Floor | Mini Canal | MICL.01143014/RMN | 11 | 430 | 14 | 14 | 848 | 848 | 848 | 0.02019 | 330 | 0.0078571 | 966 | 0.023 | 1.362 | A04 | MICL0.01143014/RMN
Build-In Floor | Mini Canal | MICL.01143014/RMV | 11 | 430 | 14 | 14 | 848 | 848 | 848 | 0.02019 | 330 | 0.0078571 | 966 | 0.023 | 1.362 | A04 | MICL0.01143014/RMV
Build-In Floor | Mini Canal | MICL.01143014/RNA | 11 | 430 | 14 | 14 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01143014/RNA
Build-In Floor | Mini Canal | MICL.01143014/RON | 11 | 430 | 14 | 14 | 848 | 848 | 848 | 0.02019 | 330 | 0.0078571 | 966 | 0.023 | 1.362 | A04 | MICL0.01143014/RON
Build-In Floor | Mini Canal | MICL.01143014/ROV | 11 | 430 | 14 | 14 | 848 | 848 | 848 | 0.02019 | 330 | 0.0078571 | 966 | 0.023 | 1.362 | A04 | MICL0.01143014/ROV
Build-In Floor | Mini Canal | MICL.01143014/RSS | 11 | 430 | 14 | 14 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.01143014/RSS
Build-In Floor | Mini Canal | MICL.01143014/SBL | 11 | 430 | 14 | 14 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01143014/SBL
Build-In Floor | Mini Canal | MICL.01143014/SBR | 11 | 430 | 14 | 14 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01143014/SBR
Build-In Floor | Mini Canal | MICL.01143014/SDB | 11 | 430 | 14 | 14 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01143014/SDB
Build-In Floor | Mini Canal | MICL.01143014/SNA | 11 | 430 | 14 | 14 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01143014/SNA
Build-In Floor | Mini Canal | MICL.01143014/SNC | 11 | 430 | 14 | 14 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01143014/SNC
Build-In Floor | Mini Canal | MICL.01143018/ANA | 11 | 430 | 18 | 18 | 777 | 777 | 777 | 0.0185 | 302 | 0.0071905 | 885 | 0.021071 | 1.362 | A04 | MICL0.01143018/ANA
Build-In Floor | Mini Canal | MICL.01143018/DBL | 11 | 430 | 18 | 18 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01143018/DBL
Build-In Floor | Mini Canal | MICL.01143018/DBN | 11 | 430 | 18 | 18 | 963 | 963 | 963 | 0.022929 | 375 | 0.0089286 | 1097 | 0.026119 | 1.362 | A04 | MICL0.01143018/DBN
Build-In Floor | Mini Canal | MICL.01143018/DBR | 11 | 430 | 18 | 18 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01143018/DBR
Build-In Floor | Mini Canal | MICL.01143018/DBV | 11 | 430 | 18 | 18 | 963 | 963 | 963 | 0.022929 | 375 | 0.0089286 | 1097 | 0.026119 | 1.362 | A04 | MICL0.01143018/DBV
Build-In Floor | Mini Canal | MICL.01143018/DDB | 11 | 430 | 18 | 18 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01143018/DDB
Build-In Floor | Mini Canal | MICL.01143018/DMN | 11 | 430 | 18 | 18 | 963 | 963 | 963 | 0.022929 | 375 | 0.0089286 | 1097 | 0.026119 | 1.362 | A04 | MICL0.01143018/DMN
Build-In Floor | Mini Canal | MICL.01143018/DMV | 11 | 430 | 18 | 18 | 963 | 963 | 963 | 0.022929 | 375 | 0.0089286 | 1097 | 0.026119 | 1.362 | A04 | MICL0.01143018/DMV
Build-In Floor | Mini Canal | MICL.01143018/DNA | 11 | 430 | 18 | 18 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01143018/DNA
Build-In Floor | Mini Canal | MICL.01143018/DNC | 11 | 430 | 18 | 18 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01143018/DNC
Build-In Floor | Mini Canal | MICL.01143018/DON | 11 | 430 | 18 | 18 | 963 | 963 | 963 | 0.022929 | 375 | 0.0089286 | 1097 | 0.026119 | 1.362 | A04 | MICL0.01143018/DON
Build-In Floor | Mini Canal | MICL.01143018/DOV | 11 | 430 | 18 | 18 | 963 | 963 | 963 | 0.022929 | 375 | 0.0089286 | 1097 | 0.026119 | 1.362 | A04 | MICL0.01143018/DOV
Build-In Floor | Mini Canal | MICL.01143018/RBL | 11 | 430 | 18 | 18 | 1036 | 1036 | 1036 | 0.024667 | 403 | 0.0095952 | 1180 | 0.028095 | 1.362 | A04 | MICL0.01143018/RBL
Build-In Floor | Mini Canal | MICL.01143018/RBN | 11 | 430 | 18 | 18 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01143018/RBN
Build-In Floor | Mini Canal | MICL.01143018/RBR | 11 | 430 | 18 | 18 | 1036 | 1036 | 1036 | 0.024667 | 403 | 0.0095952 | 1180 | 0.028095 | 1.362 | A04 | MICL0.01143018/RBR
Build-In Floor | Mini Canal | MICL.01143018/RBV | 11 | 430 | 18 | 18 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01143018/RBV
Build-In Floor | Mini Canal | MICL.01143018/RDB | 11 | 430 | 18 | 18 | 1036 | 1036 | 1036 | 0.024667 | 403 | 0.0095952 | 1180 | 0.028095 | 1.362 | A04 | MICL0.01143018/RDB
Build-In Floor | Mini Canal | MICL.01143018/RMN | 11 | 430 | 18 | 18 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01143018/RMN
Build-In Floor | Mini Canal | MICL.01143018/RMV | 11 | 430 | 18 | 18 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01143018/RMV
Build-In Floor | Mini Canal | MICL.01143018/RNA | 11 | 430 | 18 | 18 | 1036 | 1036 | 1036 | 0.024667 | 403 | 0.0095952 | 1180 | 0.028095 | 1.362 | A04 | MICL0.01143018/RNA
Build-In Floor | Mini Canal | MICL.01143018/RON | 11 | 430 | 18 | 18 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01143018/RON
Build-In Floor | Mini Canal | MICL.01143018/ROV | 11 | 430 | 18 | 18 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01143018/ROV
Build-In Floor | Mini Canal | MICL.01143018/RSS | 11 | 430 | 18 | 18 | 995 | 995 | 995 | 0.02369 | 387 | 0.0092143 | 1133 | 0.026976 | 1.362 | A04 | MICL0.01143018/RSS
Build-In Floor | Mini Canal | MICL.01143018/SBL | 11 | 430 | 18 | 18 | 1036 | 1036 | 1036 | 0.024667 | 403 | 0.0095952 | 1180 | 0.028095 | 1.362 | A04 | MICL0.01143018/SBL
Build-In Floor | Mini Canal | MICL.01143018/SBR | 11 | 430 | 18 | 18 | 1036 | 1036 | 1036 | 0.024667 | 403 | 0.0095952 | 1180 | 0.028095 | 1.362 | A04 | MICL0.01143018/SBR
Build-In Floor | Mini Canal | MICL.01143018/SDB | 11 | 430 | 18 | 18 | 1036 | 1036 | 1036 | 0.024667 | 403 | 0.0095952 | 1180 | 0.028095 | 1.362 | A04 | MICL0.01143018/SDB
Build-In Floor | Mini Canal | MICL.01143018/SNA | 11 | 430 | 18 | 18 | 1036 | 1036 | 1036 | 0.024667 | 403 | 0.0095952 | 1180 | 0.028095 | 1.362 | A04 | MICL0.01143018/SNA
Build-In Floor | Mini Canal | MICL.01143018/SNC | 11 | 430 | 18 | 18 | 1036 | 1036 | 1036 | 0.024667 | 403 | 0.0095952 | 1180 | 0.028095 | 1.362 | A04 | MICL0.01143018/SNC
Build-In Floor | Mini Canal | MICL.01143026/ANA | 11 | 430 | 26 | 26 | 1049 | 1049 | 1049 | 0.024976 | 408 | 0.0097143 | 1195 | 0.028452 | 1.362 | A04 | MICL0.01143026/ANA
Build-In Floor | Mini Canal | MICL.01143026/DBL | 11 | 430 | 26 | 26 | 1356 | 1356 | 1356 | 0.032286 | 527 | 0.012548 | 1544 | 0.036762 | 1.362 | A04 | MICL0.01143026/DBL
Build-In Floor | Mini Canal | MICL.01143026/DBN | 11 | 430 | 26 | 26 | 1300 | 1300 | 1300 | 0.030952 | 506 | 0.012048 | 1481 | 0.035262 | 1.362 | A04 | MICL0.01143026/DBN
Build-In Floor | Mini Canal | MICL.01143026/DBR | 11 | 430 | 26 | 26 | 1356 | 1356 | 1356 | 0.032286 | 527 | 0.012548 | 1544 | 0.036762 | 1.362 | A04 | MICL0.01143026/DBR
Build-In Floor | Mini Canal | MICL.01143026/DBV | 11 | 430 | 26 | 26 | 1300 | 1300 | 1300 | 0.030952 | 506 | 0.012048 | 1481 | 0.035262 | 1.362 | A04 | MICL0.01143026/DBV
Build-In Floor | Mini Canal | MICL.01143026/DDB | 11 | 430 | 26 | 26 | 1356 | 1356 | 1356 | 0.032286 | 527 | 0.012548 | 1544 | 0.036762 | 1.362 | A04 | MICL0.01143026/DDB
Build-In Floor | Mini Canal | MICL.01143026/DMN | 11 | 430 | 26 | 26 | 1300 | 1300 | 1300 | 0.030952 | 506 | 0.012048 | 1481 | 0.035262 | 1.362 | A04 | MICL0.01143026/DMN
Build-In Floor | Mini Canal | MICL.01143026/DMV | 11 | 430 | 26 | 26 | 1300 | 1300 | 1300 | 0.030952 | 506 | 0.012048 | 1481 | 0.035262 | 1.362 | A04 | MICL0.01143026/DMV
Build-In Floor | Mini Canal | MICL.01143026/DNA | 11 | 430 | 26 | 26 | 1356 | 1356 | 1356 | 0.032286 | 527 | 0.012548 | 1544 | 0.036762 | 1.362 | A04 | MICL0.01143026/DNA
Build-In Floor | Mini Canal | MICL.01143026/DNC | 11 | 430 | 26 | 26 | 1356 | 1356 | 1356 | 0.032286 | 527 | 0.012548 | 1544 | 0.036762 | 1.362 | A04 | MICL0.01143026/DNC
Build-In Floor | Mini Canal | MICL.01143026/DON | 11 | 430 | 26 | 26 | 1300 | 1300 | 1300 | 0.030952 | 506 | 0.012048 | 1481 | 0.035262 | 1.362 | A04 | MICL0.01143026/DON
Build-In Floor | Mini Canal | MICL.01143026/DOV | 11 | 430 | 26 | 26 | 1300 | 1300 | 1300 | 0.030952 | 506 | 0.012048 | 1481 | 0.035262 | 1.362 | A04 | MICL0.01143026/DOV
Build-In Floor | Mini Canal | MICL.01143026/PNC | 11 | 430 | 26 | 26 | 1188 | 1188 | 1188 | 0.028286 | 462 | 0.011 | 1353 | 0.032214 | 1.362 | A04 | MICL0.01143026/PNC
Build-In Floor | Mini Canal | MICL.01143026/RBL | 11 | 430 | 26 | 26 | 1398 | 1398 | 1398 | 0.033286 | 544 | 0.012952 | 1592 | 0.037905 | 1.362 | A04 | MICL0.01143026/RBL
Build-In Floor | Mini Canal | MICL.01143026/RBN | 11 | 430 | 26 | 26 | 1356 | 1356 | 1356 | 0.032286 | 527 | 0.012548 | 1544 | 0.036762 | 1.362 | A04 | MICL0.01143026/RBN
Build-In Floor | Mini Canal | MICL.01143026/RBR | 11 | 430 | 26 | 26 | 1398 | 1398 | 1398 | 0.033286 | 544 | 0.012952 | 1592 | 0.037905 | 1.362 | A04 | MICL0.01143026/RBR
Build-In Floor | Mini Canal | MICL.01143026/RBV | 11 | 430 | 26 | 26 | 1356 | 1356 | 1356 | 0.032286 | 527 | 0.012548 | 1544 | 0.036762 | 1.362 | A04 | MICL0.01143026/RBV
Build-In Floor | Mini Canal | MICL.01143026/RDB | 11 | 430 | 26 | 26 | 1398 | 1398 | 1398 | 0.033286 | 544 | 0.012952 | 1592 | 0.037905 | 1.362 | A04 | MICL0.01143026/RDB
Build-In Floor | Mini Canal | MICL.01143026/RMN | 11 | 430 | 26 | 26 | 1356 | 1356 | 1356 | 0.032286 | 527 | 0.012548 | 1544 | 0.036762 | 1.362 | A04 | MICL0.01143026/RMN
Build-In Floor | Mini Canal | MICL.01143026/RMV | 11 | 430 | 26 | 26 | 1356 | 1356 | 1356 | 0.032286 | 527 | 0.012548 | 1544 | 0.036762 | 1.362 | A04 | MICL0.01143026/RMV
Build-In Floor | Mini Canal | MICL.01143026/RNA | 11 | 430 | 26 | 26 | 1398 | 1398 | 1398 | 0.033286 | 544 | 0.012952 | 1592 | 0.037905 | 1.362 | A04 | MICL0.01143026/RNA
Build-In Floor | Mini Canal | MICL.01143026/RON | 11 | 430 | 26 | 26 | 1356 | 1356 | 1356 | 0.032286 | 527 | 0.012548 | 1544 | 0.036762 | 1.362 | A04 | MICL0.01143026/RON
Build-In Floor | Mini Canal | MICL.01143026/ROV | 11 | 430 | 26 | 26 | 1356 | 1356 | 1356 | 0.032286 | 527 | 0.012548 | 1544 | 0.036762 | 1.362 | A04 | MICL0.01143026/ROV
Build-In Floor | Mini Canal | MICL.01143026/RSS | 11 | 430 | 26 | 26 | 1342 | 1342 | 1342 | 0.031952 | 522 | 0.012429 | 1529 | 0.036405 | 1.362 | A04 | MICL0.01143026/RSS
Build-In Floor | Mini Canal | MICL.01143026/SBL | 11 | 430 | 26 | 26 | 1398 | 1398 | 1398 | 0.033286 | 544 | 0.012952 | 1592 | 0.037905 | 1.362 | A04 | MICL0.01143026/SBL
Build-In Floor | Mini Canal | MICL.01143026/SBR | 11 | 430 | 26 | 26 | 1398 | 1398 | 1398 | 0.033286 | 544 | 0.012952 | 1592 | 0.037905 | 1.362 | A04 | MICL0.01143026/SBR
Build-In Floor | Mini Canal | MICL.01143026/SDB | 11 | 430 | 26 | 26 | 1398 | 1398 | 1398 | 0.033286 | 544 | 0.012952 | 1592 | 0.037905 | 1.362 | A04 | MICL0.01143026/SDB
Build-In Floor | Mini Canal | MICL.01143026/SNA | 11 | 430 | 26 | 26 | 1398 | 1398 | 1398 | 0.033286 | 544 | 0.012952 | 1592 | 0.037905 | 1.362 | A04 | MICL0.01143026/SNA
Build-In Floor | Mini Canal | MICL.01143026/SNC | 11 | 430 | 26 | 26 | 1398 | 1398 | 1398 | 0.033286 | 544 | 0.012952 | 1592 | 0.037905 | 1.362 | A04 | MICL0.01143026/SNC
Build-In Floor | Mini Canal | MICL.01143034/ANA | 11 | 430 | 34 | 34 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01143034/ANA
Build-In Floor | Mini Canal | MICL.01143034/DBL | 11 | 430 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01143034/DBL
Build-In Floor | Mini Canal | MICL.01143034/DBN | 11 | 430 | 34 | 34 | 1689 | 1689 | 1689 | 0.040214 | 657 | 0.015643 | 1924 | 0.04581 | 1.362 | A04 | MICL0.01143034/DBN
Build-In Floor | Mini Canal | MICL.01143034/DBR | 11 | 430 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01143034/DBR
Build-In Floor | Mini Canal | MICL.01143034/DBV | 11 | 430 | 34 | 34 | 1689 | 1689 | 1689 | 0.040214 | 657 | 0.015643 | 1924 | 0.04581 | 1.362 | A04 | MICL0.01143034/DBV
Build-In Floor | Mini Canal | MICL.01143034/DDB | 11 | 430 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01143034/DDB
Build-In Floor | Mini Canal | MICL.01143034/DMN | 11 | 430 | 34 | 34 | 1689 | 1689 | 1689 | 0.040214 | 657 | 0.015643 | 1924 | 0.04581 | 1.362 | A04 | MICL0.01143034/DMN
Build-In Floor | Mini Canal | MICL.01143034/DMV | 11 | 430 | 34 | 34 | 1689 | 1689 | 1689 | 0.040214 | 657 | 0.015643 | 1924 | 0.04581 | 1.362 | A04 | MICL0.01143034/DMV
Build-In Floor | Mini Canal | MICL.01143034/DNA | 11 | 430 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01143034/DNA
Build-In Floor | Mini Canal | MICL.01143034/DNC | 11 | 430 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01143034/DNC
Build-In Floor | Mini Canal | MICL.01143034/DON | 11 | 430 | 34 | 34 | 1689 | 1689 | 1689 | 0.040214 | 657 | 0.015643 | 1924 | 0.04581 | 1.362 | A04 | MICL0.01143034/DON
Build-In Floor | Mini Canal | MICL.01143034/DOV | 11 | 430 | 34 | 34 | 1689 | 1689 | 1689 | 0.040214 | 657 | 0.015643 | 1924 | 0.04581 | 1.362 | A04 | MICL0.01143034/DOV
Build-In Floor | Mini Canal | MICL.01143034/PNC | 11 | 430 | 34 | 34 | 1544 | 1544 | 1544 | 0.036762 | 601 | 0.01431 | 1759 | 0.041881 | 1.362 | A04 | MICL0.01143034/PNC
Build-In Floor | Mini Canal | MICL.01143034/RBL | 11 | 430 | 34 | 34 | 1816 | 1816 | 1816 | 0.043238 | 706 | 0.01681 | 2068 | 0.049238 | 1.362 | A04 | MICL0.01143034/RBL
Build-In Floor | Mini Canal | MICL.01143034/RBN | 11 | 430 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01143034/RBN
Build-In Floor | Mini Canal | MICL.01143034/RBR | 11 | 430 | 34 | 34 | 1816 | 1816 | 1816 | 0.043238 | 706 | 0.01681 | 2068 | 0.049238 | 1.362 | A04 | MICL0.01143034/RBR
Build-In Floor | Mini Canal | MICL.01143034/RBV | 11 | 430 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01143034/RBV
Build-In Floor | Mini Canal | MICL.01143034/RDB | 11 | 430 | 34 | 34 | 1816 | 1816 | 1816 | 0.043238 | 706 | 0.01681 | 2068 | 0.049238 | 1.362 | A04 | MICL0.01143034/RDB
Build-In Floor | Mini Canal | MICL.01143034/RMN | 11 | 430 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01143034/RMN
Build-In Floor | Mini Canal | MICL.01143034/RMV | 11 | 430 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01143034/RMV
Build-In Floor | Mini Canal | MICL.01143034/RNA | 11 | 430 | 34 | 34 | 1816 | 1816 | 1816 | 0.043238 | 706 | 0.01681 | 2068 | 0.049238 | 1.362 | A04 | MICL0.01143034/RNA
Build-In Floor | Mini Canal | MICL.01143034/RON | 11 | 430 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01143034/RON
Build-In Floor | Mini Canal | MICL.01143034/ROV | 11 | 430 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01143034/ROV
Build-In Floor | Mini Canal | MICL.01143034/RSS | 11 | 430 | 34 | 34 | 1743 | 1743 | 1743 | 0.0415 | 678 | 0.016143 | 1985 | 0.047262 | 1.362 | A04 | MICL0.01143034/RSS
Build-In Floor | Mini Canal | MICL.01143034/SBL | 11 | 430 | 34 | 34 | 1816 | 1816 | 1816 | 0.043238 | 706 | 0.01681 | 2068 | 0.049238 | 1.362 | A04 | MICL0.01143034/SBL
Build-In Floor | Mini Canal | MICL.01143034/SBR | 11 | 430 | 34 | 34 | 1816 | 1816 | 1816 | 0.043238 | 706 | 0.01681 | 2068 | 0.049238 | 1.362 | A04 | MICL0.01143034/SBR
Build-In Floor | Mini Canal | MICL.01143034/SDB | 11 | 430 | 34 | 34 | 1816 | 1816 | 1816 | 0.043238 | 706 | 0.01681 | 2068 | 0.049238 | 1.362 | A04 | MICL0.01143034/SDB
Build-In Floor | Mini Canal | MICL.01143034/SNA | 11 | 430 | 34 | 34 | 1816 | 1816 | 1816 | 0.043238 | 706 | 0.01681 | 2068 | 0.049238 | 1.362 | A04 | MICL0.01143034/SNA
Build-In Floor | Mini Canal | MICL.01143034/SNC | 11 | 430 | 34 | 34 | 1816 | 1816 | 1816 | 0.043238 | 706 | 0.01681 | 2068 | 0.049238 | 1.362 | A04 | MICL0.01143034/SNC
Build-In Floor | Mini Canal | MICL.01143042/ANA | 11 | 430 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01143042/ANA
Build-In Floor | Mini Canal | MICL.01143042/DBL | 11 | 430 | 42 | 42 | 2475 | 2475 | 2475 | 0.058929 | 963 | 0.022929 | 2819 | 0.067119 | 1.362 | A04 | MICL0.01143042/DBL
Build-In Floor | Mini Canal | MICL.01143042/DBN | 11 | 430 | 42 | 42 | 2373 | 2373 | 2373 | 0.0565 | 923 | 0.021976 | 2703 | 0.064357 | 1.362 | A04 | MICL0.01143042/DBN
Build-In Floor | Mini Canal | MICL.01143042/DBR | 11 | 430 | 42 | 42 | 2475 | 2475 | 2475 | 0.058929 | 963 | 0.022929 | 2819 | 0.067119 | 1.362 | A04 | MICL0.01143042/DBR
Build-In Floor | Mini Canal | MICL.01143042/DBV | 11 | 430 | 42 | 42 | 2373 | 2373 | 2373 | 0.0565 | 923 | 0.021976 | 2703 | 0.064357 | 1.362 | A04 | MICL0.01143042/DBV
Build-In Floor | Mini Canal | MICL.01143042/DDB | 11 | 430 | 42 | 42 | 2475 | 2475 | 2475 | 0.058929 | 963 | 0.022929 | 2819 | 0.067119 | 1.362 | A04 | MICL0.01143042/DDB
Build-In Floor | Mini Canal | MICL.01143042/DMN | 11 | 430 | 42 | 42 | 2373 | 2373 | 2373 | 0.0565 | 923 | 0.021976 | 2703 | 0.064357 | 1.362 | A04 | MICL0.01143042/DMN
Build-In Floor | Mini Canal | MICL.01143042/DMV | 11 | 430 | 42 | 42 | 2373 | 2373 | 2373 | 0.0565 | 923 | 0.021976 | 2703 | 0.064357 | 1.362 | A04 | MICL0.01143042/DMV
Build-In Floor | Mini Canal | MICL.01143042/DNA | 11 | 430 | 42 | 42 | 2475 | 2475 | 2475 | 0.058929 | 963 | 0.022929 | 2819 | 0.067119 | 1.362 | A04 | MICL0.01143042/DNA
Build-In Floor | Mini Canal | MICL.01143042/DNC | 11 | 430 | 42 | 42 | 2475 | 2475 | 2475 | 0.058929 | 963 | 0.022929 | 2819 | 0.067119 | 1.362 | A04 | MICL0.01143042/DNC
Build-In Floor | Mini Canal | MICL.01143042/DON | 11 | 430 | 42 | 42 | 2373 | 2373 | 2373 | 0.0565 | 923 | 0.021976 | 2703 | 0.064357 | 1.362 | A04 | MICL0.01143042/DON
Build-In Floor | Mini Canal | MICL.01143042/DOV | 11 | 430 | 42 | 42 | 2373 | 2373 | 2373 | 0.0565 | 923 | 0.021976 | 2703 | 0.064357 | 1.362 | A04 | MICL0.01143042/DOV
Build-In Floor | Mini Canal | MICL.01143042/PNC | 11 | 430 | 42 | 42 | 2169 | 2169 | 2169 | 0.051643 | 844 | 0.020095 | 2470 | 0.05881 | 1.362 | A04 | MICL0.01143042/PNC
Build-In Floor | Mini Canal | MICL.01143042/RBL | 11 | 430 | 42 | 42 | 2552 | 2552 | 2552 | 0.060762 | 993 | 0.023643 | 2907 | 0.069214 | 1.362 | A04 | MICL0.01143042/RBL
Build-In Floor | Mini Canal | MICL.01143042/RBN | 11 | 430 | 42 | 42 | 2475 | 2475 | 2475 | 0.058929 | 963 | 0.022929 | 2819 | 0.067119 | 1.362 | A04 | MICL0.01143042/RBN
Build-In Floor | Mini Canal | MICL.01143042/RBR | 11 | 430 | 42 | 42 | 2552 | 2552 | 2552 | 0.060762 | 993 | 0.023643 | 2907 | 0.069214 | 1.362 | A04 | MICL0.01143042/RBR
Build-In Floor | Mini Canal | MICL.01143042/RBV | 11 | 430 | 42 | 42 | 2475 | 2475 | 2475 | 0.058929 | 963 | 0.022929 | 2819 | 0.067119 | 1.362 | A04 | MICL0.01143042/RBV
Build-In Floor | Mini Canal | MICL.01143042/RDB | 11 | 430 | 42 | 42 | 2552 | 2552 | 2552 | 0.060762 | 993 | 0.023643 | 2907 | 0.069214 | 1.362 | A04 | MICL0.01143042/RDB
Build-In Floor | Mini Canal | MICL.01143042/RMN | 11 | 430 | 42 | 42 | 2475 | 2475 | 2475 | 0.058929 | 963 | 0.022929 | 2819 | 0.067119 | 1.362 | A04 | MICL0.01143042/RMN
Build-In Floor | Mini Canal | MICL.01143042/RMV | 11 | 430 | 42 | 42 | 2475 | 2475 | 2475 | 0.058929 | 963 | 0.022929 | 2819 | 0.067119 | 1.362 | A04 | MICL0.01143042/RMV
Build-In Floor | Mini Canal | MICL.01143042/RNA | 11 | 430 | 42 | 42 | 2552 | 2552 | 2552 | 0.060762 | 993 | 0.023643 | 2907 | 0.069214 | 1.362 | A04 | MICL0.01143042/RNA
Build-In Floor | Mini Canal | MICL.01143042/RON | 11 | 430 | 42 | 42 | 2475 | 2475 | 2475 | 0.058929 | 963 | 0.022929 | 2819 | 0.067119 | 1.362 | A04 | MICL0.01143042/RON
Build-In Floor | Mini Canal | MICL.01143042/ROV | 11 | 430 | 42 | 42 | 2475 | 2475 | 2475 | 0.058929 | 963 | 0.022929 | 2819 | 0.067119 | 1.362 | A04 | MICL0.01143042/ROV
Build-In Floor | Mini Canal | MICL.01143042/RSS | 11 | 430 | 42 | 42 | 2450 | 2450 | 2450 | 0.058333 | 953 | 0.02269 | 2791 | 0.066452 | 1.362 | A04 | MICL0.01143042/RSS
Build-In Floor | Mini Canal | MICL.01143042/SBL | 11 | 430 | 42 | 42 | 2552 | 2552 | 2552 | 0.060762 | 993 | 0.023643 | 2907 | 0.069214 | 1.362 | A04 | MICL0.01143042/SBL
Build-In Floor | Mini Canal | MICL.01143042/SBR | 11 | 430 | 42 | 42 | 2552 | 2552 | 2552 | 0.060762 | 993 | 0.023643 | 2907 | 0.069214 | 1.362 | A04 | MICL0.01143042/SBR
Build-In Floor | Mini Canal | MICL.01143042/SDB | 11 | 430 | 42 | 42 | 2552 | 2552 | 2552 | 0.060762 | 993 | 0.023643 | 2907 | 0.069214 | 1.362 | A04 | MICL0.01143042/SDB
Build-In Floor | Mini Canal | MICL.01143042/SNA | 11 | 430 | 42 | 42 | 2552 | 2552 | 2552 | 0.060762 | 993 | 0.023643 | 2907 | 0.069214 | 1.362 | A04 | MICL0.01143042/SNA
Build-In Floor | Mini Canal | MICL.01143042/SNC | 11 | 430 | 42 | 42 | 2552 | 2552 | 2552 | 0.060762 | 993 | 0.023643 | 2907 | 0.069214 | 1.362 | A04 | MICL0.01143042/SNC
Build-In Floor | Mini Canal | MICL.01145014/ANA | 11 | 450 | 14 | 14 | 688 | 688 | 688 | 0.016381 | 268 | 0.006381 | 784 | 0.018667 | 1.362 | A04 | MICL0.01145014/ANA
Build-In Floor | Mini Canal | MICL.01145014/DBL | 11 | 450 | 14 | 14 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.01145014/DBL
Build-In Floor | Mini Canal | MICL.01145014/DBN | 11 | 450 | 14 | 14 | 853 | 853 | 853 | 0.02031 | 332 | 0.0079048 | 972 | 0.023143 | 1.362 | A04 | MICL0.01145014/DBN
Build-In Floor | Mini Canal | MICL.01145014/DBR | 11 | 450 | 14 | 14 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.01145014/DBR
Build-In Floor | Mini Canal | MICL.01145014/DBV | 11 | 450 | 14 | 14 | 853 | 853 | 853 | 0.02031 | 332 | 0.0079048 | 972 | 0.023143 | 1.362 | A04 | MICL0.01145014/DBV
Build-In Floor | Mini Canal | MICL.01145014/DDB | 11 | 450 | 14 | 14 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.01145014/DDB
Build-In Floor | Mini Canal | MICL.01145014/DMN | 11 | 450 | 14 | 14 | 853 | 853 | 853 | 0.02031 | 332 | 0.0079048 | 972 | 0.023143 | 1.362 | A04 | MICL0.01145014/DMN
Build-In Floor | Mini Canal | MICL.01145014/DMV | 11 | 450 | 14 | 14 | 853 | 853 | 853 | 0.02031 | 332 | 0.0079048 | 972 | 0.023143 | 1.362 | A04 | MICL0.01145014/DMV
Build-In Floor | Mini Canal | MICL.01145014/DNA | 11 | 450 | 14 | 14 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.01145014/DNA
Build-In Floor | Mini Canal | MICL.01145014/DNC | 11 | 450 | 14 | 14 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.01145014/DNC
Build-In Floor | Mini Canal | MICL.01145014/DON | 11 | 450 | 14 | 14 | 853 | 853 | 853 | 0.02031 | 332 | 0.0079048 | 972 | 0.023143 | 1.362 | A04 | MICL0.01145014/DON
Build-In Floor | Mini Canal | MICL.01145014/DOV | 11 | 450 | 14 | 14 | 853 | 853 | 853 | 0.02031 | 332 | 0.0079048 | 972 | 0.023143 | 1.362 | A04 | MICL0.01145014/DOV
Build-In Floor | Mini Canal | MICL.01145014/RBL | 11 | 450 | 14 | 14 | 917 | 917 | 917 | 0.021833 | 357 | 0.0085 | 1044 | 0.024857 | 1.362 | A04 | MICL0.01145014/RBL
Build-In Floor | Mini Canal | MICL.01145014/RBN | 11 | 450 | 14 | 14 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.01145014/RBN
Build-In Floor | Mini Canal | MICL.01145014/RBR | 11 | 450 | 14 | 14 | 917 | 917 | 917 | 0.021833 | 357 | 0.0085 | 1044 | 0.024857 | 1.362 | A04 | MICL0.01145014/RBR
Build-In Floor | Mini Canal | MICL.01145014/RBV | 11 | 450 | 14 | 14 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.01145014/RBV
Build-In Floor | Mini Canal | MICL.01145014/RDB | 11 | 450 | 14 | 14 | 917 | 917 | 917 | 0.021833 | 357 | 0.0085 | 1044 | 0.024857 | 1.362 | A04 | MICL0.01145014/RDB
Build-In Floor | Mini Canal | MICL.01145014/RMN | 11 | 450 | 14 | 14 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.01145014/RMN
Build-In Floor | Mini Canal | MICL.01145014/RMV | 11 | 450 | 14 | 14 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.01145014/RMV
Build-In Floor | Mini Canal | MICL.01145014/RNA | 11 | 450 | 14 | 14 | 917 | 917 | 917 | 0.021833 | 357 | 0.0085 | 1044 | 0.024857 | 1.362 | A04 | MICL0.01145014/RNA
Build-In Floor | Mini Canal | MICL.01145014/RON | 11 | 450 | 14 | 14 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.01145014/RON
Build-In Floor | Mini Canal | MICL.01145014/ROV | 11 | 450 | 14 | 14 | 889 | 889 | 889 | 0.021167 | 346 | 0.0082381 | 1013 | 0.024119 | 1.362 | A04 | MICL0.01145014/ROV
Build-In Floor | Mini Canal | MICL.01145014/RSS | 11 | 450 | 14 | 14 | 880 | 880 | 880 | 0.020952 | 342 | 0.0081429 | 1002 | 0.023857 | 1.362 | A04 | MICL0.01145014/RSS
Build-In Floor | Mini Canal | MICL.01145014/SBL | 11 | 450 | 14 | 14 | 917 | 917 | 917 | 0.021833 | 357 | 0.0085 | 1044 | 0.024857 | 1.362 | A04 | MICL0.01145014/SBL
Build-In Floor | Mini Canal | MICL.01145014/SBR | 11 | 450 | 14 | 14 | 917 | 917 | 917 | 0.021833 | 357 | 0.0085 | 1044 | 0.024857 | 1.362 | A04 | MICL0.01145014/SBR
Build-In Floor | Mini Canal | MICL.01145014/SDB | 11 | 450 | 14 | 14 | 917 | 917 | 917 | 0.021833 | 357 | 0.0085 | 1044 | 0.024857 | 1.362 | A04 | MICL0.01145014/SDB
Build-In Floor | Mini Canal | MICL.01145014/SNA | 11 | 450 | 14 | 14 | 917 | 917 | 917 | 0.021833 | 357 | 0.0085 | 1044 | 0.024857 | 1.362 | A04 | MICL0.01145014/SNA
Build-In Floor | Mini Canal | MICL.01145014/SNC | 11 | 450 | 14 | 14 | 917 | 917 | 917 | 0.021833 | 357 | 0.0085 | 1044 | 0.024857 | 1.362 | A04 | MICL0.01145014/SNC
Build-In Floor | Mini Canal | MICL.01145018/ANA | 11 | 450 | 18 | 18 | 815 | 815 | 815 | 0.019405 | 317 | 0.0075476 | 928 | 0.022095 | 1.362 | A04 | MICL0.01145018/ANA
Build-In Floor | Mini Canal | MICL.01145018/DBL | 11 | 450 | 18 | 18 | 1054 | 1054 | 1054 | 0.025095 | 410 | 0.0097619 | 1201 | 0.028595 | 1.362 | A04 | MICL0.01145018/DBL
Build-In Floor | Mini Canal | MICL.01145018/DBN | 11 | 450 | 18 | 18 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01145018/DBN
Build-In Floor | Mini Canal | MICL.01145018/DBR | 11 | 450 | 18 | 18 | 1054 | 1054 | 1054 | 0.025095 | 410 | 0.0097619 | 1201 | 0.028595 | 1.362 | A04 | MICL0.01145018/DBR
Build-In Floor | Mini Canal | MICL.01145018/DBV | 11 | 450 | 18 | 18 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01145018/DBV
Build-In Floor | Mini Canal | MICL.01145018/DDB | 11 | 450 | 18 | 18 | 1054 | 1054 | 1054 | 0.025095 | 410 | 0.0097619 | 1201 | 0.028595 | 1.362 | A04 | MICL0.01145018/DDB
Build-In Floor | Mini Canal | MICL.01145018/DMN | 11 | 450 | 18 | 18 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01145018/DMN
Build-In Floor | Mini Canal | MICL.01145018/DMV | 11 | 450 | 18 | 18 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01145018/DMV
Build-In Floor | Mini Canal | MICL.01145018/DNA | 11 | 450 | 18 | 18 | 1054 | 1054 | 1054 | 0.025095 | 410 | 0.0097619 | 1201 | 0.028595 | 1.362 | A04 | MICL0.01145018/DNA
Build-In Floor | Mini Canal | MICL.01145018/DNC | 11 | 450 | 18 | 18 | 1054 | 1054 | 1054 | 0.025095 | 410 | 0.0097619 | 1201 | 0.028595 | 1.362 | A04 | MICL0.01145018/DNC
Build-In Floor | Mini Canal | MICL.01145018/DON | 11 | 450 | 18 | 18 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01145018/DON
Build-In Floor | Mini Canal | MICL.01145018/DOV | 11 | 450 | 18 | 18 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01145018/DOV
Build-In Floor | Mini Canal | MICL.01145018/RBL | 11 | 450 | 18 | 18 | 1087 | 1087 | 1087 | 0.025881 | 423 | 0.010071 | 1238 | 0.029476 | 1.362 | A04 | MICL0.01145018/RBL
Build-In Floor | Mini Canal | MICL.01145018/RBN | 11 | 450 | 18 | 18 | 1054 | 1054 | 1054 | 0.025095 | 410 | 0.0097619 | 1201 | 0.028595 | 1.362 | A04 | MICL0.01145018/RBN
Build-In Floor | Mini Canal | MICL.01145018/RBR | 11 | 450 | 18 | 18 | 1087 | 1087 | 1087 | 0.025881 | 423 | 0.010071 | 1238 | 0.029476 | 1.362 | A04 | MICL0.01145018/RBR
Build-In Floor | Mini Canal | MICL.01145018/RBV | 11 | 450 | 18 | 18 | 1054 | 1054 | 1054 | 0.025095 | 410 | 0.0097619 | 1201 | 0.028595 | 1.362 | A04 | MICL0.01145018/RBV
Build-In Floor | Mini Canal | MICL.01145018/RDB | 11 | 450 | 18 | 18 | 1087 | 1087 | 1087 | 0.025881 | 423 | 0.010071 | 1238 | 0.029476 | 1.362 | A04 | MICL0.01145018/RDB
Build-In Floor | Mini Canal | MICL.01145018/RMN | 11 | 450 | 18 | 18 | 1054 | 1054 | 1054 | 0.025095 | 410 | 0.0097619 | 1201 | 0.028595 | 1.362 | A04 | MICL0.01145018/RMN
Build-In Floor | Mini Canal | MICL.01145018/RMV | 11 | 450 | 18 | 18 | 1054 | 1054 | 1054 | 0.025095 | 410 | 0.0097619 | 1201 | 0.028595 | 1.362 | A04 | MICL0.01145018/RMV
Build-In Floor | Mini Canal | MICL.01145018/RNA | 11 | 450 | 18 | 18 | 1087 | 1087 | 1087 | 0.025881 | 423 | 0.010071 | 1238 | 0.029476 | 1.362 | A04 | MICL0.01145018/RNA
Build-In Floor | Mini Canal | MICL.01145018/RON | 11 | 450 | 18 | 18 | 1054 | 1054 | 1054 | 0.025095 | 410 | 0.0097619 | 1201 | 0.028595 | 1.362 | A04 | MICL0.01145018/RON
Build-In Floor | Mini Canal | MICL.01145018/ROV | 11 | 450 | 18 | 18 | 1054 | 1054 | 1054 | 0.025095 | 410 | 0.0097619 | 1201 | 0.028595 | 1.362 | A04 | MICL0.01145018/ROV
Build-In Floor | Mini Canal | MICL.01145018/RSS | 11 | 450 | 18 | 18 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.01145018/RSS
Build-In Floor | Mini Canal | MICL.01145018/SBL | 11 | 450 | 18 | 18 | 1087 | 1087 | 1087 | 0.025881 | 423 | 0.010071 | 1238 | 0.029476 | 1.362 | A04 | MICL0.01145018/SBL
Build-In Floor | Mini Canal | MICL.01145018/SBR | 11 | 450 | 18 | 18 | 1087 | 1087 | 1087 | 0.025881 | 423 | 0.010071 | 1238 | 0.029476 | 1.362 | A04 | MICL0.01145018/SBR
Build-In Floor | Mini Canal | MICL.01145018/SDB | 11 | 450 | 18 | 18 | 1087 | 1087 | 1087 | 0.025881 | 423 | 0.010071 | 1238 | 0.029476 | 1.362 | A04 | MICL0.01145018/SDB
Build-In Floor | Mini Canal | MICL.01145018/SNA | 11 | 450 | 18 | 18 | 1087 | 1087 | 1087 | 0.025881 | 423 | 0.010071 | 1238 | 0.029476 | 1.362 | A04 | MICL0.01145018/SNA
Build-In Floor | Mini Canal | MICL.01145018/SNC | 11 | 450 | 18 | 18 | 1087 | 1087 | 1087 | 0.025881 | 423 | 0.010071 | 1238 | 0.029476 | 1.362 | A04 | MICL0.01145018/SNC
Build-In Floor | Mini Canal | MICL.01145026/ANA | 11 | 450 | 26 | 26 | 1101 | 1101 | 1101 | 0.026214 | 428 | 0.01019 | 1254 | 0.029857 | 1.362 | A04 | MICL0.01145026/ANA
Build-In Floor | Mini Canal | MICL.01145026/DBL | 11 | 450 | 26 | 26 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01145026/DBL
Build-In Floor | Mini Canal | MICL.01145026/DBN | 11 | 450 | 26 | 26 | 1365 | 1365 | 1365 | 0.0325 | 531 | 0.012643 | 1555 | 0.037024 | 1.362 | A04 | MICL0.01145026/DBN
Build-In Floor | Mini Canal | MICL.01145026/DBR | 11 | 450 | 26 | 26 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01145026/DBR
Build-In Floor | Mini Canal | MICL.01145026/DBV | 11 | 450 | 26 | 26 | 1365 | 1365 | 1365 | 0.0325 | 531 | 0.012643 | 1555 | 0.037024 | 1.362 | A04 | MICL0.01145026/DBV
Build-In Floor | Mini Canal | MICL.01145026/DDB | 11 | 450 | 26 | 26 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01145026/DDB
Build-In Floor | Mini Canal | MICL.01145026/DMN | 11 | 450 | 26 | 26 | 1365 | 1365 | 1365 | 0.0325 | 531 | 0.012643 | 1555 | 0.037024 | 1.362 | A04 | MICL0.01145026/DMN
Build-In Floor | Mini Canal | MICL.01145026/DMV | 11 | 450 | 26 | 26 | 1365 | 1365 | 1365 | 0.0325 | 531 | 0.012643 | 1555 | 0.037024 | 1.362 | A04 | MICL0.01145026/DMV
Build-In Floor | Mini Canal | MICL.01145026/DNA | 11 | 450 | 26 | 26 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01145026/DNA
Build-In Floor | Mini Canal | MICL.01145026/DNC | 11 | 450 | 26 | 26 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01145026/DNC
Build-In Floor | Mini Canal | MICL.01145026/DON | 11 | 450 | 26 | 26 | 1365 | 1365 | 1365 | 0.0325 | 531 | 0.012643 | 1555 | 0.037024 | 1.362 | A04 | MICL0.01145026/DON
Build-In Floor | Mini Canal | MICL.01145026/DOV | 11 | 450 | 26 | 26 | 1365 | 1365 | 1365 | 0.0325 | 531 | 0.012643 | 1555 | 0.037024 | 1.362 | A04 | MICL0.01145026/DOV
Build-In Floor | Mini Canal | MICL.01145026/PNC | 11 | 450 | 26 | 26 | 1248 | 1248 | 1248 | 0.029714 | 485 | 0.011548 | 1421 | 0.033833 | 1.362 | A04 | MICL0.01145026/PNC
Build-In Floor | Mini Canal | MICL.01145026/RBL | 11 | 450 | 26 | 26 | 1468 | 1468 | 1468 | 0.034952 | 571 | 0.013595 | 1672 | 0.03981 | 1.362 | A04 | MICL0.01145026/RBL
Build-In Floor | Mini Canal | MICL.01145026/RBN | 11 | 450 | 26 | 26 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01145026/RBN
Build-In Floor | Mini Canal | MICL.01145026/RBR | 11 | 450 | 26 | 26 | 1468 | 1468 | 1468 | 0.034952 | 571 | 0.013595 | 1672 | 0.03981 | 1.362 | A04 | MICL0.01145026/RBR
Build-In Floor | Mini Canal | MICL.01145026/RBV | 11 | 450 | 26 | 26 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01145026/RBV
Build-In Floor | Mini Canal | MICL.01145026/RDB | 11 | 450 | 26 | 26 | 1468 | 1468 | 1468 | 0.034952 | 571 | 0.013595 | 1672 | 0.03981 | 1.362 | A04 | MICL0.01145026/RDB
Build-In Floor | Mini Canal | MICL.01145026/RMN | 11 | 450 | 26 | 26 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01145026/RMN
Build-In Floor | Mini Canal | MICL.01145026/RMV | 11 | 450 | 26 | 26 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01145026/RMV
Build-In Floor | Mini Canal | MICL.01145026/RNA | 11 | 450 | 26 | 26 | 1468 | 1468 | 1468 | 0.034952 | 571 | 0.013595 | 1672 | 0.03981 | 1.362 | A04 | MICL0.01145026/RNA
Build-In Floor | Mini Canal | MICL.01145026/RON | 11 | 450 | 26 | 26 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01145026/RON
Build-In Floor | Mini Canal | MICL.01145026/ROV | 11 | 450 | 26 | 26 | 1424 | 1424 | 1424 | 0.033905 | 554 | 0.01319 | 1622 | 0.038619 | 1.362 | A04 | MICL0.01145026/ROV
Build-In Floor | Mini Canal | MICL.01145026/RSS | 11 | 450 | 26 | 26 | 1409 | 1409 | 1409 | 0.033548 | 548 | 0.013048 | 1605 | 0.038214 | 1.362 | A04 | MICL0.01145026/RSS
Build-In Floor | Mini Canal | MICL.01145026/SBL | 11 | 450 | 26 | 26 | 1468 | 1468 | 1468 | 0.034952 | 571 | 0.013595 | 1672 | 0.03981 | 1.362 | A04 | MICL0.01145026/SBL
Build-In Floor | Mini Canal | MICL.01145026/SBR | 11 | 450 | 26 | 26 | 1468 | 1468 | 1468 | 0.034952 | 571 | 0.013595 | 1672 | 0.03981 | 1.362 | A04 | MICL0.01145026/SBR
Build-In Floor | Mini Canal | MICL.01145026/SDB | 11 | 450 | 26 | 26 | 1468 | 1468 | 1468 | 0.034952 | 571 | 0.013595 | 1672 | 0.03981 | 1.362 | A04 | MICL0.01145026/SDB
Build-In Floor | Mini Canal | MICL.01145026/SNA | 11 | 450 | 26 | 26 | 1468 | 1468 | 1468 | 0.034952 | 571 | 0.013595 | 1672 | 0.03981 | 1.362 | A04 | MICL0.01145026/SNA
Build-In Floor | Mini Canal | MICL.01145026/SNC | 11 | 450 | 26 | 26 | 1468 | 1468 | 1468 | 0.034952 | 571 | 0.013595 | 1672 | 0.03981 | 1.362 | A04 | MICL0.01145026/SNC
Build-In Floor | Mini Canal | MICL.01145034/ANA | 11 | 450 | 34 | 34 | 1430 | 1430 | 1430 | 0.034048 | 556 | 0.013238 | 1629 | 0.038786 | 1.362 | A04 | MICL0.01145034/ANA
Build-In Floor | Mini Canal | MICL.01145034/DBL | 11 | 450 | 34 | 34 | 1849 | 1849 | 1849 | 0.044024 | 719 | 0.017119 | 2106 | 0.050143 | 1.362 | A04 | MICL0.01145034/DBL
Build-In Floor | Mini Canal | MICL.01145034/DBN | 11 | 450 | 34 | 34 | 1773 | 1773 | 1773 | 0.042214 | 690 | 0.016429 | 2019 | 0.048071 | 1.362 | A04 | MICL0.01145034/DBN
Build-In Floor | Mini Canal | MICL.01145034/DBR | 11 | 450 | 34 | 34 | 1849 | 1849 | 1849 | 0.044024 | 719 | 0.017119 | 2106 | 0.050143 | 1.362 | A04 | MICL0.01145034/DBR
Build-In Floor | Mini Canal | MICL.01145034/DBV | 11 | 450 | 34 | 34 | 1773 | 1773 | 1773 | 0.042214 | 690 | 0.016429 | 2019 | 0.048071 | 1.362 | A04 | MICL0.01145034/DBV
Build-In Floor | Mini Canal | MICL.01145034/DDB | 11 | 450 | 34 | 34 | 1849 | 1849 | 1849 | 0.044024 | 719 | 0.017119 | 2106 | 0.050143 | 1.362 | A04 | MICL0.01145034/DDB
Build-In Floor | Mini Canal | MICL.01145034/DMN | 11 | 450 | 34 | 34 | 1773 | 1773 | 1773 | 0.042214 | 690 | 0.016429 | 2019 | 0.048071 | 1.362 | A04 | MICL0.01145034/DMN
Build-In Floor | Mini Canal | MICL.01145034/DMV | 11 | 450 | 34 | 34 | 1773 | 1773 | 1773 | 0.042214 | 690 | 0.016429 | 2019 | 0.048071 | 1.362 | A04 | MICL0.01145034/DMV
Build-In Floor | Mini Canal | MICL.01145034/DNA | 11 | 450 | 34 | 34 | 1849 | 1849 | 1849 | 0.044024 | 719 | 0.017119 | 2106 | 0.050143 | 1.362 | A04 | MICL0.01145034/DNA
Build-In Floor | Mini Canal | MICL.01145034/DNC | 11 | 450 | 34 | 34 | 1849 | 1849 | 1849 | 0.044024 | 719 | 0.017119 | 2106 | 0.050143 | 1.362 | A04 | MICL0.01145034/DNC
Build-In Floor | Mini Canal | MICL.01145034/DON | 11 | 450 | 34 | 34 | 1773 | 1773 | 1773 | 0.042214 | 690 | 0.016429 | 2019 | 0.048071 | 1.362 | A04 | MICL0.01145034/DON
Build-In Floor | Mini Canal | MICL.01145034/DOV | 11 | 450 | 34 | 34 | 1773 | 1773 | 1773 | 0.042214 | 690 | 0.016429 | 2019 | 0.048071 | 1.362 | A04 | MICL0.01145034/DOV
Build-In Floor | Mini Canal | MICL.01145034/PNC | 11 | 450 | 34 | 34 | 1620 | 1620 | 1620 | 0.038571 | 630 | 0.015 | 1845 | 0.043929 | 1.362 | A04 | MICL0.01145034/PNC
Build-In Floor | Mini Canal | MICL.01145034/RBL | 11 | 450 | 34 | 34 | 1906 | 1906 | 1906 | 0.045381 | 741 | 0.017643 | 2171 | 0.05169 | 1.362 | A04 | MICL0.01145034/RBL
Build-In Floor | Mini Canal | MICL.01145034/RBN | 11 | 450 | 34 | 34 | 1849 | 1849 | 1849 | 0.044024 | 719 | 0.017119 | 2106 | 0.050143 | 1.362 | A04 | MICL0.01145034/RBN
Build-In Floor | Mini Canal | MICL.01145034/RBR | 11 | 450 | 34 | 34 | 1906 | 1906 | 1906 | 0.045381 | 741 | 0.017643 | 2171 | 0.05169 | 1.362 | A04 | MICL0.01145034/RBR
Build-In Floor | Mini Canal | MICL.01145034/RBV | 11 | 450 | 34 | 34 | 1849 | 1849 | 1849 | 0.044024 | 719 | 0.017119 | 2106 | 0.050143 | 1.362 | A04 | MICL0.01145034/RBV
Build-In Floor | Mini Canal | MICL.01145034/RDB | 11 | 450 | 34 | 34 | 1906 | 1906 | 1906 | 0.045381 | 741 | 0.017643 | 2171 | 0.05169 | 1.362 | A04 | MICL0.01145034/RDB
Build-In Floor | Mini Canal | MICL.01145034/RMN | 11 | 450 | 34 | 34 | 1849 | 1849 | 1849 | 0.044024 | 719 | 0.017119 | 2106 | 0.050143 | 1.362 | A04 | MICL0.01145034/RMN
Build-In Floor | Mini Canal | MICL.01145034/RMV | 11 | 450 | 34 | 34 | 1849 | 1849 | 1849 | 0.044024 | 719 | 0.017119 | 2106 | 0.050143 | 1.362 | A04 | MICL0.01145034/RMV
Build-In Floor | Mini Canal | MICL.01145034/RNA | 11 | 450 | 34 | 34 | 1906 | 1906 | 1906 | 0.045381 | 741 | 0.017643 | 2171 | 0.05169 | 1.362 | A04 | MICL0.01145034/RNA
Build-In Floor | Mini Canal | MICL.01145034/RON | 11 | 450 | 34 | 34 | 1849 | 1849 | 1849 | 0.044024 | 719 | 0.017119 | 2106 | 0.050143 | 1.362 | A04 | MICL0.01145034/RON
Build-In Floor | Mini Canal | MICL.01145034/ROV | 11 | 450 | 34 | 34 | 1849 | 1849 | 1849 | 0.044024 | 719 | 0.017119 | 2106 | 0.050143 | 1.362 | A04 | MICL0.01145034/ROV
Build-In Floor | Mini Canal | MICL.01145034/RSS | 11 | 450 | 34 | 34 | 1830 | 1830 | 1830 | 0.043571 | 712 | 0.016952 | 2084 | 0.049619 | 1.362 | A04 | MICL0.01145034/RSS
Build-In Floor | Mini Canal | MICL.01145034/SBL | 11 | 450 | 34 | 34 | 1906 | 1906 | 1906 | 0.045381 | 741 | 0.017643 | 2171 | 0.05169 | 1.362 | A04 | MICL0.01145034/SBL
Build-In Floor | Mini Canal | MICL.01145034/SBR | 11 | 450 | 34 | 34 | 1906 | 1906 | 1906 | 0.045381 | 741 | 0.017643 | 2171 | 0.05169 | 1.362 | A04 | MICL0.01145034/SBR
Build-In Floor | Mini Canal | MICL.01145034/SDB | 11 | 450 | 34 | 34 | 1906 | 1906 | 1906 | 0.045381 | 741 | 0.017643 | 2171 | 0.05169 | 1.362 | A04 | MICL0.01145034/SDB
Build-In Floor | Mini Canal | MICL.01145034/SNA | 11 | 450 | 34 | 34 | 1906 | 1906 | 1906 | 0.045381 | 741 | 0.017643 | 2171 | 0.05169 | 1.362 | A04 | MICL0.01145034/SNA
Build-In Floor | Mini Canal | MICL.01145034/SNC | 11 | 450 | 34 | 34 | 1906 | 1906 | 1906 | 0.045381 | 741 | 0.017643 | 2171 | 0.05169 | 1.362 | A04 | MICL0.01145034/SNC
Build-In Floor | Mini Canal | MICL.01145042/ANA | 11 | 450 | 42 | 42 | 2010 | 2010 | 2010 | 0.047857 | 782 | 0.018619 | 2289 | 0.0545 | 1.362 | A04 | MICL0.01145042/ANA
Build-In Floor | Mini Canal | MICL.01145042/DBL | 11 | 450 | 42 | 42 | 2600 | 2600 | 2600 | 0.061905 | 1011 | 0.024071 | 2961 | 0.0705 | 1.362 | A04 | MICL0.01145042/DBL
Build-In Floor | Mini Canal | MICL.01145042/DBN | 11 | 450 | 42 | 42 | 2492 | 2492 | 2492 | 0.059333 | 969 | 0.023071 | 2838 | 0.067571 | 1.362 | A04 | MICL0.01145042/DBN
Build-In Floor | Mini Canal | MICL.01145042/DBR | 11 | 450 | 42 | 42 | 2600 | 2600 | 2600 | 0.061905 | 1011 | 0.024071 | 2961 | 0.0705 | 1.362 | A04 | MICL0.01145042/DBR
Build-In Floor | Mini Canal | MICL.01145042/DBV | 11 | 450 | 42 | 42 | 2492 | 2492 | 2492 | 0.059333 | 969 | 0.023071 | 2838 | 0.067571 | 1.362 | A04 | MICL0.01145042/DBV
Build-In Floor | Mini Canal | MICL.01145042/DDB | 11 | 450 | 42 | 42 | 2600 | 2600 | 2600 | 0.061905 | 1011 | 0.024071 | 2961 | 0.0705 | 1.362 | A04 | MICL0.01145042/DDB
Build-In Floor | Mini Canal | MICL.01145042/DMN | 11 | 450 | 42 | 42 | 2492 | 2492 | 2492 | 0.059333 | 969 | 0.023071 | 2838 | 0.067571 | 1.362 | A04 | MICL0.01145042/DMN
Build-In Floor | Mini Canal | MICL.01145042/DMV | 11 | 450 | 42 | 42 | 2492 | 2492 | 2492 | 0.059333 | 969 | 0.023071 | 2838 | 0.067571 | 1.362 | A04 | MICL0.01145042/DMV
Build-In Floor | Mini Canal | MICL.01145042/DNA | 11 | 450 | 42 | 42 | 2600 | 2600 | 2600 | 0.061905 | 1011 | 0.024071 | 2961 | 0.0705 | 1.362 | A04 | MICL0.01145042/DNA
Build-In Floor | Mini Canal | MICL.01145042/DNC | 11 | 450 | 42 | 42 | 2600 | 2600 | 2600 | 0.061905 | 1011 | 0.024071 | 2961 | 0.0705 | 1.362 | A04 | MICL0.01145042/DNC
Build-In Floor | Mini Canal | MICL.01145042/DON | 11 | 450 | 42 | 42 | 2492 | 2492 | 2492 | 0.059333 | 969 | 0.023071 | 2838 | 0.067571 | 1.362 | A04 | MICL0.01145042/DON
Build-In Floor | Mini Canal | MICL.01145042/DOV | 11 | 450 | 42 | 42 | 2492 | 2492 | 2492 | 0.059333 | 969 | 0.023071 | 2838 | 0.067571 | 1.362 | A04 | MICL0.01145042/DOV
Build-In Floor | Mini Canal | MICL.01145042/PNC | 11 | 450 | 42 | 42 | 2278 | 2278 | 2278 | 0.054238 | 886 | 0.021095 | 2595 | 0.061786 | 1.362 | A04 | MICL0.01145042/PNC
Build-In Floor | Mini Canal | MICL.01145042/RBL | 11 | 450 | 42 | 42 | 2680 | 2680 | 2680 | 0.06381 | 1043 | 0.024833 | 3053 | 0.07269 | 1.362 | A04 | MICL0.01145042/RBL
Build-In Floor | Mini Canal | MICL.01145042/RBN | 11 | 450 | 42 | 42 | 2600 | 2600 | 2600 | 0.061905 | 1011 | 0.024071 | 2961 | 0.0705 | 1.362 | A04 | MICL0.01145042/RBN
Build-In Floor | Mini Canal | MICL.01145042/RBR | 11 | 450 | 42 | 42 | 2680 | 2680 | 2680 | 0.06381 | 1043 | 0.024833 | 3053 | 0.07269 | 1.362 | A04 | MICL0.01145042/RBR
Build-In Floor | Mini Canal | MICL.01145042/RBV | 11 | 450 | 42 | 42 | 2600 | 2600 | 2600 | 0.061905 | 1011 | 0.024071 | 2961 | 0.0705 | 1.362 | A04 | MICL0.01145042/RBV
Build-In Floor | Mini Canal | MICL.01145042/RDB | 11 | 450 | 42 | 42 | 2680 | 2680 | 2680 | 0.06381 | 1043 | 0.024833 | 3053 | 0.07269 | 1.362 | A04 | MICL0.01145042/RDB
Build-In Floor | Mini Canal | MICL.01145042/RMN | 11 | 450 | 42 | 42 | 2600 | 2600 | 2600 | 0.061905 | 1011 | 0.024071 | 2961 | 0.0705 | 1.362 | A04 | MICL0.01145042/RMN
Build-In Floor | Mini Canal | MICL.01145042/RMV | 11 | 450 | 42 | 42 | 2600 | 2600 | 2600 | 0.061905 | 1011 | 0.024071 | 2961 | 0.0705 | 1.362 | A04 | MICL0.01145042/RMV
Build-In Floor | Mini Canal | MICL.01145042/RNA | 11 | 450 | 42 | 42 | 2680 | 2680 | 2680 | 0.06381 | 1043 | 0.024833 | 3053 | 0.07269 | 1.362 | A04 | MICL0.01145042/RNA
Build-In Floor | Mini Canal | MICL.01145042/RON | 11 | 450 | 42 | 42 | 2600 | 2600 | 2600 | 0.061905 | 1011 | 0.024071 | 2961 | 0.0705 | 1.362 | A04 | MICL0.01145042/RON
Build-In Floor | Mini Canal | MICL.01145042/ROV | 11 | 450 | 42 | 42 | 2600 | 2600 | 2600 | 0.061905 | 1011 | 0.024071 | 2961 | 0.0705 | 1.362 | A04 | MICL0.01145042/ROV
Build-In Floor | Mini Canal | MICL.01145042/RSS | 11 | 450 | 42 | 42 | 2573 | 2573 | 2573 | 0.061262 | 1001 | 0.023833 | 2931 | 0.069786 | 1.362 | A04 | MICL0.01145042/RSS
Build-In Floor | Mini Canal | MICL.01145042/SBL | 11 | 450 | 42 | 42 | 2680 | 2680 | 2680 | 0.06381 | 1043 | 0.024833 | 3053 | 0.07269 | 1.362 | A04 | MICL0.01145042/SBL
Build-In Floor | Mini Canal | MICL.01145042/SBR | 11 | 450 | 42 | 42 | 2680 | 2680 | 2680 | 0.06381 | 1043 | 0.024833 | 3053 | 0.07269 | 1.362 | A04 | MICL0.01145042/SBR
Build-In Floor | Mini Canal | MICL.01145042/SDB | 11 | 450 | 42 | 42 | 2680 | 2680 | 2680 | 0.06381 | 1043 | 0.024833 | 3053 | 0.07269 | 1.362 | A04 | MICL0.01145042/SDB
Build-In Floor | Mini Canal | MICL.01145042/SNA | 11 | 450 | 42 | 42 | 2680 | 2680 | 2680 | 0.06381 | 1043 | 0.024833 | 3053 | 0.07269 | 1.362 | A04 | MICL0.01145042/SNA
Build-In Floor | Mini Canal | MICL.01145042/SNC | 11 | 450 | 42 | 42 | 2680 | 2680 | 2680 | 0.06381 | 1043 | 0.024833 | 3053 | 0.07269 | 1.362 | A04 | MICL0.01145042/SNC
Build-In Floor | Mini Canal | MICL.01147014/ANA | 11 | 470 | 14 | 14 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01147014/ANA
Build-In Floor | Mini Canal | MICL.01147014/DBL | 11 | 470 | 14 | 14 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01147014/DBL
Build-In Floor | Mini Canal | MICL.01147014/DBN | 11 | 470 | 14 | 14 | 894 | 894 | 894 | 0.021286 | 348 | 0.0082857 | 1018 | 0.024238 | 1.362 | A04 | MICL0.01147014/DBN
Build-In Floor | Mini Canal | MICL.01147014/DBR | 11 | 470 | 14 | 14 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01147014/DBR
Build-In Floor | Mini Canal | MICL.01147014/DBV | 11 | 470 | 14 | 14 | 894 | 894 | 894 | 0.021286 | 348 | 0.0082857 | 1018 | 0.024238 | 1.362 | A04 | MICL0.01147014/DBV
Build-In Floor | Mini Canal | MICL.01147014/DDB | 11 | 470 | 14 | 14 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01147014/DDB
Build-In Floor | Mini Canal | MICL.01147014/DMN | 11 | 470 | 14 | 14 | 894 | 894 | 894 | 0.021286 | 348 | 0.0082857 | 1018 | 0.024238 | 1.362 | A04 | MICL0.01147014/DMN
Build-In Floor | Mini Canal | MICL.01147014/DMV | 11 | 470 | 14 | 14 | 894 | 894 | 894 | 0.021286 | 348 | 0.0082857 | 1018 | 0.024238 | 1.362 | A04 | MICL0.01147014/DMV
Build-In Floor | Mini Canal | MICL.01147014/DNA | 11 | 470 | 14 | 14 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01147014/DNA
Build-In Floor | Mini Canal | MICL.01147014/DNC | 11 | 470 | 14 | 14 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01147014/DNC
Build-In Floor | Mini Canal | MICL.01147014/DON | 11 | 470 | 14 | 14 | 894 | 894 | 894 | 0.021286 | 348 | 0.0082857 | 1018 | 0.024238 | 1.362 | A04 | MICL0.01147014/DON
Build-In Floor | Mini Canal | MICL.01147014/DOV | 11 | 470 | 14 | 14 | 894 | 894 | 894 | 0.021286 | 348 | 0.0082857 | 1018 | 0.024238 | 1.362 | A04 | MICL0.01147014/DOV
Build-In Floor | Mini Canal | MICL.01147014/RBL | 11 | 470 | 14 | 14 | 961 | 961 | 961 | 0.022881 | 374 | 0.0089048 | 1095 | 0.026071 | 1.362 | A04 | MICL0.01147014/RBL
Build-In Floor | Mini Canal | MICL.01147014/RBN | 11 | 470 | 14 | 14 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01147014/RBN
Build-In Floor | Mini Canal | MICL.01147014/RBR | 11 | 470 | 14 | 14 | 961 | 961 | 961 | 0.022881 | 374 | 0.0089048 | 1095 | 0.026071 | 1.362 | A04 | MICL0.01147014/RBR
Build-In Floor | Mini Canal | MICL.01147014/RBV | 11 | 470 | 14 | 14 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01147014/RBV
Build-In Floor | Mini Canal | MICL.01147014/RDB | 11 | 470 | 14 | 14 | 961 | 961 | 961 | 0.022881 | 374 | 0.0089048 | 1095 | 0.026071 | 1.362 | A04 | MICL0.01147014/RDB
Build-In Floor | Mini Canal | MICL.01147014/RMN | 11 | 470 | 14 | 14 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01147014/RMN
Build-In Floor | Mini Canal | MICL.01147014/RMV | 11 | 470 | 14 | 14 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01147014/RMV
Build-In Floor | Mini Canal | MICL.01147014/RNA | 11 | 470 | 14 | 14 | 961 | 961 | 961 | 0.022881 | 374 | 0.0089048 | 1095 | 0.026071 | 1.362 | A04 | MICL0.01147014/RNA
Build-In Floor | Mini Canal | MICL.01147014/RON | 11 | 470 | 14 | 14 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01147014/RON
Build-In Floor | Mini Canal | MICL.01147014/ROV | 11 | 470 | 14 | 14 | 932 | 932 | 932 | 0.02219 | 363 | 0.0086429 | 1062 | 0.025286 | 1.362 | A04 | MICL0.01147014/ROV
Build-In Floor | Mini Canal | MICL.01147014/RSS | 11 | 470 | 14 | 14 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.01147014/RSS
Build-In Floor | Mini Canal | MICL.01147014/SBL | 11 | 470 | 14 | 14 | 961 | 961 | 961 | 0.022881 | 374 | 0.0089048 | 1095 | 0.026071 | 1.362 | A04 | MICL0.01147014/SBL
Build-In Floor | Mini Canal | MICL.01147014/SBR | 11 | 470 | 14 | 14 | 961 | 961 | 961 | 0.022881 | 374 | 0.0089048 | 1095 | 0.026071 | 1.362 | A04 | MICL0.01147014/SBR
Build-In Floor | Mini Canal | MICL.01147014/SDB | 11 | 470 | 14 | 14 | 961 | 961 | 961 | 0.022881 | 374 | 0.0089048 | 1095 | 0.026071 | 1.362 | A04 | MICL0.01147014/SDB
Build-In Floor | Mini Canal | MICL.01147014/SNA | 11 | 470 | 14 | 14 | 961 | 961 | 961 | 0.022881 | 374 | 0.0089048 | 1095 | 0.026071 | 1.362 | A04 | MICL0.01147014/SNA
Build-In Floor | Mini Canal | MICL.01147014/SNC | 11 | 470 | 14 | 14 | 961 | 961 | 961 | 0.022881 | 374 | 0.0089048 | 1095 | 0.026071 | 1.362 | A04 | MICL0.01147014/SNC
Build-In Floor | Mini Canal | MICL.01147018/ANA | 11 | 470 | 18 | 18 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01147018/ANA
Build-In Floor | Mini Canal | MICL.01147018/DBL | 11 | 470 | 18 | 18 | 1106 | 1106 | 1106 | 0.026333 | 430 | 0.010238 | 1260 | 0.03 | 1.362 | A04 | MICL0.01147018/DBL
Build-In Floor | Mini Canal | MICL.01147018/DBN | 11 | 470 | 18 | 18 | 1060 | 1060 | 1060 | 0.025238 | 412 | 0.0098095 | 1207 | 0.028738 | 1.362 | A04 | MICL0.01147018/DBN
Build-In Floor | Mini Canal | MICL.01147018/DBR | 11 | 470 | 18 | 18 | 1106 | 1106 | 1106 | 0.026333 | 430 | 0.010238 | 1260 | 0.03 | 1.362 | A04 | MICL0.01147018/DBR
Build-In Floor | Mini Canal | MICL.01147018/DBV | 11 | 470 | 18 | 18 | 1060 | 1060 | 1060 | 0.025238 | 412 | 0.0098095 | 1207 | 0.028738 | 1.362 | A04 | MICL0.01147018/DBV
Build-In Floor | Mini Canal | MICL.01147018/DDB | 11 | 470 | 18 | 18 | 1106 | 1106 | 1106 | 0.026333 | 430 | 0.010238 | 1260 | 0.03 | 1.362 | A04 | MICL0.01147018/DDB
Build-In Floor | Mini Canal | MICL.01147018/DMN | 11 | 470 | 18 | 18 | 1060 | 1060 | 1060 | 0.025238 | 412 | 0.0098095 | 1207 | 0.028738 | 1.362 | A04 | MICL0.01147018/DMN
Build-In Floor | Mini Canal | MICL.01147018/DMV | 11 | 470 | 18 | 18 | 1060 | 1060 | 1060 | 0.025238 | 412 | 0.0098095 | 1207 | 0.028738 | 1.362 | A04 | MICL0.01147018/DMV
Build-In Floor | Mini Canal | MICL.01147018/DNA | 11 | 470 | 18 | 18 | 1106 | 1106 | 1106 | 0.026333 | 430 | 0.010238 | 1260 | 0.03 | 1.362 | A04 | MICL0.01147018/DNA
Build-In Floor | Mini Canal | MICL.01147018/DNC | 11 | 470 | 18 | 18 | 1106 | 1106 | 1106 | 0.026333 | 430 | 0.010238 | 1260 | 0.03 | 1.362 | A04 | MICL0.01147018/DNC
Build-In Floor | Mini Canal | MICL.01147018/DON | 11 | 470 | 18 | 18 | 1060 | 1060 | 1060 | 0.025238 | 412 | 0.0098095 | 1207 | 0.028738 | 1.362 | A04 | MICL0.01147018/DON
Build-In Floor | Mini Canal | MICL.01147018/DOV | 11 | 470 | 18 | 18 | 1060 | 1060 | 1060 | 0.025238 | 412 | 0.0098095 | 1207 | 0.028738 | 1.362 | A04 | MICL0.01147018/DOV
Build-In Floor | Mini Canal | MICL.01147018/RBL | 11 | 470 | 18 | 18 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01147018/RBL
Build-In Floor | Mini Canal | MICL.01147018/RBN | 11 | 470 | 18 | 18 | 1106 | 1106 | 1106 | 0.026333 | 430 | 0.010238 | 1260 | 0.03 | 1.362 | A04 | MICL0.01147018/RBN
Build-In Floor | Mini Canal | MICL.01147018/RBR | 11 | 470 | 18 | 18 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01147018/RBR
Build-In Floor | Mini Canal | MICL.01147018/RBV | 11 | 470 | 18 | 18 | 1106 | 1106 | 1106 | 0.026333 | 430 | 0.010238 | 1260 | 0.03 | 1.362 | A04 | MICL0.01147018/RBV
Build-In Floor | Mini Canal | MICL.01147018/RDB | 11 | 470 | 18 | 18 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01147018/RDB
Build-In Floor | Mini Canal | MICL.01147018/RMN | 11 | 470 | 18 | 18 | 1106 | 1106 | 1106 | 0.026333 | 430 | 0.010238 | 1260 | 0.03 | 1.362 | A04 | MICL0.01147018/RMN
Build-In Floor | Mini Canal | MICL.01147018/RMV | 11 | 470 | 18 | 18 | 1106 | 1106 | 1106 | 0.026333 | 430 | 0.010238 | 1260 | 0.03 | 1.362 | A04 | MICL0.01147018/RMV
Build-In Floor | Mini Canal | MICL.01147018/RNA | 11 | 470 | 18 | 18 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01147018/RNA
Build-In Floor | Mini Canal | MICL.01147018/RON | 11 | 470 | 18 | 18 | 1106 | 1106 | 1106 | 0.026333 | 430 | 0.010238 | 1260 | 0.03 | 1.362 | A04 | MICL0.01147018/RON
Build-In Floor | Mini Canal | MICL.01147018/ROV | 11 | 470 | 18 | 18 | 1106 | 1106 | 1106 | 0.026333 | 430 | 0.010238 | 1260 | 0.03 | 1.362 | A04 | MICL0.01147018/ROV
Build-In Floor | Mini Canal | MICL.01147018/RSS | 11 | 470 | 18 | 18 | 1094 | 1094 | 1094 | 0.026048 | 426 | 0.010143 | 1246 | 0.029667 | 1.362 | A04 | MICL0.01147018/RSS
Build-In Floor | Mini Canal | MICL.01147018/SBL | 11 | 470 | 18 | 18 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01147018/SBL
Build-In Floor | Mini Canal | MICL.01147018/SBR | 11 | 470 | 18 | 18 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01147018/SBR
Build-In Floor | Mini Canal | MICL.01147018/SDB | 11 | 470 | 18 | 18 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01147018/SDB
Build-In Floor | Mini Canal | MICL.01147018/SNA | 11 | 470 | 18 | 18 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01147018/SNA
Build-In Floor | Mini Canal | MICL.01147018/SNC | 11 | 470 | 18 | 18 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01147018/SNC
Build-In Floor | Mini Canal | MICL.01147026/ANA | 11 | 470 | 26 | 26 | 1153 | 1153 | 1153 | 0.027452 | 449 | 0.01069 | 1313 | 0.031262 | 1.362 | A04 | MICL0.01147026/ANA
Build-In Floor | Mini Canal | MICL.01147026/DBL | 11 | 470 | 26 | 26 | 1491 | 1491 | 1491 | 0.0355 | 580 | 0.01381 | 1698 | 0.040429 | 1.362 | A04 | MICL0.01147026/DBL
Build-In Floor | Mini Canal | MICL.01147026/DBN | 11 | 470 | 26 | 26 | 1429 | 1429 | 1429 | 0.034024 | 556 | 0.013238 | 1628 | 0.038762 | 1.362 | A04 | MICL0.01147026/DBN
Build-In Floor | Mini Canal | MICL.01147026/DBR | 11 | 470 | 26 | 26 | 1491 | 1491 | 1491 | 0.0355 | 580 | 0.01381 | 1698 | 0.040429 | 1.362 | A04 | MICL0.01147026/DBR
Build-In Floor | Mini Canal | MICL.01147026/DBV | 11 | 470 | 26 | 26 | 1429 | 1429 | 1429 | 0.034024 | 556 | 0.013238 | 1628 | 0.038762 | 1.362 | A04 | MICL0.01147026/DBV
Build-In Floor | Mini Canal | MICL.01147026/DDB | 11 | 470 | 26 | 26 | 1491 | 1491 | 1491 | 0.0355 | 580 | 0.01381 | 1698 | 0.040429 | 1.362 | A04 | MICL0.01147026/DDB
Build-In Floor | Mini Canal | MICL.01147026/DMN | 11 | 470 | 26 | 26 | 1429 | 1429 | 1429 | 0.034024 | 556 | 0.013238 | 1628 | 0.038762 | 1.362 | A04 | MICL0.01147026/DMN
Build-In Floor | Mini Canal | MICL.01147026/DMV | 11 | 470 | 26 | 26 | 1429 | 1429 | 1429 | 0.034024 | 556 | 0.013238 | 1628 | 0.038762 | 1.362 | A04 | MICL0.01147026/DMV
Build-In Floor | Mini Canal | MICL.01147026/DNA | 11 | 470 | 26 | 26 | 1491 | 1491 | 1491 | 0.0355 | 580 | 0.01381 | 1698 | 0.040429 | 1.362 | A04 | MICL0.01147026/DNA
Build-In Floor | Mini Canal | MICL.01147026/DNC | 11 | 470 | 26 | 26 | 1491 | 1491 | 1491 | 0.0355 | 580 | 0.01381 | 1698 | 0.040429 | 1.362 | A04 | MICL0.01147026/DNC
Build-In Floor | Mini Canal | MICL.01147026/DON | 11 | 470 | 26 | 26 | 1429 | 1429 | 1429 | 0.034024 | 556 | 0.013238 | 1628 | 0.038762 | 1.362 | A04 | MICL0.01147026/DON
Build-In Floor | Mini Canal | MICL.01147026/DOV | 11 | 470 | 26 | 26 | 1429 | 1429 | 1429 | 0.034024 | 556 | 0.013238 | 1628 | 0.038762 | 1.362 | A04 | MICL0.01147026/DOV
Build-In Floor | Mini Canal | MICL.01147026/PNC | 11 | 470 | 26 | 26 | 1306 | 1306 | 1306 | 0.031095 | 508 | 0.012095 | 1488 | 0.035429 | 1.362 | A04 | MICL0.01147026/PNC
Build-In Floor | Mini Canal | MICL.01147026/RBL | 11 | 470 | 26 | 26 | 1537 | 1537 | 1537 | 0.036595 | 598 | 0.014238 | 1751 | 0.04169 | 1.362 | A04 | MICL0.01147026/RBL
Build-In Floor | Mini Canal | MICL.01147026/RBN | 11 | 470 | 26 | 26 | 1491 | 1491 | 1491 | 0.0355 | 580 | 0.01381 | 1698 | 0.040429 | 1.362 | A04 | MICL0.01147026/RBN
Build-In Floor | Mini Canal | MICL.01147026/RBR | 11 | 470 | 26 | 26 | 1537 | 1537 | 1537 | 0.036595 | 598 | 0.014238 | 1751 | 0.04169 | 1.362 | A04 | MICL0.01147026/RBR
Build-In Floor | Mini Canal | MICL.01147026/RBV | 11 | 470 | 26 | 26 | 1491 | 1491 | 1491 | 0.0355 | 580 | 0.01381 | 1698 | 0.040429 | 1.362 | A04 | MICL0.01147026/RBV
Build-In Floor | Mini Canal | MICL.01147026/RDB | 11 | 470 | 26 | 26 | 1537 | 1537 | 1537 | 0.036595 | 598 | 0.014238 | 1751 | 0.04169 | 1.362 | A04 | MICL0.01147026/RDB
Build-In Floor | Mini Canal | MICL.01147026/RMN | 11 | 470 | 26 | 26 | 1491 | 1491 | 1491 | 0.0355 | 580 | 0.01381 | 1698 | 0.040429 | 1.362 | A04 | MICL0.01147026/RMN
Build-In Floor | Mini Canal | MICL.01147026/RMV | 11 | 470 | 26 | 26 | 1491 | 1491 | 1491 | 0.0355 | 580 | 0.01381 | 1698 | 0.040429 | 1.362 | A04 | MICL0.01147026/RMV
Build-In Floor | Mini Canal | MICL.01147026/RNA | 11 | 470 | 26 | 26 | 1537 | 1537 | 1537 | 0.036595 | 598 | 0.014238 | 1751 | 0.04169 | 1.362 | A04 | MICL0.01147026/RNA
Build-In Floor | Mini Canal | MICL.01147026/RON | 11 | 470 | 26 | 26 | 1491 | 1491 | 1491 | 0.0355 | 580 | 0.01381 | 1698 | 0.040429 | 1.362 | A04 | MICL0.01147026/RON
Build-In Floor | Mini Canal | MICL.01147026/ROV | 11 | 470 | 26 | 26 | 1491 | 1491 | 1491 | 0.0355 | 580 | 0.01381 | 1698 | 0.040429 | 1.362 | A04 | MICL0.01147026/ROV
Build-In Floor | Mini Canal | MICL.01147026/RSS | 11 | 470 | 26 | 26 | 1476 | 1476 | 1476 | 0.035143 | 574 | 0.013667 | 1681 | 0.040024 | 1.362 | A04 | MICL0.01147026/RSS
Build-In Floor | Mini Canal | MICL.01147026/SBL | 11 | 470 | 26 | 26 | 1537 | 1537 | 1537 | 0.036595 | 598 | 0.014238 | 1751 | 0.04169 | 1.362 | A04 | MICL0.01147026/SBL
Build-In Floor | Mini Canal | MICL.01147026/SBR | 11 | 470 | 26 | 26 | 1537 | 1537 | 1537 | 0.036595 | 598 | 0.014238 | 1751 | 0.04169 | 1.362 | A04 | MICL0.01147026/SBR
Build-In Floor | Mini Canal | MICL.01147026/SDB | 11 | 470 | 26 | 26 | 1537 | 1537 | 1537 | 0.036595 | 598 | 0.014238 | 1751 | 0.04169 | 1.362 | A04 | MICL0.01147026/SDB
Build-In Floor | Mini Canal | MICL.01147026/SNA | 11 | 470 | 26 | 26 | 1537 | 1537 | 1537 | 0.036595 | 598 | 0.014238 | 1751 | 0.04169 | 1.362 | A04 | MICL0.01147026/SNA
Build-In Floor | Mini Canal | MICL.01147026/SNC | 11 | 470 | 26 | 26 | 1537 | 1537 | 1537 | 0.036595 | 598 | 0.014238 | 1751 | 0.04169 | 1.362 | A04 | MICL0.01147026/SNC
Build-In Floor | Mini Canal | MICL.01147034/ANA | 11 | 470 | 34 | 34 | 1499 | 1499 | 1499 | 0.03569 | 583 | 0.013881 | 1707 | 0.040643 | 1.362 | A04 | MICL0.01147034/ANA
Build-In Floor | Mini Canal | MICL.01147034/DBL | 11 | 470 | 34 | 34 | 1938 | 1938 | 1938 | 0.046143 | 754 | 0.017952 | 2207 | 0.052548 | 1.362 | A04 | MICL0.01147034/DBL
Build-In Floor | Mini Canal | MICL.01147034/DBN | 11 | 470 | 34 | 34 | 1858 | 1858 | 1858 | 0.044238 | 723 | 0.017214 | 2116 | 0.050381 | 1.362 | A04 | MICL0.01147034/DBN
Build-In Floor | Mini Canal | MICL.01147034/DBR | 11 | 470 | 34 | 34 | 1938 | 1938 | 1938 | 0.046143 | 754 | 0.017952 | 2207 | 0.052548 | 1.362 | A04 | MICL0.01147034/DBR
Build-In Floor | Mini Canal | MICL.01147034/DBV | 11 | 470 | 34 | 34 | 1858 | 1858 | 1858 | 0.044238 | 723 | 0.017214 | 2116 | 0.050381 | 1.362 | A04 | MICL0.01147034/DBV
Build-In Floor | Mini Canal | MICL.01147034/DDB | 11 | 470 | 34 | 34 | 1938 | 1938 | 1938 | 0.046143 | 754 | 0.017952 | 2207 | 0.052548 | 1.362 | A04 | MICL0.01147034/DDB
Build-In Floor | Mini Canal | MICL.01147034/DMN | 11 | 470 | 34 | 34 | 1858 | 1858 | 1858 | 0.044238 | 723 | 0.017214 | 2116 | 0.050381 | 1.362 | A04 | MICL0.01147034/DMN
Build-In Floor | Mini Canal | MICL.01147034/DMV | 11 | 470 | 34 | 34 | 1858 | 1858 | 1858 | 0.044238 | 723 | 0.017214 | 2116 | 0.050381 | 1.362 | A04 | MICL0.01147034/DMV
Build-In Floor | Mini Canal | MICL.01147034/DNA | 11 | 470 | 34 | 34 | 1938 | 1938 | 1938 | 0.046143 | 754 | 0.017952 | 2207 | 0.052548 | 1.362 | A04 | MICL0.01147034/DNA
Build-In Floor | Mini Canal | MICL.01147034/DNC | 11 | 470 | 34 | 34 | 1938 | 1938 | 1938 | 0.046143 | 754 | 0.017952 | 2207 | 0.052548 | 1.362 | A04 | MICL0.01147034/DNC
Build-In Floor | Mini Canal | MICL.01147034/DON | 11 | 470 | 34 | 34 | 1858 | 1858 | 1858 | 0.044238 | 723 | 0.017214 | 2116 | 0.050381 | 1.362 | A04 | MICL0.01147034/DON
Build-In Floor | Mini Canal | MICL.01147034/DOV | 11 | 470 | 34 | 34 | 1858 | 1858 | 1858 | 0.044238 | 723 | 0.017214 | 2116 | 0.050381 | 1.362 | A04 | MICL0.01147034/DOV
Build-In Floor | Mini Canal | MICL.01147034/PNC | 11 | 470 | 34 | 34 | 1698 | 1698 | 1698 | 0.040429 | 661 | 0.015738 | 1934 | 0.046048 | 1.362 | A04 | MICL0.01147034/PNC
Build-In Floor | Mini Canal | MICL.01147034/RBL | 11 | 470 | 34 | 34 | 1998 | 1998 | 1998 | 0.047571 | 777 | 0.0185 | 2276 | 0.05419 | 1.362 | A04 | MICL0.01147034/RBL
Build-In Floor | Mini Canal | MICL.01147034/RBN | 11 | 470 | 34 | 34 | 1938 | 1938 | 1938 | 0.046143 | 754 | 0.017952 | 2207 | 0.052548 | 1.362 | A04 | MICL0.01147034/RBN
Build-In Floor | Mini Canal | MICL.01147034/RBR | 11 | 470 | 34 | 34 | 1998 | 1998 | 1998 | 0.047571 | 777 | 0.0185 | 2276 | 0.05419 | 1.362 | A04 | MICL0.01147034/RBR
Build-In Floor | Mini Canal | MICL.01147034/RBV | 11 | 470 | 34 | 34 | 1938 | 1938 | 1938 | 0.046143 | 754 | 0.017952 | 2207 | 0.052548 | 1.362 | A04 | MICL0.01147034/RBV
Build-In Floor | Mini Canal | MICL.01147034/RDB | 11 | 470 | 34 | 34 | 1998 | 1998 | 1998 | 0.047571 | 777 | 0.0185 | 2276 | 0.05419 | 1.362 | A04 | MICL0.01147034/RDB
Build-In Floor | Mini Canal | MICL.01147034/RMN | 11 | 470 | 34 | 34 | 1938 | 1938 | 1938 | 0.046143 | 754 | 0.017952 | 2207 | 0.052548 | 1.362 | A04 | MICL0.01147034/RMN
Build-In Floor | Mini Canal | MICL.01147034/RMV | 11 | 470 | 34 | 34 | 1938 | 1938 | 1938 | 0.046143 | 754 | 0.017952 | 2207 | 0.052548 | 1.362 | A04 | MICL0.01147034/RMV
Build-In Floor | Mini Canal | MICL.01147034/RNA | 11 | 470 | 34 | 34 | 1998 | 1998 | 1998 | 0.047571 | 777 | 0.0185 | 2276 | 0.05419 | 1.362 | A04 | MICL0.01147034/RNA
Build-In Floor | Mini Canal | MICL.01147034/RON | 11 | 470 | 34 | 34 | 1938 | 1938 | 1938 | 0.046143 | 754 | 0.017952 | 2207 | 0.052548 | 1.362 | A04 | MICL0.01147034/RON
Build-In Floor | Mini Canal | MICL.01147034/ROV | 11 | 470 | 34 | 34 | 1938 | 1938 | 1938 | 0.046143 | 754 | 0.017952 | 2207 | 0.052548 | 1.362 | A04 | MICL0.01147034/ROV
Build-In Floor | Mini Canal | MICL.01147034/RSS | 11 | 470 | 34 | 34 | 1918 | 1918 | 1918 | 0.045667 | 746 | 0.017762 | 2185 | 0.052024 | 1.362 | A04 | MICL0.01147034/RSS
Build-In Floor | Mini Canal | MICL.01147034/SBL | 11 | 470 | 34 | 34 | 1998 | 1998 | 1998 | 0.047571 | 777 | 0.0185 | 2276 | 0.05419 | 1.362 | A04 | MICL0.01147034/SBL
Build-In Floor | Mini Canal | MICL.01147034/SBR | 11 | 470 | 34 | 34 | 1998 | 1998 | 1998 | 0.047571 | 777 | 0.0185 | 2276 | 0.05419 | 1.362 | A04 | MICL0.01147034/SBR
Build-In Floor | Mini Canal | MICL.01147034/SDB | 11 | 470 | 34 | 34 | 1998 | 1998 | 1998 | 0.047571 | 777 | 0.0185 | 2276 | 0.05419 | 1.362 | A04 | MICL0.01147034/SDB
Build-In Floor | Mini Canal | MICL.01147034/SNA | 11 | 470 | 34 | 34 | 1998 | 1998 | 1998 | 0.047571 | 777 | 0.0185 | 2276 | 0.05419 | 1.362 | A04 | MICL0.01147034/SNA
Build-In Floor | Mini Canal | MICL.01147034/SNC | 11 | 470 | 34 | 34 | 1998 | 1998 | 1998 | 0.047571 | 777 | 0.0185 | 2276 | 0.05419 | 1.362 | A04 | MICL0.01147034/SNC
Build-In Floor | Mini Canal | MICL.01147042/ANA | 11 | 470 | 42 | 42 | 2105 | 2105 | 2105 | 0.050119 | 819 | 0.0195 | 2398 | 0.057095 | 1.362 | A04 | MICL0.01147042/ANA
Build-In Floor | Mini Canal | MICL.01147042/DBL | 11 | 470 | 42 | 42 | 2723 | 2723 | 2723 | 0.064833 | 1059 | 0.025214 | 3101 | 0.073833 | 1.362 | A04 | MICL0.01147042/DBL
Build-In Floor | Mini Canal | MICL.01147042/DBN | 11 | 470 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01147042/DBN
Build-In Floor | Mini Canal | MICL.01147042/DBR | 11 | 470 | 42 | 42 | 2723 | 2723 | 2723 | 0.064833 | 1059 | 0.025214 | 3101 | 0.073833 | 1.362 | A04 | MICL0.01147042/DBR
Build-In Floor | Mini Canal | MICL.01147042/DBV | 11 | 470 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01147042/DBV
Build-In Floor | Mini Canal | MICL.01147042/DDB | 11 | 470 | 42 | 42 | 2723 | 2723 | 2723 | 0.064833 | 1059 | 0.025214 | 3101 | 0.073833 | 1.362 | A04 | MICL0.01147042/DDB
Build-In Floor | Mini Canal | MICL.01147042/DMN | 11 | 470 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01147042/DMN
Build-In Floor | Mini Canal | MICL.01147042/DMV | 11 | 470 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01147042/DMV
Build-In Floor | Mini Canal | MICL.01147042/DNA | 11 | 470 | 42 | 42 | 2723 | 2723 | 2723 | 0.064833 | 1059 | 0.025214 | 3101 | 0.073833 | 1.362 | A04 | MICL0.01147042/DNA
Build-In Floor | Mini Canal | MICL.01147042/DNC | 11 | 470 | 42 | 42 | 2723 | 2723 | 2723 | 0.064833 | 1059 | 0.025214 | 3101 | 0.073833 | 1.362 | A04 | MICL0.01147042/DNC
Build-In Floor | Mini Canal | MICL.01147042/DON | 11 | 470 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01147042/DON
Build-In Floor | Mini Canal | MICL.01147042/DOV | 11 | 470 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01147042/DOV
Build-In Floor | Mini Canal | MICL.01147042/PNC | 11 | 470 | 42 | 42 | 2386 | 2386 | 2386 | 0.05681 | 928 | 0.022095 | 2718 | 0.064714 | 1.362 | A04 | MICL0.01147042/PNC
Build-In Floor | Mini Canal | MICL.01147042/RBL | 11 | 470 | 42 | 42 | 2807 | 2807 | 2807 | 0.066833 | 1092 | 0.026 | 3197 | 0.076119 | 1.362 | A04 | MICL0.01147042/RBL
Build-In Floor | Mini Canal | MICL.01147042/RBN | 11 | 470 | 42 | 42 | 2723 | 2723 | 2723 | 0.064833 | 1059 | 0.025214 | 3101 | 0.073833 | 1.362 | A04 | MICL0.01147042/RBN
Build-In Floor | Mini Canal | MICL.01147042/RBR | 11 | 470 | 42 | 42 | 2807 | 2807 | 2807 | 0.066833 | 1092 | 0.026 | 3197 | 0.076119 | 1.362 | A04 | MICL0.01147042/RBR
Build-In Floor | Mini Canal | MICL.01147042/RBV | 11 | 470 | 42 | 42 | 2723 | 2723 | 2723 | 0.064833 | 1059 | 0.025214 | 3101 | 0.073833 | 1.362 | A04 | MICL0.01147042/RBV
Build-In Floor | Mini Canal | MICL.01147042/RDB | 11 | 470 | 42 | 42 | 2807 | 2807 | 2807 | 0.066833 | 1092 | 0.026 | 3197 | 0.076119 | 1.362 | A04 | MICL0.01147042/RDB
Build-In Floor | Mini Canal | MICL.01147042/RMN | 11 | 470 | 42 | 42 | 2723 | 2723 | 2723 | 0.064833 | 1059 | 0.025214 | 3101 | 0.073833 | 1.362 | A04 | MICL0.01147042/RMN
Build-In Floor | Mini Canal | MICL.01147042/RMV | 11 | 470 | 42 | 42 | 2723 | 2723 | 2723 | 0.064833 | 1059 | 0.025214 | 3101 | 0.073833 | 1.362 | A04 | MICL0.01147042/RMV
Build-In Floor | Mini Canal | MICL.01147042/RNA | 11 | 470 | 42 | 42 | 2807 | 2807 | 2807 | 0.066833 | 1092 | 0.026 | 3197 | 0.076119 | 1.362 | A04 | MICL0.01147042/RNA
Build-In Floor | Mini Canal | MICL.01147042/RON | 11 | 470 | 42 | 42 | 2723 | 2723 | 2723 | 0.064833 | 1059 | 0.025214 | 3101 | 0.073833 | 1.362 | A04 | MICL0.01147042/RON
Build-In Floor | Mini Canal | MICL.01147042/ROV | 11 | 470 | 42 | 42 | 2723 | 2723 | 2723 | 0.064833 | 1059 | 0.025214 | 3101 | 0.073833 | 1.362 | A04 | MICL0.01147042/ROV
Build-In Floor | Mini Canal | MICL.01147042/RSS | 11 | 470 | 42 | 42 | 2695 | 2695 | 2695 | 0.064167 | 1048 | 0.024952 | 3070 | 0.073095 | 1.362 | A04 | MICL0.01147042/RSS
Build-In Floor | Mini Canal | MICL.01147042/SBL | 11 | 470 | 42 | 42 | 2807 | 2807 | 2807 | 0.066833 | 1092 | 0.026 | 3197 | 0.076119 | 1.362 | A04 | MICL0.01147042/SBL
Build-In Floor | Mini Canal | MICL.01147042/SBR | 11 | 470 | 42 | 42 | 2807 | 2807 | 2807 | 0.066833 | 1092 | 0.026 | 3197 | 0.076119 | 1.362 | A04 | MICL0.01147042/SBR
Build-In Floor | Mini Canal | MICL.01147042/SDB | 11 | 470 | 42 | 42 | 2807 | 2807 | 2807 | 0.066833 | 1092 | 0.026 | 3197 | 0.076119 | 1.362 | A04 | MICL0.01147042/SDB
Build-In Floor | Mini Canal | MICL.01147042/SNA | 11 | 470 | 42 | 42 | 2807 | 2807 | 2807 | 0.066833 | 1092 | 0.026 | 3197 | 0.076119 | 1.362 | A04 | MICL0.01147042/SNA
Build-In Floor | Mini Canal | MICL.01147042/SNC | 11 | 470 | 42 | 42 | 2807 | 2807 | 2807 | 0.066833 | 1092 | 0.026 | 3197 | 0.076119 | 1.362 | A04 | MICL0.01147042/SNC
Build-In Floor | Mini Canal | MICL.01149014/ANA | 11 | 490 | 14 | 14 | 754 | 754 | 754 | 0.017952 | 293 | 0.0069762 | 859 | 0.020452 | 1.362 | A04 | MICL0.01149014/ANA
Build-In Floor | Mini Canal | MICL.01149014/DBL | 11 | 490 | 14 | 14 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01149014/DBL
Build-In Floor | Mini Canal | MICL.01149014/DBN | 11 | 490 | 14 | 14 | 935 | 935 | 935 | 0.022262 | 364 | 0.0086667 | 1065 | 0.025357 | 1.362 | A04 | MICL0.01149014/DBN
Build-In Floor | Mini Canal | MICL.01149014/DBR | 11 | 490 | 14 | 14 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01149014/DBR
Build-In Floor | Mini Canal | MICL.01149014/DBV | 11 | 490 | 14 | 14 | 935 | 935 | 935 | 0.022262 | 364 | 0.0086667 | 1065 | 0.025357 | 1.362 | A04 | MICL0.01149014/DBV
Build-In Floor | Mini Canal | MICL.01149014/DDB | 11 | 490 | 14 | 14 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01149014/DDB
Build-In Floor | Mini Canal | MICL.01149014/DMN | 11 | 490 | 14 | 14 | 935 | 935 | 935 | 0.022262 | 364 | 0.0086667 | 1065 | 0.025357 | 1.362 | A04 | MICL0.01149014/DMN
Build-In Floor | Mini Canal | MICL.01149014/DMV | 11 | 490 | 14 | 14 | 935 | 935 | 935 | 0.022262 | 364 | 0.0086667 | 1065 | 0.025357 | 1.362 | A04 | MICL0.01149014/DMV
Build-In Floor | Mini Canal | MICL.01149014/DNA | 11 | 490 | 14 | 14 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01149014/DNA
Build-In Floor | Mini Canal | MICL.01149014/DNC | 11 | 490 | 14 | 14 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01149014/DNC
Build-In Floor | Mini Canal | MICL.01149014/DON | 11 | 490 | 14 | 14 | 935 | 935 | 935 | 0.022262 | 364 | 0.0086667 | 1065 | 0.025357 | 1.362 | A04 | MICL0.01149014/DON
Build-In Floor | Mini Canal | MICL.01149014/DOV | 11 | 490 | 14 | 14 | 935 | 935 | 935 | 0.022262 | 364 | 0.0086667 | 1065 | 0.025357 | 1.362 | A04 | MICL0.01149014/DOV
Build-In Floor | Mini Canal | MICL.01149014/RBL | 11 | 490 | 14 | 14 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01149014/RBL
Build-In Floor | Mini Canal | MICL.01149014/RBN | 11 | 490 | 14 | 14 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01149014/RBN
Build-In Floor | Mini Canal | MICL.01149014/RBR | 11 | 490 | 14 | 14 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01149014/RBR
Build-In Floor | Mini Canal | MICL.01149014/RBV | 11 | 490 | 14 | 14 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01149014/RBV
Build-In Floor | Mini Canal | MICL.01149014/RDB | 11 | 490 | 14 | 14 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01149014/RDB
Build-In Floor | Mini Canal | MICL.01149014/RMN | 11 | 490 | 14 | 14 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01149014/RMN
Build-In Floor | Mini Canal | MICL.01149014/RMV | 11 | 490 | 14 | 14 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01149014/RMV
Build-In Floor | Mini Canal | MICL.01149014/RNA | 11 | 490 | 14 | 14 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01149014/RNA
Build-In Floor | Mini Canal | MICL.01149014/RON | 11 | 490 | 14 | 14 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01149014/RON
Build-In Floor | Mini Canal | MICL.01149014/ROV | 11 | 490 | 14 | 14 | 975 | 975 | 975 | 0.023214 | 379 | 0.0090238 | 1111 | 0.026452 | 1.362 | A04 | MICL0.01149014/ROV
Build-In Floor | Mini Canal | MICL.01149014/RSS | 11 | 490 | 14 | 14 | 965 | 965 | 965 | 0.022976 | 375 | 0.0089286 | 1099 | 0.026167 | 1.362 | A04 | MICL0.01149014/RSS
Build-In Floor | Mini Canal | MICL.01149014/SBL | 11 | 490 | 14 | 14 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01149014/SBL
Build-In Floor | Mini Canal | MICL.01149014/SBR | 11 | 490 | 14 | 14 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01149014/SBR
Build-In Floor | Mini Canal | MICL.01149014/SDB | 11 | 490 | 14 | 14 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01149014/SDB
Build-In Floor | Mini Canal | MICL.01149014/SNA | 11 | 490 | 14 | 14 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01149014/SNA
Build-In Floor | Mini Canal | MICL.01149014/SNC | 11 | 490 | 14 | 14 | 1005 | 1005 | 1005 | 0.023929 | 391 | 0.0093095 | 1145 | 0.027262 | 1.362 | A04 | MICL0.01149014/SNC
Build-In Floor | Mini Canal | MICL.01149018/ANA | 11 | 490 | 18 | 18 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01149018/ANA
Build-In Floor | Mini Canal | MICL.01149018/DBL | 11 | 490 | 18 | 18 | 1155 | 1155 | 1155 | 0.0275 | 449 | 0.01069 | 1316 | 0.031333 | 1.362 | A04 | MICL0.01149018/DBL
Build-In Floor | Mini Canal | MICL.01149018/DBN | 11 | 490 | 18 | 18 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01149018/DBN
Build-In Floor | Mini Canal | MICL.01149018/DBR | 11 | 490 | 18 | 18 | 1155 | 1155 | 1155 | 0.0275 | 449 | 0.01069 | 1316 | 0.031333 | 1.362 | A04 | MICL0.01149018/DBR
Build-In Floor | Mini Canal | MICL.01149018/DBV | 11 | 490 | 18 | 18 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01149018/DBV
Build-In Floor | Mini Canal | MICL.01149018/DDB | 11 | 490 | 18 | 18 | 1155 | 1155 | 1155 | 0.0275 | 449 | 0.01069 | 1316 | 0.031333 | 1.362 | A04 | MICL0.01149018/DDB
Build-In Floor | Mini Canal | MICL.01149018/DMN | 11 | 490 | 18 | 18 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01149018/DMN
Build-In Floor | Mini Canal | MICL.01149018/DMV | 11 | 490 | 18 | 18 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01149018/DMV
Build-In Floor | Mini Canal | MICL.01149018/DNA | 11 | 490 | 18 | 18 | 1155 | 1155 | 1155 | 0.0275 | 449 | 0.01069 | 1316 | 0.031333 | 1.362 | A04 | MICL0.01149018/DNA
Build-In Floor | Mini Canal | MICL.01149018/DNC | 11 | 490 | 18 | 18 | 1155 | 1155 | 1155 | 0.0275 | 449 | 0.01069 | 1316 | 0.031333 | 1.362 | A04 | MICL0.01149018/DNC
Build-In Floor | Mini Canal | MICL.01149018/DON | 11 | 490 | 18 | 18 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01149018/DON
Build-In Floor | Mini Canal | MICL.01149018/DOV | 11 | 490 | 18 | 18 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01149018/DOV
Build-In Floor | Mini Canal | MICL.01149018/RBL | 11 | 490 | 18 | 18 | 1191 | 1191 | 1191 | 0.028357 | 463 | 0.011024 | 1357 | 0.03231 | 1.362 | A04 | MICL0.01149018/RBL
Build-In Floor | Mini Canal | MICL.01149018/RBN | 11 | 490 | 18 | 18 | 1155 | 1155 | 1155 | 0.0275 | 449 | 0.01069 | 1316 | 0.031333 | 1.362 | A04 | MICL0.01149018/RBN
Build-In Floor | Mini Canal | MICL.01149018/RBR | 11 | 490 | 18 | 18 | 1191 | 1191 | 1191 | 0.028357 | 463 | 0.011024 | 1357 | 0.03231 | 1.362 | A04 | MICL0.01149018/RBR
Build-In Floor | Mini Canal | MICL.01149018/RBV | 11 | 490 | 18 | 18 | 1155 | 1155 | 1155 | 0.0275 | 449 | 0.01069 | 1316 | 0.031333 | 1.362 | A04 | MICL0.01149018/RBV
Build-In Floor | Mini Canal | MICL.01149018/RDB | 11 | 490 | 18 | 18 | 1191 | 1191 | 1191 | 0.028357 | 463 | 0.011024 | 1357 | 0.03231 | 1.362 | A04 | MICL0.01149018/RDB
Build-In Floor | Mini Canal | MICL.01149018/RMN | 11 | 490 | 18 | 18 | 1155 | 1155 | 1155 | 0.0275 | 449 | 0.01069 | 1316 | 0.031333 | 1.362 | A04 | MICL0.01149018/RMN
Build-In Floor | Mini Canal | MICL.01149018/RMV | 11 | 490 | 18 | 18 | 1155 | 1155 | 1155 | 0.0275 | 449 | 0.01069 | 1316 | 0.031333 | 1.362 | A04 | MICL0.01149018/RMV
Build-In Floor | Mini Canal | MICL.01149018/RNA | 11 | 490 | 18 | 18 | 1191 | 1191 | 1191 | 0.028357 | 463 | 0.011024 | 1357 | 0.03231 | 1.362 | A04 | MICL0.01149018/RNA
Build-In Floor | Mini Canal | MICL.01149018/RON | 11 | 490 | 18 | 18 | 1155 | 1155 | 1155 | 0.0275 | 449 | 0.01069 | 1316 | 0.031333 | 1.362 | A04 | MICL0.01149018/RON
Build-In Floor | Mini Canal | MICL.01149018/ROV | 11 | 490 | 18 | 18 | 1155 | 1155 | 1155 | 0.0275 | 449 | 0.01069 | 1316 | 0.031333 | 1.362 | A04 | MICL0.01149018/ROV
Build-In Floor | Mini Canal | MICL.01149018/RSS | 11 | 490 | 18 | 18 | 1143 | 1143 | 1143 | 0.027214 | 445 | 0.010595 | 1302 | 0.031 | 1.362 | A04 | MICL0.01149018/RSS
Build-In Floor | Mini Canal | MICL.01149018/SBL | 11 | 490 | 18 | 18 | 1191 | 1191 | 1191 | 0.028357 | 463 | 0.011024 | 1357 | 0.03231 | 1.362 | A04 | MICL0.01149018/SBL
Build-In Floor | Mini Canal | MICL.01149018/SBR | 11 | 490 | 18 | 18 | 1191 | 1191 | 1191 | 0.028357 | 463 | 0.011024 | 1357 | 0.03231 | 1.362 | A04 | MICL0.01149018/SBR
Build-In Floor | Mini Canal | MICL.01149018/SDB | 11 | 490 | 18 | 18 | 1191 | 1191 | 1191 | 0.028357 | 463 | 0.011024 | 1357 | 0.03231 | 1.362 | A04 | MICL0.01149018/SDB
Build-In Floor | Mini Canal | MICL.01149018/SNA | 11 | 490 | 18 | 18 | 1191 | 1191 | 1191 | 0.028357 | 463 | 0.011024 | 1357 | 0.03231 | 1.362 | A04 | MICL0.01149018/SNA
Build-In Floor | Mini Canal | MICL.01149018/SNC | 11 | 490 | 18 | 18 | 1191 | 1191 | 1191 | 0.028357 | 463 | 0.011024 | 1357 | 0.03231 | 1.362 | A04 | MICL0.01149018/SNC
Build-In Floor | Mini Canal | MICL.01149026/ANA | 11 | 490 | 26 | 26 | 1206 | 1206 | 1206 | 0.028714 | 469 | 0.011167 | 1374 | 0.032714 | 1.362 | A04 | MICL0.01149026/ANA
Build-In Floor | Mini Canal | MICL.01149026/DBL | 11 | 490 | 26 | 26 | 1560 | 1560 | 1560 | 0.037143 | 607 | 0.014452 | 1777 | 0.04231 | 1.362 | A04 | MICL0.01149026/DBL
Build-In Floor | Mini Canal | MICL.01149026/DBN | 11 | 490 | 26 | 26 | 1495 | 1495 | 1495 | 0.035595 | 582 | 0.013857 | 1703 | 0.040548 | 1.362 | A04 | MICL0.01149026/DBN
Build-In Floor | Mini Canal | MICL.01149026/DBR | 11 | 490 | 26 | 26 | 1560 | 1560 | 1560 | 0.037143 | 607 | 0.014452 | 1777 | 0.04231 | 1.362 | A04 | MICL0.01149026/DBR
Build-In Floor | Mini Canal | MICL.01149026/DBV | 11 | 490 | 26 | 26 | 1495 | 1495 | 1495 | 0.035595 | 582 | 0.013857 | 1703 | 0.040548 | 1.362 | A04 | MICL0.01149026/DBV
Build-In Floor | Mini Canal | MICL.01149026/DDB | 11 | 490 | 26 | 26 | 1560 | 1560 | 1560 | 0.037143 | 607 | 0.014452 | 1777 | 0.04231 | 1.362 | A04 | MICL0.01149026/DDB
Build-In Floor | Mini Canal | MICL.01149026/DMN | 11 | 490 | 26 | 26 | 1495 | 1495 | 1495 | 0.035595 | 582 | 0.013857 | 1703 | 0.040548 | 1.362 | A04 | MICL0.01149026/DMN
Build-In Floor | Mini Canal | MICL.01149026/DMV | 11 | 490 | 26 | 26 | 1495 | 1495 | 1495 | 0.035595 | 582 | 0.013857 | 1703 | 0.040548 | 1.362 | A04 | MICL0.01149026/DMV
Build-In Floor | Mini Canal | MICL.01149026/DNA | 11 | 490 | 26 | 26 | 1560 | 1560 | 1560 | 0.037143 | 607 | 0.014452 | 1777 | 0.04231 | 1.362 | A04 | MICL0.01149026/DNA
Build-In Floor | Mini Canal | MICL.01149026/DNC | 11 | 490 | 26 | 26 | 1560 | 1560 | 1560 | 0.037143 | 607 | 0.014452 | 1777 | 0.04231 | 1.362 | A04 | MICL0.01149026/DNC
Build-In Floor | Mini Canal | MICL.01149026/DON | 11 | 490 | 26 | 26 | 1495 | 1495 | 1495 | 0.035595 | 582 | 0.013857 | 1703 | 0.040548 | 1.362 | A04 | MICL0.01149026/DON
Build-In Floor | Mini Canal | MICL.01149026/DOV | 11 | 490 | 26 | 26 | 1495 | 1495 | 1495 | 0.035595 | 582 | 0.013857 | 1703 | 0.040548 | 1.362 | A04 | MICL0.01149026/DOV
Build-In Floor | Mini Canal | MICL.01149026/PNC | 11 | 490 | 26 | 26 | 1367 | 1367 | 1367 | 0.032548 | 532 | 0.012667 | 1557 | 0.037071 | 1.362 | A04 | MICL0.01149026/PNC
Build-In Floor | Mini Canal | MICL.01149026/RBL | 11 | 490 | 26 | 26 | 1608 | 1608 | 1608 | 0.038286 | 626 | 0.014905 | 1832 | 0.043619 | 1.362 | A04 | MICL0.01149026/RBL
Build-In Floor | Mini Canal | MICL.01149026/RBN | 11 | 490 | 26 | 26 | 1560 | 1560 | 1560 | 0.037143 | 607 | 0.014452 | 1777 | 0.04231 | 1.362 | A04 | MICL0.01149026/RBN
Build-In Floor | Mini Canal | MICL.01149026/RBR | 11 | 490 | 26 | 26 | 1608 | 1608 | 1608 | 0.038286 | 626 | 0.014905 | 1832 | 0.043619 | 1.362 | A04 | MICL0.01149026/RBR
Build-In Floor | Mini Canal | MICL.01149026/RBV | 11 | 490 | 26 | 26 | 1560 | 1560 | 1560 | 0.037143 | 607 | 0.014452 | 1777 | 0.04231 | 1.362 | A04 | MICL0.01149026/RBV
Build-In Floor | Mini Canal | MICL.01149026/RDB | 11 | 490 | 26 | 26 | 1608 | 1608 | 1608 | 0.038286 | 626 | 0.014905 | 1832 | 0.043619 | 1.362 | A04 | MICL0.01149026/RDB
Build-In Floor | Mini Canal | MICL.01149026/RMN | 11 | 490 | 26 | 26 | 1560 | 1560 | 1560 | 0.037143 | 607 | 0.014452 | 1777 | 0.04231 | 1.362 | A04 | MICL0.01149026/RMN
Build-In Floor | Mini Canal | MICL.01149026/RMV | 11 | 490 | 26 | 26 | 1560 | 1560 | 1560 | 0.037143 | 607 | 0.014452 | 1777 | 0.04231 | 1.362 | A04 | MICL0.01149026/RMV
Build-In Floor | Mini Canal | MICL.01149026/RNA | 11 | 490 | 26 | 26 | 1608 | 1608 | 1608 | 0.038286 | 626 | 0.014905 | 1832 | 0.043619 | 1.362 | A04 | MICL0.01149026/RNA
Build-In Floor | Mini Canal | MICL.01149026/RON | 11 | 490 | 26 | 26 | 1560 | 1560 | 1560 | 0.037143 | 607 | 0.014452 | 1777 | 0.04231 | 1.362 | A04 | MICL0.01149026/RON
Build-In Floor | Mini Canal | MICL.01149026/ROV | 11 | 490 | 26 | 26 | 1560 | 1560 | 1560 | 0.037143 | 607 | 0.014452 | 1777 | 0.04231 | 1.362 | A04 | MICL0.01149026/ROV
Build-In Floor | Mini Canal | MICL.01149026/RSS | 11 | 490 | 26 | 26 | 1544 | 1544 | 1544 | 0.036762 | 601 | 0.01431 | 1759 | 0.041881 | 1.362 | A04 | MICL0.01149026/RSS
Build-In Floor | Mini Canal | MICL.01149026/SBL | 11 | 490 | 26 | 26 | 1608 | 1608 | 1608 | 0.038286 | 626 | 0.014905 | 1832 | 0.043619 | 1.362 | A04 | MICL0.01149026/SBL
Build-In Floor | Mini Canal | MICL.01149026/SBR | 11 | 490 | 26 | 26 | 1608 | 1608 | 1608 | 0.038286 | 626 | 0.014905 | 1832 | 0.043619 | 1.362 | A04 | MICL0.01149026/SBR
Build-In Floor | Mini Canal | MICL.01149026/SDB | 11 | 490 | 26 | 26 | 1608 | 1608 | 1608 | 0.038286 | 626 | 0.014905 | 1832 | 0.043619 | 1.362 | A04 | MICL0.01149026/SDB
Build-In Floor | Mini Canal | MICL.01149026/SNA | 11 | 490 | 26 | 26 | 1608 | 1608 | 1608 | 0.038286 | 626 | 0.014905 | 1832 | 0.043619 | 1.362 | A04 | MICL0.01149026/SNA
Build-In Floor | Mini Canal | MICL.01149026/SNC | 11 | 490 | 26 | 26 | 1608 | 1608 | 1608 | 0.038286 | 626 | 0.014905 | 1832 | 0.043619 | 1.362 | A04 | MICL0.01149026/SNC
Build-In Floor | Mini Canal | MICL.01149034/ANA | 11 | 490 | 34 | 34 | 1566 | 1566 | 1566 | 0.037286 | 609 | 0.0145 | 1784 | 0.042476 | 1.362 | A04 | MICL0.01149034/ANA
Build-In Floor | Mini Canal | MICL.01149034/DBL | 11 | 490 | 34 | 34 | 2025 | 2025 | 2025 | 0.048214 | 788 | 0.018762 | 2306 | 0.054905 | 1.362 | A04 | MICL0.01149034/DBL
Build-In Floor | Mini Canal | MICL.01149034/DBN | 11 | 490 | 34 | 34 | 1942 | 1942 | 1942 | 0.046238 | 755 | 0.017976 | 2212 | 0.052667 | 1.362 | A04 | MICL0.01149034/DBN
Build-In Floor | Mini Canal | MICL.01149034/DBR | 11 | 490 | 34 | 34 | 2025 | 2025 | 2025 | 0.048214 | 788 | 0.018762 | 2306 | 0.054905 | 1.362 | A04 | MICL0.01149034/DBR
Build-In Floor | Mini Canal | MICL.01149034/DBV | 11 | 490 | 34 | 34 | 1942 | 1942 | 1942 | 0.046238 | 755 | 0.017976 | 2212 | 0.052667 | 1.362 | A04 | MICL0.01149034/DBV
Build-In Floor | Mini Canal | MICL.01149034/DDB | 11 | 490 | 34 | 34 | 2025 | 2025 | 2025 | 0.048214 | 788 | 0.018762 | 2306 | 0.054905 | 1.362 | A04 | MICL0.01149034/DDB
Build-In Floor | Mini Canal | MICL.01149034/DMN | 11 | 490 | 34 | 34 | 1942 | 1942 | 1942 | 0.046238 | 755 | 0.017976 | 2212 | 0.052667 | 1.362 | A04 | MICL0.01149034/DMN
Build-In Floor | Mini Canal | MICL.01149034/DMV | 11 | 490 | 34 | 34 | 1942 | 1942 | 1942 | 0.046238 | 755 | 0.017976 | 2212 | 0.052667 | 1.362 | A04 | MICL0.01149034/DMV
Build-In Floor | Mini Canal | MICL.01149034/DNA | 11 | 490 | 34 | 34 | 2025 | 2025 | 2025 | 0.048214 | 788 | 0.018762 | 2306 | 0.054905 | 1.362 | A04 | MICL0.01149034/DNA
Build-In Floor | Mini Canal | MICL.01149034/DNC | 11 | 490 | 34 | 34 | 2025 | 2025 | 2025 | 0.048214 | 788 | 0.018762 | 2306 | 0.054905 | 1.362 | A04 | MICL0.01149034/DNC
Build-In Floor | Mini Canal | MICL.01149034/DON | 11 | 490 | 34 | 34 | 1942 | 1942 | 1942 | 0.046238 | 755 | 0.017976 | 2212 | 0.052667 | 1.362 | A04 | MICL0.01149034/DON
Build-In Floor | Mini Canal | MICL.01149034/DOV | 11 | 490 | 34 | 34 | 1942 | 1942 | 1942 | 0.046238 | 755 | 0.017976 | 2212 | 0.052667 | 1.362 | A04 | MICL0.01149034/DOV
Build-In Floor | Mini Canal | MICL.01149034/PNC | 11 | 490 | 34 | 34 | 1775 | 1775 | 1775 | 0.042262 | 690 | 0.016429 | 2022 | 0.048143 | 1.362 | A04 | MICL0.01149034/PNC
Build-In Floor | Mini Canal | MICL.01149034/RBL | 11 | 490 | 34 | 34 | 2088 | 2088 | 2088 | 0.049714 | 812 | 0.019333 | 2378 | 0.056619 | 1.362 | A04 | MICL0.01149034/RBL
Build-In Floor | Mini Canal | MICL.01149034/RBN | 11 | 490 | 34 | 34 | 2025 | 2025 | 2025 | 0.048214 | 788 | 0.018762 | 2306 | 0.054905 | 1.362 | A04 | MICL0.01149034/RBN
Build-In Floor | Mini Canal | MICL.01149034/RBR | 11 | 490 | 34 | 34 | 2088 | 2088 | 2088 | 0.049714 | 812 | 0.019333 | 2378 | 0.056619 | 1.362 | A04 | MICL0.01149034/RBR
Build-In Floor | Mini Canal | MICL.01149034/RBV | 11 | 490 | 34 | 34 | 2025 | 2025 | 2025 | 0.048214 | 788 | 0.018762 | 2306 | 0.054905 | 1.362 | A04 | MICL0.01149034/RBV
Build-In Floor | Mini Canal | MICL.01149034/RDB | 11 | 490 | 34 | 34 | 2088 | 2088 | 2088 | 0.049714 | 812 | 0.019333 | 2378 | 0.056619 | 1.362 | A04 | MICL0.01149034/RDB
Build-In Floor | Mini Canal | MICL.01149034/RMN | 11 | 490 | 34 | 34 | 2025 | 2025 | 2025 | 0.048214 | 788 | 0.018762 | 2306 | 0.054905 | 1.362 | A04 | MICL0.01149034/RMN
Build-In Floor | Mini Canal | MICL.01149034/RMV | 11 | 490 | 34 | 34 | 2025 | 2025 | 2025 | 0.048214 | 788 | 0.018762 | 2306 | 0.054905 | 1.362 | A04 | MICL0.01149034/RMV
Build-In Floor | Mini Canal | MICL.01149034/RNA | 11 | 490 | 34 | 34 | 2088 | 2088 | 2088 | 0.049714 | 812 | 0.019333 | 2378 | 0.056619 | 1.362 | A04 | MICL0.01149034/RNA
Build-In Floor | Mini Canal | MICL.01149034/RON | 11 | 490 | 34 | 34 | 2025 | 2025 | 2025 | 0.048214 | 788 | 0.018762 | 2306 | 0.054905 | 1.362 | A04 | MICL0.01149034/RON
Build-In Floor | Mini Canal | MICL.01149034/ROV | 11 | 490 | 34 | 34 | 2025 | 2025 | 2025 | 0.048214 | 788 | 0.018762 | 2306 | 0.054905 | 1.362 | A04 | MICL0.01149034/ROV
Build-In Floor | Mini Canal | MICL.01149034/RSS | 11 | 490 | 34 | 34 | 2004 | 2004 | 2004 | 0.047714 | 780 | 0.018571 | 2283 | 0.054357 | 1.362 | A04 | MICL0.01149034/RSS
Build-In Floor | Mini Canal | MICL.01149034/SBL | 11 | 490 | 34 | 34 | 2088 | 2088 | 2088 | 0.049714 | 812 | 0.019333 | 2378 | 0.056619 | 1.362 | A04 | MICL0.01149034/SBL
Build-In Floor | Mini Canal | MICL.01149034/SBR | 11 | 490 | 34 | 34 | 2088 | 2088 | 2088 | 0.049714 | 812 | 0.019333 | 2378 | 0.056619 | 1.362 | A04 | MICL0.01149034/SBR
Build-In Floor | Mini Canal | MICL.01149034/SDB | 11 | 490 | 34 | 34 | 2088 | 2088 | 2088 | 0.049714 | 812 | 0.019333 | 2378 | 0.056619 | 1.362 | A04 | MICL0.01149034/SDB
Build-In Floor | Mini Canal | MICL.01149034/SNA | 11 | 490 | 34 | 34 | 2088 | 2088 | 2088 | 0.049714 | 812 | 0.019333 | 2378 | 0.056619 | 1.362 | A04 | MICL0.01149034/SNA
Build-In Floor | Mini Canal | MICL.01149034/SNC | 11 | 490 | 34 | 34 | 2088 | 2088 | 2088 | 0.049714 | 812 | 0.019333 | 2378 | 0.056619 | 1.362 | A04 | MICL0.01149034/SNC
Build-In Floor | Mini Canal | MICL.01149042/ANA | 11 | 490 | 42 | 42 | 2201 | 2201 | 2201 | 0.052405 | 856 | 0.020381 | 2507 | 0.05969 | 1.362 | A04 | MICL0.01149042/ANA
Build-In Floor | Mini Canal | MICL.01149042/DBL | 11 | 490 | 42 | 42 | 2847 | 2847 | 2847 | 0.067786 | 1107 | 0.026357 | 3243 | 0.077214 | 1.362 | A04 | MICL0.01149042/DBL
Build-In Floor | Mini Canal | MICL.01149042/DBN | 11 | 490 | 42 | 42 | 2730 | 2730 | 2730 | 0.065 | 1062 | 0.025286 | 3109 | 0.074024 | 1.362 | A04 | MICL0.01149042/DBN
Build-In Floor | Mini Canal | MICL.01149042/DBR | 11 | 490 | 42 | 42 | 2847 | 2847 | 2847 | 0.067786 | 1107 | 0.026357 | 3243 | 0.077214 | 1.362 | A04 | MICL0.01149042/DBR
Build-In Floor | Mini Canal | MICL.01149042/DBV | 11 | 490 | 42 | 42 | 2730 | 2730 | 2730 | 0.065 | 1062 | 0.025286 | 3109 | 0.074024 | 1.362 | A04 | MICL0.01149042/DBV
Build-In Floor | Mini Canal | MICL.01149042/DDB | 11 | 490 | 42 | 42 | 2847 | 2847 | 2847 | 0.067786 | 1107 | 0.026357 | 3243 | 0.077214 | 1.362 | A04 | MICL0.01149042/DDB
Build-In Floor | Mini Canal | MICL.01149042/DMN | 11 | 490 | 42 | 42 | 2730 | 2730 | 2730 | 0.065 | 1062 | 0.025286 | 3109 | 0.074024 | 1.362 | A04 | MICL0.01149042/DMN
Build-In Floor | Mini Canal | MICL.01149042/DMV | 11 | 490 | 42 | 42 | 2730 | 2730 | 2730 | 0.065 | 1062 | 0.025286 | 3109 | 0.074024 | 1.362 | A04 | MICL0.01149042/DMV
Build-In Floor | Mini Canal | MICL.01149042/DNA | 11 | 490 | 42 | 42 | 2847 | 2847 | 2847 | 0.067786 | 1107 | 0.026357 | 3243 | 0.077214 | 1.362 | A04 | MICL0.01149042/DNA
Build-In Floor | Mini Canal | MICL.01149042/DNC | 11 | 490 | 42 | 42 | 2847 | 2847 | 2847 | 0.067786 | 1107 | 0.026357 | 3243 | 0.077214 | 1.362 | A04 | MICL0.01149042/DNC
Build-In Floor | Mini Canal | MICL.01149042/DON | 11 | 490 | 42 | 42 | 2730 | 2730 | 2730 | 0.065 | 1062 | 0.025286 | 3109 | 0.074024 | 1.362 | A04 | MICL0.01149042/DON
Build-In Floor | Mini Canal | MICL.01149042/DOV | 11 | 490 | 42 | 42 | 2730 | 2730 | 2730 | 0.065 | 1062 | 0.025286 | 3109 | 0.074024 | 1.362 | A04 | MICL0.01149042/DOV
Build-In Floor | Mini Canal | MICL.01149042/PNC | 11 | 490 | 42 | 42 | 2495 | 2495 | 2495 | 0.059405 | 971 | 0.023119 | 2842 | 0.067667 | 1.362 | A04 | MICL0.01149042/PNC
Build-In Floor | Mini Canal | MICL.01149042/RBL | 11 | 490 | 42 | 42 | 2935 | 2935 | 2935 | 0.069881 | 1142 | 0.02719 | 3343 | 0.079595 | 1.362 | A04 | MICL0.01149042/RBL
Build-In Floor | Mini Canal | MICL.01149042/RBN | 11 | 490 | 42 | 42 | 2847 | 2847 | 2847 | 0.067786 | 1107 | 0.026357 | 3243 | 0.077214 | 1.362 | A04 | MICL0.01149042/RBN
Build-In Floor | Mini Canal | MICL.01149042/RBR | 11 | 490 | 42 | 42 | 2935 | 2935 | 2935 | 0.069881 | 1142 | 0.02719 | 3343 | 0.079595 | 1.362 | A04 | MICL0.01149042/RBR
Build-In Floor | Mini Canal | MICL.01149042/RBV | 11 | 490 | 42 | 42 | 2847 | 2847 | 2847 | 0.067786 | 1107 | 0.026357 | 3243 | 0.077214 | 1.362 | A04 | MICL0.01149042/RBV
Build-In Floor | Mini Canal | MICL.01149042/RDB | 11 | 490 | 42 | 42 | 2935 | 2935 | 2935 | 0.069881 | 1142 | 0.02719 | 3343 | 0.079595 | 1.362 | A04 | MICL0.01149042/RDB
Build-In Floor | Mini Canal | MICL.01149042/RMN | 11 | 490 | 42 | 42 | 2847 | 2847 | 2847 | 0.067786 | 1107 | 0.026357 | 3243 | 0.077214 | 1.362 | A04 | MICL0.01149042/RMN
Build-In Floor | Mini Canal | MICL.01149042/RMV | 11 | 490 | 42 | 42 | 2847 | 2847 | 2847 | 0.067786 | 1107 | 0.026357 | 3243 | 0.077214 | 1.362 | A04 | MICL0.01149042/RMV
Build-In Floor | Mini Canal | MICL.01149042/RNA | 11 | 490 | 42 | 42 | 2935 | 2935 | 2935 | 0.069881 | 1142 | 0.02719 | 3343 | 0.079595 | 1.362 | A04 | MICL0.01149042/RNA
Build-In Floor | Mini Canal | MICL.01149042/RON | 11 | 490 | 42 | 42 | 2847 | 2847 | 2847 | 0.067786 | 1107 | 0.026357 | 3243 | 0.077214 | 1.362 | A04 | MICL0.01149042/RON
Build-In Floor | Mini Canal | MICL.01149042/ROV | 11 | 490 | 42 | 42 | 2847 | 2847 | 2847 | 0.067786 | 1107 | 0.026357 | 3243 | 0.077214 | 1.362 | A04 | MICL0.01149042/ROV
Build-In Floor | Mini Canal | MICL.01149042/RSS | 11 | 490 | 42 | 42 | 2818 | 2818 | 2818 | 0.067095 | 1096 | 0.026095 | 3210 | 0.076429 | 1.362 | A04 | MICL0.01149042/RSS
Build-In Floor | Mini Canal | MICL.01149042/SBL | 11 | 490 | 42 | 42 | 2935 | 2935 | 2935 | 0.069881 | 1142 | 0.02719 | 3343 | 0.079595 | 1.362 | A04 | MICL0.01149042/SBL
Build-In Floor | Mini Canal | MICL.01149042/SBR | 11 | 490 | 42 | 42 | 2935 | 2935 | 2935 | 0.069881 | 1142 | 0.02719 | 3343 | 0.079595 | 1.362 | A04 | MICL0.01149042/SBR
Build-In Floor | Mini Canal | MICL.01149042/SDB | 11 | 490 | 42 | 42 | 2935 | 2935 | 2935 | 0.069881 | 1142 | 0.02719 | 3343 | 0.079595 | 1.362 | A04 | MICL0.01149042/SDB
Build-In Floor | Mini Canal | MICL.01149042/SNA | 11 | 490 | 42 | 42 | 2935 | 2935 | 2935 | 0.069881 | 1142 | 0.02719 | 3343 | 0.079595 | 1.362 | A04 | MICL0.01149042/SNA
Build-In Floor | Mini Canal | MICL.01149042/SNC | 11 | 490 | 42 | 42 | 2935 | 2935 | 2935 | 0.069881 | 1142 | 0.02719 | 3343 | 0.079595 | 1.362 | A04 | MICL0.01149042/SNC
Build-In Floor | Mini Canal | MICL.01407014/ANA | 14 | 70 | 14 | 14 | 74 | 74 | 74 | 0.0017619 | 29 | 0.00069048 | 84 | 0.002 | 1.362 | A04 | MICL0.01407014/ANA
Build-In Floor | Mini Canal | MICL.01407014/DBL | 14 | 70 | 14 | 14 | 96 | 96 | 96 | 0.0022857 | 37 | 0.00088095 | 109 | 0.0025952 | 1.362 | A04 | MICL0.01407014/DBL
Build-In Floor | Mini Canal | MICL.01407014/DBN | 14 | 70 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.01407014/DBN
Build-In Floor | Mini Canal | MICL.01407014/DBR | 14 | 70 | 14 | 14 | 96 | 96 | 96 | 0.0022857 | 37 | 0.00088095 | 109 | 0.0025952 | 1.362 | A04 | MICL0.01407014/DBR
Build-In Floor | Mini Canal | MICL.01407014/DBV | 14 | 70 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.01407014/DBV
Build-In Floor | Mini Canal | MICL.01407014/DDB | 14 | 70 | 14 | 14 | 96 | 96 | 96 | 0.0022857 | 37 | 0.00088095 | 109 | 0.0025952 | 1.362 | A04 | MICL0.01407014/DDB
Build-In Floor | Mini Canal | MICL.01407014/DMN | 14 | 70 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.01407014/DMN
Build-In Floor | Mini Canal | MICL.01407014/DMV | 14 | 70 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.01407014/DMV
Build-In Floor | Mini Canal | MICL.01407014/DNA | 14 | 70 | 14 | 14 | 96 | 96 | 96 | 0.0022857 | 37 | 0.00088095 | 109 | 0.0025952 | 1.362 | A04 | MICL0.01407014/DNA
Build-In Floor | Mini Canal | MICL.01407014/DNC | 14 | 70 | 14 | 14 | 96 | 96 | 96 | 0.0022857 | 37 | 0.00088095 | 109 | 0.0025952 | 1.362 | A04 | MICL0.01407014/DNC
Build-In Floor | Mini Canal | MICL.01407014/DON | 14 | 70 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.01407014/DON
Build-In Floor | Mini Canal | MICL.01407014/DOV | 14 | 70 | 14 | 14 | 92 | 92 | 92 | 0.0021905 | 36 | 0.00085714 | 105 | 0.0025 | 1.362 | A04 | MICL0.01407014/DOV
Build-In Floor | Mini Canal | MICL.01407014/RBL | 14 | 70 | 14 | 14 | 99 | 99 | 99 | 0.0023571 | 39 | 0.00092857 | 113 | 0.0026905 | 1.362 | A04 | MICL0.01407014/RBL
Build-In Floor | Mini Canal | MICL.01407014/RBN | 14 | 70 | 14 | 14 | 96 | 96 | 96 | 0.0022857 | 37 | 0.00088095 | 109 | 0.0025952 | 1.362 | A04 | MICL0.01407014/RBN
Build-In Floor | Mini Canal | MICL.01407014/RBR | 14 | 70 | 14 | 14 | 99 | 99 | 99 | 0.0023571 | 39 | 0.00092857 | 113 | 0.0026905 | 1.362 | A04 | MICL0.01407014/RBR
Build-In Floor | Mini Canal | MICL.01407014/RBV | 14 | 70 | 14 | 14 | 96 | 96 | 96 | 0.0022857 | 37 | 0.00088095 | 109 | 0.0025952 | 1.362 | A04 | MICL0.01407014/RBV
Build-In Floor | Mini Canal | MICL.01407014/RDB | 14 | 70 | 14 | 14 | 99 | 99 | 99 | 0.0023571 | 39 | 0.00092857 | 113 | 0.0026905 | 1.362 | A04 | MICL0.01407014/RDB
Build-In Floor | Mini Canal | MICL.01407014/RMN | 14 | 70 | 14 | 14 | 96 | 96 | 96 | 0.0022857 | 37 | 0.00088095 | 109 | 0.0025952 | 1.362 | A04 | MICL0.01407014/RMN
Build-In Floor | Mini Canal | MICL.01407014/RMV | 14 | 70 | 14 | 14 | 96 | 96 | 96 | 0.0022857 | 37 | 0.00088095 | 109 | 0.0025952 | 1.362 | A04 | MICL0.01407014/RMV
Build-In Floor | Mini Canal | MICL.01407014/RNA | 14 | 70 | 14 | 14 | 99 | 99 | 99 | 0.0023571 | 39 | 0.00092857 | 113 | 0.0026905 | 1.362 | A04 | MICL0.01407014/RNA
Build-In Floor | Mini Canal | MICL.01407014/RON | 14 | 70 | 14 | 14 | 96 | 96 | 96 | 0.0022857 | 37 | 0.00088095 | 109 | 0.0025952 | 1.362 | A04 | MICL0.01407014/RON
Build-In Floor | Mini Canal | MICL.01407014/ROV | 14 | 70 | 14 | 14 | 96 | 96 | 96 | 0.0022857 | 37 | 0.00088095 | 109 | 0.0025952 | 1.362 | A04 | MICL0.01407014/ROV
Build-In Floor | Mini Canal | MICL.01407014/RSS | 14 | 70 | 14 | 14 | 95 | 95 | 95 | 0.0022619 | 37 | 0.00088095 | 108 | 0.0025714 | 1.362 | A04 | MICL0.01407014/RSS
Build-In Floor | Mini Canal | MICL.01407014/SBL | 14 | 70 | 14 | 14 | 99 | 99 | 99 | 0.0023571 | 39 | 0.00092857 | 113 | 0.0026905 | 1.362 | A04 | MICL0.01407014/SBL
Build-In Floor | Mini Canal | MICL.01407014/SBR | 14 | 70 | 14 | 14 | 99 | 99 | 99 | 0.0023571 | 39 | 0.00092857 | 113 | 0.0026905 | 1.362 | A04 | MICL0.01407014/SBR
Build-In Floor | Mini Canal | MICL.01407014/SDB | 14 | 70 | 14 | 14 | 99 | 99 | 99 | 0.0023571 | 39 | 0.00092857 | 113 | 0.0026905 | 1.362 | A04 | MICL0.01407014/SDB
Build-In Floor | Mini Canal | MICL.01407014/SNA | 14 | 70 | 14 | 14 | 99 | 99 | 99 | 0.0023571 | 39 | 0.00092857 | 113 | 0.0026905 | 1.362 | A04 | MICL0.01407014/SNA
Build-In Floor | Mini Canal | MICL.01407014/SNC | 14 | 70 | 14 | 14 | 99 | 99 | 99 | 0.0023571 | 39 | 0.00092857 | 113 | 0.0026905 | 1.362 | A04 | MICL0.01407014/SNC
Build-In Floor | Mini Canal | MICL.01407026/ANA | 14 | 70 | 26 | 26 | 129 | 129 | 129 | 0.0030714 | 50 | 0.0011905 | 147 | 0.0035 | 1.362 | A04 | MICL0.01407026/ANA
Build-In Floor | Mini Canal | MICL.01407026/DBL | 14 | 70 | 26 | 26 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.01407026/DBL
Build-In Floor | Mini Canal | MICL.01407026/DBN | 14 | 70 | 26 | 26 | 160 | 160 | 160 | 0.0038095 | 62 | 0.0014762 | 182 | 0.0043333 | 1.362 | A04 | MICL0.01407026/DBN
Build-In Floor | Mini Canal | MICL.01407026/DBR | 14 | 70 | 26 | 26 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.01407026/DBR
Build-In Floor | Mini Canal | MICL.01407026/DBV | 14 | 70 | 26 | 26 | 160 | 160 | 160 | 0.0038095 | 62 | 0.0014762 | 182 | 0.0043333 | 1.362 | A04 | MICL0.01407026/DBV
Build-In Floor | Mini Canal | MICL.01407026/DDB | 14 | 70 | 26 | 26 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.01407026/DDB
Build-In Floor | Mini Canal | MICL.01407026/DMN | 14 | 70 | 26 | 26 | 160 | 160 | 160 | 0.0038095 | 62 | 0.0014762 | 182 | 0.0043333 | 1.362 | A04 | MICL0.01407026/DMN
Build-In Floor | Mini Canal | MICL.01407026/DMV | 14 | 70 | 26 | 26 | 160 | 160 | 160 | 0.0038095 | 62 | 0.0014762 | 182 | 0.0043333 | 1.362 | A04 | MICL0.01407026/DMV
Build-In Floor | Mini Canal | MICL.01407026/DNA | 14 | 70 | 26 | 26 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.01407026/DNA
Build-In Floor | Mini Canal | MICL.01407026/DNC | 14 | 70 | 26 | 26 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.01407026/DNC
Build-In Floor | Mini Canal | MICL.01407026/DON | 14 | 70 | 26 | 26 | 160 | 160 | 160 | 0.0038095 | 62 | 0.0014762 | 182 | 0.0043333 | 1.362 | A04 | MICL0.01407026/DON
Build-In Floor | Mini Canal | MICL.01407026/DOV | 14 | 70 | 26 | 26 | 160 | 160 | 160 | 0.0038095 | 62 | 0.0014762 | 182 | 0.0043333 | 1.362 | A04 | MICL0.01407026/DOV
Build-In Floor | Mini Canal | MICL.01407026/PNC | 14 | 70 | 26 | 26 | 146 | 146 | 146 | 0.0034762 | 57 | 0.0013571 | 166 | 0.0039524 | 1.362 | A04 | MICL0.01407026/PNC
Build-In Floor | Mini Canal | MICL.01407026/RBL | 14 | 70 | 26 | 26 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.01407026/RBL
Build-In Floor | Mini Canal | MICL.01407026/RBN | 14 | 70 | 26 | 26 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.01407026/RBN
Build-In Floor | Mini Canal | MICL.01407026/RBR | 14 | 70 | 26 | 26 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.01407026/RBR
Build-In Floor | Mini Canal | MICL.01407026/RBV | 14 | 70 | 26 | 26 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.01407026/RBV
Build-In Floor | Mini Canal | MICL.01407026/RDB | 14 | 70 | 26 | 26 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.01407026/RDB
Build-In Floor | Mini Canal | MICL.01407026/RMN | 14 | 70 | 26 | 26 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.01407026/RMN
Build-In Floor | Mini Canal | MICL.01407026/RMV | 14 | 70 | 26 | 26 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.01407026/RMV
Build-In Floor | Mini Canal | MICL.01407026/RNA | 14 | 70 | 26 | 26 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.01407026/RNA
Build-In Floor | Mini Canal | MICL.01407026/RON | 14 | 70 | 26 | 26 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.01407026/RON
Build-In Floor | Mini Canal | MICL.01407026/ROV | 14 | 70 | 26 | 26 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.01407026/ROV
Build-In Floor | Mini Canal | MICL.01407026/RSS | 14 | 70 | 26 | 26 | 165 | 165 | 165 | 0.0039286 | 64 | 0.0015238 | 188 | 0.0044762 | 1.362 | A04 | MICL0.01407026/RSS
Build-In Floor | Mini Canal | MICL.01407026/SBL | 14 | 70 | 26 | 26 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.01407026/SBL
Build-In Floor | Mini Canal | MICL.01407026/SBR | 14 | 70 | 26 | 26 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.01407026/SBR
Build-In Floor | Mini Canal | MICL.01407026/SDB | 14 | 70 | 26 | 26 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.01407026/SDB
Build-In Floor | Mini Canal | MICL.01407026/SNA | 14 | 70 | 26 | 26 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.01407026/SNA
Build-In Floor | Mini Canal | MICL.01407026/SNC | 14 | 70 | 26 | 26 | 172 | 172 | 172 | 0.0040952 | 67 | 0.0015952 | 196 | 0.0046667 | 1.362 | A04 | MICL0.01407026/SNC
Build-In Floor | Mini Canal | MICL.01407034/ANA | 14 | 70 | 34 | 34 | 176 | 176 | 176 | 0.0041905 | 68 | 0.001619 | 200 | 0.0047619 | 1.362 | A04 | MICL0.01407034/ANA
Build-In Floor | Mini Canal | MICL.01407034/DBL | 14 | 70 | 34 | 34 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01407034/DBL
Build-In Floor | Mini Canal | MICL.01407034/DBN | 14 | 70 | 34 | 34 | 219 | 219 | 219 | 0.0052143 | 85 | 0.0020238 | 249 | 0.0059286 | 1.362 | A04 | MICL0.01407034/DBN
Build-In Floor | Mini Canal | MICL.01407034/DBR | 14 | 70 | 34 | 34 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01407034/DBR
Build-In Floor | Mini Canal | MICL.01407034/DBV | 14 | 70 | 34 | 34 | 219 | 219 | 219 | 0.0052143 | 85 | 0.0020238 | 249 | 0.0059286 | 1.362 | A04 | MICL0.01407034/DBV
Build-In Floor | Mini Canal | MICL.01407034/DDB | 14 | 70 | 34 | 34 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01407034/DDB
Build-In Floor | Mini Canal | MICL.01407034/DMN | 14 | 70 | 34 | 34 | 219 | 219 | 219 | 0.0052143 | 85 | 0.0020238 | 249 | 0.0059286 | 1.362 | A04 | MICL0.01407034/DMN
Build-In Floor | Mini Canal | MICL.01407034/DMV | 14 | 70 | 34 | 34 | 219 | 219 | 219 | 0.0052143 | 85 | 0.0020238 | 249 | 0.0059286 | 1.362 | A04 | MICL0.01407034/DMV
Build-In Floor | Mini Canal | MICL.01407034/DNA | 14 | 70 | 34 | 34 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01407034/DNA
Build-In Floor | Mini Canal | MICL.01407034/DNC | 14 | 70 | 34 | 34 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01407034/DNC
Build-In Floor | Mini Canal | MICL.01407034/DON | 14 | 70 | 34 | 34 | 219 | 219 | 219 | 0.0052143 | 85 | 0.0020238 | 249 | 0.0059286 | 1.362 | A04 | MICL0.01407034/DON
Build-In Floor | Mini Canal | MICL.01407034/DOV | 14 | 70 | 34 | 34 | 219 | 219 | 219 | 0.0052143 | 85 | 0.0020238 | 249 | 0.0059286 | 1.362 | A04 | MICL0.01407034/DOV
Build-In Floor | Mini Canal | MICL.01407034/PNC | 14 | 70 | 34 | 34 | 200 | 200 | 200 | 0.0047619 | 78 | 0.0018571 | 228 | 0.0054286 | 1.362 | A04 | MICL0.01407034/PNC
Build-In Floor | Mini Canal | MICL.01407034/RBL | 14 | 70 | 34 | 34 | 235 | 235 | 235 | 0.0055952 | 91 | 0.0021667 | 268 | 0.006381 | 1.362 | A04 | MICL0.01407034/RBL
Build-In Floor | Mini Canal | MICL.01407034/RBN | 14 | 70 | 34 | 34 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01407034/RBN
Build-In Floor | Mini Canal | MICL.01407034/RBR | 14 | 70 | 34 | 34 | 235 | 235 | 235 | 0.0055952 | 91 | 0.0021667 | 268 | 0.006381 | 1.362 | A04 | MICL0.01407034/RBR
Build-In Floor | Mini Canal | MICL.01407034/RBV | 14 | 70 | 34 | 34 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01407034/RBV
Build-In Floor | Mini Canal | MICL.01407034/RDB | 14 | 70 | 34 | 34 | 235 | 235 | 235 | 0.0055952 | 91 | 0.0021667 | 268 | 0.006381 | 1.362 | A04 | MICL0.01407034/RDB
Build-In Floor | Mini Canal | MICL.01407034/RMN | 14 | 70 | 34 | 34 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01407034/RMN
Build-In Floor | Mini Canal | MICL.01407034/RMV | 14 | 70 | 34 | 34 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01407034/RMV
Build-In Floor | Mini Canal | MICL.01407034/RNA | 14 | 70 | 34 | 34 | 235 | 235 | 235 | 0.0055952 | 91 | 0.0021667 | 268 | 0.006381 | 1.362 | A04 | MICL0.01407034/RNA
Build-In Floor | Mini Canal | MICL.01407034/RON | 14 | 70 | 34 | 34 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01407034/RON
Build-In Floor | Mini Canal | MICL.01407034/ROV | 14 | 70 | 34 | 34 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01407034/ROV
Build-In Floor | Mini Canal | MICL.01407034/RSS | 14 | 70 | 34 | 34 | 226 | 226 | 226 | 0.005381 | 88 | 0.0020952 | 257 | 0.006119 | 1.362 | A04 | MICL0.01407034/RSS
Build-In Floor | Mini Canal | MICL.01407034/SBL | 14 | 70 | 34 | 34 | 235 | 235 | 235 | 0.0055952 | 91 | 0.0021667 | 268 | 0.006381 | 1.362 | A04 | MICL0.01407034/SBL
Build-In Floor | Mini Canal | MICL.01407034/SBR | 14 | 70 | 34 | 34 | 235 | 235 | 235 | 0.0055952 | 91 | 0.0021667 | 268 | 0.006381 | 1.362 | A04 | MICL0.01407034/SBR
Build-In Floor | Mini Canal | MICL.01407034/SDB | 14 | 70 | 34 | 34 | 235 | 235 | 235 | 0.0055952 | 91 | 0.0021667 | 268 | 0.006381 | 1.362 | A04 | MICL0.01407034/SDB
Build-In Floor | Mini Canal | MICL.01407034/SNA | 14 | 70 | 34 | 34 | 235 | 235 | 235 | 0.0055952 | 91 | 0.0021667 | 268 | 0.006381 | 1.362 | A04 | MICL0.01407034/SNA
Build-In Floor | Mini Canal | MICL.01407034/SNC | 14 | 70 | 34 | 34 | 235 | 235 | 235 | 0.0055952 | 91 | 0.0021667 | 268 | 0.006381 | 1.362 | A04 | MICL0.01407034/SNC
Build-In Floor | Mini Canal | MICL.01407042/ANA | 14 | 70 | 42 | 42 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01407042/ANA
Build-In Floor | Mini Canal | MICL.01407042/DBL | 14 | 70 | 42 | 42 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01407042/DBL
Build-In Floor | Mini Canal | MICL.01407042/DBN | 14 | 70 | 42 | 42 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.01407042/DBN
Build-In Floor | Mini Canal | MICL.01407042/DBR | 14 | 70 | 42 | 42 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01407042/DBR
Build-In Floor | Mini Canal | MICL.01407042/DBV | 14 | 70 | 42 | 42 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.01407042/DBV
Build-In Floor | Mini Canal | MICL.01407042/DDB | 14 | 70 | 42 | 42 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01407042/DDB
Build-In Floor | Mini Canal | MICL.01407042/DMN | 14 | 70 | 42 | 42 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.01407042/DMN
Build-In Floor | Mini Canal | MICL.01407042/DMV | 14 | 70 | 42 | 42 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.01407042/DMV
Build-In Floor | Mini Canal | MICL.01407042/DNA | 14 | 70 | 42 | 42 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01407042/DNA
Build-In Floor | Mini Canal | MICL.01407042/DNC | 14 | 70 | 42 | 42 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01407042/DNC
Build-In Floor | Mini Canal | MICL.01407042/DON | 14 | 70 | 42 | 42 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.01407042/DON
Build-In Floor | Mini Canal | MICL.01407042/DOV | 14 | 70 | 42 | 42 | 295 | 295 | 295 | 0.0070238 | 115 | 0.0027381 | 336 | 0.008 | 1.362 | A04 | MICL0.01407042/DOV
Build-In Floor | Mini Canal | MICL.01407042/PNC | 14 | 70 | 42 | 42 | 269 | 269 | 269 | 0.0064048 | 105 | 0.0025 | 306 | 0.0072857 | 1.362 | A04 | MICL0.01407042/PNC
Build-In Floor | Mini Canal | MICL.01407042/RBL | 14 | 70 | 42 | 42 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01407042/RBL
Build-In Floor | Mini Canal | MICL.01407042/RBN | 14 | 70 | 42 | 42 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01407042/RBN
Build-In Floor | Mini Canal | MICL.01407042/RBR | 14 | 70 | 42 | 42 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01407042/RBR
Build-In Floor | Mini Canal | MICL.01407042/RBV | 14 | 70 | 42 | 42 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01407042/RBV
Build-In Floor | Mini Canal | MICL.01407042/RDB | 14 | 70 | 42 | 42 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01407042/RDB
Build-In Floor | Mini Canal | MICL.01407042/RMN | 14 | 70 | 42 | 42 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01407042/RMN
Build-In Floor | Mini Canal | MICL.01407042/RMV | 14 | 70 | 42 | 42 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01407042/RMV
Build-In Floor | Mini Canal | MICL.01407042/RNA | 14 | 70 | 42 | 42 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01407042/RNA
Build-In Floor | Mini Canal | MICL.01407042/RON | 14 | 70 | 42 | 42 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01407042/RON
Build-In Floor | Mini Canal | MICL.01407042/ROV | 14 | 70 | 42 | 42 | 307 | 307 | 307 | 0.0073095 | 119 | 0.0028333 | 350 | 0.0083333 | 1.362 | A04 | MICL0.01407042/ROV
Build-In Floor | Mini Canal | MICL.01407042/RSS | 14 | 70 | 42 | 42 | 304 | 304 | 304 | 0.0072381 | 118 | 0.0028095 | 346 | 0.0082381 | 1.362 | A04 | MICL0.01407042/RSS
Build-In Floor | Mini Canal | MICL.01407042/SBL | 14 | 70 | 42 | 42 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01407042/SBL
Build-In Floor | Mini Canal | MICL.01407042/SBR | 14 | 70 | 42 | 42 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01407042/SBR
Build-In Floor | Mini Canal | MICL.01407042/SDB | 14 | 70 | 42 | 42 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01407042/SDB
Build-In Floor | Mini Canal | MICL.01407042/SNA | 14 | 70 | 42 | 42 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01407042/SNA
Build-In Floor | Mini Canal | MICL.01407042/SNC | 14 | 70 | 42 | 42 | 317 | 317 | 317 | 0.0075476 | 123 | 0.0029286 | 361 | 0.0085952 | 1.362 | A04 | MICL0.01407042/SNC
Build-In Floor | Mini Canal | MICL.01408014/ANA | 14 | 80 | 14 | 14 | 93 | 93 | 93 | 0.0022143 | 36 | 0.00085714 | 106 | 0.0025238 | 1.362 | A04 | MICL0.01408014/ANA
Build-In Floor | Mini Canal | MICL.01408014/DBL | 14 | 80 | 14 | 14 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01408014/DBL
Build-In Floor | Mini Canal | MICL.01408014/DBN | 14 | 80 | 14 | 14 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.01408014/DBN
Build-In Floor | Mini Canal | MICL.01408014/DBR | 14 | 80 | 14 | 14 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01408014/DBR
Build-In Floor | Mini Canal | MICL.01408014/DBV | 14 | 80 | 14 | 14 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.01408014/DBV
Build-In Floor | Mini Canal | MICL.01408014/DDB | 14 | 80 | 14 | 14 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01408014/DDB
Build-In Floor | Mini Canal | MICL.01408014/DMN | 14 | 80 | 14 | 14 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.01408014/DMN
Build-In Floor | Mini Canal | MICL.01408014/DMV | 14 | 80 | 14 | 14 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.01408014/DMV
Build-In Floor | Mini Canal | MICL.01408014/DNA | 14 | 80 | 14 | 14 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01408014/DNA
Build-In Floor | Mini Canal | MICL.01408014/DNC | 14 | 80 | 14 | 14 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01408014/DNC
Build-In Floor | Mini Canal | MICL.01408014/DON | 14 | 80 | 14 | 14 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.01408014/DON
Build-In Floor | Mini Canal | MICL.01408014/DOV | 14 | 80 | 14 | 14 | 115 | 115 | 115 | 0.0027381 | 45 | 0.0010714 | 131 | 0.003119 | 1.362 | A04 | MICL0.01408014/DOV
Build-In Floor | Mini Canal | MICL.01408014/RBL | 14 | 80 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.01408014/RBL
Build-In Floor | Mini Canal | MICL.01408014/RBN | 14 | 80 | 14 | 14 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01408014/RBN
Build-In Floor | Mini Canal | MICL.01408014/RBR | 14 | 80 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.01408014/RBR
Build-In Floor | Mini Canal | MICL.01408014/RBV | 14 | 80 | 14 | 14 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01408014/RBV
Build-In Floor | Mini Canal | MICL.01408014/RDB | 14 | 80 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.01408014/RDB
Build-In Floor | Mini Canal | MICL.01408014/RMN | 14 | 80 | 14 | 14 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01408014/RMN
Build-In Floor | Mini Canal | MICL.01408014/RMV | 14 | 80 | 14 | 14 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01408014/RMV
Build-In Floor | Mini Canal | MICL.01408014/RNA | 14 | 80 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.01408014/RNA
Build-In Floor | Mini Canal | MICL.01408014/RON | 14 | 80 | 14 | 14 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01408014/RON
Build-In Floor | Mini Canal | MICL.01408014/ROV | 14 | 80 | 14 | 14 | 120 | 120 | 120 | 0.0028571 | 47 | 0.001119 | 137 | 0.0032619 | 1.362 | A04 | MICL0.01408014/ROV
Build-In Floor | Mini Canal | MICL.01408014/RSS | 14 | 80 | 14 | 14 | 119 | 119 | 119 | 0.0028333 | 46 | 0.0010952 | 136 | 0.0032381 | 1.362 | A04 | MICL0.01408014/RSS
Build-In Floor | Mini Canal | MICL.01408014/SBL | 14 | 80 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.01408014/SBL
Build-In Floor | Mini Canal | MICL.01408014/SBR | 14 | 80 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.01408014/SBR
Build-In Floor | Mini Canal | MICL.01408014/SDB | 14 | 80 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.01408014/SDB
Build-In Floor | Mini Canal | MICL.01408014/SNA | 14 | 80 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.01408014/SNA
Build-In Floor | Mini Canal | MICL.01408014/SNC | 14 | 80 | 14 | 14 | 124 | 124 | 124 | 0.0029524 | 48 | 0.0011429 | 141 | 0.0033571 | 1.362 | A04 | MICL0.01408014/SNC
Build-In Floor | Mini Canal | MICL.01408026/ANA | 14 | 80 | 26 | 26 | 161 | 161 | 161 | 0.0038333 | 63 | 0.0015 | 183 | 0.0043571 | 1.362 | A04 | MICL0.01408026/ANA
Build-In Floor | Mini Canal | MICL.01408026/DBL | 14 | 80 | 26 | 26 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.01408026/DBL
Build-In Floor | Mini Canal | MICL.01408026/DBN | 14 | 80 | 26 | 26 | 200 | 200 | 200 | 0.0047619 | 78 | 0.0018571 | 228 | 0.0054286 | 1.362 | A04 | MICL0.01408026/DBN
Build-In Floor | Mini Canal | MICL.01408026/DBR | 14 | 80 | 26 | 26 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.01408026/DBR
Build-In Floor | Mini Canal | MICL.01408026/DBV | 14 | 80 | 26 | 26 | 200 | 200 | 200 | 0.0047619 | 78 | 0.0018571 | 228 | 0.0054286 | 1.362 | A04 | MICL0.01408026/DBV
Build-In Floor | Mini Canal | MICL.01408026/DDB | 14 | 80 | 26 | 26 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.01408026/DDB
Build-In Floor | Mini Canal | MICL.01408026/DMN | 14 | 80 | 26 | 26 | 200 | 200 | 200 | 0.0047619 | 78 | 0.0018571 | 228 | 0.0054286 | 1.362 | A04 | MICL0.01408026/DMN
Build-In Floor | Mini Canal | MICL.01408026/DMV | 14 | 80 | 26 | 26 | 200 | 200 | 200 | 0.0047619 | 78 | 0.0018571 | 228 | 0.0054286 | 1.362 | A04 | MICL0.01408026/DMV
Build-In Floor | Mini Canal | MICL.01408026/DNA | 14 | 80 | 26 | 26 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.01408026/DNA
Build-In Floor | Mini Canal | MICL.01408026/DNC | 14 | 80 | 26 | 26 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.01408026/DNC
Build-In Floor | Mini Canal | MICL.01408026/DON | 14 | 80 | 26 | 26 | 200 | 200 | 200 | 0.0047619 | 78 | 0.0018571 | 228 | 0.0054286 | 1.362 | A04 | MICL0.01408026/DON
Build-In Floor | Mini Canal | MICL.01408026/DOV | 14 | 80 | 26 | 26 | 200 | 200 | 200 | 0.0047619 | 78 | 0.0018571 | 228 | 0.0054286 | 1.362 | A04 | MICL0.01408026/DOV
Build-In Floor | Mini Canal | MICL.01408026/PNC | 14 | 80 | 26 | 26 | 183 | 183 | 183 | 0.0043571 | 71 | 0.0016905 | 208 | 0.0049524 | 1.362 | A04 | MICL0.01408026/PNC
Build-In Floor | Mini Canal | MICL.01408026/RBL | 14 | 80 | 26 | 26 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.01408026/RBL
Build-In Floor | Mini Canal | MICL.01408026/RBN | 14 | 80 | 26 | 26 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.01408026/RBN
Build-In Floor | Mini Canal | MICL.01408026/RBR | 14 | 80 | 26 | 26 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.01408026/RBR
Build-In Floor | Mini Canal | MICL.01408026/RBV | 14 | 80 | 26 | 26 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.01408026/RBV
Build-In Floor | Mini Canal | MICL.01408026/RDB | 14 | 80 | 26 | 26 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.01408026/RDB
Build-In Floor | Mini Canal | MICL.01408026/RMN | 14 | 80 | 26 | 26 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.01408026/RMN
Build-In Floor | Mini Canal | MICL.01408026/RMV | 14 | 80 | 26 | 26 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.01408026/RMV
Build-In Floor | Mini Canal | MICL.01408026/RNA | 14 | 80 | 26 | 26 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.01408026/RNA
Build-In Floor | Mini Canal | MICL.01408026/RON | 14 | 80 | 26 | 26 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.01408026/RON
Build-In Floor | Mini Canal | MICL.01408026/ROV | 14 | 80 | 26 | 26 | 209 | 209 | 209 | 0.0049762 | 81 | 0.0019286 | 238 | 0.0056667 | 1.362 | A04 | MICL0.01408026/ROV
Build-In Floor | Mini Canal | MICL.01408026/RSS | 14 | 80 | 26 | 26 | 206 | 206 | 206 | 0.0049048 | 80 | 0.0019048 | 235 | 0.0055952 | 1.362 | A04 | MICL0.01408026/RSS
Build-In Floor | Mini Canal | MICL.01408026/SBL | 14 | 80 | 26 | 26 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.01408026/SBL
Build-In Floor | Mini Canal | MICL.01408026/SBR | 14 | 80 | 26 | 26 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.01408026/SBR
Build-In Floor | Mini Canal | MICL.01408026/SDB | 14 | 80 | 26 | 26 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.01408026/SDB
Build-In Floor | Mini Canal | MICL.01408026/SNA | 14 | 80 | 26 | 26 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.01408026/SNA
Build-In Floor | Mini Canal | MICL.01408026/SNC | 14 | 80 | 26 | 26 | 215 | 215 | 215 | 0.005119 | 84 | 0.002 | 245 | 0.0058333 | 1.362 | A04 | MICL0.01408026/SNC
Build-In Floor | Mini Canal | MICL.01408034/ANA | 14 | 80 | 34 | 34 | 221 | 221 | 221 | 0.0052619 | 86 | 0.0020476 | 252 | 0.006 | 1.362 | A04 | MICL0.01408034/ANA
Build-In Floor | Mini Canal | MICL.01408034/DBL | 14 | 80 | 34 | 34 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01408034/DBL
Build-In Floor | Mini Canal | MICL.01408034/DBN | 14 | 80 | 34 | 34 | 273 | 273 | 273 | 0.0065 | 106 | 0.0025238 | 311 | 0.0074048 | 1.362 | A04 | MICL0.01408034/DBN
Build-In Floor | Mini Canal | MICL.01408034/DBR | 14 | 80 | 34 | 34 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01408034/DBR
Build-In Floor | Mini Canal | MICL.01408034/DBV | 14 | 80 | 34 | 34 | 273 | 273 | 273 | 0.0065 | 106 | 0.0025238 | 311 | 0.0074048 | 1.362 | A04 | MICL0.01408034/DBV
Build-In Floor | Mini Canal | MICL.01408034/DDB | 14 | 80 | 34 | 34 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01408034/DDB
Build-In Floor | Mini Canal | MICL.01408034/DMN | 14 | 80 | 34 | 34 | 273 | 273 | 273 | 0.0065 | 106 | 0.0025238 | 311 | 0.0074048 | 1.362 | A04 | MICL0.01408034/DMN
Build-In Floor | Mini Canal | MICL.01408034/DMV | 14 | 80 | 34 | 34 | 273 | 273 | 273 | 0.0065 | 106 | 0.0025238 | 311 | 0.0074048 | 1.362 | A04 | MICL0.01408034/DMV
Build-In Floor | Mini Canal | MICL.01408034/DNA | 14 | 80 | 34 | 34 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01408034/DNA
Build-In Floor | Mini Canal | MICL.01408034/DNC | 14 | 80 | 34 | 34 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01408034/DNC
Build-In Floor | Mini Canal | MICL.01408034/DON | 14 | 80 | 34 | 34 | 273 | 273 | 273 | 0.0065 | 106 | 0.0025238 | 311 | 0.0074048 | 1.362 | A04 | MICL0.01408034/DON
Build-In Floor | Mini Canal | MICL.01408034/DOV | 14 | 80 | 34 | 34 | 273 | 273 | 273 | 0.0065 | 106 | 0.0025238 | 311 | 0.0074048 | 1.362 | A04 | MICL0.01408034/DOV
Build-In Floor | Mini Canal | MICL.01408034/PNC | 14 | 80 | 34 | 34 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.01408034/PNC
Build-In Floor | Mini Canal | MICL.01408034/RBL | 14 | 80 | 34 | 34 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.01408034/RBL
Build-In Floor | Mini Canal | MICL.01408034/RBN | 14 | 80 | 34 | 34 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01408034/RBN
Build-In Floor | Mini Canal | MICL.01408034/RBR | 14 | 80 | 34 | 34 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.01408034/RBR
Build-In Floor | Mini Canal | MICL.01408034/RBV | 14 | 80 | 34 | 34 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01408034/RBV
Build-In Floor | Mini Canal | MICL.01408034/RDB | 14 | 80 | 34 | 34 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.01408034/RDB
Build-In Floor | Mini Canal | MICL.01408034/RMN | 14 | 80 | 34 | 34 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01408034/RMN
Build-In Floor | Mini Canal | MICL.01408034/RMV | 14 | 80 | 34 | 34 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01408034/RMV
Build-In Floor | Mini Canal | MICL.01408034/RNA | 14 | 80 | 34 | 34 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.01408034/RNA
Build-In Floor | Mini Canal | MICL.01408034/RON | 14 | 80 | 34 | 34 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01408034/RON
Build-In Floor | Mini Canal | MICL.01408034/ROV | 14 | 80 | 34 | 34 | 285 | 285 | 285 | 0.0067857 | 111 | 0.0026429 | 325 | 0.0077381 | 1.362 | A04 | MICL0.01408034/ROV
Build-In Floor | Mini Canal | MICL.01408034/RSS | 14 | 80 | 34 | 34 | 282 | 282 | 282 | 0.0067143 | 110 | 0.002619 | 321 | 0.0076429 | 1.362 | A04 | MICL0.01408034/RSS
Build-In Floor | Mini Canal | MICL.01408034/SBL | 14 | 80 | 34 | 34 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.01408034/SBL
Build-In Floor | Mini Canal | MICL.01408034/SBR | 14 | 80 | 34 | 34 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.01408034/SBR
Build-In Floor | Mini Canal | MICL.01408034/SDB | 14 | 80 | 34 | 34 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.01408034/SDB
Build-In Floor | Mini Canal | MICL.01408034/SNA | 14 | 80 | 34 | 34 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.01408034/SNA
Build-In Floor | Mini Canal | MICL.01408034/SNC | 14 | 80 | 34 | 34 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.01408034/SNC
Build-In Floor | Mini Canal | MICL.01408042/ANA | 14 | 80 | 42 | 42 | 297 | 297 | 297 | 0.0070714 | 116 | 0.0027619 | 338 | 0.0080476 | 1.362 | A04 | MICL0.01408042/ANA
Build-In Floor | Mini Canal | MICL.01408042/DBL | 14 | 80 | 42 | 42 | 384 | 384 | 384 | 0.0091429 | 149 | 0.0035476 | 437 | 0.010405 | 1.362 | A04 | MICL0.01408042/DBL
Build-In Floor | Mini Canal | MICL.01408042/DBN | 14 | 80 | 42 | 42 | 368 | 368 | 368 | 0.0087619 | 143 | 0.0034048 | 419 | 0.0099762 | 1.362 | A04 | MICL0.01408042/DBN
Build-In Floor | Mini Canal | MICL.01408042/DBR | 14 | 80 | 42 | 42 | 384 | 384 | 384 | 0.0091429 | 149 | 0.0035476 | 437 | 0.010405 | 1.362 | A04 | MICL0.01408042/DBR
Build-In Floor | Mini Canal | MICL.01408042/DBV | 14 | 80 | 42 | 42 | 368 | 368 | 368 | 0.0087619 | 143 | 0.0034048 | 419 | 0.0099762 | 1.362 | A04 | MICL0.01408042/DBV
Build-In Floor | Mini Canal | MICL.01408042/DDB | 14 | 80 | 42 | 42 | 384 | 384 | 384 | 0.0091429 | 149 | 0.0035476 | 437 | 0.010405 | 1.362 | A04 | MICL0.01408042/DDB
Build-In Floor | Mini Canal | MICL.01408042/DMN | 14 | 80 | 42 | 42 | 368 | 368 | 368 | 0.0087619 | 143 | 0.0034048 | 419 | 0.0099762 | 1.362 | A04 | MICL0.01408042/DMN
Build-In Floor | Mini Canal | MICL.01408042/DMV | 14 | 80 | 42 | 42 | 368 | 368 | 368 | 0.0087619 | 143 | 0.0034048 | 419 | 0.0099762 | 1.362 | A04 | MICL0.01408042/DMV
Build-In Floor | Mini Canal | MICL.01408042/DNA | 14 | 80 | 42 | 42 | 384 | 384 | 384 | 0.0091429 | 149 | 0.0035476 | 437 | 0.010405 | 1.362 | A04 | MICL0.01408042/DNA
Build-In Floor | Mini Canal | MICL.01408042/DNC | 14 | 80 | 42 | 42 | 384 | 384 | 384 | 0.0091429 | 149 | 0.0035476 | 437 | 0.010405 | 1.362 | A04 | MICL0.01408042/DNC
Build-In Floor | Mini Canal | MICL.01408042/DON | 14 | 80 | 42 | 42 | 368 | 368 | 368 | 0.0087619 | 143 | 0.0034048 | 419 | 0.0099762 | 1.362 | A04 | MICL0.01408042/DON
Build-In Floor | Mini Canal | MICL.01408042/DOV | 14 | 80 | 42 | 42 | 368 | 368 | 368 | 0.0087619 | 143 | 0.0034048 | 419 | 0.0099762 | 1.362 | A04 | MICL0.01408042/DOV
Build-In Floor | Mini Canal | MICL.01408042/PNC | 14 | 80 | 42 | 42 | 337 | 337 | 337 | 0.0080238 | 131 | 0.003119 | 384 | 0.0091429 | 1.362 | A04 | MICL0.01408042/PNC
Build-In Floor | Mini Canal | MICL.01408042/RBL | 14 | 80 | 42 | 42 | 396 | 396 | 396 | 0.0094286 | 154 | 0.0036667 | 451 | 0.010738 | 1.362 | A04 | MICL0.01408042/RBL
Build-In Floor | Mini Canal | MICL.01408042/RBN | 14 | 80 | 42 | 42 | 384 | 384 | 384 | 0.0091429 | 149 | 0.0035476 | 437 | 0.010405 | 1.362 | A04 | MICL0.01408042/RBN
Build-In Floor | Mini Canal | MICL.01408042/RBR | 14 | 80 | 42 | 42 | 396 | 396 | 396 | 0.0094286 | 154 | 0.0036667 | 451 | 0.010738 | 1.362 | A04 | MICL0.01408042/RBR
Build-In Floor | Mini Canal | MICL.01408042/RBV | 14 | 80 | 42 | 42 | 384 | 384 | 384 | 0.0091429 | 149 | 0.0035476 | 437 | 0.010405 | 1.362 | A04 | MICL0.01408042/RBV
Build-In Floor | Mini Canal | MICL.01408042/RDB | 14 | 80 | 42 | 42 | 396 | 396 | 396 | 0.0094286 | 154 | 0.0036667 | 451 | 0.010738 | 1.362 | A04 | MICL0.01408042/RDB
Build-In Floor | Mini Canal | MICL.01408042/RMN | 14 | 80 | 42 | 42 | 384 | 384 | 384 | 0.0091429 | 149 | 0.0035476 | 437 | 0.010405 | 1.362 | A04 | MICL0.01408042/RMN
Build-In Floor | Mini Canal | MICL.01408042/RMV | 14 | 80 | 42 | 42 | 384 | 384 | 384 | 0.0091429 | 149 | 0.0035476 | 437 | 0.010405 | 1.362 | A04 | MICL0.01408042/RMV
Build-In Floor | Mini Canal | MICL.01408042/RNA | 14 | 80 | 42 | 42 | 396 | 396 | 396 | 0.0094286 | 154 | 0.0036667 | 451 | 0.010738 | 1.362 | A04 | MICL0.01408042/RNA
Build-In Floor | Mini Canal | MICL.01408042/RON | 14 | 80 | 42 | 42 | 384 | 384 | 384 | 0.0091429 | 149 | 0.0035476 | 437 | 0.010405 | 1.362 | A04 | MICL0.01408042/RON
Build-In Floor | Mini Canal | MICL.01408042/ROV | 14 | 80 | 42 | 42 | 384 | 384 | 384 | 0.0091429 | 149 | 0.0035476 | 437 | 0.010405 | 1.362 | A04 | MICL0.01408042/ROV
Build-In Floor | Mini Canal | MICL.01408042/RSS | 14 | 80 | 42 | 42 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01408042/RSS
Build-In Floor | Mini Canal | MICL.01408042/SBL | 14 | 80 | 42 | 42 | 396 | 396 | 396 | 0.0094286 | 154 | 0.0036667 | 451 | 0.010738 | 1.362 | A04 | MICL0.01408042/SBL
Build-In Floor | Mini Canal | MICL.01408042/SBR | 14 | 80 | 42 | 42 | 396 | 396 | 396 | 0.0094286 | 154 | 0.0036667 | 451 | 0.010738 | 1.362 | A04 | MICL0.01408042/SBR
Build-In Floor | Mini Canal | MICL.01408042/SDB | 14 | 80 | 42 | 42 | 396 | 396 | 396 | 0.0094286 | 154 | 0.0036667 | 451 | 0.010738 | 1.362 | A04 | MICL0.01408042/SDB
Build-In Floor | Mini Canal | MICL.01408042/SNA | 14 | 80 | 42 | 42 | 396 | 396 | 396 | 0.0094286 | 154 | 0.0036667 | 451 | 0.010738 | 1.362 | A04 | MICL0.01408042/SNA
Build-In Floor | Mini Canal | MICL.01408042/SNC | 14 | 80 | 42 | 42 | 396 | 396 | 396 | 0.0094286 | 154 | 0.0036667 | 451 | 0.010738 | 1.362 | A04 | MICL0.01408042/SNC
Build-In Floor | Mini Canal | MICL.01409014/ANA | 14 | 90 | 14 | 14 | 112 | 112 | 112 | 0.0026667 | 44 | 0.0010476 | 128 | 0.0030476 | 1.362 | A04 | MICL0.01409014/ANA
Build-In Floor | Mini Canal | MICL.01409014/DBL | 14 | 90 | 14 | 14 | 145 | 145 | 145 | 0.0034524 | 56 | 0.0013333 | 165 | 0.0039286 | 1.362 | A04 | MICL0.01409014/DBL
Build-In Floor | Mini Canal | MICL.01409014/DBN | 14 | 90 | 14 | 14 | 139 | 139 | 139 | 0.0033095 | 54 | 0.0012857 | 158 | 0.0037619 | 1.362 | A04 | MICL0.01409014/DBN
Build-In Floor | Mini Canal | MICL.01409014/DBR | 14 | 90 | 14 | 14 | 145 | 145 | 145 | 0.0034524 | 56 | 0.0013333 | 165 | 0.0039286 | 1.362 | A04 | MICL0.01409014/DBR
Build-In Floor | Mini Canal | MICL.01409014/DBV | 14 | 90 | 14 | 14 | 139 | 139 | 139 | 0.0033095 | 54 | 0.0012857 | 158 | 0.0037619 | 1.362 | A04 | MICL0.01409014/DBV
Build-In Floor | Mini Canal | MICL.01409014/DDB | 14 | 90 | 14 | 14 | 145 | 145 | 145 | 0.0034524 | 56 | 0.0013333 | 165 | 0.0039286 | 1.362 | A04 | MICL0.01409014/DDB
Build-In Floor | Mini Canal | MICL.01409014/DMN | 14 | 90 | 14 | 14 | 139 | 139 | 139 | 0.0033095 | 54 | 0.0012857 | 158 | 0.0037619 | 1.362 | A04 | MICL0.01409014/DMN
Build-In Floor | Mini Canal | MICL.01409014/DMV | 14 | 90 | 14 | 14 | 139 | 139 | 139 | 0.0033095 | 54 | 0.0012857 | 158 | 0.0037619 | 1.362 | A04 | MICL0.01409014/DMV
Build-In Floor | Mini Canal | MICL.01409014/DNA | 14 | 90 | 14 | 14 | 145 | 145 | 145 | 0.0034524 | 56 | 0.0013333 | 165 | 0.0039286 | 1.362 | A04 | MICL0.01409014/DNA
Build-In Floor | Mini Canal | MICL.01409014/DNC | 14 | 90 | 14 | 14 | 145 | 145 | 145 | 0.0034524 | 56 | 0.0013333 | 165 | 0.0039286 | 1.362 | A04 | MICL0.01409014/DNC
Build-In Floor | Mini Canal | MICL.01409014/DON | 14 | 90 | 14 | 14 | 139 | 139 | 139 | 0.0033095 | 54 | 0.0012857 | 158 | 0.0037619 | 1.362 | A04 | MICL0.01409014/DON
Build-In Floor | Mini Canal | MICL.01409014/DOV | 14 | 90 | 14 | 14 | 139 | 139 | 139 | 0.0033095 | 54 | 0.0012857 | 158 | 0.0037619 | 1.362 | A04 | MICL0.01409014/DOV
Build-In Floor | Mini Canal | MICL.01409014/RBL | 14 | 90 | 14 | 14 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.01409014/RBL
Build-In Floor | Mini Canal | MICL.01409014/RBN | 14 | 90 | 14 | 14 | 145 | 145 | 145 | 0.0034524 | 56 | 0.0013333 | 165 | 0.0039286 | 1.362 | A04 | MICL0.01409014/RBN
Build-In Floor | Mini Canal | MICL.01409014/RBR | 14 | 90 | 14 | 14 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.01409014/RBR
Build-In Floor | Mini Canal | MICL.01409014/RBV | 14 | 90 | 14 | 14 | 145 | 145 | 145 | 0.0034524 | 56 | 0.0013333 | 165 | 0.0039286 | 1.362 | A04 | MICL0.01409014/RBV
Build-In Floor | Mini Canal | MICL.01409014/RDB | 14 | 90 | 14 | 14 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.01409014/RDB
Build-In Floor | Mini Canal | MICL.01409014/RMN | 14 | 90 | 14 | 14 | 145 | 145 | 145 | 0.0034524 | 56 | 0.0013333 | 165 | 0.0039286 | 1.362 | A04 | MICL0.01409014/RMN
Build-In Floor | Mini Canal | MICL.01409014/RMV | 14 | 90 | 14 | 14 | 145 | 145 | 145 | 0.0034524 | 56 | 0.0013333 | 165 | 0.0039286 | 1.362 | A04 | MICL0.01409014/RMV
Build-In Floor | Mini Canal | MICL.01409014/RNA | 14 | 90 | 14 | 14 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.01409014/RNA
Build-In Floor | Mini Canal | MICL.01409014/RON | 14 | 90 | 14 | 14 | 145 | 145 | 145 | 0.0034524 | 56 | 0.0013333 | 165 | 0.0039286 | 1.362 | A04 | MICL0.01409014/RON
Build-In Floor | Mini Canal | MICL.01409014/ROV | 14 | 90 | 14 | 14 | 145 | 145 | 145 | 0.0034524 | 56 | 0.0013333 | 165 | 0.0039286 | 1.362 | A04 | MICL0.01409014/ROV
Build-In Floor | Mini Canal | MICL.01409014/RSS | 14 | 90 | 14 | 14 | 143 | 143 | 143 | 0.0034048 | 56 | 0.0013333 | 163 | 0.003881 | 1.362 | A04 | MICL0.01409014/RSS
Build-In Floor | Mini Canal | MICL.01409014/SBL | 14 | 90 | 14 | 14 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.01409014/SBL
Build-In Floor | Mini Canal | MICL.01409014/SBR | 14 | 90 | 14 | 14 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.01409014/SBR
Build-In Floor | Mini Canal | MICL.01409014/SDB | 14 | 90 | 14 | 14 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.01409014/SDB
Build-In Floor | Mini Canal | MICL.01409014/SNA | 14 | 90 | 14 | 14 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.01409014/SNA
Build-In Floor | Mini Canal | MICL.01409014/SNC | 14 | 90 | 14 | 14 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.01409014/SNC
Build-In Floor | Mini Canal | MICL.01409026/ANA | 14 | 90 | 26 | 26 | 194 | 194 | 194 | 0.004619 | 75 | 0.0017857 | 221 | 0.0052619 | 1.362 | A04 | MICL0.01409026/ANA
Build-In Floor | Mini Canal | MICL.01409026/DBL | 14 | 90 | 26 | 26 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.01409026/DBL
Build-In Floor | Mini Canal | MICL.01409026/DBN | 14 | 90 | 26 | 26 | 240 | 240 | 240 | 0.0057143 | 93 | 0.0022143 | 273 | 0.0065 | 1.362 | A04 | MICL0.01409026/DBN
Build-In Floor | Mini Canal | MICL.01409026/DBR | 14 | 90 | 26 | 26 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.01409026/DBR
Build-In Floor | Mini Canal | MICL.01409026/DBV | 14 | 90 | 26 | 26 | 240 | 240 | 240 | 0.0057143 | 93 | 0.0022143 | 273 | 0.0065 | 1.362 | A04 | MICL0.01409026/DBV
Build-In Floor | Mini Canal | MICL.01409026/DDB | 14 | 90 | 26 | 26 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.01409026/DDB
Build-In Floor | Mini Canal | MICL.01409026/DMN | 14 | 90 | 26 | 26 | 240 | 240 | 240 | 0.0057143 | 93 | 0.0022143 | 273 | 0.0065 | 1.362 | A04 | MICL0.01409026/DMN
Build-In Floor | Mini Canal | MICL.01409026/DMV | 14 | 90 | 26 | 26 | 240 | 240 | 240 | 0.0057143 | 93 | 0.0022143 | 273 | 0.0065 | 1.362 | A04 | MICL0.01409026/DMV
Build-In Floor | Mini Canal | MICL.01409026/DNA | 14 | 90 | 26 | 26 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.01409026/DNA
Build-In Floor | Mini Canal | MICL.01409026/DNC | 14 | 90 | 26 | 26 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.01409026/DNC
Build-In Floor | Mini Canal | MICL.01409026/DON | 14 | 90 | 26 | 26 | 240 | 240 | 240 | 0.0057143 | 93 | 0.0022143 | 273 | 0.0065 | 1.362 | A04 | MICL0.01409026/DON
Build-In Floor | Mini Canal | MICL.01409026/DOV | 14 | 90 | 26 | 26 | 240 | 240 | 240 | 0.0057143 | 93 | 0.0022143 | 273 | 0.0065 | 1.362 | A04 | MICL0.01409026/DOV
Build-In Floor | Mini Canal | MICL.01409026/PNC | 14 | 90 | 26 | 26 | 219 | 219 | 219 | 0.0052143 | 85 | 0.0020238 | 249 | 0.0059286 | 1.362 | A04 | MICL0.01409026/PNC
Build-In Floor | Mini Canal | MICL.01409026/RBL | 14 | 90 | 26 | 26 | 258 | 258 | 258 | 0.0061429 | 100 | 0.002381 | 294 | 0.007 | 1.362 | A04 | MICL0.01409026/RBL
Build-In Floor | Mini Canal | MICL.01409026/RBN | 14 | 90 | 26 | 26 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.01409026/RBN
Build-In Floor | Mini Canal | MICL.01409026/RBR | 14 | 90 | 26 | 26 | 258 | 258 | 258 | 0.0061429 | 100 | 0.002381 | 294 | 0.007 | 1.362 | A04 | MICL0.01409026/RBR
Build-In Floor | Mini Canal | MICL.01409026/RBV | 14 | 90 | 26 | 26 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.01409026/RBV
Build-In Floor | Mini Canal | MICL.01409026/RDB | 14 | 90 | 26 | 26 | 258 | 258 | 258 | 0.0061429 | 100 | 0.002381 | 294 | 0.007 | 1.362 | A04 | MICL0.01409026/RDB
Build-In Floor | Mini Canal | MICL.01409026/RMN | 14 | 90 | 26 | 26 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.01409026/RMN
Build-In Floor | Mini Canal | MICL.01409026/RMV | 14 | 90 | 26 | 26 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.01409026/RMV
Build-In Floor | Mini Canal | MICL.01409026/RNA | 14 | 90 | 26 | 26 | 258 | 258 | 258 | 0.0061429 | 100 | 0.002381 | 294 | 0.007 | 1.362 | A04 | MICL0.01409026/RNA
Build-In Floor | Mini Canal | MICL.01409026/RON | 14 | 90 | 26 | 26 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.01409026/RON
Build-In Floor | Mini Canal | MICL.01409026/ROV | 14 | 90 | 26 | 26 | 250 | 250 | 250 | 0.0059524 | 97 | 0.0023095 | 285 | 0.0067857 | 1.362 | A04 | MICL0.01409026/ROV
Build-In Floor | Mini Canal | MICL.01409026/RSS | 14 | 90 | 26 | 26 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.01409026/RSS
Build-In Floor | Mini Canal | MICL.01409026/SBL | 14 | 90 | 26 | 26 | 258 | 258 | 258 | 0.0061429 | 100 | 0.002381 | 294 | 0.007 | 1.362 | A04 | MICL0.01409026/SBL
Build-In Floor | Mini Canal | MICL.01409026/SBR | 14 | 90 | 26 | 26 | 258 | 258 | 258 | 0.0061429 | 100 | 0.002381 | 294 | 0.007 | 1.362 | A04 | MICL0.01409026/SBR
Build-In Floor | Mini Canal | MICL.01409026/SDB | 14 | 90 | 26 | 26 | 258 | 258 | 258 | 0.0061429 | 100 | 0.002381 | 294 | 0.007 | 1.362 | A04 | MICL0.01409026/SDB
Build-In Floor | Mini Canal | MICL.01409026/SNA | 14 | 90 | 26 | 26 | 258 | 258 | 258 | 0.0061429 | 100 | 0.002381 | 294 | 0.007 | 1.362 | A04 | MICL0.01409026/SNA
Build-In Floor | Mini Canal | MICL.01409026/SNC | 14 | 90 | 26 | 26 | 258 | 258 | 258 | 0.0061429 | 100 | 0.002381 | 294 | 0.007 | 1.362 | A04 | MICL0.01409026/SNC
Build-In Floor | Mini Canal | MICL.01409034/ANA | 14 | 90 | 34 | 34 | 265 | 265 | 265 | 0.0063095 | 103 | 0.0024524 | 302 | 0.0071905 | 1.362 | A04 | MICL0.01409034/ANA
Build-In Floor | Mini Canal | MICL.01409034/DBL | 14 | 90 | 34 | 34 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01409034/DBL
Build-In Floor | Mini Canal | MICL.01409034/DBN | 14 | 90 | 34 | 34 | 328 | 328 | 328 | 0.0078095 | 128 | 0.0030476 | 374 | 0.0089048 | 1.362 | A04 | MICL0.01409034/DBN
Build-In Floor | Mini Canal | MICL.01409034/DBR | 14 | 90 | 34 | 34 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01409034/DBR
Build-In Floor | Mini Canal | MICL.01409034/DBV | 14 | 90 | 34 | 34 | 328 | 328 | 328 | 0.0078095 | 128 | 0.0030476 | 374 | 0.0089048 | 1.362 | A04 | MICL0.01409034/DBV
Build-In Floor | Mini Canal | MICL.01409034/DDB | 14 | 90 | 34 | 34 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01409034/DDB
Build-In Floor | Mini Canal | MICL.01409034/DMN | 14 | 90 | 34 | 34 | 328 | 328 | 328 | 0.0078095 | 128 | 0.0030476 | 374 | 0.0089048 | 1.362 | A04 | MICL0.01409034/DMN
Build-In Floor | Mini Canal | MICL.01409034/DMV | 14 | 90 | 34 | 34 | 328 | 328 | 328 | 0.0078095 | 128 | 0.0030476 | 374 | 0.0089048 | 1.362 | A04 | MICL0.01409034/DMV
Build-In Floor | Mini Canal | MICL.01409034/DNA | 14 | 90 | 34 | 34 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01409034/DNA
Build-In Floor | Mini Canal | MICL.01409034/DNC | 14 | 90 | 34 | 34 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01409034/DNC
Build-In Floor | Mini Canal | MICL.01409034/DON | 14 | 90 | 34 | 34 | 328 | 328 | 328 | 0.0078095 | 128 | 0.0030476 | 374 | 0.0089048 | 1.362 | A04 | MICL0.01409034/DON
Build-In Floor | Mini Canal | MICL.01409034/DOV | 14 | 90 | 34 | 34 | 328 | 328 | 328 | 0.0078095 | 128 | 0.0030476 | 374 | 0.0089048 | 1.362 | A04 | MICL0.01409034/DOV
Build-In Floor | Mini Canal | MICL.01409034/PNC | 14 | 90 | 34 | 34 | 300 | 300 | 300 | 0.0071429 | 117 | 0.0027857 | 342 | 0.0081429 | 1.362 | A04 | MICL0.01409034/PNC
Build-In Floor | Mini Canal | MICL.01409034/RBL | 14 | 90 | 34 | 34 | 353 | 353 | 353 | 0.0084048 | 137 | 0.0032619 | 402 | 0.0095714 | 1.362 | A04 | MICL0.01409034/RBL
Build-In Floor | Mini Canal | MICL.01409034/RBN | 14 | 90 | 34 | 34 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01409034/RBN
Build-In Floor | Mini Canal | MICL.01409034/RBR | 14 | 90 | 34 | 34 | 353 | 353 | 353 | 0.0084048 | 137 | 0.0032619 | 402 | 0.0095714 | 1.362 | A04 | MICL0.01409034/RBR
Build-In Floor | Mini Canal | MICL.01409034/RBV | 14 | 90 | 34 | 34 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01409034/RBV
Build-In Floor | Mini Canal | MICL.01409034/RDB | 14 | 90 | 34 | 34 | 353 | 353 | 353 | 0.0084048 | 137 | 0.0032619 | 402 | 0.0095714 | 1.362 | A04 | MICL0.01409034/RDB
Build-In Floor | Mini Canal | MICL.01409034/RMN | 14 | 90 | 34 | 34 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01409034/RMN
Build-In Floor | Mini Canal | MICL.01409034/RMV | 14 | 90 | 34 | 34 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01409034/RMV
Build-In Floor | Mini Canal | MICL.01409034/RNA | 14 | 90 | 34 | 34 | 353 | 353 | 353 | 0.0084048 | 137 | 0.0032619 | 402 | 0.0095714 | 1.362 | A04 | MICL0.01409034/RNA
Build-In Floor | Mini Canal | MICL.01409034/RON | 14 | 90 | 34 | 34 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01409034/RON
Build-In Floor | Mini Canal | MICL.01409034/ROV | 14 | 90 | 34 | 34 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01409034/ROV
Build-In Floor | Mini Canal | MICL.01409034/RSS | 14 | 90 | 34 | 34 | 339 | 339 | 339 | 0.0080714 | 132 | 0.0031429 | 386 | 0.0091905 | 1.362 | A04 | MICL0.01409034/RSS
Build-In Floor | Mini Canal | MICL.01409034/SBL | 14 | 90 | 34 | 34 | 353 | 353 | 353 | 0.0084048 | 137 | 0.0032619 | 402 | 0.0095714 | 1.362 | A04 | MICL0.01409034/SBL
Build-In Floor | Mini Canal | MICL.01409034/SBR | 14 | 90 | 34 | 34 | 353 | 353 | 353 | 0.0084048 | 137 | 0.0032619 | 402 | 0.0095714 | 1.362 | A04 | MICL0.01409034/SBR
Build-In Floor | Mini Canal | MICL.01409034/SDB | 14 | 90 | 34 | 34 | 353 | 353 | 353 | 0.0084048 | 137 | 0.0032619 | 402 | 0.0095714 | 1.362 | A04 | MICL0.01409034/SDB
Build-In Floor | Mini Canal | MICL.01409034/SNA | 14 | 90 | 34 | 34 | 353 | 353 | 353 | 0.0084048 | 137 | 0.0032619 | 402 | 0.0095714 | 1.362 | A04 | MICL0.01409034/SNA
Build-In Floor | Mini Canal | MICL.01409034/SNC | 14 | 90 | 34 | 34 | 353 | 353 | 353 | 0.0084048 | 137 | 0.0032619 | 402 | 0.0095714 | 1.362 | A04 | MICL0.01409034/SNC
Build-In Floor | Mini Canal | MICL.01409042/ANA | 14 | 90 | 42 | 42 | 356 | 356 | 356 | 0.0084762 | 138 | 0.0032857 | 405 | 0.0096429 | 1.362 | A04 | MICL0.01409042/ANA
Build-In Floor | Mini Canal | MICL.01409042/DBL | 14 | 90 | 42 | 42 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01409042/DBL
Build-In Floor | Mini Canal | MICL.01409042/DBN | 14 | 90 | 42 | 42 | 442 | 442 | 442 | 0.010524 | 172 | 0.0040952 | 503 | 0.011976 | 1.362 | A04 | MICL0.01409042/DBN
Build-In Floor | Mini Canal | MICL.01409042/DBR | 14 | 90 | 42 | 42 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01409042/DBR
Build-In Floor | Mini Canal | MICL.01409042/DBV | 14 | 90 | 42 | 42 | 442 | 442 | 442 | 0.010524 | 172 | 0.0040952 | 503 | 0.011976 | 1.362 | A04 | MICL0.01409042/DBV
Build-In Floor | Mini Canal | MICL.01409042/DDB | 14 | 90 | 42 | 42 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01409042/DDB
Build-In Floor | Mini Canal | MICL.01409042/DMN | 14 | 90 | 42 | 42 | 442 | 442 | 442 | 0.010524 | 172 | 0.0040952 | 503 | 0.011976 | 1.362 | A04 | MICL0.01409042/DMN
Build-In Floor | Mini Canal | MICL.01409042/DMV | 14 | 90 | 42 | 42 | 442 | 442 | 442 | 0.010524 | 172 | 0.0040952 | 503 | 0.011976 | 1.362 | A04 | MICL0.01409042/DMV
Build-In Floor | Mini Canal | MICL.01409042/DNA | 14 | 90 | 42 | 42 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01409042/DNA
Build-In Floor | Mini Canal | MICL.01409042/DNC | 14 | 90 | 42 | 42 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01409042/DNC
Build-In Floor | Mini Canal | MICL.01409042/DON | 14 | 90 | 42 | 42 | 442 | 442 | 442 | 0.010524 | 172 | 0.0040952 | 503 | 0.011976 | 1.362 | A04 | MICL0.01409042/DON
Build-In Floor | Mini Canal | MICL.01409042/DOV | 14 | 90 | 42 | 42 | 442 | 442 | 442 | 0.010524 | 172 | 0.0040952 | 503 | 0.011976 | 1.362 | A04 | MICL0.01409042/DOV
Build-In Floor | Mini Canal | MICL.01409042/PNC | 14 | 90 | 42 | 42 | 404 | 404 | 404 | 0.009619 | 157 | 0.0037381 | 460 | 0.010952 | 1.362 | A04 | MICL0.01409042/PNC
Build-In Floor | Mini Canal | MICL.01409042/RBL | 14 | 90 | 42 | 42 | 475 | 475 | 475 | 0.01131 | 185 | 0.0044048 | 541 | 0.012881 | 1.362 | A04 | MICL0.01409042/RBL
Build-In Floor | Mini Canal | MICL.01409042/RBN | 14 | 90 | 42 | 42 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01409042/RBN
Build-In Floor | Mini Canal | MICL.01409042/RBR | 14 | 90 | 42 | 42 | 475 | 475 | 475 | 0.01131 | 185 | 0.0044048 | 541 | 0.012881 | 1.362 | A04 | MICL0.01409042/RBR
Build-In Floor | Mini Canal | MICL.01409042/RBV | 14 | 90 | 42 | 42 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01409042/RBV
Build-In Floor | Mini Canal | MICL.01409042/RDB | 14 | 90 | 42 | 42 | 475 | 475 | 475 | 0.01131 | 185 | 0.0044048 | 541 | 0.012881 | 1.362 | A04 | MICL0.01409042/RDB
Build-In Floor | Mini Canal | MICL.01409042/RMN | 14 | 90 | 42 | 42 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01409042/RMN
Build-In Floor | Mini Canal | MICL.01409042/RMV | 14 | 90 | 42 | 42 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01409042/RMV
Build-In Floor | Mini Canal | MICL.01409042/RNA | 14 | 90 | 42 | 42 | 475 | 475 | 475 | 0.01131 | 185 | 0.0044048 | 541 | 0.012881 | 1.362 | A04 | MICL0.01409042/RNA
Build-In Floor | Mini Canal | MICL.01409042/RON | 14 | 90 | 42 | 42 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01409042/RON
Build-In Floor | Mini Canal | MICL.01409042/ROV | 14 | 90 | 42 | 42 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01409042/ROV
Build-In Floor | Mini Canal | MICL.01409042/RSS | 14 | 90 | 42 | 42 | 456 | 456 | 456 | 0.010857 | 177 | 0.0042143 | 519 | 0.012357 | 1.362 | A04 | MICL0.01409042/RSS
Build-In Floor | Mini Canal | MICL.01409042/SBL | 14 | 90 | 42 | 42 | 475 | 475 | 475 | 0.01131 | 185 | 0.0044048 | 541 | 0.012881 | 1.362 | A04 | MICL0.01409042/SBL
Build-In Floor | Mini Canal | MICL.01409042/SBR | 14 | 90 | 42 | 42 | 475 | 475 | 475 | 0.01131 | 185 | 0.0044048 | 541 | 0.012881 | 1.362 | A04 | MICL0.01409042/SBR
Build-In Floor | Mini Canal | MICL.01409042/SDB | 14 | 90 | 42 | 42 | 475 | 475 | 475 | 0.01131 | 185 | 0.0044048 | 541 | 0.012881 | 1.362 | A04 | MICL0.01409042/SDB
Build-In Floor | Mini Canal | MICL.01409042/SNA | 14 | 90 | 42 | 42 | 475 | 475 | 475 | 0.01131 | 185 | 0.0044048 | 541 | 0.012881 | 1.362 | A04 | MICL0.01409042/SNA
Build-In Floor | Mini Canal | MICL.01409042/SNC | 14 | 90 | 42 | 42 | 475 | 475 | 475 | 0.01131 | 185 | 0.0044048 | 541 | 0.012881 | 1.362 | A04 | MICL0.01409042/SNC
Build-In Floor | Mini Canal | MICL.01410014/ANA | 14 | 100 | 14 | 14 | 131 | 131 | 131 | 0.003119 | 51 | 0.0012143 | 149 | 0.0035476 | 1.362 | A04 | MICL0.01410014/ANA
Build-In Floor | Mini Canal | MICL.01410014/DBL | 14 | 100 | 14 | 14 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01410014/DBL
Build-In Floor | Mini Canal | MICL.01410014/DBN | 14 | 100 | 14 | 14 | 162 | 162 | 162 | 0.0038571 | 63 | 0.0015 | 185 | 0.0044048 | 1.362 | A04 | MICL0.01410014/DBN
Build-In Floor | Mini Canal | MICL.01410014/DBR | 14 | 100 | 14 | 14 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01410014/DBR
Build-In Floor | Mini Canal | MICL.01410014/DBV | 14 | 100 | 14 | 14 | 162 | 162 | 162 | 0.0038571 | 63 | 0.0015 | 185 | 0.0044048 | 1.362 | A04 | MICL0.01410014/DBV
Build-In Floor | Mini Canal | MICL.01410014/DDB | 14 | 100 | 14 | 14 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01410014/DDB
Build-In Floor | Mini Canal | MICL.01410014/DMN | 14 | 100 | 14 | 14 | 162 | 162 | 162 | 0.0038571 | 63 | 0.0015 | 185 | 0.0044048 | 1.362 | A04 | MICL0.01410014/DMN
Build-In Floor | Mini Canal | MICL.01410014/DMV | 14 | 100 | 14 | 14 | 162 | 162 | 162 | 0.0038571 | 63 | 0.0015 | 185 | 0.0044048 | 1.362 | A04 | MICL0.01410014/DMV
Build-In Floor | Mini Canal | MICL.01410014/DNA | 14 | 100 | 14 | 14 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01410014/DNA
Build-In Floor | Mini Canal | MICL.01410014/DNC | 14 | 100 | 14 | 14 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01410014/DNC
Build-In Floor | Mini Canal | MICL.01410014/DON | 14 | 100 | 14 | 14 | 162 | 162 | 162 | 0.0038571 | 63 | 0.0015 | 185 | 0.0044048 | 1.362 | A04 | MICL0.01410014/DON
Build-In Floor | Mini Canal | MICL.01410014/DOV | 14 | 100 | 14 | 14 | 162 | 162 | 162 | 0.0038571 | 63 | 0.0015 | 185 | 0.0044048 | 1.362 | A04 | MICL0.01410014/DOV
Build-In Floor | Mini Canal | MICL.01410014/RBL | 14 | 100 | 14 | 14 | 174 | 174 | 174 | 0.0041429 | 68 | 0.001619 | 198 | 0.0047143 | 1.362 | A04 | MICL0.01410014/RBL
Build-In Floor | Mini Canal | MICL.01410014/RBN | 14 | 100 | 14 | 14 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01410014/RBN
Build-In Floor | Mini Canal | MICL.01410014/RBR | 14 | 100 | 14 | 14 | 174 | 174 | 174 | 0.0041429 | 68 | 0.001619 | 198 | 0.0047143 | 1.362 | A04 | MICL0.01410014/RBR
Build-In Floor | Mini Canal | MICL.01410014/RBV | 14 | 100 | 14 | 14 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01410014/RBV
Build-In Floor | Mini Canal | MICL.01410014/RDB | 14 | 100 | 14 | 14 | 174 | 174 | 174 | 0.0041429 | 68 | 0.001619 | 198 | 0.0047143 | 1.362 | A04 | MICL0.01410014/RDB
Build-In Floor | Mini Canal | MICL.01410014/RMN | 14 | 100 | 14 | 14 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01410014/RMN
Build-In Floor | Mini Canal | MICL.01410014/RMV | 14 | 100 | 14 | 14 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01410014/RMV
Build-In Floor | Mini Canal | MICL.01410014/RNA | 14 | 100 | 14 | 14 | 174 | 174 | 174 | 0.0041429 | 68 | 0.001619 | 198 | 0.0047143 | 1.362 | A04 | MICL0.01410014/RNA
Build-In Floor | Mini Canal | MICL.01410014/RON | 14 | 100 | 14 | 14 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01410014/RON
Build-In Floor | Mini Canal | MICL.01410014/ROV | 14 | 100 | 14 | 14 | 169 | 169 | 169 | 0.0040238 | 66 | 0.0015714 | 192 | 0.0045714 | 1.362 | A04 | MICL0.01410014/ROV
Build-In Floor | Mini Canal | MICL.01410014/RSS | 14 | 100 | 14 | 14 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.01410014/RSS
Build-In Floor | Mini Canal | MICL.01410014/SBL | 14 | 100 | 14 | 14 | 174 | 174 | 174 | 0.0041429 | 68 | 0.001619 | 198 | 0.0047143 | 1.362 | A04 | MICL0.01410014/SBL
Build-In Floor | Mini Canal | MICL.01410014/SBR | 14 | 100 | 14 | 14 | 174 | 174 | 174 | 0.0041429 | 68 | 0.001619 | 198 | 0.0047143 | 1.362 | A04 | MICL0.01410014/SBR
Build-In Floor | Mini Canal | MICL.01410014/SDB | 14 | 100 | 14 | 14 | 174 | 174 | 174 | 0.0041429 | 68 | 0.001619 | 198 | 0.0047143 | 1.362 | A04 | MICL0.01410014/SDB
Build-In Floor | Mini Canal | MICL.01410014/SNA | 14 | 100 | 14 | 14 | 174 | 174 | 174 | 0.0041429 | 68 | 0.001619 | 198 | 0.0047143 | 1.362 | A04 | MICL0.01410014/SNA
Build-In Floor | Mini Canal | MICL.01410014/SNC | 14 | 100 | 14 | 14 | 174 | 174 | 174 | 0.0041429 | 68 | 0.001619 | 198 | 0.0047143 | 1.362 | A04 | MICL0.01410014/SNC
Build-In Floor | Mini Canal | MICL.01410026/ANA | 14 | 100 | 26 | 26 | 226 | 226 | 226 | 0.005381 | 88 | 0.0020952 | 257 | 0.006119 | 1.362 | A04 | MICL0.01410026/ANA
Build-In Floor | Mini Canal | MICL.01410026/DBL | 14 | 100 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01410026/DBL
Build-In Floor | Mini Canal | MICL.01410026/DBN | 14 | 100 | 26 | 26 | 280 | 280 | 280 | 0.0066667 | 109 | 0.0025952 | 319 | 0.0075952 | 1.362 | A04 | MICL0.01410026/DBN
Build-In Floor | Mini Canal | MICL.01410026/DBR | 14 | 100 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01410026/DBR
Build-In Floor | Mini Canal | MICL.01410026/DBV | 14 | 100 | 26 | 26 | 280 | 280 | 280 | 0.0066667 | 109 | 0.0025952 | 319 | 0.0075952 | 1.362 | A04 | MICL0.01410026/DBV
Build-In Floor | Mini Canal | MICL.01410026/DDB | 14 | 100 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01410026/DDB
Build-In Floor | Mini Canal | MICL.01410026/DMN | 14 | 100 | 26 | 26 | 280 | 280 | 280 | 0.0066667 | 109 | 0.0025952 | 319 | 0.0075952 | 1.362 | A04 | MICL0.01410026/DMN
Build-In Floor | Mini Canal | MICL.01410026/DMV | 14 | 100 | 26 | 26 | 280 | 280 | 280 | 0.0066667 | 109 | 0.0025952 | 319 | 0.0075952 | 1.362 | A04 | MICL0.01410026/DMV
Build-In Floor | Mini Canal | MICL.01410026/DNA | 14 | 100 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01410026/DNA
Build-In Floor | Mini Canal | MICL.01410026/DNC | 14 | 100 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01410026/DNC
Build-In Floor | Mini Canal | MICL.01410026/DON | 14 | 100 | 26 | 26 | 280 | 280 | 280 | 0.0066667 | 109 | 0.0025952 | 319 | 0.0075952 | 1.362 | A04 | MICL0.01410026/DON
Build-In Floor | Mini Canal | MICL.01410026/DOV | 14 | 100 | 26 | 26 | 280 | 280 | 280 | 0.0066667 | 109 | 0.0025952 | 319 | 0.0075952 | 1.362 | A04 | MICL0.01410026/DOV
Build-In Floor | Mini Canal | MICL.01410026/PNC | 14 | 100 | 26 | 26 | 256 | 256 | 256 | 0.0060952 | 100 | 0.002381 | 292 | 0.0069524 | 1.362 | A04 | MICL0.01410026/PNC
Build-In Floor | Mini Canal | MICL.01410026/RBL | 14 | 100 | 26 | 26 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01410026/RBL
Build-In Floor | Mini Canal | MICL.01410026/RBN | 14 | 100 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01410026/RBN
Build-In Floor | Mini Canal | MICL.01410026/RBR | 14 | 100 | 26 | 26 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01410026/RBR
Build-In Floor | Mini Canal | MICL.01410026/RBV | 14 | 100 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01410026/RBV
Build-In Floor | Mini Canal | MICL.01410026/RDB | 14 | 100 | 26 | 26 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01410026/RDB
Build-In Floor | Mini Canal | MICL.01410026/RMN | 14 | 100 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01410026/RMN
Build-In Floor | Mini Canal | MICL.01410026/RMV | 14 | 100 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01410026/RMV
Build-In Floor | Mini Canal | MICL.01410026/RNA | 14 | 100 | 26 | 26 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01410026/RNA
Build-In Floor | Mini Canal | MICL.01410026/RON | 14 | 100 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01410026/RON
Build-In Floor | Mini Canal | MICL.01410026/ROV | 14 | 100 | 26 | 26 | 292 | 292 | 292 | 0.0069524 | 114 | 0.0027143 | 333 | 0.0079286 | 1.362 | A04 | MICL0.01410026/ROV
Build-In Floor | Mini Canal | MICL.01410026/RSS | 14 | 100 | 26 | 26 | 289 | 289 | 289 | 0.006881 | 112 | 0.0026667 | 329 | 0.0078333 | 1.362 | A04 | MICL0.01410026/RSS
Build-In Floor | Mini Canal | MICL.01410026/SBL | 14 | 100 | 26 | 26 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01410026/SBL
Build-In Floor | Mini Canal | MICL.01410026/SBR | 14 | 100 | 26 | 26 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01410026/SBR
Build-In Floor | Mini Canal | MICL.01410026/SDB | 14 | 100 | 26 | 26 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01410026/SDB
Build-In Floor | Mini Canal | MICL.01410026/SNA | 14 | 100 | 26 | 26 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01410026/SNA
Build-In Floor | Mini Canal | MICL.01410026/SNC | 14 | 100 | 26 | 26 | 301 | 301 | 301 | 0.0071667 | 117 | 0.0027857 | 343 | 0.0081667 | 1.362 | A04 | MICL0.01410026/SNC
Build-In Floor | Mini Canal | MICL.01410034/ANA | 14 | 100 | 34 | 34 | 308 | 308 | 308 | 0.0073333 | 120 | 0.0028571 | 351 | 0.0083571 | 1.362 | A04 | MICL0.01410034/ANA
Build-In Floor | Mini Canal | MICL.01410034/DBL | 14 | 100 | 34 | 34 | 399 | 399 | 399 | 0.0095 | 155 | 0.0036905 | 454 | 0.01081 | 1.362 | A04 | MICL0.01410034/DBL
Build-In Floor | Mini Canal | MICL.01410034/DBN | 14 | 100 | 34 | 34 | 382 | 382 | 382 | 0.0090952 | 149 | 0.0035476 | 435 | 0.010357 | 1.362 | A04 | MICL0.01410034/DBN
Build-In Floor | Mini Canal | MICL.01410034/DBR | 14 | 100 | 34 | 34 | 399 | 399 | 399 | 0.0095 | 155 | 0.0036905 | 454 | 0.01081 | 1.362 | A04 | MICL0.01410034/DBR
Build-In Floor | Mini Canal | MICL.01410034/DBV | 14 | 100 | 34 | 34 | 382 | 382 | 382 | 0.0090952 | 149 | 0.0035476 | 435 | 0.010357 | 1.362 | A04 | MICL0.01410034/DBV
Build-In Floor | Mini Canal | MICL.01410034/DDB | 14 | 100 | 34 | 34 | 399 | 399 | 399 | 0.0095 | 155 | 0.0036905 | 454 | 0.01081 | 1.362 | A04 | MICL0.01410034/DDB
Build-In Floor | Mini Canal | MICL.01410034/DMN | 14 | 100 | 34 | 34 | 382 | 382 | 382 | 0.0090952 | 149 | 0.0035476 | 435 | 0.010357 | 1.362 | A04 | MICL0.01410034/DMN
Build-In Floor | Mini Canal | MICL.01410034/DMV | 14 | 100 | 34 | 34 | 382 | 382 | 382 | 0.0090952 | 149 | 0.0035476 | 435 | 0.010357 | 1.362 | A04 | MICL0.01410034/DMV
Build-In Floor | Mini Canal | MICL.01410034/DNA | 14 | 100 | 34 | 34 | 399 | 399 | 399 | 0.0095 | 155 | 0.0036905 | 454 | 0.01081 | 1.362 | A04 | MICL0.01410034/DNA
Build-In Floor | Mini Canal | MICL.01410034/DNC | 14 | 100 | 34 | 34 | 399 | 399 | 399 | 0.0095 | 155 | 0.0036905 | 454 | 0.01081 | 1.362 | A04 | MICL0.01410034/DNC
Build-In Floor | Mini Canal | MICL.01410034/DON | 14 | 100 | 34 | 34 | 382 | 382 | 382 | 0.0090952 | 149 | 0.0035476 | 435 | 0.010357 | 1.362 | A04 | MICL0.01410034/DON
Build-In Floor | Mini Canal | MICL.01410034/DOV | 14 | 100 | 34 | 34 | 382 | 382 | 382 | 0.0090952 | 149 | 0.0035476 | 435 | 0.010357 | 1.362 | A04 | MICL0.01410034/DOV
Build-In Floor | Mini Canal | MICL.01410034/PNC | 14 | 100 | 34 | 34 | 349 | 349 | 349 | 0.0083095 | 136 | 0.0032381 | 398 | 0.0094762 | 1.362 | A04 | MICL0.01410034/PNC
Build-In Floor | Mini Canal | MICL.01410034/RBL | 14 | 100 | 34 | 34 | 411 | 411 | 411 | 0.0097857 | 160 | 0.0038095 | 468 | 0.011143 | 1.362 | A04 | MICL0.01410034/RBL
Build-In Floor | Mini Canal | MICL.01410034/RBN | 14 | 100 | 34 | 34 | 399 | 399 | 399 | 0.0095 | 155 | 0.0036905 | 454 | 0.01081 | 1.362 | A04 | MICL0.01410034/RBN
Build-In Floor | Mini Canal | MICL.01410034/RBR | 14 | 100 | 34 | 34 | 411 | 411 | 411 | 0.0097857 | 160 | 0.0038095 | 468 | 0.011143 | 1.362 | A04 | MICL0.01410034/RBR
Build-In Floor | Mini Canal | MICL.01410034/RBV | 14 | 100 | 34 | 34 | 399 | 399 | 399 | 0.0095 | 155 | 0.0036905 | 454 | 0.01081 | 1.362 | A04 | MICL0.01410034/RBV
Build-In Floor | Mini Canal | MICL.01410034/RDB | 14 | 100 | 34 | 34 | 411 | 411 | 411 | 0.0097857 | 160 | 0.0038095 | 468 | 0.011143 | 1.362 | A04 | MICL0.01410034/RDB
Build-In Floor | Mini Canal | MICL.01410034/RMN | 14 | 100 | 34 | 34 | 399 | 399 | 399 | 0.0095 | 155 | 0.0036905 | 454 | 0.01081 | 1.362 | A04 | MICL0.01410034/RMN
Build-In Floor | Mini Canal | MICL.01410034/RMV | 14 | 100 | 34 | 34 | 399 | 399 | 399 | 0.0095 | 155 | 0.0036905 | 454 | 0.01081 | 1.362 | A04 | MICL0.01410034/RMV
Build-In Floor | Mini Canal | MICL.01410034/RNA | 14 | 100 | 34 | 34 | 411 | 411 | 411 | 0.0097857 | 160 | 0.0038095 | 468 | 0.011143 | 1.362 | A04 | MICL0.01410034/RNA
Build-In Floor | Mini Canal | MICL.01410034/RON | 14 | 100 | 34 | 34 | 399 | 399 | 399 | 0.0095 | 155 | 0.0036905 | 454 | 0.01081 | 1.362 | A04 | MICL0.01410034/RON
Build-In Floor | Mini Canal | MICL.01410034/ROV | 14 | 100 | 34 | 34 | 399 | 399 | 399 | 0.0095 | 155 | 0.0036905 | 454 | 0.01081 | 1.362 | A04 | MICL0.01410034/ROV
Build-In Floor | Mini Canal | MICL.01410034/RSS | 14 | 100 | 34 | 34 | 395 | 395 | 395 | 0.0094048 | 154 | 0.0036667 | 450 | 0.010714 | 1.362 | A04 | MICL0.01410034/RSS
Build-In Floor | Mini Canal | MICL.01410034/SBL | 14 | 100 | 34 | 34 | 411 | 411 | 411 | 0.0097857 | 160 | 0.0038095 | 468 | 0.011143 | 1.362 | A04 | MICL0.01410034/SBL
Build-In Floor | Mini Canal | MICL.01410034/SBR | 14 | 100 | 34 | 34 | 411 | 411 | 411 | 0.0097857 | 160 | 0.0038095 | 468 | 0.011143 | 1.362 | A04 | MICL0.01410034/SBR
Build-In Floor | Mini Canal | MICL.01410034/SDB | 14 | 100 | 34 | 34 | 411 | 411 | 411 | 0.0097857 | 160 | 0.0038095 | 468 | 0.011143 | 1.362 | A04 | MICL0.01410034/SDB
Build-In Floor | Mini Canal | MICL.01410034/SNA | 14 | 100 | 34 | 34 | 411 | 411 | 411 | 0.0097857 | 160 | 0.0038095 | 468 | 0.011143 | 1.362 | A04 | MICL0.01410034/SNA
Build-In Floor | Mini Canal | MICL.01410034/SNC | 14 | 100 | 34 | 34 | 411 | 411 | 411 | 0.0097857 | 160 | 0.0038095 | 468 | 0.011143 | 1.362 | A04 | MICL0.01410034/SNC
Build-In Floor | Mini Canal | MICL.01410042/ANA | 14 | 100 | 42 | 42 | 416 | 416 | 416 | 0.0099048 | 162 | 0.0038571 | 474 | 0.011286 | 1.362 | A04 | MICL0.01410042/ANA
Build-In Floor | Mini Canal | MICL.01410042/DBL | 14 | 100 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.01410042/DBL
Build-In Floor | Mini Canal | MICL.01410042/DBN | 14 | 100 | 42 | 42 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01410042/DBN
Build-In Floor | Mini Canal | MICL.01410042/DBR | 14 | 100 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.01410042/DBR
Build-In Floor | Mini Canal | MICL.01410042/DBV | 14 | 100 | 42 | 42 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01410042/DBV
Build-In Floor | Mini Canal | MICL.01410042/DDB | 14 | 100 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.01410042/DDB
Build-In Floor | Mini Canal | MICL.01410042/DMN | 14 | 100 | 42 | 42 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01410042/DMN
Build-In Floor | Mini Canal | MICL.01410042/DMV | 14 | 100 | 42 | 42 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01410042/DMV
Build-In Floor | Mini Canal | MICL.01410042/DNA | 14 | 100 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.01410042/DNA
Build-In Floor | Mini Canal | MICL.01410042/DNC | 14 | 100 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.01410042/DNC
Build-In Floor | Mini Canal | MICL.01410042/DON | 14 | 100 | 42 | 42 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01410042/DON
Build-In Floor | Mini Canal | MICL.01410042/DOV | 14 | 100 | 42 | 42 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01410042/DOV
Build-In Floor | Mini Canal | MICL.01410042/PNC | 14 | 100 | 42 | 42 | 472 | 472 | 472 | 0.011238 | 184 | 0.004381 | 538 | 0.01281 | 1.362 | A04 | MICL0.01410042/PNC
Build-In Floor | Mini Canal | MICL.01410042/RBL | 14 | 100 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.01410042/RBL
Build-In Floor | Mini Canal | MICL.01410042/RBN | 14 | 100 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.01410042/RBN
Build-In Floor | Mini Canal | MICL.01410042/RBR | 14 | 100 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.01410042/RBR
Build-In Floor | Mini Canal | MICL.01410042/RBV | 14 | 100 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.01410042/RBV
Build-In Floor | Mini Canal | MICL.01410042/RDB | 14 | 100 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.01410042/RDB
Build-In Floor | Mini Canal | MICL.01410042/RMN | 14 | 100 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.01410042/RMN
Build-In Floor | Mini Canal | MICL.01410042/RMV | 14 | 100 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.01410042/RMV
Build-In Floor | Mini Canal | MICL.01410042/RNA | 14 | 100 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.01410042/RNA
Build-In Floor | Mini Canal | MICL.01410042/RON | 14 | 100 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.01410042/RON
Build-In Floor | Mini Canal | MICL.01410042/ROV | 14 | 100 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.01410042/ROV
Build-In Floor | Mini Canal | MICL.01410042/RSS | 14 | 100 | 42 | 42 | 533 | 533 | 533 | 0.01269 | 207 | 0.0049286 | 607 | 0.014452 | 1.362 | A04 | MICL0.01410042/RSS
Build-In Floor | Mini Canal | MICL.01410042/SBL | 14 | 100 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.01410042/SBL
Build-In Floor | Mini Canal | MICL.01410042/SBR | 14 | 100 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.01410042/SBR
Build-In Floor | Mini Canal | MICL.01410042/SDB | 14 | 100 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.01410042/SDB
Build-In Floor | Mini Canal | MICL.01410042/SNA | 14 | 100 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.01410042/SNA
Build-In Floor | Mini Canal | MICL.01410042/SNC | 14 | 100 | 42 | 42 | 555 | 555 | 555 | 0.013214 | 216 | 0.0051429 | 632 | 0.015048 | 1.362 | A04 | MICL0.01410042/SNC
Build-In Floor | Mini Canal | MICL.01411014/ANA | 14 | 110 | 14 | 14 | 149 | 149 | 149 | 0.0035476 | 58 | 0.001381 | 170 | 0.0040476 | 1.362 | A04 | MICL0.01411014/ANA
Build-In Floor | Mini Canal | MICL.01411014/DBL | 14 | 110 | 14 | 14 | 192 | 192 | 192 | 0.0045714 | 75 | 0.0017857 | 219 | 0.0052143 | 1.362 | A04 | MICL0.01411014/DBL
Build-In Floor | Mini Canal | MICL.01411014/DBN | 14 | 110 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.01411014/DBN
Build-In Floor | Mini Canal | MICL.01411014/DBR | 14 | 110 | 14 | 14 | 192 | 192 | 192 | 0.0045714 | 75 | 0.0017857 | 219 | 0.0052143 | 1.362 | A04 | MICL0.01411014/DBR
Build-In Floor | Mini Canal | MICL.01411014/DBV | 14 | 110 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.01411014/DBV
Build-In Floor | Mini Canal | MICL.01411014/DDB | 14 | 110 | 14 | 14 | 192 | 192 | 192 | 0.0045714 | 75 | 0.0017857 | 219 | 0.0052143 | 1.362 | A04 | MICL0.01411014/DDB
Build-In Floor | Mini Canal | MICL.01411014/DMN | 14 | 110 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.01411014/DMN
Build-In Floor | Mini Canal | MICL.01411014/DMV | 14 | 110 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.01411014/DMV
Build-In Floor | Mini Canal | MICL.01411014/DNA | 14 | 110 | 14 | 14 | 192 | 192 | 192 | 0.0045714 | 75 | 0.0017857 | 219 | 0.0052143 | 1.362 | A04 | MICL0.01411014/DNA
Build-In Floor | Mini Canal | MICL.01411014/DNC | 14 | 110 | 14 | 14 | 192 | 192 | 192 | 0.0045714 | 75 | 0.0017857 | 219 | 0.0052143 | 1.362 | A04 | MICL0.01411014/DNC
Build-In Floor | Mini Canal | MICL.01411014/DON | 14 | 110 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.01411014/DON
Build-In Floor | Mini Canal | MICL.01411014/DOV | 14 | 110 | 14 | 14 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.01411014/DOV
Build-In Floor | Mini Canal | MICL.01411014/RBL | 14 | 110 | 14 | 14 | 198 | 198 | 198 | 0.0047143 | 77 | 0.0018333 | 226 | 0.005381 | 1.362 | A04 | MICL0.01411014/RBL
Build-In Floor | Mini Canal | MICL.01411014/RBN | 14 | 110 | 14 | 14 | 192 | 192 | 192 | 0.0045714 | 75 | 0.0017857 | 219 | 0.0052143 | 1.362 | A04 | MICL0.01411014/RBN
Build-In Floor | Mini Canal | MICL.01411014/RBR | 14 | 110 | 14 | 14 | 198 | 198 | 198 | 0.0047143 | 77 | 0.0018333 | 226 | 0.005381 | 1.362 | A04 | MICL0.01411014/RBR
Build-In Floor | Mini Canal | MICL.01411014/RBV | 14 | 110 | 14 | 14 | 192 | 192 | 192 | 0.0045714 | 75 | 0.0017857 | 219 | 0.0052143 | 1.362 | A04 | MICL0.01411014/RBV
Build-In Floor | Mini Canal | MICL.01411014/RDB | 14 | 110 | 14 | 14 | 198 | 198 | 198 | 0.0047143 | 77 | 0.0018333 | 226 | 0.005381 | 1.362 | A04 | MICL0.01411014/RDB
Build-In Floor | Mini Canal | MICL.01411014/RMN | 14 | 110 | 14 | 14 | 192 | 192 | 192 | 0.0045714 | 75 | 0.0017857 | 219 | 0.0052143 | 1.362 | A04 | MICL0.01411014/RMN
Build-In Floor | Mini Canal | MICL.01411014/RMV | 14 | 110 | 14 | 14 | 192 | 192 | 192 | 0.0045714 | 75 | 0.0017857 | 219 | 0.0052143 | 1.362 | A04 | MICL0.01411014/RMV
Build-In Floor | Mini Canal | MICL.01411014/RNA | 14 | 110 | 14 | 14 | 198 | 198 | 198 | 0.0047143 | 77 | 0.0018333 | 226 | 0.005381 | 1.362 | A04 | MICL0.01411014/RNA
Build-In Floor | Mini Canal | MICL.01411014/RON | 14 | 110 | 14 | 14 | 192 | 192 | 192 | 0.0045714 | 75 | 0.0017857 | 219 | 0.0052143 | 1.362 | A04 | MICL0.01411014/RON
Build-In Floor | Mini Canal | MICL.01411014/ROV | 14 | 110 | 14 | 14 | 192 | 192 | 192 | 0.0045714 | 75 | 0.0017857 | 219 | 0.0052143 | 1.362 | A04 | MICL0.01411014/ROV
Build-In Floor | Mini Canal | MICL.01411014/RSS | 14 | 110 | 14 | 14 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.01411014/RSS
Build-In Floor | Mini Canal | MICL.01411014/SBL | 14 | 110 | 14 | 14 | 198 | 198 | 198 | 0.0047143 | 77 | 0.0018333 | 226 | 0.005381 | 1.362 | A04 | MICL0.01411014/SBL
Build-In Floor | Mini Canal | MICL.01411014/SBR | 14 | 110 | 14 | 14 | 198 | 198 | 198 | 0.0047143 | 77 | 0.0018333 | 226 | 0.005381 | 1.362 | A04 | MICL0.01411014/SBR
Build-In Floor | Mini Canal | MICL.01411014/SDB | 14 | 110 | 14 | 14 | 198 | 198 | 198 | 0.0047143 | 77 | 0.0018333 | 226 | 0.005381 | 1.362 | A04 | MICL0.01411014/SDB
Build-In Floor | Mini Canal | MICL.01411014/SNA | 14 | 110 | 14 | 14 | 198 | 198 | 198 | 0.0047143 | 77 | 0.0018333 | 226 | 0.005381 | 1.362 | A04 | MICL0.01411014/SNA
Build-In Floor | Mini Canal | MICL.01411014/SNC | 14 | 110 | 14 | 14 | 198 | 198 | 198 | 0.0047143 | 77 | 0.0018333 | 226 | 0.005381 | 1.362 | A04 | MICL0.01411014/SNC
Build-In Floor | Mini Canal | MICL.01411026/ANA | 14 | 110 | 26 | 26 | 259 | 259 | 259 | 0.0061667 | 101 | 0.0024048 | 295 | 0.0070238 | 1.362 | A04 | MICL0.01411026/ANA
Build-In Floor | Mini Canal | MICL.01411026/DBL | 14 | 110 | 26 | 26 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01411026/DBL
Build-In Floor | Mini Canal | MICL.01411026/DBN | 14 | 110 | 26 | 26 | 321 | 321 | 321 | 0.0076429 | 125 | 0.0029762 | 366 | 0.0087143 | 1.362 | A04 | MICL0.01411026/DBN
Build-In Floor | Mini Canal | MICL.01411026/DBR | 14 | 110 | 26 | 26 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01411026/DBR
Build-In Floor | Mini Canal | MICL.01411026/DBV | 14 | 110 | 26 | 26 | 321 | 321 | 321 | 0.0076429 | 125 | 0.0029762 | 366 | 0.0087143 | 1.362 | A04 | MICL0.01411026/DBV
Build-In Floor | Mini Canal | MICL.01411026/DDB | 14 | 110 | 26 | 26 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01411026/DDB
Build-In Floor | Mini Canal | MICL.01411026/DMN | 14 | 110 | 26 | 26 | 321 | 321 | 321 | 0.0076429 | 125 | 0.0029762 | 366 | 0.0087143 | 1.362 | A04 | MICL0.01411026/DMN
Build-In Floor | Mini Canal | MICL.01411026/DMV | 14 | 110 | 26 | 26 | 321 | 321 | 321 | 0.0076429 | 125 | 0.0029762 | 366 | 0.0087143 | 1.362 | A04 | MICL0.01411026/DMV
Build-In Floor | Mini Canal | MICL.01411026/DNA | 14 | 110 | 26 | 26 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01411026/DNA
Build-In Floor | Mini Canal | MICL.01411026/DNC | 14 | 110 | 26 | 26 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01411026/DNC
Build-In Floor | Mini Canal | MICL.01411026/DON | 14 | 110 | 26 | 26 | 321 | 321 | 321 | 0.0076429 | 125 | 0.0029762 | 366 | 0.0087143 | 1.362 | A04 | MICL0.01411026/DON
Build-In Floor | Mini Canal | MICL.01411026/DOV | 14 | 110 | 26 | 26 | 321 | 321 | 321 | 0.0076429 | 125 | 0.0029762 | 366 | 0.0087143 | 1.362 | A04 | MICL0.01411026/DOV
Build-In Floor | Mini Canal | MICL.01411026/PNC | 14 | 110 | 26 | 26 | 293 | 293 | 293 | 0.0069762 | 114 | 0.0027143 | 334 | 0.0079524 | 1.362 | A04 | MICL0.01411026/PNC
Build-In Floor | Mini Canal | MICL.01411026/RBL | 14 | 110 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.01411026/RBL
Build-In Floor | Mini Canal | MICL.01411026/RBN | 14 | 110 | 26 | 26 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01411026/RBN
Build-In Floor | Mini Canal | MICL.01411026/RBR | 14 | 110 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.01411026/RBR
Build-In Floor | Mini Canal | MICL.01411026/RBV | 14 | 110 | 26 | 26 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01411026/RBV
Build-In Floor | Mini Canal | MICL.01411026/RDB | 14 | 110 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.01411026/RDB
Build-In Floor | Mini Canal | MICL.01411026/RMN | 14 | 110 | 26 | 26 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01411026/RMN
Build-In Floor | Mini Canal | MICL.01411026/RMV | 14 | 110 | 26 | 26 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01411026/RMV
Build-In Floor | Mini Canal | MICL.01411026/RNA | 14 | 110 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.01411026/RNA
Build-In Floor | Mini Canal | MICL.01411026/RON | 14 | 110 | 26 | 26 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01411026/RON
Build-In Floor | Mini Canal | MICL.01411026/ROV | 14 | 110 | 26 | 26 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01411026/ROV
Build-In Floor | Mini Canal | MICL.01411026/RSS | 14 | 110 | 26 | 26 | 331 | 331 | 331 | 0.007881 | 129 | 0.0030714 | 377 | 0.0089762 | 1.362 | A04 | MICL0.01411026/RSS
Build-In Floor | Mini Canal | MICL.01411026/SBL | 14 | 110 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.01411026/SBL
Build-In Floor | Mini Canal | MICL.01411026/SBR | 14 | 110 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.01411026/SBR
Build-In Floor | Mini Canal | MICL.01411026/SDB | 14 | 110 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.01411026/SDB
Build-In Floor | Mini Canal | MICL.01411026/SNA | 14 | 110 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.01411026/SNA
Build-In Floor | Mini Canal | MICL.01411026/SNC | 14 | 110 | 26 | 26 | 345 | 345 | 345 | 0.0082143 | 134 | 0.0031905 | 393 | 0.0093571 | 1.362 | A04 | MICL0.01411026/SNC
Build-In Floor | Mini Canal | MICL.01411034/ANA | 14 | 110 | 34 | 34 | 353 | 353 | 353 | 0.0084048 | 137 | 0.0032619 | 402 | 0.0095714 | 1.362 | A04 | MICL0.01411034/ANA
Build-In Floor | Mini Canal | MICL.01411034/DBL | 14 | 110 | 34 | 34 | 456 | 456 | 456 | 0.010857 | 177 | 0.0042143 | 519 | 0.012357 | 1.362 | A04 | MICL0.01411034/DBL
Build-In Floor | Mini Canal | MICL.01411034/DBN | 14 | 110 | 34 | 34 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01411034/DBN
Build-In Floor | Mini Canal | MICL.01411034/DBR | 14 | 110 | 34 | 34 | 456 | 456 | 456 | 0.010857 | 177 | 0.0042143 | 519 | 0.012357 | 1.362 | A04 | MICL0.01411034/DBR
Build-In Floor | Mini Canal | MICL.01411034/DBV | 14 | 110 | 34 | 34 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01411034/DBV
Build-In Floor | Mini Canal | MICL.01411034/DDB | 14 | 110 | 34 | 34 | 456 | 456 | 456 | 0.010857 | 177 | 0.0042143 | 519 | 0.012357 | 1.362 | A04 | MICL0.01411034/DDB
Build-In Floor | Mini Canal | MICL.01411034/DMN | 14 | 110 | 34 | 34 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01411034/DMN
Build-In Floor | Mini Canal | MICL.01411034/DMV | 14 | 110 | 34 | 34 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01411034/DMV
Build-In Floor | Mini Canal | MICL.01411034/DNA | 14 | 110 | 34 | 34 | 456 | 456 | 456 | 0.010857 | 177 | 0.0042143 | 519 | 0.012357 | 1.362 | A04 | MICL0.01411034/DNA
Build-In Floor | Mini Canal | MICL.01411034/DNC | 14 | 110 | 34 | 34 | 456 | 456 | 456 | 0.010857 | 177 | 0.0042143 | 519 | 0.012357 | 1.362 | A04 | MICL0.01411034/DNC
Build-In Floor | Mini Canal | MICL.01411034/DON | 14 | 110 | 34 | 34 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01411034/DON
Build-In Floor | Mini Canal | MICL.01411034/DOV | 14 | 110 | 34 | 34 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01411034/DOV
Build-In Floor | Mini Canal | MICL.01411034/PNC | 14 | 110 | 34 | 34 | 400 | 400 | 400 | 0.0095238 | 156 | 0.0037143 | 456 | 0.010857 | 1.362 | A04 | MICL0.01411034/PNC
Build-In Floor | Mini Canal | MICL.01411034/RBL | 14 | 110 | 34 | 34 | 470 | 470 | 470 | 0.01119 | 183 | 0.0043571 | 535 | 0.012738 | 1.362 | A04 | MICL0.01411034/RBL
Build-In Floor | Mini Canal | MICL.01411034/RBN | 14 | 110 | 34 | 34 | 456 | 456 | 456 | 0.010857 | 177 | 0.0042143 | 519 | 0.012357 | 1.362 | A04 | MICL0.01411034/RBN
Build-In Floor | Mini Canal | MICL.01411034/RBR | 14 | 110 | 34 | 34 | 470 | 470 | 470 | 0.01119 | 183 | 0.0043571 | 535 | 0.012738 | 1.362 | A04 | MICL0.01411034/RBR
Build-In Floor | Mini Canal | MICL.01411034/RBV | 14 | 110 | 34 | 34 | 456 | 456 | 456 | 0.010857 | 177 | 0.0042143 | 519 | 0.012357 | 1.362 | A04 | MICL0.01411034/RBV
Build-In Floor | Mini Canal | MICL.01411034/RDB | 14 | 110 | 34 | 34 | 470 | 470 | 470 | 0.01119 | 183 | 0.0043571 | 535 | 0.012738 | 1.362 | A04 | MICL0.01411034/RDB
Build-In Floor | Mini Canal | MICL.01411034/RMN | 14 | 110 | 34 | 34 | 456 | 456 | 456 | 0.010857 | 177 | 0.0042143 | 519 | 0.012357 | 1.362 | A04 | MICL0.01411034/RMN
Build-In Floor | Mini Canal | MICL.01411034/RMV | 14 | 110 | 34 | 34 | 456 | 456 | 456 | 0.010857 | 177 | 0.0042143 | 519 | 0.012357 | 1.362 | A04 | MICL0.01411034/RMV
Build-In Floor | Mini Canal | MICL.01411034/RNA | 14 | 110 | 34 | 34 | 470 | 470 | 470 | 0.01119 | 183 | 0.0043571 | 535 | 0.012738 | 1.362 | A04 | MICL0.01411034/RNA
Build-In Floor | Mini Canal | MICL.01411034/RON | 14 | 110 | 34 | 34 | 456 | 456 | 456 | 0.010857 | 177 | 0.0042143 | 519 | 0.012357 | 1.362 | A04 | MICL0.01411034/RON
Build-In Floor | Mini Canal | MICL.01411034/ROV | 14 | 110 | 34 | 34 | 456 | 456 | 456 | 0.010857 | 177 | 0.0042143 | 519 | 0.012357 | 1.362 | A04 | MICL0.01411034/ROV
Build-In Floor | Mini Canal | MICL.01411034/RSS | 14 | 110 | 34 | 34 | 451 | 451 | 451 | 0.010738 | 175 | 0.0041667 | 514 | 0.012238 | 1.362 | A04 | MICL0.01411034/RSS
Build-In Floor | Mini Canal | MICL.01411034/SBL | 14 | 110 | 34 | 34 | 470 | 470 | 470 | 0.01119 | 183 | 0.0043571 | 535 | 0.012738 | 1.362 | A04 | MICL0.01411034/SBL
Build-In Floor | Mini Canal | MICL.01411034/SBR | 14 | 110 | 34 | 34 | 470 | 470 | 470 | 0.01119 | 183 | 0.0043571 | 535 | 0.012738 | 1.362 | A04 | MICL0.01411034/SBR
Build-In Floor | Mini Canal | MICL.01411034/SDB | 14 | 110 | 34 | 34 | 470 | 470 | 470 | 0.01119 | 183 | 0.0043571 | 535 | 0.012738 | 1.362 | A04 | MICL0.01411034/SDB
Build-In Floor | Mini Canal | MICL.01411034/SNA | 14 | 110 | 34 | 34 | 470 | 470 | 470 | 0.01119 | 183 | 0.0043571 | 535 | 0.012738 | 1.362 | A04 | MICL0.01411034/SNA
Build-In Floor | Mini Canal | MICL.01411034/SNC | 14 | 110 | 34 | 34 | 470 | 470 | 470 | 0.01119 | 183 | 0.0043571 | 535 | 0.012738 | 1.362 | A04 | MICL0.01411034/SNC
Build-In Floor | Mini Canal | MICL.01411042/ANA | 14 | 110 | 42 | 42 | 475 | 475 | 475 | 0.01131 | 185 | 0.0044048 | 541 | 0.012881 | 1.362 | A04 | MICL0.01411042/ANA
Build-In Floor | Mini Canal | MICL.01411042/DBL | 14 | 110 | 42 | 42 | 614 | 614 | 614 | 0.014619 | 239 | 0.0056905 | 699 | 0.016643 | 1.362 | A04 | MICL0.01411042/DBL
Build-In Floor | Mini Canal | MICL.01411042/DBN | 14 | 110 | 42 | 42 | 589 | 589 | 589 | 0.014024 | 229 | 0.0054524 | 671 | 0.015976 | 1.362 | A04 | MICL0.01411042/DBN
Build-In Floor | Mini Canal | MICL.01411042/DBR | 14 | 110 | 42 | 42 | 614 | 614 | 614 | 0.014619 | 239 | 0.0056905 | 699 | 0.016643 | 1.362 | A04 | MICL0.01411042/DBR
Build-In Floor | Mini Canal | MICL.01411042/DBV | 14 | 110 | 42 | 42 | 589 | 589 | 589 | 0.014024 | 229 | 0.0054524 | 671 | 0.015976 | 1.362 | A04 | MICL0.01411042/DBV
Build-In Floor | Mini Canal | MICL.01411042/DDB | 14 | 110 | 42 | 42 | 614 | 614 | 614 | 0.014619 | 239 | 0.0056905 | 699 | 0.016643 | 1.362 | A04 | MICL0.01411042/DDB
Build-In Floor | Mini Canal | MICL.01411042/DMN | 14 | 110 | 42 | 42 | 589 | 589 | 589 | 0.014024 | 229 | 0.0054524 | 671 | 0.015976 | 1.362 | A04 | MICL0.01411042/DMN
Build-In Floor | Mini Canal | MICL.01411042/DMV | 14 | 110 | 42 | 42 | 589 | 589 | 589 | 0.014024 | 229 | 0.0054524 | 671 | 0.015976 | 1.362 | A04 | MICL0.01411042/DMV
Build-In Floor | Mini Canal | MICL.01411042/DNA | 14 | 110 | 42 | 42 | 614 | 614 | 614 | 0.014619 | 239 | 0.0056905 | 699 | 0.016643 | 1.362 | A04 | MICL0.01411042/DNA
Build-In Floor | Mini Canal | MICL.01411042/DNC | 14 | 110 | 42 | 42 | 614 | 614 | 614 | 0.014619 | 239 | 0.0056905 | 699 | 0.016643 | 1.362 | A04 | MICL0.01411042/DNC
Build-In Floor | Mini Canal | MICL.01411042/DON | 14 | 110 | 42 | 42 | 589 | 589 | 589 | 0.014024 | 229 | 0.0054524 | 671 | 0.015976 | 1.362 | A04 | MICL0.01411042/DON
Build-In Floor | Mini Canal | MICL.01411042/DOV | 14 | 110 | 42 | 42 | 589 | 589 | 589 | 0.014024 | 229 | 0.0054524 | 671 | 0.015976 | 1.362 | A04 | MICL0.01411042/DOV
Build-In Floor | Mini Canal | MICL.01411042/PNC | 14 | 110 | 42 | 42 | 538 | 538 | 538 | 0.01281 | 209 | 0.0049762 | 613 | 0.014595 | 1.362 | A04 | MICL0.01411042/PNC
Build-In Floor | Mini Canal | MICL.01411042/RBL | 14 | 110 | 42 | 42 | 633 | 633 | 633 | 0.015071 | 246 | 0.0058571 | 721 | 0.017167 | 1.362 | A04 | MICL0.01411042/RBL
Build-In Floor | Mini Canal | MICL.01411042/RBN | 14 | 110 | 42 | 42 | 614 | 614 | 614 | 0.014619 | 239 | 0.0056905 | 699 | 0.016643 | 1.362 | A04 | MICL0.01411042/RBN
Build-In Floor | Mini Canal | MICL.01411042/RBR | 14 | 110 | 42 | 42 | 633 | 633 | 633 | 0.015071 | 246 | 0.0058571 | 721 | 0.017167 | 1.362 | A04 | MICL0.01411042/RBR
Build-In Floor | Mini Canal | MICL.01411042/RBV | 14 | 110 | 42 | 42 | 614 | 614 | 614 | 0.014619 | 239 | 0.0056905 | 699 | 0.016643 | 1.362 | A04 | MICL0.01411042/RBV
Build-In Floor | Mini Canal | MICL.01411042/RDB | 14 | 110 | 42 | 42 | 633 | 633 | 633 | 0.015071 | 246 | 0.0058571 | 721 | 0.017167 | 1.362 | A04 | MICL0.01411042/RDB
Build-In Floor | Mini Canal | MICL.01411042/RMN | 14 | 110 | 42 | 42 | 614 | 614 | 614 | 0.014619 | 239 | 0.0056905 | 699 | 0.016643 | 1.362 | A04 | MICL0.01411042/RMN
Build-In Floor | Mini Canal | MICL.01411042/RMV | 14 | 110 | 42 | 42 | 614 | 614 | 614 | 0.014619 | 239 | 0.0056905 | 699 | 0.016643 | 1.362 | A04 | MICL0.01411042/RMV
Build-In Floor | Mini Canal | MICL.01411042/RNA | 14 | 110 | 42 | 42 | 633 | 633 | 633 | 0.015071 | 246 | 0.0058571 | 721 | 0.017167 | 1.362 | A04 | MICL0.01411042/RNA
Build-In Floor | Mini Canal | MICL.01411042/RON | 14 | 110 | 42 | 42 | 614 | 614 | 614 | 0.014619 | 239 | 0.0056905 | 699 | 0.016643 | 1.362 | A04 | MICL0.01411042/RON
Build-In Floor | Mini Canal | MICL.01411042/ROV | 14 | 110 | 42 | 42 | 614 | 614 | 614 | 0.014619 | 239 | 0.0056905 | 699 | 0.016643 | 1.362 | A04 | MICL0.01411042/ROV
Build-In Floor | Mini Canal | MICL.01411042/RSS | 14 | 110 | 42 | 42 | 608 | 608 | 608 | 0.014476 | 237 | 0.0056429 | 693 | 0.0165 | 1.362 | A04 | MICL0.01411042/RSS
Build-In Floor | Mini Canal | MICL.01411042/SBL | 14 | 110 | 42 | 42 | 633 | 633 | 633 | 0.015071 | 246 | 0.0058571 | 721 | 0.017167 | 1.362 | A04 | MICL0.01411042/SBL
Build-In Floor | Mini Canal | MICL.01411042/SBR | 14 | 110 | 42 | 42 | 633 | 633 | 633 | 0.015071 | 246 | 0.0058571 | 721 | 0.017167 | 1.362 | A04 | MICL0.01411042/SBR
Build-In Floor | Mini Canal | MICL.01411042/SDB | 14 | 110 | 42 | 42 | 633 | 633 | 633 | 0.015071 | 246 | 0.0058571 | 721 | 0.017167 | 1.362 | A04 | MICL0.01411042/SDB
Build-In Floor | Mini Canal | MICL.01411042/SNA | 14 | 110 | 42 | 42 | 633 | 633 | 633 | 0.015071 | 246 | 0.0058571 | 721 | 0.017167 | 1.362 | A04 | MICL0.01411042/SNA
Build-In Floor | Mini Canal | MICL.01411042/SNC | 14 | 110 | 42 | 42 | 633 | 633 | 633 | 0.015071 | 246 | 0.0058571 | 721 | 0.017167 | 1.362 | A04 | MICL0.01411042/SNC
Build-In Floor | Mini Canal | MICL.01412014/ANA | 14 | 120 | 14 | 14 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.01412014/ANA
Build-In Floor | Mini Canal | MICL.01412014/DBL | 14 | 120 | 14 | 14 | 216 | 216 | 216 | 0.0051429 | 84 | 0.002 | 246 | 0.0058571 | 1.362 | A04 | MICL0.01412014/DBL
Build-In Floor | Mini Canal | MICL.01412014/DBN | 14 | 120 | 14 | 14 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01412014/DBN
Build-In Floor | Mini Canal | MICL.01412014/DBR | 14 | 120 | 14 | 14 | 216 | 216 | 216 | 0.0051429 | 84 | 0.002 | 246 | 0.0058571 | 1.362 | A04 | MICL0.01412014/DBR
Build-In Floor | Mini Canal | MICL.01412014/DBV | 14 | 120 | 14 | 14 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01412014/DBV
Build-In Floor | Mini Canal | MICL.01412014/DDB | 14 | 120 | 14 | 14 | 216 | 216 | 216 | 0.0051429 | 84 | 0.002 | 246 | 0.0058571 | 1.362 | A04 | MICL0.01412014/DDB
Build-In Floor | Mini Canal | MICL.01412014/DMN | 14 | 120 | 14 | 14 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01412014/DMN
Build-In Floor | Mini Canal | MICL.01412014/DMV | 14 | 120 | 14 | 14 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01412014/DMV
Build-In Floor | Mini Canal | MICL.01412014/DNA | 14 | 120 | 14 | 14 | 216 | 216 | 216 | 0.0051429 | 84 | 0.002 | 246 | 0.0058571 | 1.362 | A04 | MICL0.01412014/DNA
Build-In Floor | Mini Canal | MICL.01412014/DNC | 14 | 120 | 14 | 14 | 216 | 216 | 216 | 0.0051429 | 84 | 0.002 | 246 | 0.0058571 | 1.362 | A04 | MICL0.01412014/DNC
Build-In Floor | Mini Canal | MICL.01412014/DON | 14 | 120 | 14 | 14 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01412014/DON
Build-In Floor | Mini Canal | MICL.01412014/DOV | 14 | 120 | 14 | 14 | 207 | 207 | 207 | 0.0049286 | 81 | 0.0019286 | 236 | 0.005619 | 1.362 | A04 | MICL0.01412014/DOV
Build-In Floor | Mini Canal | MICL.01412014/RBL | 14 | 120 | 14 | 14 | 223 | 223 | 223 | 0.0053095 | 87 | 0.0020714 | 254 | 0.0060476 | 1.362 | A04 | MICL0.01412014/RBL
Build-In Floor | Mini Canal | MICL.01412014/RBN | 14 | 120 | 14 | 14 | 216 | 216 | 216 | 0.0051429 | 84 | 0.002 | 246 | 0.0058571 | 1.362 | A04 | MICL0.01412014/RBN
Build-In Floor | Mini Canal | MICL.01412014/RBR | 14 | 120 | 14 | 14 | 223 | 223 | 223 | 0.0053095 | 87 | 0.0020714 | 254 | 0.0060476 | 1.362 | A04 | MICL0.01412014/RBR
Build-In Floor | Mini Canal | MICL.01412014/RBV | 14 | 120 | 14 | 14 | 216 | 216 | 216 | 0.0051429 | 84 | 0.002 | 246 | 0.0058571 | 1.362 | A04 | MICL0.01412014/RBV
Build-In Floor | Mini Canal | MICL.01412014/RDB | 14 | 120 | 14 | 14 | 223 | 223 | 223 | 0.0053095 | 87 | 0.0020714 | 254 | 0.0060476 | 1.362 | A04 | MICL0.01412014/RDB
Build-In Floor | Mini Canal | MICL.01412014/RMN | 14 | 120 | 14 | 14 | 216 | 216 | 216 | 0.0051429 | 84 | 0.002 | 246 | 0.0058571 | 1.362 | A04 | MICL0.01412014/RMN
Build-In Floor | Mini Canal | MICL.01412014/RMV | 14 | 120 | 14 | 14 | 216 | 216 | 216 | 0.0051429 | 84 | 0.002 | 246 | 0.0058571 | 1.362 | A04 | MICL0.01412014/RMV
Build-In Floor | Mini Canal | MICL.01412014/RNA | 14 | 120 | 14 | 14 | 223 | 223 | 223 | 0.0053095 | 87 | 0.0020714 | 254 | 0.0060476 | 1.362 | A04 | MICL0.01412014/RNA
Build-In Floor | Mini Canal | MICL.01412014/RON | 14 | 120 | 14 | 14 | 216 | 216 | 216 | 0.0051429 | 84 | 0.002 | 246 | 0.0058571 | 1.362 | A04 | MICL0.01412014/RON
Build-In Floor | Mini Canal | MICL.01412014/ROV | 14 | 120 | 14 | 14 | 216 | 216 | 216 | 0.0051429 | 84 | 0.002 | 246 | 0.0058571 | 1.362 | A04 | MICL0.01412014/ROV
Build-In Floor | Mini Canal | MICL.01412014/RSS | 14 | 120 | 14 | 14 | 214 | 214 | 214 | 0.0050952 | 83 | 0.0019762 | 244 | 0.0058095 | 1.362 | A04 | MICL0.01412014/RSS
Build-In Floor | Mini Canal | MICL.01412014/SBL | 14 | 120 | 14 | 14 | 223 | 223 | 223 | 0.0053095 | 87 | 0.0020714 | 254 | 0.0060476 | 1.362 | A04 | MICL0.01412014/SBL
Build-In Floor | Mini Canal | MICL.01412014/SBR | 14 | 120 | 14 | 14 | 223 | 223 | 223 | 0.0053095 | 87 | 0.0020714 | 254 | 0.0060476 | 1.362 | A04 | MICL0.01412014/SBR
Build-In Floor | Mini Canal | MICL.01412014/SDB | 14 | 120 | 14 | 14 | 223 | 223 | 223 | 0.0053095 | 87 | 0.0020714 | 254 | 0.0060476 | 1.362 | A04 | MICL0.01412014/SDB
Build-In Floor | Mini Canal | MICL.01412014/SNA | 14 | 120 | 14 | 14 | 223 | 223 | 223 | 0.0053095 | 87 | 0.0020714 | 254 | 0.0060476 | 1.362 | A04 | MICL0.01412014/SNA
Build-In Floor | Mini Canal | MICL.01412014/SNC | 14 | 120 | 14 | 14 | 223 | 223 | 223 | 0.0053095 | 87 | 0.0020714 | 254 | 0.0060476 | 1.362 | A04 | MICL0.01412014/SNC
Build-In Floor | Mini Canal | MICL.01412026/ANA | 14 | 120 | 26 | 26 | 291 | 291 | 291 | 0.0069286 | 113 | 0.0026905 | 331 | 0.007881 | 1.362 | A04 | MICL0.01412026/ANA
Build-In Floor | Mini Canal | MICL.01412026/DBL | 14 | 120 | 26 | 26 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.01412026/DBL
Build-In Floor | Mini Canal | MICL.01412026/DBN | 14 | 120 | 26 | 26 | 361 | 361 | 361 | 0.0085952 | 140 | 0.0033333 | 411 | 0.0097857 | 1.362 | A04 | MICL0.01412026/DBN
Build-In Floor | Mini Canal | MICL.01412026/DBR | 14 | 120 | 26 | 26 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.01412026/DBR
Build-In Floor | Mini Canal | MICL.01412026/DBV | 14 | 120 | 26 | 26 | 361 | 361 | 361 | 0.0085952 | 140 | 0.0033333 | 411 | 0.0097857 | 1.362 | A04 | MICL0.01412026/DBV
Build-In Floor | Mini Canal | MICL.01412026/DDB | 14 | 120 | 26 | 26 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.01412026/DDB
Build-In Floor | Mini Canal | MICL.01412026/DMN | 14 | 120 | 26 | 26 | 361 | 361 | 361 | 0.0085952 | 140 | 0.0033333 | 411 | 0.0097857 | 1.362 | A04 | MICL0.01412026/DMN
Build-In Floor | Mini Canal | MICL.01412026/DMV | 14 | 120 | 26 | 26 | 361 | 361 | 361 | 0.0085952 | 140 | 0.0033333 | 411 | 0.0097857 | 1.362 | A04 | MICL0.01412026/DMV
Build-In Floor | Mini Canal | MICL.01412026/DNA | 14 | 120 | 26 | 26 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.01412026/DNA
Build-In Floor | Mini Canal | MICL.01412026/DNC | 14 | 120 | 26 | 26 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.01412026/DNC
Build-In Floor | Mini Canal | MICL.01412026/DON | 14 | 120 | 26 | 26 | 361 | 361 | 361 | 0.0085952 | 140 | 0.0033333 | 411 | 0.0097857 | 1.362 | A04 | MICL0.01412026/DON
Build-In Floor | Mini Canal | MICL.01412026/DOV | 14 | 120 | 26 | 26 | 361 | 361 | 361 | 0.0085952 | 140 | 0.0033333 | 411 | 0.0097857 | 1.362 | A04 | MICL0.01412026/DOV
Build-In Floor | Mini Canal | MICL.01412026/PNC | 14 | 120 | 26 | 26 | 330 | 330 | 330 | 0.0078571 | 128 | 0.0030476 | 376 | 0.0089524 | 1.362 | A04 | MICL0.01412026/PNC
Build-In Floor | Mini Canal | MICL.01412026/RBL | 14 | 120 | 26 | 26 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.01412026/RBL
Build-In Floor | Mini Canal | MICL.01412026/RBN | 14 | 120 | 26 | 26 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.01412026/RBN
Build-In Floor | Mini Canal | MICL.01412026/RBR | 14 | 120 | 26 | 26 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.01412026/RBR
Build-In Floor | Mini Canal | MICL.01412026/RBV | 14 | 120 | 26 | 26 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.01412026/RBV
Build-In Floor | Mini Canal | MICL.01412026/RDB | 14 | 120 | 26 | 26 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.01412026/RDB
Build-In Floor | Mini Canal | MICL.01412026/RMN | 14 | 120 | 26 | 26 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.01412026/RMN
Build-In Floor | Mini Canal | MICL.01412026/RMV | 14 | 120 | 26 | 26 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.01412026/RMV
Build-In Floor | Mini Canal | MICL.01412026/RNA | 14 | 120 | 26 | 26 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.01412026/RNA
Build-In Floor | Mini Canal | MICL.01412026/RON | 14 | 120 | 26 | 26 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.01412026/RON
Build-In Floor | Mini Canal | MICL.01412026/ROV | 14 | 120 | 26 | 26 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.01412026/ROV
Build-In Floor | Mini Canal | MICL.01412026/RSS | 14 | 120 | 26 | 26 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.01412026/RSS
Build-In Floor | Mini Canal | MICL.01412026/SBL | 14 | 120 | 26 | 26 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.01412026/SBL
Build-In Floor | Mini Canal | MICL.01412026/SBR | 14 | 120 | 26 | 26 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.01412026/SBR
Build-In Floor | Mini Canal | MICL.01412026/SDB | 14 | 120 | 26 | 26 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.01412026/SDB
Build-In Floor | Mini Canal | MICL.01412026/SNA | 14 | 120 | 26 | 26 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.01412026/SNA
Build-In Floor | Mini Canal | MICL.01412026/SNC | 14 | 120 | 26 | 26 | 388 | 388 | 388 | 0.0092381 | 151 | 0.0035952 | 442 | 0.010524 | 1.362 | A04 | MICL0.01412026/SNC
Build-In Floor | Mini Canal | MICL.01412034/ANA | 14 | 120 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01412034/ANA
Build-In Floor | Mini Canal | MICL.01412034/DBL | 14 | 120 | 34 | 34 | 513 | 513 | 513 | 0.012214 | 200 | 0.0047619 | 584 | 0.013905 | 1.362 | A04 | MICL0.01412034/DBL
Build-In Floor | Mini Canal | MICL.01412034/DBN | 14 | 120 | 34 | 34 | 492 | 492 | 492 | 0.011714 | 191 | 0.0045476 | 560 | 0.013333 | 1.362 | A04 | MICL0.01412034/DBN
Build-In Floor | Mini Canal | MICL.01412034/DBR | 14 | 120 | 34 | 34 | 513 | 513 | 513 | 0.012214 | 200 | 0.0047619 | 584 | 0.013905 | 1.362 | A04 | MICL0.01412034/DBR
Build-In Floor | Mini Canal | MICL.01412034/DBV | 14 | 120 | 34 | 34 | 492 | 492 | 492 | 0.011714 | 191 | 0.0045476 | 560 | 0.013333 | 1.362 | A04 | MICL0.01412034/DBV
Build-In Floor | Mini Canal | MICL.01412034/DDB | 14 | 120 | 34 | 34 | 513 | 513 | 513 | 0.012214 | 200 | 0.0047619 | 584 | 0.013905 | 1.362 | A04 | MICL0.01412034/DDB
Build-In Floor | Mini Canal | MICL.01412034/DMN | 14 | 120 | 34 | 34 | 492 | 492 | 492 | 0.011714 | 191 | 0.0045476 | 560 | 0.013333 | 1.362 | A04 | MICL0.01412034/DMN
Build-In Floor | Mini Canal | MICL.01412034/DMV | 14 | 120 | 34 | 34 | 492 | 492 | 492 | 0.011714 | 191 | 0.0045476 | 560 | 0.013333 | 1.362 | A04 | MICL0.01412034/DMV
Build-In Floor | Mini Canal | MICL.01412034/DNA | 14 | 120 | 34 | 34 | 513 | 513 | 513 | 0.012214 | 200 | 0.0047619 | 584 | 0.013905 | 1.362 | A04 | MICL0.01412034/DNA
Build-In Floor | Mini Canal | MICL.01412034/DNC | 14 | 120 | 34 | 34 | 513 | 513 | 513 | 0.012214 | 200 | 0.0047619 | 584 | 0.013905 | 1.362 | A04 | MICL0.01412034/DNC
Build-In Floor | Mini Canal | MICL.01412034/DON | 14 | 120 | 34 | 34 | 492 | 492 | 492 | 0.011714 | 191 | 0.0045476 | 560 | 0.013333 | 1.362 | A04 | MICL0.01412034/DON
Build-In Floor | Mini Canal | MICL.01412034/DOV | 14 | 120 | 34 | 34 | 492 | 492 | 492 | 0.011714 | 191 | 0.0045476 | 560 | 0.013333 | 1.362 | A04 | MICL0.01412034/DOV
Build-In Floor | Mini Canal | MICL.01412034/PNC | 14 | 120 | 34 | 34 | 450 | 450 | 450 | 0.010714 | 175 | 0.0041667 | 513 | 0.012214 | 1.362 | A04 | MICL0.01412034/PNC
Build-In Floor | Mini Canal | MICL.01412034/RBL | 14 | 120 | 34 | 34 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01412034/RBL
Build-In Floor | Mini Canal | MICL.01412034/RBN | 14 | 120 | 34 | 34 | 513 | 513 | 513 | 0.012214 | 200 | 0.0047619 | 584 | 0.013905 | 1.362 | A04 | MICL0.01412034/RBN
Build-In Floor | Mini Canal | MICL.01412034/RBR | 14 | 120 | 34 | 34 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01412034/RBR
Build-In Floor | Mini Canal | MICL.01412034/RBV | 14 | 120 | 34 | 34 | 513 | 513 | 513 | 0.012214 | 200 | 0.0047619 | 584 | 0.013905 | 1.362 | A04 | MICL0.01412034/RBV
Build-In Floor | Mini Canal | MICL.01412034/RDB | 14 | 120 | 34 | 34 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01412034/RDB
Build-In Floor | Mini Canal | MICL.01412034/RMN | 14 | 120 | 34 | 34 | 513 | 513 | 513 | 0.012214 | 200 | 0.0047619 | 584 | 0.013905 | 1.362 | A04 | MICL0.01412034/RMN
Build-In Floor | Mini Canal | MICL.01412034/RMV | 14 | 120 | 34 | 34 | 513 | 513 | 513 | 0.012214 | 200 | 0.0047619 | 584 | 0.013905 | 1.362 | A04 | MICL0.01412034/RMV
Build-In Floor | Mini Canal | MICL.01412034/RNA | 14 | 120 | 34 | 34 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01412034/RNA
Build-In Floor | Mini Canal | MICL.01412034/RON | 14 | 120 | 34 | 34 | 513 | 513 | 513 | 0.012214 | 200 | 0.0047619 | 584 | 0.013905 | 1.362 | A04 | MICL0.01412034/RON
Build-In Floor | Mini Canal | MICL.01412034/ROV | 14 | 120 | 34 | 34 | 513 | 513 | 513 | 0.012214 | 200 | 0.0047619 | 584 | 0.013905 | 1.362 | A04 | MICL0.01412034/ROV
Build-In Floor | Mini Canal | MICL.01412034/RSS | 14 | 120 | 34 | 34 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01412034/RSS
Build-In Floor | Mini Canal | MICL.01412034/SBL | 14 | 120 | 34 | 34 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01412034/SBL
Build-In Floor | Mini Canal | MICL.01412034/SBR | 14 | 120 | 34 | 34 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01412034/SBR
Build-In Floor | Mini Canal | MICL.01412034/SDB | 14 | 120 | 34 | 34 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01412034/SDB
Build-In Floor | Mini Canal | MICL.01412034/SNA | 14 | 120 | 34 | 34 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01412034/SNA
Build-In Floor | Mini Canal | MICL.01412034/SNC | 14 | 120 | 34 | 34 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01412034/SNC
Build-In Floor | Mini Canal | MICL.01412042/ANA | 14 | 120 | 42 | 42 | 535 | 535 | 535 | 0.012738 | 208 | 0.0049524 | 609 | 0.0145 | 1.362 | A04 | MICL0.01412042/ANA
Build-In Floor | Mini Canal | MICL.01412042/DBL | 14 | 120 | 42 | 42 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01412042/DBL
Build-In Floor | Mini Canal | MICL.01412042/DBN | 14 | 120 | 42 | 42 | 663 | 663 | 663 | 0.015786 | 258 | 0.0061429 | 755 | 0.017976 | 1.362 | A04 | MICL0.01412042/DBN
Build-In Floor | Mini Canal | MICL.01412042/DBR | 14 | 120 | 42 | 42 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01412042/DBR
Build-In Floor | Mini Canal | MICL.01412042/DBV | 14 | 120 | 42 | 42 | 663 | 663 | 663 | 0.015786 | 258 | 0.0061429 | 755 | 0.017976 | 1.362 | A04 | MICL0.01412042/DBV
Build-In Floor | Mini Canal | MICL.01412042/DDB | 14 | 120 | 42 | 42 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01412042/DDB
Build-In Floor | Mini Canal | MICL.01412042/DMN | 14 | 120 | 42 | 42 | 663 | 663 | 663 | 0.015786 | 258 | 0.0061429 | 755 | 0.017976 | 1.362 | A04 | MICL0.01412042/DMN
Build-In Floor | Mini Canal | MICL.01412042/DMV | 14 | 120 | 42 | 42 | 663 | 663 | 663 | 0.015786 | 258 | 0.0061429 | 755 | 0.017976 | 1.362 | A04 | MICL0.01412042/DMV
Build-In Floor | Mini Canal | MICL.01412042/DNA | 14 | 120 | 42 | 42 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01412042/DNA
Build-In Floor | Mini Canal | MICL.01412042/DNC | 14 | 120 | 42 | 42 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01412042/DNC
Build-In Floor | Mini Canal | MICL.01412042/DON | 14 | 120 | 42 | 42 | 663 | 663 | 663 | 0.015786 | 258 | 0.0061429 | 755 | 0.017976 | 1.362 | A04 | MICL0.01412042/DON
Build-In Floor | Mini Canal | MICL.01412042/DOV | 14 | 120 | 42 | 42 | 663 | 663 | 663 | 0.015786 | 258 | 0.0061429 | 755 | 0.017976 | 1.362 | A04 | MICL0.01412042/DOV
Build-In Floor | Mini Canal | MICL.01412042/PNC | 14 | 120 | 42 | 42 | 606 | 606 | 606 | 0.014429 | 236 | 0.005619 | 690 | 0.016429 | 1.362 | A04 | MICL0.01412042/PNC
Build-In Floor | Mini Canal | MICL.01412042/RBL | 14 | 120 | 42 | 42 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.01412042/RBL
Build-In Floor | Mini Canal | MICL.01412042/RBN | 14 | 120 | 42 | 42 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01412042/RBN
Build-In Floor | Mini Canal | MICL.01412042/RBR | 14 | 120 | 42 | 42 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.01412042/RBR
Build-In Floor | Mini Canal | MICL.01412042/RBV | 14 | 120 | 42 | 42 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01412042/RBV
Build-In Floor | Mini Canal | MICL.01412042/RDB | 14 | 120 | 42 | 42 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.01412042/RDB
Build-In Floor | Mini Canal | MICL.01412042/RMN | 14 | 120 | 42 | 42 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01412042/RMN
Build-In Floor | Mini Canal | MICL.01412042/RMV | 14 | 120 | 42 | 42 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01412042/RMV
Build-In Floor | Mini Canal | MICL.01412042/RNA | 14 | 120 | 42 | 42 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.01412042/RNA
Build-In Floor | Mini Canal | MICL.01412042/RON | 14 | 120 | 42 | 42 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01412042/RON
Build-In Floor | Mini Canal | MICL.01412042/ROV | 14 | 120 | 42 | 42 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01412042/ROV
Build-In Floor | Mini Canal | MICL.01412042/RSS | 14 | 120 | 42 | 42 | 684 | 684 | 684 | 0.016286 | 266 | 0.0063333 | 779 | 0.018548 | 1.362 | A04 | MICL0.01412042/RSS
Build-In Floor | Mini Canal | MICL.01412042/SBL | 14 | 120 | 42 | 42 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.01412042/SBL
Build-In Floor | Mini Canal | MICL.01412042/SBR | 14 | 120 | 42 | 42 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.01412042/SBR
Build-In Floor | Mini Canal | MICL.01412042/SDB | 14 | 120 | 42 | 42 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.01412042/SDB
Build-In Floor | Mini Canal | MICL.01412042/SNA | 14 | 120 | 42 | 42 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.01412042/SNA
Build-In Floor | Mini Canal | MICL.01412042/SNC | 14 | 120 | 42 | 42 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.01412042/SNC
Build-In Floor | Mini Canal | MICL.01413014/ANA | 14 | 130 | 14 | 14 | 186 | 186 | 186 | 0.0044286 | 72 | 0.0017143 | 212 | 0.0050476 | 1.362 | A04 | MICL0.01413014/ANA
Build-In Floor | Mini Canal | MICL.01413014/DBL | 14 | 130 | 14 | 14 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01413014/DBL
Build-In Floor | Mini Canal | MICL.01413014/DBN | 14 | 130 | 14 | 14 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.01413014/DBN
Build-In Floor | Mini Canal | MICL.01413014/DBR | 14 | 130 | 14 | 14 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01413014/DBR
Build-In Floor | Mini Canal | MICL.01413014/DBV | 14 | 130 | 14 | 14 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.01413014/DBV
Build-In Floor | Mini Canal | MICL.01413014/DDB | 14 | 130 | 14 | 14 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01413014/DDB
Build-In Floor | Mini Canal | MICL.01413014/DMN | 14 | 130 | 14 | 14 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.01413014/DMN
Build-In Floor | Mini Canal | MICL.01413014/DMV | 14 | 130 | 14 | 14 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.01413014/DMV
Build-In Floor | Mini Canal | MICL.01413014/DNA | 14 | 130 | 14 | 14 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01413014/DNA
Build-In Floor | Mini Canal | MICL.01413014/DNC | 14 | 130 | 14 | 14 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01413014/DNC
Build-In Floor | Mini Canal | MICL.01413014/DON | 14 | 130 | 14 | 14 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.01413014/DON
Build-In Floor | Mini Canal | MICL.01413014/DOV | 14 | 130 | 14 | 14 | 231 | 231 | 231 | 0.0055 | 90 | 0.0021429 | 263 | 0.0062619 | 1.362 | A04 | MICL0.01413014/DOV
Build-In Floor | Mini Canal | MICL.01413014/RBL | 14 | 130 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.01413014/RBL
Build-In Floor | Mini Canal | MICL.01413014/RBN | 14 | 130 | 14 | 14 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01413014/RBN
Build-In Floor | Mini Canal | MICL.01413014/RBR | 14 | 130 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.01413014/RBR
Build-In Floor | Mini Canal | MICL.01413014/RBV | 14 | 130 | 14 | 14 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01413014/RBV
Build-In Floor | Mini Canal | MICL.01413014/RDB | 14 | 130 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.01413014/RDB
Build-In Floor | Mini Canal | MICL.01413014/RMN | 14 | 130 | 14 | 14 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01413014/RMN
Build-In Floor | Mini Canal | MICL.01413014/RMV | 14 | 130 | 14 | 14 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01413014/RMV
Build-In Floor | Mini Canal | MICL.01413014/RNA | 14 | 130 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.01413014/RNA
Build-In Floor | Mini Canal | MICL.01413014/RON | 14 | 130 | 14 | 14 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01413014/RON
Build-In Floor | Mini Canal | MICL.01413014/ROV | 14 | 130 | 14 | 14 | 241 | 241 | 241 | 0.0057381 | 94 | 0.0022381 | 274 | 0.0065238 | 1.362 | A04 | MICL0.01413014/ROV
Build-In Floor | Mini Canal | MICL.01413014/RSS | 14 | 130 | 14 | 14 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01413014/RSS
Build-In Floor | Mini Canal | MICL.01413014/SBL | 14 | 130 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.01413014/SBL
Build-In Floor | Mini Canal | MICL.01413014/SBR | 14 | 130 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.01413014/SBR
Build-In Floor | Mini Canal | MICL.01413014/SDB | 14 | 130 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.01413014/SDB
Build-In Floor | Mini Canal | MICL.01413014/SNA | 14 | 130 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.01413014/SNA
Build-In Floor | Mini Canal | MICL.01413014/SNC | 14 | 130 | 14 | 14 | 248 | 248 | 248 | 0.0059048 | 96 | 0.0022857 | 282 | 0.0067143 | 1.362 | A04 | MICL0.01413014/SNC
Build-In Floor | Mini Canal | MICL.01413026/ANA | 14 | 130 | 26 | 26 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.01413026/ANA
Build-In Floor | Mini Canal | MICL.01413026/DBL | 14 | 130 | 26 | 26 | 418 | 418 | 418 | 0.0099524 | 163 | 0.003881 | 476 | 0.011333 | 1.362 | A04 | MICL0.01413026/DBL
Build-In Floor | Mini Canal | MICL.01413026/DBN | 14 | 130 | 26 | 26 | 401 | 401 | 401 | 0.0095476 | 156 | 0.0037143 | 457 | 0.010881 | 1.362 | A04 | MICL0.01413026/DBN
Build-In Floor | Mini Canal | MICL.01413026/DBR | 14 | 130 | 26 | 26 | 418 | 418 | 418 | 0.0099524 | 163 | 0.003881 | 476 | 0.011333 | 1.362 | A04 | MICL0.01413026/DBR
Build-In Floor | Mini Canal | MICL.01413026/DBV | 14 | 130 | 26 | 26 | 401 | 401 | 401 | 0.0095476 | 156 | 0.0037143 | 457 | 0.010881 | 1.362 | A04 | MICL0.01413026/DBV
Build-In Floor | Mini Canal | MICL.01413026/DDB | 14 | 130 | 26 | 26 | 418 | 418 | 418 | 0.0099524 | 163 | 0.003881 | 476 | 0.011333 | 1.362 | A04 | MICL0.01413026/DDB
Build-In Floor | Mini Canal | MICL.01413026/DMN | 14 | 130 | 26 | 26 | 401 | 401 | 401 | 0.0095476 | 156 | 0.0037143 | 457 | 0.010881 | 1.362 | A04 | MICL0.01413026/DMN
Build-In Floor | Mini Canal | MICL.01413026/DMV | 14 | 130 | 26 | 26 | 401 | 401 | 401 | 0.0095476 | 156 | 0.0037143 | 457 | 0.010881 | 1.362 | A04 | MICL0.01413026/DMV
Build-In Floor | Mini Canal | MICL.01413026/DNA | 14 | 130 | 26 | 26 | 418 | 418 | 418 | 0.0099524 | 163 | 0.003881 | 476 | 0.011333 | 1.362 | A04 | MICL0.01413026/DNA
Build-In Floor | Mini Canal | MICL.01413026/DNC | 14 | 130 | 26 | 26 | 418 | 418 | 418 | 0.0099524 | 163 | 0.003881 | 476 | 0.011333 | 1.362 | A04 | MICL0.01413026/DNC
Build-In Floor | Mini Canal | MICL.01413026/DON | 14 | 130 | 26 | 26 | 401 | 401 | 401 | 0.0095476 | 156 | 0.0037143 | 457 | 0.010881 | 1.362 | A04 | MICL0.01413026/DON
Build-In Floor | Mini Canal | MICL.01413026/DOV | 14 | 130 | 26 | 26 | 401 | 401 | 401 | 0.0095476 | 156 | 0.0037143 | 457 | 0.010881 | 1.362 | A04 | MICL0.01413026/DOV
Build-In Floor | Mini Canal | MICL.01413026/PNC | 14 | 130 | 26 | 26 | 366 | 366 | 366 | 0.0087143 | 142 | 0.003381 | 417 | 0.0099286 | 1.362 | A04 | MICL0.01413026/PNC
Build-In Floor | Mini Canal | MICL.01413026/RBL | 14 | 130 | 26 | 26 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01413026/RBL
Build-In Floor | Mini Canal | MICL.01413026/RBN | 14 | 130 | 26 | 26 | 418 | 418 | 418 | 0.0099524 | 163 | 0.003881 | 476 | 0.011333 | 1.362 | A04 | MICL0.01413026/RBN
Build-In Floor | Mini Canal | MICL.01413026/RBR | 14 | 130 | 26 | 26 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01413026/RBR
Build-In Floor | Mini Canal | MICL.01413026/RBV | 14 | 130 | 26 | 26 | 418 | 418 | 418 | 0.0099524 | 163 | 0.003881 | 476 | 0.011333 | 1.362 | A04 | MICL0.01413026/RBV
Build-In Floor | Mini Canal | MICL.01413026/RDB | 14 | 130 | 26 | 26 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01413026/RDB
Build-In Floor | Mini Canal | MICL.01413026/RMN | 14 | 130 | 26 | 26 | 418 | 418 | 418 | 0.0099524 | 163 | 0.003881 | 476 | 0.011333 | 1.362 | A04 | MICL0.01413026/RMN
Build-In Floor | Mini Canal | MICL.01413026/RMV | 14 | 130 | 26 | 26 | 418 | 418 | 418 | 0.0099524 | 163 | 0.003881 | 476 | 0.011333 | 1.362 | A04 | MICL0.01413026/RMV
Build-In Floor | Mini Canal | MICL.01413026/RNA | 14 | 130 | 26 | 26 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01413026/RNA
Build-In Floor | Mini Canal | MICL.01413026/RON | 14 | 130 | 26 | 26 | 418 | 418 | 418 | 0.0099524 | 163 | 0.003881 | 476 | 0.011333 | 1.362 | A04 | MICL0.01413026/RON
Build-In Floor | Mini Canal | MICL.01413026/ROV | 14 | 130 | 26 | 26 | 418 | 418 | 418 | 0.0099524 | 163 | 0.003881 | 476 | 0.011333 | 1.362 | A04 | MICL0.01413026/ROV
Build-In Floor | Mini Canal | MICL.01413026/RSS | 14 | 130 | 26 | 26 | 414 | 414 | 414 | 0.0098571 | 161 | 0.0038333 | 472 | 0.011238 | 1.362 | A04 | MICL0.01413026/RSS
Build-In Floor | Mini Canal | MICL.01413026/SBL | 14 | 130 | 26 | 26 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01413026/SBL
Build-In Floor | Mini Canal | MICL.01413026/SBR | 14 | 130 | 26 | 26 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01413026/SBR
Build-In Floor | Mini Canal | MICL.01413026/SDB | 14 | 130 | 26 | 26 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01413026/SDB
Build-In Floor | Mini Canal | MICL.01413026/SNA | 14 | 130 | 26 | 26 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01413026/SNA
Build-In Floor | Mini Canal | MICL.01413026/SNC | 14 | 130 | 26 | 26 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01413026/SNC
Build-In Floor | Mini Canal | MICL.01413034/ANA | 14 | 130 | 34 | 34 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01413034/ANA
Build-In Floor | Mini Canal | MICL.01413034/DBL | 14 | 130 | 34 | 34 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01413034/DBL
Build-In Floor | Mini Canal | MICL.01413034/DBN | 14 | 130 | 34 | 34 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01413034/DBN
Build-In Floor | Mini Canal | MICL.01413034/DBR | 14 | 130 | 34 | 34 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01413034/DBR
Build-In Floor | Mini Canal | MICL.01413034/DBV | 14 | 130 | 34 | 34 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01413034/DBV
Build-In Floor | Mini Canal | MICL.01413034/DDB | 14 | 130 | 34 | 34 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01413034/DDB
Build-In Floor | Mini Canal | MICL.01413034/DMN | 14 | 130 | 34 | 34 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01413034/DMN
Build-In Floor | Mini Canal | MICL.01413034/DMV | 14 | 130 | 34 | 34 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01413034/DMV
Build-In Floor | Mini Canal | MICL.01413034/DNA | 14 | 130 | 34 | 34 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01413034/DNA
Build-In Floor | Mini Canal | MICL.01413034/DNC | 14 | 130 | 34 | 34 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01413034/DNC
Build-In Floor | Mini Canal | MICL.01413034/DON | 14 | 130 | 34 | 34 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01413034/DON
Build-In Floor | Mini Canal | MICL.01413034/DOV | 14 | 130 | 34 | 34 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01413034/DOV
Build-In Floor | Mini Canal | MICL.01413034/PNC | 14 | 130 | 34 | 34 | 499 | 499 | 499 | 0.011881 | 194 | 0.004619 | 568 | 0.013524 | 1.362 | A04 | MICL0.01413034/PNC
Build-In Floor | Mini Canal | MICL.01413034/RBL | 14 | 130 | 34 | 34 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01413034/RBL
Build-In Floor | Mini Canal | MICL.01413034/RBN | 14 | 130 | 34 | 34 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01413034/RBN
Build-In Floor | Mini Canal | MICL.01413034/RBR | 14 | 130 | 34 | 34 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01413034/RBR
Build-In Floor | Mini Canal | MICL.01413034/RBV | 14 | 130 | 34 | 34 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01413034/RBV
Build-In Floor | Mini Canal | MICL.01413034/RDB | 14 | 130 | 34 | 34 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01413034/RDB
Build-In Floor | Mini Canal | MICL.01413034/RMN | 14 | 130 | 34 | 34 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01413034/RMN
Build-In Floor | Mini Canal | MICL.01413034/RMV | 14 | 130 | 34 | 34 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01413034/RMV
Build-In Floor | Mini Canal | MICL.01413034/RNA | 14 | 130 | 34 | 34 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01413034/RNA
Build-In Floor | Mini Canal | MICL.01413034/RON | 14 | 130 | 34 | 34 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01413034/RON
Build-In Floor | Mini Canal | MICL.01413034/ROV | 14 | 130 | 34 | 34 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01413034/ROV
Build-In Floor | Mini Canal | MICL.01413034/RSS | 14 | 130 | 34 | 34 | 564 | 564 | 564 | 0.013429 | 219 | 0.0052143 | 642 | 0.015286 | 1.362 | A04 | MICL0.01413034/RSS
Build-In Floor | Mini Canal | MICL.01413034/SBL | 14 | 130 | 34 | 34 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01413034/SBL
Build-In Floor | Mini Canal | MICL.01413034/SBR | 14 | 130 | 34 | 34 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01413034/SBR
Build-In Floor | Mini Canal | MICL.01413034/SDB | 14 | 130 | 34 | 34 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01413034/SDB
Build-In Floor | Mini Canal | MICL.01413034/SNA | 14 | 130 | 34 | 34 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01413034/SNA
Build-In Floor | Mini Canal | MICL.01413034/SNC | 14 | 130 | 34 | 34 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01413034/SNC
Build-In Floor | Mini Canal | MICL.01413042/ANA | 14 | 130 | 42 | 42 | 594 | 594 | 594 | 0.014143 | 231 | 0.0055 | 677 | 0.016119 | 1.362 | A04 | MICL0.01413042/ANA
Build-In Floor | Mini Canal | MICL.01413042/DBL | 14 | 130 | 42 | 42 | 768 | 768 | 768 | 0.018286 | 299 | 0.007119 | 875 | 0.020833 | 1.362 | A04 | MICL0.01413042/DBL
Build-In Floor | Mini Canal | MICL.01413042/DBN | 14 | 130 | 42 | 42 | 737 | 737 | 737 | 0.017548 | 287 | 0.0068333 | 839 | 0.019976 | 1.362 | A04 | MICL0.01413042/DBN
Build-In Floor | Mini Canal | MICL.01413042/DBR | 14 | 130 | 42 | 42 | 768 | 768 | 768 | 0.018286 | 299 | 0.007119 | 875 | 0.020833 | 1.362 | A04 | MICL0.01413042/DBR
Build-In Floor | Mini Canal | MICL.01413042/DBV | 14 | 130 | 42 | 42 | 737 | 737 | 737 | 0.017548 | 287 | 0.0068333 | 839 | 0.019976 | 1.362 | A04 | MICL0.01413042/DBV
Build-In Floor | Mini Canal | MICL.01413042/DDB | 14 | 130 | 42 | 42 | 768 | 768 | 768 | 0.018286 | 299 | 0.007119 | 875 | 0.020833 | 1.362 | A04 | MICL0.01413042/DDB
Build-In Floor | Mini Canal | MICL.01413042/DMN | 14 | 130 | 42 | 42 | 737 | 737 | 737 | 0.017548 | 287 | 0.0068333 | 839 | 0.019976 | 1.362 | A04 | MICL0.01413042/DMN
Build-In Floor | Mini Canal | MICL.01413042/DMV | 14 | 130 | 42 | 42 | 737 | 737 | 737 | 0.017548 | 287 | 0.0068333 | 839 | 0.019976 | 1.362 | A04 | MICL0.01413042/DMV
Build-In Floor | Mini Canal | MICL.01413042/DNA | 14 | 130 | 42 | 42 | 768 | 768 | 768 | 0.018286 | 299 | 0.007119 | 875 | 0.020833 | 1.362 | A04 | MICL0.01413042/DNA
Build-In Floor | Mini Canal | MICL.01413042/DNC | 14 | 130 | 42 | 42 | 768 | 768 | 768 | 0.018286 | 299 | 0.007119 | 875 | 0.020833 | 1.362 | A04 | MICL0.01413042/DNC
Build-In Floor | Mini Canal | MICL.01413042/DON | 14 | 130 | 42 | 42 | 737 | 737 | 737 | 0.017548 | 287 | 0.0068333 | 839 | 0.019976 | 1.362 | A04 | MICL0.01413042/DON
Build-In Floor | Mini Canal | MICL.01413042/DOV | 14 | 130 | 42 | 42 | 737 | 737 | 737 | 0.017548 | 287 | 0.0068333 | 839 | 0.019976 | 1.362 | A04 | MICL0.01413042/DOV
Build-In Floor | Mini Canal | MICL.01413042/PNC | 14 | 130 | 42 | 42 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01413042/PNC
Build-In Floor | Mini Canal | MICL.01413042/RBL | 14 | 130 | 42 | 42 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01413042/RBL
Build-In Floor | Mini Canal | MICL.01413042/RBN | 14 | 130 | 42 | 42 | 768 | 768 | 768 | 0.018286 | 299 | 0.007119 | 875 | 0.020833 | 1.362 | A04 | MICL0.01413042/RBN
Build-In Floor | Mini Canal | MICL.01413042/RBR | 14 | 130 | 42 | 42 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01413042/RBR
Build-In Floor | Mini Canal | MICL.01413042/RBV | 14 | 130 | 42 | 42 | 768 | 768 | 768 | 0.018286 | 299 | 0.007119 | 875 | 0.020833 | 1.362 | A04 | MICL0.01413042/RBV
Build-In Floor | Mini Canal | MICL.01413042/RDB | 14 | 130 | 42 | 42 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01413042/RDB
Build-In Floor | Mini Canal | MICL.01413042/RMN | 14 | 130 | 42 | 42 | 768 | 768 | 768 | 0.018286 | 299 | 0.007119 | 875 | 0.020833 | 1.362 | A04 | MICL0.01413042/RMN
Build-In Floor | Mini Canal | MICL.01413042/RMV | 14 | 130 | 42 | 42 | 768 | 768 | 768 | 0.018286 | 299 | 0.007119 | 875 | 0.020833 | 1.362 | A04 | MICL0.01413042/RMV
Build-In Floor | Mini Canal | MICL.01413042/RNA | 14 | 130 | 42 | 42 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01413042/RNA
Build-In Floor | Mini Canal | MICL.01413042/RON | 14 | 130 | 42 | 42 | 768 | 768 | 768 | 0.018286 | 299 | 0.007119 | 875 | 0.020833 | 1.362 | A04 | MICL0.01413042/RON
Build-In Floor | Mini Canal | MICL.01413042/ROV | 14 | 130 | 42 | 42 | 768 | 768 | 768 | 0.018286 | 299 | 0.007119 | 875 | 0.020833 | 1.362 | A04 | MICL0.01413042/ROV
Build-In Floor | Mini Canal | MICL.01413042/RSS | 14 | 130 | 42 | 42 | 760 | 760 | 760 | 0.018095 | 296 | 0.0070476 | 866 | 0.020619 | 1.362 | A04 | MICL0.01413042/RSS
Build-In Floor | Mini Canal | MICL.01413042/SBL | 14 | 130 | 42 | 42 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01413042/SBL
Build-In Floor | Mini Canal | MICL.01413042/SBR | 14 | 130 | 42 | 42 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01413042/SBR
Build-In Floor | Mini Canal | MICL.01413042/SDB | 14 | 130 | 42 | 42 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01413042/SDB
Build-In Floor | Mini Canal | MICL.01413042/SNA | 14 | 130 | 42 | 42 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01413042/SNA
Build-In Floor | Mini Canal | MICL.01413042/SNC | 14 | 130 | 42 | 42 | 792 | 792 | 792 | 0.018857 | 308 | 0.0073333 | 902 | 0.021476 | 1.362 | A04 | MICL0.01413042/SNC
Build-In Floor | Mini Canal | MICL.01415014/ANA | 14 | 150 | 14 | 14 | 224 | 224 | 224 | 0.0053333 | 87 | 0.0020714 | 255 | 0.0060714 | 1.362 | A04 | MICL0.01415014/ANA
Build-In Floor | Mini Canal | MICL.01415014/DBL | 14 | 150 | 14 | 14 | 289 | 289 | 289 | 0.006881 | 112 | 0.0026667 | 329 | 0.0078333 | 1.362 | A04 | MICL0.01415014/DBL
Build-In Floor | Mini Canal | MICL.01415014/DBN | 14 | 150 | 14 | 14 | 277 | 277 | 277 | 0.0065952 | 108 | 0.0025714 | 316 | 0.0075238 | 1.362 | A04 | MICL0.01415014/DBN
Build-In Floor | Mini Canal | MICL.01415014/DBR | 14 | 150 | 14 | 14 | 289 | 289 | 289 | 0.006881 | 112 | 0.0026667 | 329 | 0.0078333 | 1.362 | A04 | MICL0.01415014/DBR
Build-In Floor | Mini Canal | MICL.01415014/DBV | 14 | 150 | 14 | 14 | 277 | 277 | 277 | 0.0065952 | 108 | 0.0025714 | 316 | 0.0075238 | 1.362 | A04 | MICL0.01415014/DBV
Build-In Floor | Mini Canal | MICL.01415014/DDB | 14 | 150 | 14 | 14 | 289 | 289 | 289 | 0.006881 | 112 | 0.0026667 | 329 | 0.0078333 | 1.362 | A04 | MICL0.01415014/DDB
Build-In Floor | Mini Canal | MICL.01415014/DMN | 14 | 150 | 14 | 14 | 277 | 277 | 277 | 0.0065952 | 108 | 0.0025714 | 316 | 0.0075238 | 1.362 | A04 | MICL0.01415014/DMN
Build-In Floor | Mini Canal | MICL.01415014/DMV | 14 | 150 | 14 | 14 | 277 | 277 | 277 | 0.0065952 | 108 | 0.0025714 | 316 | 0.0075238 | 1.362 | A04 | MICL0.01415014/DMV
Build-In Floor | Mini Canal | MICL.01415014/DNA | 14 | 150 | 14 | 14 | 289 | 289 | 289 | 0.006881 | 112 | 0.0026667 | 329 | 0.0078333 | 1.362 | A04 | MICL0.01415014/DNA
Build-In Floor | Mini Canal | MICL.01415014/DNC | 14 | 150 | 14 | 14 | 289 | 289 | 289 | 0.006881 | 112 | 0.0026667 | 329 | 0.0078333 | 1.362 | A04 | MICL0.01415014/DNC
Build-In Floor | Mini Canal | MICL.01415014/DON | 14 | 150 | 14 | 14 | 277 | 277 | 277 | 0.0065952 | 108 | 0.0025714 | 316 | 0.0075238 | 1.362 | A04 | MICL0.01415014/DON
Build-In Floor | Mini Canal | MICL.01415014/DOV | 14 | 150 | 14 | 14 | 277 | 277 | 277 | 0.0065952 | 108 | 0.0025714 | 316 | 0.0075238 | 1.362 | A04 | MICL0.01415014/DOV
Build-In Floor | Mini Canal | MICL.01415014/RBL | 14 | 150 | 14 | 14 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.01415014/RBL
Build-In Floor | Mini Canal | MICL.01415014/RBN | 14 | 150 | 14 | 14 | 289 | 289 | 289 | 0.006881 | 112 | 0.0026667 | 329 | 0.0078333 | 1.362 | A04 | MICL0.01415014/RBN
Build-In Floor | Mini Canal | MICL.01415014/RBR | 14 | 150 | 14 | 14 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.01415014/RBR
Build-In Floor | Mini Canal | MICL.01415014/RBV | 14 | 150 | 14 | 14 | 289 | 289 | 289 | 0.006881 | 112 | 0.0026667 | 329 | 0.0078333 | 1.362 | A04 | MICL0.01415014/RBV
Build-In Floor | Mini Canal | MICL.01415014/RDB | 14 | 150 | 14 | 14 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.01415014/RDB
Build-In Floor | Mini Canal | MICL.01415014/RMN | 14 | 150 | 14 | 14 | 289 | 289 | 289 | 0.006881 | 112 | 0.0026667 | 329 | 0.0078333 | 1.362 | A04 | MICL0.01415014/RMN
Build-In Floor | Mini Canal | MICL.01415014/RMV | 14 | 150 | 14 | 14 | 289 | 289 | 289 | 0.006881 | 112 | 0.0026667 | 329 | 0.0078333 | 1.362 | A04 | MICL0.01415014/RMV
Build-In Floor | Mini Canal | MICL.01415014/RNA | 14 | 150 | 14 | 14 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.01415014/RNA
Build-In Floor | Mini Canal | MICL.01415014/RON | 14 | 150 | 14 | 14 | 289 | 289 | 289 | 0.006881 | 112 | 0.0026667 | 329 | 0.0078333 | 1.362 | A04 | MICL0.01415014/RON
Build-In Floor | Mini Canal | MICL.01415014/ROV | 14 | 150 | 14 | 14 | 289 | 289 | 289 | 0.006881 | 112 | 0.0026667 | 329 | 0.0078333 | 1.362 | A04 | MICL0.01415014/ROV
Build-In Floor | Mini Canal | MICL.01415014/RSS | 14 | 150 | 14 | 14 | 286 | 286 | 286 | 0.0068095 | 111 | 0.0026429 | 326 | 0.0077619 | 1.362 | A04 | MICL0.01415014/RSS
Build-In Floor | Mini Canal | MICL.01415014/SBL | 14 | 150 | 14 | 14 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.01415014/SBL
Build-In Floor | Mini Canal | MICL.01415014/SBR | 14 | 150 | 14 | 14 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.01415014/SBR
Build-In Floor | Mini Canal | MICL.01415014/SDB | 14 | 150 | 14 | 14 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.01415014/SDB
Build-In Floor | Mini Canal | MICL.01415014/SNA | 14 | 150 | 14 | 14 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.01415014/SNA
Build-In Floor | Mini Canal | MICL.01415014/SNC | 14 | 150 | 14 | 14 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.01415014/SNC
Build-In Floor | Mini Canal | MICL.01415026/ANA | 14 | 150 | 26 | 26 | 387 | 387 | 387 | 0.0092143 | 151 | 0.0035952 | 441 | 0.0105 | 1.362 | A04 | MICL0.01415026/ANA
Build-In Floor | Mini Canal | MICL.01415026/DBL | 14 | 150 | 26 | 26 | 501 | 501 | 501 | 0.011929 | 195 | 0.0046429 | 571 | 0.013595 | 1.362 | A04 | MICL0.01415026/DBL
Build-In Floor | Mini Canal | MICL.01415026/DBN | 14 | 150 | 26 | 26 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01415026/DBN
Build-In Floor | Mini Canal | MICL.01415026/DBR | 14 | 150 | 26 | 26 | 501 | 501 | 501 | 0.011929 | 195 | 0.0046429 | 571 | 0.013595 | 1.362 | A04 | MICL0.01415026/DBR
Build-In Floor | Mini Canal | MICL.01415026/DBV | 14 | 150 | 26 | 26 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01415026/DBV
Build-In Floor | Mini Canal | MICL.01415026/DDB | 14 | 150 | 26 | 26 | 501 | 501 | 501 | 0.011929 | 195 | 0.0046429 | 571 | 0.013595 | 1.362 | A04 | MICL0.01415026/DDB
Build-In Floor | Mini Canal | MICL.01415026/DMN | 14 | 150 | 26 | 26 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01415026/DMN
Build-In Floor | Mini Canal | MICL.01415026/DMV | 14 | 150 | 26 | 26 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01415026/DMV
Build-In Floor | Mini Canal | MICL.01415026/DNA | 14 | 150 | 26 | 26 | 501 | 501 | 501 | 0.011929 | 195 | 0.0046429 | 571 | 0.013595 | 1.362 | A04 | MICL0.01415026/DNA
Build-In Floor | Mini Canal | MICL.01415026/DNC | 14 | 150 | 26 | 26 | 501 | 501 | 501 | 0.011929 | 195 | 0.0046429 | 571 | 0.013595 | 1.362 | A04 | MICL0.01415026/DNC
Build-In Floor | Mini Canal | MICL.01415026/DON | 14 | 150 | 26 | 26 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01415026/DON
Build-In Floor | Mini Canal | MICL.01415026/DOV | 14 | 150 | 26 | 26 | 480 | 480 | 480 | 0.011429 | 187 | 0.0044524 | 547 | 0.013024 | 1.362 | A04 | MICL0.01415026/DOV
Build-In Floor | Mini Canal | MICL.01415026/PNC | 14 | 150 | 26 | 26 | 439 | 439 | 439 | 0.010452 | 171 | 0.0040714 | 500 | 0.011905 | 1.362 | A04 | MICL0.01415026/PNC
Build-In Floor | Mini Canal | MICL.01415026/RBL | 14 | 150 | 26 | 26 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01415026/RBL
Build-In Floor | Mini Canal | MICL.01415026/RBN | 14 | 150 | 26 | 26 | 501 | 501 | 501 | 0.011929 | 195 | 0.0046429 | 571 | 0.013595 | 1.362 | A04 | MICL0.01415026/RBN
Build-In Floor | Mini Canal | MICL.01415026/RBR | 14 | 150 | 26 | 26 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01415026/RBR
Build-In Floor | Mini Canal | MICL.01415026/RBV | 14 | 150 | 26 | 26 | 501 | 501 | 501 | 0.011929 | 195 | 0.0046429 | 571 | 0.013595 | 1.362 | A04 | MICL0.01415026/RBV
Build-In Floor | Mini Canal | MICL.01415026/RDB | 14 | 150 | 26 | 26 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01415026/RDB
Build-In Floor | Mini Canal | MICL.01415026/RMN | 14 | 150 | 26 | 26 | 501 | 501 | 501 | 0.011929 | 195 | 0.0046429 | 571 | 0.013595 | 1.362 | A04 | MICL0.01415026/RMN
Build-In Floor | Mini Canal | MICL.01415026/RMV | 14 | 150 | 26 | 26 | 501 | 501 | 501 | 0.011929 | 195 | 0.0046429 | 571 | 0.013595 | 1.362 | A04 | MICL0.01415026/RMV
Build-In Floor | Mini Canal | MICL.01415026/RNA | 14 | 150 | 26 | 26 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01415026/RNA
Build-In Floor | Mini Canal | MICL.01415026/RON | 14 | 150 | 26 | 26 | 501 | 501 | 501 | 0.011929 | 195 | 0.0046429 | 571 | 0.013595 | 1.362 | A04 | MICL0.01415026/RON
Build-In Floor | Mini Canal | MICL.01415026/ROV | 14 | 150 | 26 | 26 | 501 | 501 | 501 | 0.011929 | 195 | 0.0046429 | 571 | 0.013595 | 1.362 | A04 | MICL0.01415026/ROV
Build-In Floor | Mini Canal | MICL.01415026/RSS | 14 | 150 | 26 | 26 | 495 | 495 | 495 | 0.011786 | 193 | 0.0045952 | 564 | 0.013429 | 1.362 | A04 | MICL0.01415026/RSS
Build-In Floor | Mini Canal | MICL.01415026/SBL | 14 | 150 | 26 | 26 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01415026/SBL
Build-In Floor | Mini Canal | MICL.01415026/SBR | 14 | 150 | 26 | 26 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01415026/SBR
Build-In Floor | Mini Canal | MICL.01415026/SDB | 14 | 150 | 26 | 26 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01415026/SDB
Build-In Floor | Mini Canal | MICL.01415026/SNA | 14 | 150 | 26 | 26 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01415026/SNA
Build-In Floor | Mini Canal | MICL.01415026/SNC | 14 | 150 | 26 | 26 | 516 | 516 | 516 | 0.012286 | 201 | 0.0047857 | 588 | 0.014 | 1.362 | A04 | MICL0.01415026/SNC
Build-In Floor | Mini Canal | MICL.01415034/ANA | 14 | 150 | 34 | 34 | 529 | 529 | 529 | 0.012595 | 206 | 0.0049048 | 603 | 0.014357 | 1.362 | A04 | MICL0.01415034/ANA
Build-In Floor | Mini Canal | MICL.01415034/DBL | 14 | 150 | 34 | 34 | 684 | 684 | 684 | 0.016286 | 266 | 0.0063333 | 779 | 0.018548 | 1.362 | A04 | MICL0.01415034/DBL
Build-In Floor | Mini Canal | MICL.01415034/DBN | 14 | 150 | 34 | 34 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.01415034/DBN
Build-In Floor | Mini Canal | MICL.01415034/DBR | 14 | 150 | 34 | 34 | 684 | 684 | 684 | 0.016286 | 266 | 0.0063333 | 779 | 0.018548 | 1.362 | A04 | MICL0.01415034/DBR
Build-In Floor | Mini Canal | MICL.01415034/DBV | 14 | 150 | 34 | 34 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.01415034/DBV
Build-In Floor | Mini Canal | MICL.01415034/DDB | 14 | 150 | 34 | 34 | 684 | 684 | 684 | 0.016286 | 266 | 0.0063333 | 779 | 0.018548 | 1.362 | A04 | MICL0.01415034/DDB
Build-In Floor | Mini Canal | MICL.01415034/DMN | 14 | 150 | 34 | 34 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.01415034/DMN
Build-In Floor | Mini Canal | MICL.01415034/DMV | 14 | 150 | 34 | 34 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.01415034/DMV
Build-In Floor | Mini Canal | MICL.01415034/DNA | 14 | 150 | 34 | 34 | 684 | 684 | 684 | 0.016286 | 266 | 0.0063333 | 779 | 0.018548 | 1.362 | A04 | MICL0.01415034/DNA
Build-In Floor | Mini Canal | MICL.01415034/DNC | 14 | 150 | 34 | 34 | 684 | 684 | 684 | 0.016286 | 266 | 0.0063333 | 779 | 0.018548 | 1.362 | A04 | MICL0.01415034/DNC
Build-In Floor | Mini Canal | MICL.01415034/DON | 14 | 150 | 34 | 34 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.01415034/DON
Build-In Floor | Mini Canal | MICL.01415034/DOV | 14 | 150 | 34 | 34 | 656 | 656 | 656 | 0.015619 | 255 | 0.0060714 | 747 | 0.017786 | 1.362 | A04 | MICL0.01415034/DOV
Build-In Floor | Mini Canal | MICL.01415034/PNC | 14 | 150 | 34 | 34 | 599 | 599 | 599 | 0.014262 | 233 | 0.0055476 | 682 | 0.016238 | 1.362 | A04 | MICL0.01415034/PNC
Build-In Floor | Mini Canal | MICL.01415034/RBL | 14 | 150 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 274 | 0.0065238 | 803 | 0.019119 | 1.362 | A04 | MICL0.01415034/RBL
Build-In Floor | Mini Canal | MICL.01415034/RBN | 14 | 150 | 34 | 34 | 684 | 684 | 684 | 0.016286 | 266 | 0.0063333 | 779 | 0.018548 | 1.362 | A04 | MICL0.01415034/RBN
Build-In Floor | Mini Canal | MICL.01415034/RBR | 14 | 150 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 274 | 0.0065238 | 803 | 0.019119 | 1.362 | A04 | MICL0.01415034/RBR
Build-In Floor | Mini Canal | MICL.01415034/RBV | 14 | 150 | 34 | 34 | 684 | 684 | 684 | 0.016286 | 266 | 0.0063333 | 779 | 0.018548 | 1.362 | A04 | MICL0.01415034/RBV
Build-In Floor | Mini Canal | MICL.01415034/RDB | 14 | 150 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 274 | 0.0065238 | 803 | 0.019119 | 1.362 | A04 | MICL0.01415034/RDB
Build-In Floor | Mini Canal | MICL.01415034/RMN | 14 | 150 | 34 | 34 | 684 | 684 | 684 | 0.016286 | 266 | 0.0063333 | 779 | 0.018548 | 1.362 | A04 | MICL0.01415034/RMN
Build-In Floor | Mini Canal | MICL.01415034/RMV | 14 | 150 | 34 | 34 | 684 | 684 | 684 | 0.016286 | 266 | 0.0063333 | 779 | 0.018548 | 1.362 | A04 | MICL0.01415034/RMV
Build-In Floor | Mini Canal | MICL.01415034/RNA | 14 | 150 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 274 | 0.0065238 | 803 | 0.019119 | 1.362 | A04 | MICL0.01415034/RNA
Build-In Floor | Mini Canal | MICL.01415034/RON | 14 | 150 | 34 | 34 | 684 | 684 | 684 | 0.016286 | 266 | 0.0063333 | 779 | 0.018548 | 1.362 | A04 | MICL0.01415034/RON
Build-In Floor | Mini Canal | MICL.01415034/ROV | 14 | 150 | 34 | 34 | 684 | 684 | 684 | 0.016286 | 266 | 0.0063333 | 779 | 0.018548 | 1.362 | A04 | MICL0.01415034/ROV
Build-In Floor | Mini Canal | MICL.01415034/RSS | 14 | 150 | 34 | 34 | 677 | 677 | 677 | 0.016119 | 263 | 0.0062619 | 771 | 0.018357 | 1.362 | A04 | MICL0.01415034/RSS
Build-In Floor | Mini Canal | MICL.01415034/SBL | 14 | 150 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 274 | 0.0065238 | 803 | 0.019119 | 1.362 | A04 | MICL0.01415034/SBL
Build-In Floor | Mini Canal | MICL.01415034/SBR | 14 | 150 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 274 | 0.0065238 | 803 | 0.019119 | 1.362 | A04 | MICL0.01415034/SBR
Build-In Floor | Mini Canal | MICL.01415034/SDB | 14 | 150 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 274 | 0.0065238 | 803 | 0.019119 | 1.362 | A04 | MICL0.01415034/SDB
Build-In Floor | Mini Canal | MICL.01415034/SNA | 14 | 150 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 274 | 0.0065238 | 803 | 0.019119 | 1.362 | A04 | MICL0.01415034/SNA
Build-In Floor | Mini Canal | MICL.01415034/SNC | 14 | 150 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 274 | 0.0065238 | 803 | 0.019119 | 1.362 | A04 | MICL0.01415034/SNC
Build-In Floor | Mini Canal | MICL.01415042/ANA | 14 | 150 | 42 | 42 | 713 | 713 | 713 | 0.016976 | 277 | 0.0065952 | 812 | 0.019333 | 1.362 | A04 | MICL0.01415042/ANA
Build-In Floor | Mini Canal | MICL.01415042/DBL | 14 | 150 | 42 | 42 | 922 | 922 | 922 | 0.021952 | 359 | 0.0085476 | 1050 | 0.025 | 1.362 | A04 | MICL0.01415042/DBL
Build-In Floor | Mini Canal | MICL.01415042/DBN | 14 | 150 | 42 | 42 | 884 | 884 | 884 | 0.021048 | 344 | 0.0081905 | 1007 | 0.023976 | 1.362 | A04 | MICL0.01415042/DBN
Build-In Floor | Mini Canal | MICL.01415042/DBR | 14 | 150 | 42 | 42 | 922 | 922 | 922 | 0.021952 | 359 | 0.0085476 | 1050 | 0.025 | 1.362 | A04 | MICL0.01415042/DBR
Build-In Floor | Mini Canal | MICL.01415042/DBV | 14 | 150 | 42 | 42 | 884 | 884 | 884 | 0.021048 | 344 | 0.0081905 | 1007 | 0.023976 | 1.362 | A04 | MICL0.01415042/DBV
Build-In Floor | Mini Canal | MICL.01415042/DDB | 14 | 150 | 42 | 42 | 922 | 922 | 922 | 0.021952 | 359 | 0.0085476 | 1050 | 0.025 | 1.362 | A04 | MICL0.01415042/DDB
Build-In Floor | Mini Canal | MICL.01415042/DMN | 14 | 150 | 42 | 42 | 884 | 884 | 884 | 0.021048 | 344 | 0.0081905 | 1007 | 0.023976 | 1.362 | A04 | MICL0.01415042/DMN
Build-In Floor | Mini Canal | MICL.01415042/DMV | 14 | 150 | 42 | 42 | 884 | 884 | 884 | 0.021048 | 344 | 0.0081905 | 1007 | 0.023976 | 1.362 | A04 | MICL0.01415042/DMV
Build-In Floor | Mini Canal | MICL.01415042/DNA | 14 | 150 | 42 | 42 | 922 | 922 | 922 | 0.021952 | 359 | 0.0085476 | 1050 | 0.025 | 1.362 | A04 | MICL0.01415042/DNA
Build-In Floor | Mini Canal | MICL.01415042/DNC | 14 | 150 | 42 | 42 | 922 | 922 | 922 | 0.021952 | 359 | 0.0085476 | 1050 | 0.025 | 1.362 | A04 | MICL0.01415042/DNC
Build-In Floor | Mini Canal | MICL.01415042/DON | 14 | 150 | 42 | 42 | 884 | 884 | 884 | 0.021048 | 344 | 0.0081905 | 1007 | 0.023976 | 1.362 | A04 | MICL0.01415042/DON
Build-In Floor | Mini Canal | MICL.01415042/DOV | 14 | 150 | 42 | 42 | 884 | 884 | 884 | 0.021048 | 344 | 0.0081905 | 1007 | 0.023976 | 1.362 | A04 | MICL0.01415042/DOV
Build-In Floor | Mini Canal | MICL.01415042/PNC | 14 | 150 | 42 | 42 | 808 | 808 | 808 | 0.019238 | 314 | 0.0074762 | 920 | 0.021905 | 1.362 | A04 | MICL0.01415042/PNC
Build-In Floor | Mini Canal | MICL.01415042/RBL | 14 | 150 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01415042/RBL
Build-In Floor | Mini Canal | MICL.01415042/RBN | 14 | 150 | 42 | 42 | 922 | 922 | 922 | 0.021952 | 359 | 0.0085476 | 1050 | 0.025 | 1.362 | A04 | MICL0.01415042/RBN
Build-In Floor | Mini Canal | MICL.01415042/RBR | 14 | 150 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01415042/RBR
Build-In Floor | Mini Canal | MICL.01415042/RBV | 14 | 150 | 42 | 42 | 922 | 922 | 922 | 0.021952 | 359 | 0.0085476 | 1050 | 0.025 | 1.362 | A04 | MICL0.01415042/RBV
Build-In Floor | Mini Canal | MICL.01415042/RDB | 14 | 150 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01415042/RDB
Build-In Floor | Mini Canal | MICL.01415042/RMN | 14 | 150 | 42 | 42 | 922 | 922 | 922 | 0.021952 | 359 | 0.0085476 | 1050 | 0.025 | 1.362 | A04 | MICL0.01415042/RMN
Build-In Floor | Mini Canal | MICL.01415042/RMV | 14 | 150 | 42 | 42 | 922 | 922 | 922 | 0.021952 | 359 | 0.0085476 | 1050 | 0.025 | 1.362 | A04 | MICL0.01415042/RMV
Build-In Floor | Mini Canal | MICL.01415042/RNA | 14 | 150 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01415042/RNA
Build-In Floor | Mini Canal | MICL.01415042/RON | 14 | 150 | 42 | 42 | 922 | 922 | 922 | 0.021952 | 359 | 0.0085476 | 1050 | 0.025 | 1.362 | A04 | MICL0.01415042/RON
Build-In Floor | Mini Canal | MICL.01415042/ROV | 14 | 150 | 42 | 42 | 922 | 922 | 922 | 0.021952 | 359 | 0.0085476 | 1050 | 0.025 | 1.362 | A04 | MICL0.01415042/ROV
Build-In Floor | Mini Canal | MICL.01415042/RSS | 14 | 150 | 42 | 42 | 912 | 912 | 912 | 0.021714 | 355 | 0.0084524 | 1039 | 0.024738 | 1.362 | A04 | MICL0.01415042/RSS
Build-In Floor | Mini Canal | MICL.01415042/SBL | 14 | 150 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01415042/SBL
Build-In Floor | Mini Canal | MICL.01415042/SBR | 14 | 150 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01415042/SBR
Build-In Floor | Mini Canal | MICL.01415042/SDB | 14 | 150 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01415042/SDB
Build-In Floor | Mini Canal | MICL.01415042/SNA | 14 | 150 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01415042/SNA
Build-In Floor | Mini Canal | MICL.01415042/SNC | 14 | 150 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01415042/SNC
Build-In Floor | Mini Canal | MICL.01417014/ANA | 14 | 170 | 14 | 14 | 260 | 260 | 260 | 0.0061905 | 101 | 0.0024048 | 296 | 0.0070476 | 1.362 | A04 | MICL0.01417014/ANA
Build-In Floor | Mini Canal | MICL.01417014/DBL | 14 | 170 | 14 | 14 | 337 | 337 | 337 | 0.0080238 | 131 | 0.003119 | 384 | 0.0091429 | 1.362 | A04 | MICL0.01417014/DBL
Build-In Floor | Mini Canal | MICL.01417014/DBN | 14 | 170 | 14 | 14 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.01417014/DBN
Build-In Floor | Mini Canal | MICL.01417014/DBR | 14 | 170 | 14 | 14 | 337 | 337 | 337 | 0.0080238 | 131 | 0.003119 | 384 | 0.0091429 | 1.362 | A04 | MICL0.01417014/DBR
Build-In Floor | Mini Canal | MICL.01417014/DBV | 14 | 170 | 14 | 14 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.01417014/DBV
Build-In Floor | Mini Canal | MICL.01417014/DDB | 14 | 170 | 14 | 14 | 337 | 337 | 337 | 0.0080238 | 131 | 0.003119 | 384 | 0.0091429 | 1.362 | A04 | MICL0.01417014/DDB
Build-In Floor | Mini Canal | MICL.01417014/DMN | 14 | 170 | 14 | 14 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.01417014/DMN
Build-In Floor | Mini Canal | MICL.01417014/DMV | 14 | 170 | 14 | 14 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.01417014/DMV
Build-In Floor | Mini Canal | MICL.01417014/DNA | 14 | 170 | 14 | 14 | 337 | 337 | 337 | 0.0080238 | 131 | 0.003119 | 384 | 0.0091429 | 1.362 | A04 | MICL0.01417014/DNA
Build-In Floor | Mini Canal | MICL.01417014/DNC | 14 | 170 | 14 | 14 | 337 | 337 | 337 | 0.0080238 | 131 | 0.003119 | 384 | 0.0091429 | 1.362 | A04 | MICL0.01417014/DNC
Build-In Floor | Mini Canal | MICL.01417014/DON | 14 | 170 | 14 | 14 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.01417014/DON
Build-In Floor | Mini Canal | MICL.01417014/DOV | 14 | 170 | 14 | 14 | 323 | 323 | 323 | 0.0076905 | 126 | 0.003 | 368 | 0.0087619 | 1.362 | A04 | MICL0.01417014/DOV
Build-In Floor | Mini Canal | MICL.01417014/RBL | 14 | 170 | 14 | 14 | 347 | 347 | 347 | 0.0082619 | 135 | 0.0032143 | 395 | 0.0094048 | 1.362 | A04 | MICL0.01417014/RBL
Build-In Floor | Mini Canal | MICL.01417014/RBN | 14 | 170 | 14 | 14 | 337 | 337 | 337 | 0.0080238 | 131 | 0.003119 | 384 | 0.0091429 | 1.362 | A04 | MICL0.01417014/RBN
Build-In Floor | Mini Canal | MICL.01417014/RBR | 14 | 170 | 14 | 14 | 347 | 347 | 347 | 0.0082619 | 135 | 0.0032143 | 395 | 0.0094048 | 1.362 | A04 | MICL0.01417014/RBR
Build-In Floor | Mini Canal | MICL.01417014/RBV | 14 | 170 | 14 | 14 | 337 | 337 | 337 | 0.0080238 | 131 | 0.003119 | 384 | 0.0091429 | 1.362 | A04 | MICL0.01417014/RBV
Build-In Floor | Mini Canal | MICL.01417014/RDB | 14 | 170 | 14 | 14 | 347 | 347 | 347 | 0.0082619 | 135 | 0.0032143 | 395 | 0.0094048 | 1.362 | A04 | MICL0.01417014/RDB
Build-In Floor | Mini Canal | MICL.01417014/RMN | 14 | 170 | 14 | 14 | 337 | 337 | 337 | 0.0080238 | 131 | 0.003119 | 384 | 0.0091429 | 1.362 | A04 | MICL0.01417014/RMN
Build-In Floor | Mini Canal | MICL.01417014/RMV | 14 | 170 | 14 | 14 | 337 | 337 | 337 | 0.0080238 | 131 | 0.003119 | 384 | 0.0091429 | 1.362 | A04 | MICL0.01417014/RMV
Build-In Floor | Mini Canal | MICL.01417014/RNA | 14 | 170 | 14 | 14 | 347 | 347 | 347 | 0.0082619 | 135 | 0.0032143 | 395 | 0.0094048 | 1.362 | A04 | MICL0.01417014/RNA
Build-In Floor | Mini Canal | MICL.01417014/RON | 14 | 170 | 14 | 14 | 337 | 337 | 337 | 0.0080238 | 131 | 0.003119 | 384 | 0.0091429 | 1.362 | A04 | MICL0.01417014/RON
Build-In Floor | Mini Canal | MICL.01417014/ROV | 14 | 170 | 14 | 14 | 337 | 337 | 337 | 0.0080238 | 131 | 0.003119 | 384 | 0.0091429 | 1.362 | A04 | MICL0.01417014/ROV
Build-In Floor | Mini Canal | MICL.01417014/RSS | 14 | 170 | 14 | 14 | 333 | 333 | 333 | 0.0079286 | 130 | 0.0030952 | 379 | 0.0090238 | 1.362 | A04 | MICL0.01417014/RSS
Build-In Floor | Mini Canal | MICL.01417014/SBL | 14 | 170 | 14 | 14 | 347 | 347 | 347 | 0.0082619 | 135 | 0.0032143 | 395 | 0.0094048 | 1.362 | A04 | MICL0.01417014/SBL
Build-In Floor | Mini Canal | MICL.01417014/SBR | 14 | 170 | 14 | 14 | 347 | 347 | 347 | 0.0082619 | 135 | 0.0032143 | 395 | 0.0094048 | 1.362 | A04 | MICL0.01417014/SBR
Build-In Floor | Mini Canal | MICL.01417014/SDB | 14 | 170 | 14 | 14 | 347 | 347 | 347 | 0.0082619 | 135 | 0.0032143 | 395 | 0.0094048 | 1.362 | A04 | MICL0.01417014/SDB
Build-In Floor | Mini Canal | MICL.01417014/SNA | 14 | 170 | 14 | 14 | 347 | 347 | 347 | 0.0082619 | 135 | 0.0032143 | 395 | 0.0094048 | 1.362 | A04 | MICL0.01417014/SNA
Build-In Floor | Mini Canal | MICL.01417014/SNC | 14 | 170 | 14 | 14 | 347 | 347 | 347 | 0.0082619 | 135 | 0.0032143 | 395 | 0.0094048 | 1.362 | A04 | MICL0.01417014/SNC
Build-In Floor | Mini Canal | MICL.01417026/ANA | 14 | 170 | 26 | 26 | 452 | 452 | 452 | 0.010762 | 176 | 0.0041905 | 515 | 0.012262 | 1.362 | A04 | MICL0.01417026/ANA
Build-In Floor | Mini Canal | MICL.01417026/DBL | 14 | 170 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01417026/DBL
Build-In Floor | Mini Canal | MICL.01417026/DBN | 14 | 170 | 26 | 26 | 561 | 561 | 561 | 0.013357 | 218 | 0.0051905 | 639 | 0.015214 | 1.362 | A04 | MICL0.01417026/DBN
Build-In Floor | Mini Canal | MICL.01417026/DBR | 14 | 170 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01417026/DBR
Build-In Floor | Mini Canal | MICL.01417026/DBV | 14 | 170 | 26 | 26 | 561 | 561 | 561 | 0.013357 | 218 | 0.0051905 | 639 | 0.015214 | 1.362 | A04 | MICL0.01417026/DBV
Build-In Floor | Mini Canal | MICL.01417026/DDB | 14 | 170 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01417026/DDB
Build-In Floor | Mini Canal | MICL.01417026/DMN | 14 | 170 | 26 | 26 | 561 | 561 | 561 | 0.013357 | 218 | 0.0051905 | 639 | 0.015214 | 1.362 | A04 | MICL0.01417026/DMN
Build-In Floor | Mini Canal | MICL.01417026/DMV | 14 | 170 | 26 | 26 | 561 | 561 | 561 | 0.013357 | 218 | 0.0051905 | 639 | 0.015214 | 1.362 | A04 | MICL0.01417026/DMV
Build-In Floor | Mini Canal | MICL.01417026/DNA | 14 | 170 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01417026/DNA
Build-In Floor | Mini Canal | MICL.01417026/DNC | 14 | 170 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01417026/DNC
Build-In Floor | Mini Canal | MICL.01417026/DON | 14 | 170 | 26 | 26 | 561 | 561 | 561 | 0.013357 | 218 | 0.0051905 | 639 | 0.015214 | 1.362 | A04 | MICL0.01417026/DON
Build-In Floor | Mini Canal | MICL.01417026/DOV | 14 | 170 | 26 | 26 | 561 | 561 | 561 | 0.013357 | 218 | 0.0051905 | 639 | 0.015214 | 1.362 | A04 | MICL0.01417026/DOV
Build-In Floor | Mini Canal | MICL.01417026/PNC | 14 | 170 | 26 | 26 | 513 | 513 | 513 | 0.012214 | 200 | 0.0047619 | 584 | 0.013905 | 1.362 | A04 | MICL0.01417026/PNC
Build-In Floor | Mini Canal | MICL.01417026/RBL | 14 | 170 | 26 | 26 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01417026/RBL
Build-In Floor | Mini Canal | MICL.01417026/RBN | 14 | 170 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01417026/RBN
Build-In Floor | Mini Canal | MICL.01417026/RBR | 14 | 170 | 26 | 26 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01417026/RBR
Build-In Floor | Mini Canal | MICL.01417026/RBV | 14 | 170 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01417026/RBV
Build-In Floor | Mini Canal | MICL.01417026/RDB | 14 | 170 | 26 | 26 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01417026/RDB
Build-In Floor | Mini Canal | MICL.01417026/RMN | 14 | 170 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01417026/RMN
Build-In Floor | Mini Canal | MICL.01417026/RMV | 14 | 170 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01417026/RMV
Build-In Floor | Mini Canal | MICL.01417026/RNA | 14 | 170 | 26 | 26 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01417026/RNA
Build-In Floor | Mini Canal | MICL.01417026/RON | 14 | 170 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01417026/RON
Build-In Floor | Mini Canal | MICL.01417026/ROV | 14 | 170 | 26 | 26 | 585 | 585 | 585 | 0.013929 | 228 | 0.0054286 | 666 | 0.015857 | 1.362 | A04 | MICL0.01417026/ROV
Build-In Floor | Mini Canal | MICL.01417026/RSS | 14 | 170 | 26 | 26 | 579 | 579 | 579 | 0.013786 | 225 | 0.0053571 | 659 | 0.01569 | 1.362 | A04 | MICL0.01417026/RSS
Build-In Floor | Mini Canal | MICL.01417026/SBL | 14 | 170 | 26 | 26 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01417026/SBL
Build-In Floor | Mini Canal | MICL.01417026/SBR | 14 | 170 | 26 | 26 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01417026/SBR
Build-In Floor | Mini Canal | MICL.01417026/SDB | 14 | 170 | 26 | 26 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01417026/SDB
Build-In Floor | Mini Canal | MICL.01417026/SNA | 14 | 170 | 26 | 26 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01417026/SNA
Build-In Floor | Mini Canal | MICL.01417026/SNC | 14 | 170 | 26 | 26 | 603 | 603 | 603 | 0.014357 | 235 | 0.0055952 | 687 | 0.016357 | 1.362 | A04 | MICL0.01417026/SNC
Build-In Floor | Mini Canal | MICL.01417034/ANA | 14 | 170 | 34 | 34 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01417034/ANA
Build-In Floor | Mini Canal | MICL.01417034/DBL | 14 | 170 | 34 | 34 | 797 | 797 | 797 | 0.018976 | 310 | 0.007381 | 908 | 0.021619 | 1.362 | A04 | MICL0.01417034/DBL
Build-In Floor | Mini Canal | MICL.01417034/DBN | 14 | 170 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 297 | 0.0070714 | 870 | 0.020714 | 1.362 | A04 | MICL0.01417034/DBN
Build-In Floor | Mini Canal | MICL.01417034/DBR | 14 | 170 | 34 | 34 | 797 | 797 | 797 | 0.018976 | 310 | 0.007381 | 908 | 0.021619 | 1.362 | A04 | MICL0.01417034/DBR
Build-In Floor | Mini Canal | MICL.01417034/DBV | 14 | 170 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 297 | 0.0070714 | 870 | 0.020714 | 1.362 | A04 | MICL0.01417034/DBV
Build-In Floor | Mini Canal | MICL.01417034/DDB | 14 | 170 | 34 | 34 | 797 | 797 | 797 | 0.018976 | 310 | 0.007381 | 908 | 0.021619 | 1.362 | A04 | MICL0.01417034/DDB
Build-In Floor | Mini Canal | MICL.01417034/DMN | 14 | 170 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 297 | 0.0070714 | 870 | 0.020714 | 1.362 | A04 | MICL0.01417034/DMN
Build-In Floor | Mini Canal | MICL.01417034/DMV | 14 | 170 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 297 | 0.0070714 | 870 | 0.020714 | 1.362 | A04 | MICL0.01417034/DMV
Build-In Floor | Mini Canal | MICL.01417034/DNA | 14 | 170 | 34 | 34 | 797 | 797 | 797 | 0.018976 | 310 | 0.007381 | 908 | 0.021619 | 1.362 | A04 | MICL0.01417034/DNA
Build-In Floor | Mini Canal | MICL.01417034/DNC | 14 | 170 | 34 | 34 | 797 | 797 | 797 | 0.018976 | 310 | 0.007381 | 908 | 0.021619 | 1.362 | A04 | MICL0.01417034/DNC
Build-In Floor | Mini Canal | MICL.01417034/DON | 14 | 170 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 297 | 0.0070714 | 870 | 0.020714 | 1.362 | A04 | MICL0.01417034/DON
Build-In Floor | Mini Canal | MICL.01417034/DOV | 14 | 170 | 34 | 34 | 764 | 764 | 764 | 0.01819 | 297 | 0.0070714 | 870 | 0.020714 | 1.362 | A04 | MICL0.01417034/DOV
Build-In Floor | Mini Canal | MICL.01417034/PNC | 14 | 170 | 34 | 34 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01417034/PNC
Build-In Floor | Mini Canal | MICL.01417034/RBL | 14 | 170 | 34 | 34 | 822 | 822 | 822 | 0.019571 | 320 | 0.007619 | 936 | 0.022286 | 1.362 | A04 | MICL0.01417034/RBL
Build-In Floor | Mini Canal | MICL.01417034/RBN | 14 | 170 | 34 | 34 | 797 | 797 | 797 | 0.018976 | 310 | 0.007381 | 908 | 0.021619 | 1.362 | A04 | MICL0.01417034/RBN
Build-In Floor | Mini Canal | MICL.01417034/RBR | 14 | 170 | 34 | 34 | 822 | 822 | 822 | 0.019571 | 320 | 0.007619 | 936 | 0.022286 | 1.362 | A04 | MICL0.01417034/RBR
Build-In Floor | Mini Canal | MICL.01417034/RBV | 14 | 170 | 34 | 34 | 797 | 797 | 797 | 0.018976 | 310 | 0.007381 | 908 | 0.021619 | 1.362 | A04 | MICL0.01417034/RBV
Build-In Floor | Mini Canal | MICL.01417034/RDB | 14 | 170 | 34 | 34 | 822 | 822 | 822 | 0.019571 | 320 | 0.007619 | 936 | 0.022286 | 1.362 | A04 | MICL0.01417034/RDB
Build-In Floor | Mini Canal | MICL.01417034/RMN | 14 | 170 | 34 | 34 | 797 | 797 | 797 | 0.018976 | 310 | 0.007381 | 908 | 0.021619 | 1.362 | A04 | MICL0.01417034/RMN
Build-In Floor | Mini Canal | MICL.01417034/RMV | 14 | 170 | 34 | 34 | 797 | 797 | 797 | 0.018976 | 310 | 0.007381 | 908 | 0.021619 | 1.362 | A04 | MICL0.01417034/RMV
Build-In Floor | Mini Canal | MICL.01417034/RNA | 14 | 170 | 34 | 34 | 822 | 822 | 822 | 0.019571 | 320 | 0.007619 | 936 | 0.022286 | 1.362 | A04 | MICL0.01417034/RNA
Build-In Floor | Mini Canal | MICL.01417034/RON | 14 | 170 | 34 | 34 | 797 | 797 | 797 | 0.018976 | 310 | 0.007381 | 908 | 0.021619 | 1.362 | A04 | MICL0.01417034/RON
Build-In Floor | Mini Canal | MICL.01417034/ROV | 14 | 170 | 34 | 34 | 797 | 797 | 797 | 0.018976 | 310 | 0.007381 | 908 | 0.021619 | 1.362 | A04 | MICL0.01417034/ROV
Build-In Floor | Mini Canal | MICL.01417034/RSS | 14 | 170 | 34 | 34 | 789 | 789 | 789 | 0.018786 | 307 | 0.0073095 | 899 | 0.021405 | 1.362 | A04 | MICL0.01417034/RSS
Build-In Floor | Mini Canal | MICL.01417034/SBL | 14 | 170 | 34 | 34 | 822 | 822 | 822 | 0.019571 | 320 | 0.007619 | 936 | 0.022286 | 1.362 | A04 | MICL0.01417034/SBL
Build-In Floor | Mini Canal | MICL.01417034/SBR | 14 | 170 | 34 | 34 | 822 | 822 | 822 | 0.019571 | 320 | 0.007619 | 936 | 0.022286 | 1.362 | A04 | MICL0.01417034/SBR
Build-In Floor | Mini Canal | MICL.01417034/SDB | 14 | 170 | 34 | 34 | 822 | 822 | 822 | 0.019571 | 320 | 0.007619 | 936 | 0.022286 | 1.362 | A04 | MICL0.01417034/SDB
Build-In Floor | Mini Canal | MICL.01417034/SNA | 14 | 170 | 34 | 34 | 822 | 822 | 822 | 0.019571 | 320 | 0.007619 | 936 | 0.022286 | 1.362 | A04 | MICL0.01417034/SNA
Build-In Floor | Mini Canal | MICL.01417034/SNC | 14 | 170 | 34 | 34 | 822 | 822 | 822 | 0.019571 | 320 | 0.007619 | 936 | 0.022286 | 1.362 | A04 | MICL0.01417034/SNC
Build-In Floor | Mini Canal | MICL.01417042/ANA | 14 | 170 | 42 | 42 | 831 | 831 | 831 | 0.019786 | 323 | 0.0076905 | 947 | 0.022548 | 1.362 | A04 | MICL0.01417042/ANA
Build-In Floor | Mini Canal | MICL.01417042/DBL | 14 | 170 | 42 | 42 | 1075 | 1075 | 1075 | 0.025595 | 418 | 0.0099524 | 1224 | 0.029143 | 1.362 | A04 | MICL0.01417042/DBL
Build-In Floor | Mini Canal | MICL.01417042/DBN | 14 | 170 | 42 | 42 | 1030 | 1030 | 1030 | 0.024524 | 401 | 0.0095476 | 1173 | 0.027929 | 1.362 | A04 | MICL0.01417042/DBN
Build-In Floor | Mini Canal | MICL.01417042/DBR | 14 | 170 | 42 | 42 | 1075 | 1075 | 1075 | 0.025595 | 418 | 0.0099524 | 1224 | 0.029143 | 1.362 | A04 | MICL0.01417042/DBR
Build-In Floor | Mini Canal | MICL.01417042/DBV | 14 | 170 | 42 | 42 | 1030 | 1030 | 1030 | 0.024524 | 401 | 0.0095476 | 1173 | 0.027929 | 1.362 | A04 | MICL0.01417042/DBV
Build-In Floor | Mini Canal | MICL.01417042/DDB | 14 | 170 | 42 | 42 | 1075 | 1075 | 1075 | 0.025595 | 418 | 0.0099524 | 1224 | 0.029143 | 1.362 | A04 | MICL0.01417042/DDB
Build-In Floor | Mini Canal | MICL.01417042/DMN | 14 | 170 | 42 | 42 | 1030 | 1030 | 1030 | 0.024524 | 401 | 0.0095476 | 1173 | 0.027929 | 1.362 | A04 | MICL0.01417042/DMN
Build-In Floor | Mini Canal | MICL.01417042/DMV | 14 | 170 | 42 | 42 | 1030 | 1030 | 1030 | 0.024524 | 401 | 0.0095476 | 1173 | 0.027929 | 1.362 | A04 | MICL0.01417042/DMV
Build-In Floor | Mini Canal | MICL.01417042/DNA | 14 | 170 | 42 | 42 | 1075 | 1075 | 1075 | 0.025595 | 418 | 0.0099524 | 1224 | 0.029143 | 1.362 | A04 | MICL0.01417042/DNA
Build-In Floor | Mini Canal | MICL.01417042/DNC | 14 | 170 | 42 | 42 | 1075 | 1075 | 1075 | 0.025595 | 418 | 0.0099524 | 1224 | 0.029143 | 1.362 | A04 | MICL0.01417042/DNC
Build-In Floor | Mini Canal | MICL.01417042/DON | 14 | 170 | 42 | 42 | 1030 | 1030 | 1030 | 0.024524 | 401 | 0.0095476 | 1173 | 0.027929 | 1.362 | A04 | MICL0.01417042/DON
Build-In Floor | Mini Canal | MICL.01417042/DOV | 14 | 170 | 42 | 42 | 1030 | 1030 | 1030 | 0.024524 | 401 | 0.0095476 | 1173 | 0.027929 | 1.362 | A04 | MICL0.01417042/DOV
Build-In Floor | Mini Canal | MICL.01417042/PNC | 14 | 170 | 42 | 42 | 942 | 942 | 942 | 0.022429 | 366 | 0.0087143 | 1073 | 0.025548 | 1.362 | A04 | MICL0.01417042/PNC
Build-In Floor | Mini Canal | MICL.01417042/RBL | 14 | 170 | 42 | 42 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01417042/RBL
Build-In Floor | Mini Canal | MICL.01417042/RBN | 14 | 170 | 42 | 42 | 1075 | 1075 | 1075 | 0.025595 | 418 | 0.0099524 | 1224 | 0.029143 | 1.362 | A04 | MICL0.01417042/RBN
Build-In Floor | Mini Canal | MICL.01417042/RBR | 14 | 170 | 42 | 42 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01417042/RBR
Build-In Floor | Mini Canal | MICL.01417042/RBV | 14 | 170 | 42 | 42 | 1075 | 1075 | 1075 | 0.025595 | 418 | 0.0099524 | 1224 | 0.029143 | 1.362 | A04 | MICL0.01417042/RBV
Build-In Floor | Mini Canal | MICL.01417042/RDB | 14 | 170 | 42 | 42 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01417042/RDB
Build-In Floor | Mini Canal | MICL.01417042/RMN | 14 | 170 | 42 | 42 | 1075 | 1075 | 1075 | 0.025595 | 418 | 0.0099524 | 1224 | 0.029143 | 1.362 | A04 | MICL0.01417042/RMN
Build-In Floor | Mini Canal | MICL.01417042/RMV | 14 | 170 | 42 | 42 | 1075 | 1075 | 1075 | 0.025595 | 418 | 0.0099524 | 1224 | 0.029143 | 1.362 | A04 | MICL0.01417042/RMV
Build-In Floor | Mini Canal | MICL.01417042/RNA | 14 | 170 | 42 | 42 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01417042/RNA
Build-In Floor | Mini Canal | MICL.01417042/RON | 14 | 170 | 42 | 42 | 1075 | 1075 | 1075 | 0.025595 | 418 | 0.0099524 | 1224 | 0.029143 | 1.362 | A04 | MICL0.01417042/RON
Build-In Floor | Mini Canal | MICL.01417042/ROV | 14 | 170 | 42 | 42 | 1075 | 1075 | 1075 | 0.025595 | 418 | 0.0099524 | 1224 | 0.029143 | 1.362 | A04 | MICL0.01417042/ROV
Build-In Floor | Mini Canal | MICL.01417042/RSS | 14 | 170 | 42 | 42 | 1064 | 1064 | 1064 | 0.025333 | 414 | 0.0098571 | 1212 | 0.028857 | 1.362 | A04 | MICL0.01417042/RSS
Build-In Floor | Mini Canal | MICL.01417042/SBL | 14 | 170 | 42 | 42 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01417042/SBL
Build-In Floor | Mini Canal | MICL.01417042/SBR | 14 | 170 | 42 | 42 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01417042/SBR
Build-In Floor | Mini Canal | MICL.01417042/SDB | 14 | 170 | 42 | 42 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01417042/SDB
Build-In Floor | Mini Canal | MICL.01417042/SNA | 14 | 170 | 42 | 42 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01417042/SNA
Build-In Floor | Mini Canal | MICL.01417042/SNC | 14 | 170 | 42 | 42 | 1108 | 1108 | 1108 | 0.026381 | 431 | 0.010262 | 1262 | 0.030048 | 1.362 | A04 | MICL0.01417042/SNC
Build-In Floor | Mini Canal | MICL.01419014/ANA | 14 | 190 | 14 | 14 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.01419014/ANA
Build-In Floor | Mini Canal | MICL.01419014/DBL | 14 | 190 | 14 | 14 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01419014/DBL
Build-In Floor | Mini Canal | MICL.01419014/DBN | 14 | 190 | 14 | 14 | 369 | 369 | 369 | 0.0087857 | 144 | 0.0034286 | 420 | 0.01 | 1.362 | A04 | MICL0.01419014/DBN
Build-In Floor | Mini Canal | MICL.01419014/DBR | 14 | 190 | 14 | 14 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01419014/DBR
Build-In Floor | Mini Canal | MICL.01419014/DBV | 14 | 190 | 14 | 14 | 369 | 369 | 369 | 0.0087857 | 144 | 0.0034286 | 420 | 0.01 | 1.362 | A04 | MICL0.01419014/DBV
Build-In Floor | Mini Canal | MICL.01419014/DDB | 14 | 190 | 14 | 14 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01419014/DDB
Build-In Floor | Mini Canal | MICL.01419014/DMN | 14 | 190 | 14 | 14 | 369 | 369 | 369 | 0.0087857 | 144 | 0.0034286 | 420 | 0.01 | 1.362 | A04 | MICL0.01419014/DMN
Build-In Floor | Mini Canal | MICL.01419014/DMV | 14 | 190 | 14 | 14 | 369 | 369 | 369 | 0.0087857 | 144 | 0.0034286 | 420 | 0.01 | 1.362 | A04 | MICL0.01419014/DMV
Build-In Floor | Mini Canal | MICL.01419014/DNA | 14 | 190 | 14 | 14 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01419014/DNA
Build-In Floor | Mini Canal | MICL.01419014/DNC | 14 | 190 | 14 | 14 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01419014/DNC
Build-In Floor | Mini Canal | MICL.01419014/DON | 14 | 190 | 14 | 14 | 369 | 369 | 369 | 0.0087857 | 144 | 0.0034286 | 420 | 0.01 | 1.362 | A04 | MICL0.01419014/DON
Build-In Floor | Mini Canal | MICL.01419014/DOV | 14 | 190 | 14 | 14 | 369 | 369 | 369 | 0.0087857 | 144 | 0.0034286 | 420 | 0.01 | 1.362 | A04 | MICL0.01419014/DOV
Build-In Floor | Mini Canal | MICL.01419014/RBL | 14 | 190 | 14 | 14 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01419014/RBL
Build-In Floor | Mini Canal | MICL.01419014/RBN | 14 | 190 | 14 | 14 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01419014/RBN
Build-In Floor | Mini Canal | MICL.01419014/RBR | 14 | 190 | 14 | 14 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01419014/RBR
Build-In Floor | Mini Canal | MICL.01419014/RBV | 14 | 190 | 14 | 14 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01419014/RBV
Build-In Floor | Mini Canal | MICL.01419014/RDB | 14 | 190 | 14 | 14 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01419014/RDB
Build-In Floor | Mini Canal | MICL.01419014/RMN | 14 | 190 | 14 | 14 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01419014/RMN
Build-In Floor | Mini Canal | MICL.01419014/RMV | 14 | 190 | 14 | 14 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01419014/RMV
Build-In Floor | Mini Canal | MICL.01419014/RNA | 14 | 190 | 14 | 14 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01419014/RNA
Build-In Floor | Mini Canal | MICL.01419014/RON | 14 | 190 | 14 | 14 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01419014/RON
Build-In Floor | Mini Canal | MICL.01419014/ROV | 14 | 190 | 14 | 14 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01419014/ROV
Build-In Floor | Mini Canal | MICL.01419014/RSS | 14 | 190 | 14 | 14 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.01419014/RSS
Build-In Floor | Mini Canal | MICL.01419014/SBL | 14 | 190 | 14 | 14 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01419014/SBL
Build-In Floor | Mini Canal | MICL.01419014/SBR | 14 | 190 | 14 | 14 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01419014/SBR
Build-In Floor | Mini Canal | MICL.01419014/SDB | 14 | 190 | 14 | 14 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01419014/SDB
Build-In Floor | Mini Canal | MICL.01419014/SNA | 14 | 190 | 14 | 14 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01419014/SNA
Build-In Floor | Mini Canal | MICL.01419014/SNC | 14 | 190 | 14 | 14 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01419014/SNC
Build-In Floor | Mini Canal | MICL.01419026/ANA | 14 | 190 | 26 | 26 | 517 | 517 | 517 | 0.01231 | 201 | 0.0047857 | 589 | 0.014024 | 1.362 | A04 | MICL0.01419026/ANA
Build-In Floor | Mini Canal | MICL.01419026/DBL | 14 | 190 | 26 | 26 | 668 | 668 | 668 | 0.015905 | 260 | 0.0061905 | 761 | 0.018119 | 1.362 | A04 | MICL0.01419026/DBL
Build-In Floor | Mini Canal | MICL.01419026/DBN | 14 | 190 | 26 | 26 | 641 | 641 | 641 | 0.015262 | 249 | 0.0059286 | 730 | 0.017381 | 1.362 | A04 | MICL0.01419026/DBN
Build-In Floor | Mini Canal | MICL.01419026/DBR | 14 | 190 | 26 | 26 | 668 | 668 | 668 | 0.015905 | 260 | 0.0061905 | 761 | 0.018119 | 1.362 | A04 | MICL0.01419026/DBR
Build-In Floor | Mini Canal | MICL.01419026/DBV | 14 | 190 | 26 | 26 | 641 | 641 | 641 | 0.015262 | 249 | 0.0059286 | 730 | 0.017381 | 1.362 | A04 | MICL0.01419026/DBV
Build-In Floor | Mini Canal | MICL.01419026/DDB | 14 | 190 | 26 | 26 | 668 | 668 | 668 | 0.015905 | 260 | 0.0061905 | 761 | 0.018119 | 1.362 | A04 | MICL0.01419026/DDB
Build-In Floor | Mini Canal | MICL.01419026/DMN | 14 | 190 | 26 | 26 | 641 | 641 | 641 | 0.015262 | 249 | 0.0059286 | 730 | 0.017381 | 1.362 | A04 | MICL0.01419026/DMN
Build-In Floor | Mini Canal | MICL.01419026/DMV | 14 | 190 | 26 | 26 | 641 | 641 | 641 | 0.015262 | 249 | 0.0059286 | 730 | 0.017381 | 1.362 | A04 | MICL0.01419026/DMV
Build-In Floor | Mini Canal | MICL.01419026/DNA | 14 | 190 | 26 | 26 | 668 | 668 | 668 | 0.015905 | 260 | 0.0061905 | 761 | 0.018119 | 1.362 | A04 | MICL0.01419026/DNA
Build-In Floor | Mini Canal | MICL.01419026/DNC | 14 | 190 | 26 | 26 | 668 | 668 | 668 | 0.015905 | 260 | 0.0061905 | 761 | 0.018119 | 1.362 | A04 | MICL0.01419026/DNC
Build-In Floor | Mini Canal | MICL.01419026/DON | 14 | 190 | 26 | 26 | 641 | 641 | 641 | 0.015262 | 249 | 0.0059286 | 730 | 0.017381 | 1.362 | A04 | MICL0.01419026/DON
Build-In Floor | Mini Canal | MICL.01419026/DOV | 14 | 190 | 26 | 26 | 641 | 641 | 641 | 0.015262 | 249 | 0.0059286 | 730 | 0.017381 | 1.362 | A04 | MICL0.01419026/DOV
Build-In Floor | Mini Canal | MICL.01419026/PNC | 14 | 190 | 26 | 26 | 586 | 586 | 586 | 0.013952 | 228 | 0.0054286 | 667 | 0.015881 | 1.362 | A04 | MICL0.01419026/PNC
Build-In Floor | Mini Canal | MICL.01419026/RBL | 14 | 190 | 26 | 26 | 689 | 689 | 689 | 0.016405 | 268 | 0.006381 | 785 | 0.01869 | 1.362 | A04 | MICL0.01419026/RBL
Build-In Floor | Mini Canal | MICL.01419026/RBN | 14 | 190 | 26 | 26 | 668 | 668 | 668 | 0.015905 | 260 | 0.0061905 | 761 | 0.018119 | 1.362 | A04 | MICL0.01419026/RBN
Build-In Floor | Mini Canal | MICL.01419026/RBR | 14 | 190 | 26 | 26 | 689 | 689 | 689 | 0.016405 | 268 | 0.006381 | 785 | 0.01869 | 1.362 | A04 | MICL0.01419026/RBR
Build-In Floor | Mini Canal | MICL.01419026/RBV | 14 | 190 | 26 | 26 | 668 | 668 | 668 | 0.015905 | 260 | 0.0061905 | 761 | 0.018119 | 1.362 | A04 | MICL0.01419026/RBV
Build-In Floor | Mini Canal | MICL.01419026/RDB | 14 | 190 | 26 | 26 | 689 | 689 | 689 | 0.016405 | 268 | 0.006381 | 785 | 0.01869 | 1.362 | A04 | MICL0.01419026/RDB
Build-In Floor | Mini Canal | MICL.01419026/RMN | 14 | 190 | 26 | 26 | 668 | 668 | 668 | 0.015905 | 260 | 0.0061905 | 761 | 0.018119 | 1.362 | A04 | MICL0.01419026/RMN
Build-In Floor | Mini Canal | MICL.01419026/RMV | 14 | 190 | 26 | 26 | 668 | 668 | 668 | 0.015905 | 260 | 0.0061905 | 761 | 0.018119 | 1.362 | A04 | MICL0.01419026/RMV
Build-In Floor | Mini Canal | MICL.01419026/RNA | 14 | 190 | 26 | 26 | 689 | 689 | 689 | 0.016405 | 268 | 0.006381 | 785 | 0.01869 | 1.362 | A04 | MICL0.01419026/RNA
Build-In Floor | Mini Canal | MICL.01419026/RON | 14 | 190 | 26 | 26 | 668 | 668 | 668 | 0.015905 | 260 | 0.0061905 | 761 | 0.018119 | 1.362 | A04 | MICL0.01419026/RON
Build-In Floor | Mini Canal | MICL.01419026/ROV | 14 | 190 | 26 | 26 | 668 | 668 | 668 | 0.015905 | 260 | 0.0061905 | 761 | 0.018119 | 1.362 | A04 | MICL0.01419026/ROV
Build-In Floor | Mini Canal | MICL.01419026/RSS | 14 | 190 | 26 | 26 | 661 | 661 | 661 | 0.015738 | 257 | 0.006119 | 753 | 0.017929 | 1.362 | A04 | MICL0.01419026/RSS
Build-In Floor | Mini Canal | MICL.01419026/SBL | 14 | 190 | 26 | 26 | 689 | 689 | 689 | 0.016405 | 268 | 0.006381 | 785 | 0.01869 | 1.362 | A04 | MICL0.01419026/SBL
Build-In Floor | Mini Canal | MICL.01419026/SBR | 14 | 190 | 26 | 26 | 689 | 689 | 689 | 0.016405 | 268 | 0.006381 | 785 | 0.01869 | 1.362 | A04 | MICL0.01419026/SBR
Build-In Floor | Mini Canal | MICL.01419026/SDB | 14 | 190 | 26 | 26 | 689 | 689 | 689 | 0.016405 | 268 | 0.006381 | 785 | 0.01869 | 1.362 | A04 | MICL0.01419026/SDB
Build-In Floor | Mini Canal | MICL.01419026/SNA | 14 | 190 | 26 | 26 | 689 | 689 | 689 | 0.016405 | 268 | 0.006381 | 785 | 0.01869 | 1.362 | A04 | MICL0.01419026/SNA
Build-In Floor | Mini Canal | MICL.01419026/SNC | 14 | 190 | 26 | 26 | 689 | 689 | 689 | 0.016405 | 268 | 0.006381 | 785 | 0.01869 | 1.362 | A04 | MICL0.01419026/SNC
Build-In Floor | Mini Canal | MICL.01419034/ANA | 14 | 190 | 34 | 34 | 705 | 705 | 705 | 0.016786 | 274 | 0.0065238 | 803 | 0.019119 | 1.362 | A04 | MICL0.01419034/ANA
Build-In Floor | Mini Canal | MICL.01419034/DBL | 14 | 190 | 34 | 34 | 912 | 912 | 912 | 0.021714 | 355 | 0.0084524 | 1039 | 0.024738 | 1.362 | A04 | MICL0.01419034/DBL
Build-In Floor | Mini Canal | MICL.01419034/DBN | 14 | 190 | 34 | 34 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01419034/DBN
Build-In Floor | Mini Canal | MICL.01419034/DBR | 14 | 190 | 34 | 34 | 912 | 912 | 912 | 0.021714 | 355 | 0.0084524 | 1039 | 0.024738 | 1.362 | A04 | MICL0.01419034/DBR
Build-In Floor | Mini Canal | MICL.01419034/DBV | 14 | 190 | 34 | 34 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01419034/DBV
Build-In Floor | Mini Canal | MICL.01419034/DDB | 14 | 190 | 34 | 34 | 912 | 912 | 912 | 0.021714 | 355 | 0.0084524 | 1039 | 0.024738 | 1.362 | A04 | MICL0.01419034/DDB
Build-In Floor | Mini Canal | MICL.01419034/DMN | 14 | 190 | 34 | 34 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01419034/DMN
Build-In Floor | Mini Canal | MICL.01419034/DMV | 14 | 190 | 34 | 34 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01419034/DMV
Build-In Floor | Mini Canal | MICL.01419034/DNA | 14 | 190 | 34 | 34 | 912 | 912 | 912 | 0.021714 | 355 | 0.0084524 | 1039 | 0.024738 | 1.362 | A04 | MICL0.01419034/DNA
Build-In Floor | Mini Canal | MICL.01419034/DNC | 14 | 190 | 34 | 34 | 912 | 912 | 912 | 0.021714 | 355 | 0.0084524 | 1039 | 0.024738 | 1.362 | A04 | MICL0.01419034/DNC
Build-In Floor | Mini Canal | MICL.01419034/DON | 14 | 190 | 34 | 34 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01419034/DON
Build-In Floor | Mini Canal | MICL.01419034/DOV | 14 | 190 | 34 | 34 | 874 | 874 | 874 | 0.02081 | 340 | 0.0080952 | 995 | 0.02369 | 1.362 | A04 | MICL0.01419034/DOV
Build-In Floor | Mini Canal | MICL.01419034/PNC | 14 | 190 | 34 | 34 | 799 | 799 | 799 | 0.019024 | 311 | 0.0074048 | 910 | 0.021667 | 1.362 | A04 | MICL0.01419034/PNC
Build-In Floor | Mini Canal | MICL.01419034/RBL | 14 | 190 | 34 | 34 | 940 | 940 | 940 | 0.022381 | 366 | 0.0087143 | 1071 | 0.0255 | 1.362 | A04 | MICL0.01419034/RBL
Build-In Floor | Mini Canal | MICL.01419034/RBN | 14 | 190 | 34 | 34 | 912 | 912 | 912 | 0.021714 | 355 | 0.0084524 | 1039 | 0.024738 | 1.362 | A04 | MICL0.01419034/RBN
Build-In Floor | Mini Canal | MICL.01419034/RBR | 14 | 190 | 34 | 34 | 940 | 940 | 940 | 0.022381 | 366 | 0.0087143 | 1071 | 0.0255 | 1.362 | A04 | MICL0.01419034/RBR
Build-In Floor | Mini Canal | MICL.01419034/RBV | 14 | 190 | 34 | 34 | 912 | 912 | 912 | 0.021714 | 355 | 0.0084524 | 1039 | 0.024738 | 1.362 | A04 | MICL0.01419034/RBV
Build-In Floor | Mini Canal | MICL.01419034/RDB | 14 | 190 | 34 | 34 | 940 | 940 | 940 | 0.022381 | 366 | 0.0087143 | 1071 | 0.0255 | 1.362 | A04 | MICL0.01419034/RDB
Build-In Floor | Mini Canal | MICL.01419034/RMN | 14 | 190 | 34 | 34 | 912 | 912 | 912 | 0.021714 | 355 | 0.0084524 | 1039 | 0.024738 | 1.362 | A04 | MICL0.01419034/RMN
Build-In Floor | Mini Canal | MICL.01419034/RMV | 14 | 190 | 34 | 34 | 912 | 912 | 912 | 0.021714 | 355 | 0.0084524 | 1039 | 0.024738 | 1.362 | A04 | MICL0.01419034/RMV
Build-In Floor | Mini Canal | MICL.01419034/RNA | 14 | 190 | 34 | 34 | 940 | 940 | 940 | 0.022381 | 366 | 0.0087143 | 1071 | 0.0255 | 1.362 | A04 | MICL0.01419034/RNA
Build-In Floor | Mini Canal | MICL.01419034/RON | 14 | 190 | 34 | 34 | 912 | 912 | 912 | 0.021714 | 355 | 0.0084524 | 1039 | 0.024738 | 1.362 | A04 | MICL0.01419034/RON
Build-In Floor | Mini Canal | MICL.01419034/ROV | 14 | 190 | 34 | 34 | 912 | 912 | 912 | 0.021714 | 355 | 0.0084524 | 1039 | 0.024738 | 1.362 | A04 | MICL0.01419034/ROV
Build-In Floor | Mini Canal | MICL.01419034/RSS | 14 | 190 | 34 | 34 | 902 | 902 | 902 | 0.021476 | 351 | 0.0083571 | 1027 | 0.024452 | 1.362 | A04 | MICL0.01419034/RSS
Build-In Floor | Mini Canal | MICL.01419034/SBL | 14 | 190 | 34 | 34 | 940 | 940 | 940 | 0.022381 | 366 | 0.0087143 | 1071 | 0.0255 | 1.362 | A04 | MICL0.01419034/SBL
Build-In Floor | Mini Canal | MICL.01419034/SBR | 14 | 190 | 34 | 34 | 940 | 940 | 940 | 0.022381 | 366 | 0.0087143 | 1071 | 0.0255 | 1.362 | A04 | MICL0.01419034/SBR
Build-In Floor | Mini Canal | MICL.01419034/SDB | 14 | 190 | 34 | 34 | 940 | 940 | 940 | 0.022381 | 366 | 0.0087143 | 1071 | 0.0255 | 1.362 | A04 | MICL0.01419034/SDB
Build-In Floor | Mini Canal | MICL.01419034/SNA | 14 | 190 | 34 | 34 | 940 | 940 | 940 | 0.022381 | 366 | 0.0087143 | 1071 | 0.0255 | 1.362 | A04 | MICL0.01419034/SNA
Build-In Floor | Mini Canal | MICL.01419034/SNC | 14 | 190 | 34 | 34 | 940 | 940 | 940 | 0.022381 | 366 | 0.0087143 | 1071 | 0.0255 | 1.362 | A04 | MICL0.01419034/SNC
Build-In Floor | Mini Canal | MICL.01419042/ANA | 14 | 190 | 42 | 42 | 950 | 950 | 950 | 0.022619 | 370 | 0.0088095 | 1082 | 0.025762 | 1.362 | A04 | MICL0.01419042/ANA
Build-In Floor | Mini Canal | MICL.01419042/DBL | 14 | 190 | 42 | 42 | 1229 | 1229 | 1229 | 0.029262 | 478 | 0.011381 | 1400 | 0.033333 | 1.362 | A04 | MICL0.01419042/DBL
Build-In Floor | Mini Canal | MICL.01419042/DBN | 14 | 190 | 42 | 42 | 1178 | 1178 | 1178 | 0.028048 | 458 | 0.010905 | 1342 | 0.031952 | 1.362 | A04 | MICL0.01419042/DBN
Build-In Floor | Mini Canal | MICL.01419042/DBR | 14 | 190 | 42 | 42 | 1229 | 1229 | 1229 | 0.029262 | 478 | 0.011381 | 1400 | 0.033333 | 1.362 | A04 | MICL0.01419042/DBR
Build-In Floor | Mini Canal | MICL.01419042/DBV | 14 | 190 | 42 | 42 | 1178 | 1178 | 1178 | 0.028048 | 458 | 0.010905 | 1342 | 0.031952 | 1.362 | A04 | MICL0.01419042/DBV
Build-In Floor | Mini Canal | MICL.01419042/DDB | 14 | 190 | 42 | 42 | 1229 | 1229 | 1229 | 0.029262 | 478 | 0.011381 | 1400 | 0.033333 | 1.362 | A04 | MICL0.01419042/DDB
Build-In Floor | Mini Canal | MICL.01419042/DMN | 14 | 190 | 42 | 42 | 1178 | 1178 | 1178 | 0.028048 | 458 | 0.010905 | 1342 | 0.031952 | 1.362 | A04 | MICL0.01419042/DMN
Build-In Floor | Mini Canal | MICL.01419042/DMV | 14 | 190 | 42 | 42 | 1178 | 1178 | 1178 | 0.028048 | 458 | 0.010905 | 1342 | 0.031952 | 1.362 | A04 | MICL0.01419042/DMV
Build-In Floor | Mini Canal | MICL.01419042/DNA | 14 | 190 | 42 | 42 | 1229 | 1229 | 1229 | 0.029262 | 478 | 0.011381 | 1400 | 0.033333 | 1.362 | A04 | MICL0.01419042/DNA
Build-In Floor | Mini Canal | MICL.01419042/DNC | 14 | 190 | 42 | 42 | 1229 | 1229 | 1229 | 0.029262 | 478 | 0.011381 | 1400 | 0.033333 | 1.362 | A04 | MICL0.01419042/DNC
Build-In Floor | Mini Canal | MICL.01419042/DON | 14 | 190 | 42 | 42 | 1178 | 1178 | 1178 | 0.028048 | 458 | 0.010905 | 1342 | 0.031952 | 1.362 | A04 | MICL0.01419042/DON
Build-In Floor | Mini Canal | MICL.01419042/DOV | 14 | 190 | 42 | 42 | 1178 | 1178 | 1178 | 0.028048 | 458 | 0.010905 | 1342 | 0.031952 | 1.362 | A04 | MICL0.01419042/DOV
Build-In Floor | Mini Canal | MICL.01419042/PNC | 14 | 190 | 42 | 42 | 1077 | 1077 | 1077 | 0.025643 | 419 | 0.0099762 | 1227 | 0.029214 | 1.362 | A04 | MICL0.01419042/PNC
Build-In Floor | Mini Canal | MICL.01419042/RBL | 14 | 190 | 42 | 42 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01419042/RBL
Build-In Floor | Mini Canal | MICL.01419042/RBN | 14 | 190 | 42 | 42 | 1229 | 1229 | 1229 | 0.029262 | 478 | 0.011381 | 1400 | 0.033333 | 1.362 | A04 | MICL0.01419042/RBN
Build-In Floor | Mini Canal | MICL.01419042/RBR | 14 | 190 | 42 | 42 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01419042/RBR
Build-In Floor | Mini Canal | MICL.01419042/RBV | 14 | 190 | 42 | 42 | 1229 | 1229 | 1229 | 0.029262 | 478 | 0.011381 | 1400 | 0.033333 | 1.362 | A04 | MICL0.01419042/RBV
Build-In Floor | Mini Canal | MICL.01419042/RDB | 14 | 190 | 42 | 42 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01419042/RDB
Build-In Floor | Mini Canal | MICL.01419042/RMN | 14 | 190 | 42 | 42 | 1229 | 1229 | 1229 | 0.029262 | 478 | 0.011381 | 1400 | 0.033333 | 1.362 | A04 | MICL0.01419042/RMN
Build-In Floor | Mini Canal | MICL.01419042/RMV | 14 | 190 | 42 | 42 | 1229 | 1229 | 1229 | 0.029262 | 478 | 0.011381 | 1400 | 0.033333 | 1.362 | A04 | MICL0.01419042/RMV
Build-In Floor | Mini Canal | MICL.01419042/RNA | 14 | 190 | 42 | 42 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01419042/RNA
Build-In Floor | Mini Canal | MICL.01419042/RON | 14 | 190 | 42 | 42 | 1229 | 1229 | 1229 | 0.029262 | 478 | 0.011381 | 1400 | 0.033333 | 1.362 | A04 | MICL0.01419042/RON
Build-In Floor | Mini Canal | MICL.01419042/ROV | 14 | 190 | 42 | 42 | 1229 | 1229 | 1229 | 0.029262 | 478 | 0.011381 | 1400 | 0.033333 | 1.362 | A04 | MICL0.01419042/ROV
Build-In Floor | Mini Canal | MICL.01419042/RSS | 14 | 190 | 42 | 42 | 1216 | 1216 | 1216 | 0.028952 | 473 | 0.011262 | 1385 | 0.032976 | 1.362 | A04 | MICL0.01419042/RSS
Build-In Floor | Mini Canal | MICL.01419042/SBL | 14 | 190 | 42 | 42 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01419042/SBL
Build-In Floor | Mini Canal | MICL.01419042/SBR | 14 | 190 | 42 | 42 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01419042/SBR
Build-In Floor | Mini Canal | MICL.01419042/SDB | 14 | 190 | 42 | 42 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01419042/SDB
Build-In Floor | Mini Canal | MICL.01419042/SNA | 14 | 190 | 42 | 42 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01419042/SNA
Build-In Floor | Mini Canal | MICL.01419042/SNC | 14 | 190 | 42 | 42 | 1267 | 1267 | 1267 | 0.030167 | 493 | 0.011738 | 1443 | 0.034357 | 1.362 | A04 | MICL0.01419042/SNC
Build-In Floor | Mini Canal | MICL.01421014/ANA | 14 | 210 | 14 | 14 | 335 | 335 | 335 | 0.0079762 | 130 | 0.0030952 | 382 | 0.0090952 | 1.362 | A04 | MICL0.01421014/ANA
Build-In Floor | Mini Canal | MICL.01421014/DBL | 14 | 210 | 14 | 14 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01421014/DBL
Build-In Floor | Mini Canal | MICL.01421014/DBN | 14 | 210 | 14 | 14 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.01421014/DBN
Build-In Floor | Mini Canal | MICL.01421014/DBR | 14 | 210 | 14 | 14 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01421014/DBR
Build-In Floor | Mini Canal | MICL.01421014/DBV | 14 | 210 | 14 | 14 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.01421014/DBV
Build-In Floor | Mini Canal | MICL.01421014/DDB | 14 | 210 | 14 | 14 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01421014/DDB
Build-In Floor | Mini Canal | MICL.01421014/DMN | 14 | 210 | 14 | 14 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.01421014/DMN
Build-In Floor | Mini Canal | MICL.01421014/DMV | 14 | 210 | 14 | 14 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.01421014/DMV
Build-In Floor | Mini Canal | MICL.01421014/DNA | 14 | 210 | 14 | 14 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01421014/DNA
Build-In Floor | Mini Canal | MICL.01421014/DNC | 14 | 210 | 14 | 14 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01421014/DNC
Build-In Floor | Mini Canal | MICL.01421014/DON | 14 | 210 | 14 | 14 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.01421014/DON
Build-In Floor | Mini Canal | MICL.01421014/DOV | 14 | 210 | 14 | 14 | 415 | 415 | 415 | 0.009881 | 161 | 0.0038333 | 473 | 0.011262 | 1.362 | A04 | MICL0.01421014/DOV
Build-In Floor | Mini Canal | MICL.01421014/RBL | 14 | 210 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01421014/RBL
Build-In Floor | Mini Canal | MICL.01421014/RBN | 14 | 210 | 14 | 14 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01421014/RBN
Build-In Floor | Mini Canal | MICL.01421014/RBR | 14 | 210 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01421014/RBR
Build-In Floor | Mini Canal | MICL.01421014/RBV | 14 | 210 | 14 | 14 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01421014/RBV
Build-In Floor | Mini Canal | MICL.01421014/RDB | 14 | 210 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01421014/RDB
Build-In Floor | Mini Canal | MICL.01421014/RMN | 14 | 210 | 14 | 14 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01421014/RMN
Build-In Floor | Mini Canal | MICL.01421014/RMV | 14 | 210 | 14 | 14 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01421014/RMV
Build-In Floor | Mini Canal | MICL.01421014/RNA | 14 | 210 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01421014/RNA
Build-In Floor | Mini Canal | MICL.01421014/RON | 14 | 210 | 14 | 14 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01421014/RON
Build-In Floor | Mini Canal | MICL.01421014/ROV | 14 | 210 | 14 | 14 | 433 | 433 | 433 | 0.01031 | 168 | 0.004 | 493 | 0.011738 | 1.362 | A04 | MICL0.01421014/ROV
Build-In Floor | Mini Canal | MICL.01421014/RSS | 14 | 210 | 14 | 14 | 428 | 428 | 428 | 0.01019 | 166 | 0.0039524 | 487 | 0.011595 | 1.362 | A04 | MICL0.01421014/RSS
Build-In Floor | Mini Canal | MICL.01421014/SBL | 14 | 210 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01421014/SBL
Build-In Floor | Mini Canal | MICL.01421014/SBR | 14 | 210 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01421014/SBR
Build-In Floor | Mini Canal | MICL.01421014/SDB | 14 | 210 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01421014/SDB
Build-In Floor | Mini Canal | MICL.01421014/SNA | 14 | 210 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01421014/SNA
Build-In Floor | Mini Canal | MICL.01421014/SNC | 14 | 210 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01421014/SNC
Build-In Floor | Mini Canal | MICL.01421026/ANA | 14 | 210 | 26 | 26 | 581 | 581 | 581 | 0.013833 | 226 | 0.005381 | 662 | 0.015762 | 1.362 | A04 | MICL0.01421026/ANA
Build-In Floor | Mini Canal | MICL.01421026/DBL | 14 | 210 | 26 | 26 | 752 | 752 | 752 | 0.017905 | 293 | 0.0069762 | 857 | 0.020405 | 1.362 | A04 | MICL0.01421026/DBL
Build-In Floor | Mini Canal | MICL.01421026/DBN | 14 | 210 | 26 | 26 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01421026/DBN
Build-In Floor | Mini Canal | MICL.01421026/DBR | 14 | 210 | 26 | 26 | 752 | 752 | 752 | 0.017905 | 293 | 0.0069762 | 857 | 0.020405 | 1.362 | A04 | MICL0.01421026/DBR
Build-In Floor | Mini Canal | MICL.01421026/DBV | 14 | 210 | 26 | 26 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01421026/DBV
Build-In Floor | Mini Canal | MICL.01421026/DDB | 14 | 210 | 26 | 26 | 752 | 752 | 752 | 0.017905 | 293 | 0.0069762 | 857 | 0.020405 | 1.362 | A04 | MICL0.01421026/DDB
Build-In Floor | Mini Canal | MICL.01421026/DMN | 14 | 210 | 26 | 26 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01421026/DMN
Build-In Floor | Mini Canal | MICL.01421026/DMV | 14 | 210 | 26 | 26 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01421026/DMV
Build-In Floor | Mini Canal | MICL.01421026/DNA | 14 | 210 | 26 | 26 | 752 | 752 | 752 | 0.017905 | 293 | 0.0069762 | 857 | 0.020405 | 1.362 | A04 | MICL0.01421026/DNA
Build-In Floor | Mini Canal | MICL.01421026/DNC | 14 | 210 | 26 | 26 | 752 | 752 | 752 | 0.017905 | 293 | 0.0069762 | 857 | 0.020405 | 1.362 | A04 | MICL0.01421026/DNC
Build-In Floor | Mini Canal | MICL.01421026/DON | 14 | 210 | 26 | 26 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01421026/DON
Build-In Floor | Mini Canal | MICL.01421026/DOV | 14 | 210 | 26 | 26 | 721 | 721 | 721 | 0.017167 | 280 | 0.0066667 | 821 | 0.019548 | 1.362 | A04 | MICL0.01421026/DOV
Build-In Floor | Mini Canal | MICL.01421026/PNC | 14 | 210 | 26 | 26 | 659 | 659 | 659 | 0.01569 | 256 | 0.0060952 | 751 | 0.017881 | 1.362 | A04 | MICL0.01421026/PNC
Build-In Floor | Mini Canal | MICL.01421026/RBL | 14 | 210 | 26 | 26 | 775 | 775 | 775 | 0.018452 | 301 | 0.0071667 | 883 | 0.021024 | 1.362 | A04 | MICL0.01421026/RBL
Build-In Floor | Mini Canal | MICL.01421026/RBN | 14 | 210 | 26 | 26 | 752 | 752 | 752 | 0.017905 | 293 | 0.0069762 | 857 | 0.020405 | 1.362 | A04 | MICL0.01421026/RBN
Build-In Floor | Mini Canal | MICL.01421026/RBR | 14 | 210 | 26 | 26 | 775 | 775 | 775 | 0.018452 | 301 | 0.0071667 | 883 | 0.021024 | 1.362 | A04 | MICL0.01421026/RBR
Build-In Floor | Mini Canal | MICL.01421026/RBV | 14 | 210 | 26 | 26 | 752 | 752 | 752 | 0.017905 | 293 | 0.0069762 | 857 | 0.020405 | 1.362 | A04 | MICL0.01421026/RBV
Build-In Floor | Mini Canal | MICL.01421026/RDB | 14 | 210 | 26 | 26 | 775 | 775 | 775 | 0.018452 | 301 | 0.0071667 | 883 | 0.021024 | 1.362 | A04 | MICL0.01421026/RDB
Build-In Floor | Mini Canal | MICL.01421026/RMN | 14 | 210 | 26 | 26 | 752 | 752 | 752 | 0.017905 | 293 | 0.0069762 | 857 | 0.020405 | 1.362 | A04 | MICL0.01421026/RMN
Build-In Floor | Mini Canal | MICL.01421026/RMV | 14 | 210 | 26 | 26 | 752 | 752 | 752 | 0.017905 | 293 | 0.0069762 | 857 | 0.020405 | 1.362 | A04 | MICL0.01421026/RMV
Build-In Floor | Mini Canal | MICL.01421026/RNA | 14 | 210 | 26 | 26 | 775 | 775 | 775 | 0.018452 | 301 | 0.0071667 | 883 | 0.021024 | 1.362 | A04 | MICL0.01421026/RNA
Build-In Floor | Mini Canal | MICL.01421026/RON | 14 | 210 | 26 | 26 | 752 | 752 | 752 | 0.017905 | 293 | 0.0069762 | 857 | 0.020405 | 1.362 | A04 | MICL0.01421026/RON
Build-In Floor | Mini Canal | MICL.01421026/ROV | 14 | 210 | 26 | 26 | 752 | 752 | 752 | 0.017905 | 293 | 0.0069762 | 857 | 0.020405 | 1.362 | A04 | MICL0.01421026/ROV
Build-In Floor | Mini Canal | MICL.01421026/RSS | 14 | 210 | 26 | 26 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.01421026/RSS
Build-In Floor | Mini Canal | MICL.01421026/SBL | 14 | 210 | 26 | 26 | 775 | 775 | 775 | 0.018452 | 301 | 0.0071667 | 883 | 0.021024 | 1.362 | A04 | MICL0.01421026/SBL
Build-In Floor | Mini Canal | MICL.01421026/SBR | 14 | 210 | 26 | 26 | 775 | 775 | 775 | 0.018452 | 301 | 0.0071667 | 883 | 0.021024 | 1.362 | A04 | MICL0.01421026/SBR
Build-In Floor | Mini Canal | MICL.01421026/SDB | 14 | 210 | 26 | 26 | 775 | 775 | 775 | 0.018452 | 301 | 0.0071667 | 883 | 0.021024 | 1.362 | A04 | MICL0.01421026/SDB
Build-In Floor | Mini Canal | MICL.01421026/SNA | 14 | 210 | 26 | 26 | 775 | 775 | 775 | 0.018452 | 301 | 0.0071667 | 883 | 0.021024 | 1.362 | A04 | MICL0.01421026/SNA
Build-In Floor | Mini Canal | MICL.01421026/SNC | 14 | 210 | 26 | 26 | 775 | 775 | 775 | 0.018452 | 301 | 0.0071667 | 883 | 0.021024 | 1.362 | A04 | MICL0.01421026/SNC
Build-In Floor | Mini Canal | MICL.01421034/ANA | 14 | 210 | 34 | 34 | 793 | 793 | 793 | 0.018881 | 308 | 0.0073333 | 903 | 0.0215 | 1.362 | A04 | MICL0.01421034/ANA
Build-In Floor | Mini Canal | MICL.01421034/DBL | 14 | 210 | 34 | 34 | 1025 | 1025 | 1025 | 0.024405 | 399 | 0.0095 | 1167 | 0.027786 | 1.362 | A04 | MICL0.01421034/DBL
Build-In Floor | Mini Canal | MICL.01421034/DBN | 14 | 210 | 34 | 34 | 983 | 983 | 983 | 0.023405 | 382 | 0.0090952 | 1120 | 0.026667 | 1.362 | A04 | MICL0.01421034/DBN
Build-In Floor | Mini Canal | MICL.01421034/DBR | 14 | 210 | 34 | 34 | 1025 | 1025 | 1025 | 0.024405 | 399 | 0.0095 | 1167 | 0.027786 | 1.362 | A04 | MICL0.01421034/DBR
Build-In Floor | Mini Canal | MICL.01421034/DBV | 14 | 210 | 34 | 34 | 983 | 983 | 983 | 0.023405 | 382 | 0.0090952 | 1120 | 0.026667 | 1.362 | A04 | MICL0.01421034/DBV
Build-In Floor | Mini Canal | MICL.01421034/DDB | 14 | 210 | 34 | 34 | 1025 | 1025 | 1025 | 0.024405 | 399 | 0.0095 | 1167 | 0.027786 | 1.362 | A04 | MICL0.01421034/DDB
Build-In Floor | Mini Canal | MICL.01421034/DMN | 14 | 210 | 34 | 34 | 983 | 983 | 983 | 0.023405 | 382 | 0.0090952 | 1120 | 0.026667 | 1.362 | A04 | MICL0.01421034/DMN
Build-In Floor | Mini Canal | MICL.01421034/DMV | 14 | 210 | 34 | 34 | 983 | 983 | 983 | 0.023405 | 382 | 0.0090952 | 1120 | 0.026667 | 1.362 | A04 | MICL0.01421034/DMV
Build-In Floor | Mini Canal | MICL.01421034/DNA | 14 | 210 | 34 | 34 | 1025 | 1025 | 1025 | 0.024405 | 399 | 0.0095 | 1167 | 0.027786 | 1.362 | A04 | MICL0.01421034/DNA
Build-In Floor | Mini Canal | MICL.01421034/DNC | 14 | 210 | 34 | 34 | 1025 | 1025 | 1025 | 0.024405 | 399 | 0.0095 | 1167 | 0.027786 | 1.362 | A04 | MICL0.01421034/DNC
Build-In Floor | Mini Canal | MICL.01421034/DON | 14 | 210 | 34 | 34 | 983 | 983 | 983 | 0.023405 | 382 | 0.0090952 | 1120 | 0.026667 | 1.362 | A04 | MICL0.01421034/DON
Build-In Floor | Mini Canal | MICL.01421034/DOV | 14 | 210 | 34 | 34 | 983 | 983 | 983 | 0.023405 | 382 | 0.0090952 | 1120 | 0.026667 | 1.362 | A04 | MICL0.01421034/DOV
Build-In Floor | Mini Canal | MICL.01421034/PNC | 14 | 210 | 34 | 34 | 898 | 898 | 898 | 0.021381 | 349 | 0.0083095 | 1023 | 0.024357 | 1.362 | A04 | MICL0.01421034/PNC
Build-In Floor | Mini Canal | MICL.01421034/RBL | 14 | 210 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01421034/RBL
Build-In Floor | Mini Canal | MICL.01421034/RBN | 14 | 210 | 34 | 34 | 1025 | 1025 | 1025 | 0.024405 | 399 | 0.0095 | 1167 | 0.027786 | 1.362 | A04 | MICL0.01421034/RBN
Build-In Floor | Mini Canal | MICL.01421034/RBR | 14 | 210 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01421034/RBR
Build-In Floor | Mini Canal | MICL.01421034/RBV | 14 | 210 | 34 | 34 | 1025 | 1025 | 1025 | 0.024405 | 399 | 0.0095 | 1167 | 0.027786 | 1.362 | A04 | MICL0.01421034/RBV
Build-In Floor | Mini Canal | MICL.01421034/RDB | 14 | 210 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01421034/RDB
Build-In Floor | Mini Canal | MICL.01421034/RMN | 14 | 210 | 34 | 34 | 1025 | 1025 | 1025 | 0.024405 | 399 | 0.0095 | 1167 | 0.027786 | 1.362 | A04 | MICL0.01421034/RMN
Build-In Floor | Mini Canal | MICL.01421034/RMV | 14 | 210 | 34 | 34 | 1025 | 1025 | 1025 | 0.024405 | 399 | 0.0095 | 1167 | 0.027786 | 1.362 | A04 | MICL0.01421034/RMV
Build-In Floor | Mini Canal | MICL.01421034/RNA | 14 | 210 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01421034/RNA
Build-In Floor | Mini Canal | MICL.01421034/RON | 14 | 210 | 34 | 34 | 1025 | 1025 | 1025 | 0.024405 | 399 | 0.0095 | 1167 | 0.027786 | 1.362 | A04 | MICL0.01421034/RON
Build-In Floor | Mini Canal | MICL.01421034/ROV | 14 | 210 | 34 | 34 | 1025 | 1025 | 1025 | 0.024405 | 399 | 0.0095 | 1167 | 0.027786 | 1.362 | A04 | MICL0.01421034/ROV
Build-In Floor | Mini Canal | MICL.01421034/RSS | 14 | 210 | 34 | 34 | 1015 | 1015 | 1015 | 0.024167 | 395 | 0.0094048 | 1156 | 0.027524 | 1.362 | A04 | MICL0.01421034/RSS
Build-In Floor | Mini Canal | MICL.01421034/SBL | 14 | 210 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01421034/SBL
Build-In Floor | Mini Canal | MICL.01421034/SBR | 14 | 210 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01421034/SBR
Build-In Floor | Mini Canal | MICL.01421034/SDB | 14 | 210 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01421034/SDB
Build-In Floor | Mini Canal | MICL.01421034/SNA | 14 | 210 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01421034/SNA
Build-In Floor | Mini Canal | MICL.01421034/SNC | 14 | 210 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01421034/SNC
Build-In Floor | Mini Canal | MICL.01421042/ANA | 14 | 210 | 42 | 42 | 1069 | 1069 | 1069 | 0.025452 | 416 | 0.0099048 | 1218 | 0.029 | 1.362 | A04 | MICL0.01421042/ANA
Build-In Floor | Mini Canal | MICL.01421042/DBL | 14 | 210 | 42 | 42 | 1382 | 1382 | 1382 | 0.032905 | 538 | 0.01281 | 1574 | 0.037476 | 1.362 | A04 | MICL0.01421042/DBL
Build-In Floor | Mini Canal | MICL.01421042/DBN | 14 | 210 | 42 | 42 | 1325 | 1325 | 1325 | 0.031548 | 515 | 0.012262 | 1509 | 0.035929 | 1.362 | A04 | MICL0.01421042/DBN
Build-In Floor | Mini Canal | MICL.01421042/DBR | 14 | 210 | 42 | 42 | 1382 | 1382 | 1382 | 0.032905 | 538 | 0.01281 | 1574 | 0.037476 | 1.362 | A04 | MICL0.01421042/DBR
Build-In Floor | Mini Canal | MICL.01421042/DBV | 14 | 210 | 42 | 42 | 1325 | 1325 | 1325 | 0.031548 | 515 | 0.012262 | 1509 | 0.035929 | 1.362 | A04 | MICL0.01421042/DBV
Build-In Floor | Mini Canal | MICL.01421042/DDB | 14 | 210 | 42 | 42 | 1382 | 1382 | 1382 | 0.032905 | 538 | 0.01281 | 1574 | 0.037476 | 1.362 | A04 | MICL0.01421042/DDB
Build-In Floor | Mini Canal | MICL.01421042/DMN | 14 | 210 | 42 | 42 | 1325 | 1325 | 1325 | 0.031548 | 515 | 0.012262 | 1509 | 0.035929 | 1.362 | A04 | MICL0.01421042/DMN
Build-In Floor | Mini Canal | MICL.01421042/DMV | 14 | 210 | 42 | 42 | 1325 | 1325 | 1325 | 0.031548 | 515 | 0.012262 | 1509 | 0.035929 | 1.362 | A04 | MICL0.01421042/DMV
Build-In Floor | Mini Canal | MICL.01421042/DNA | 14 | 210 | 42 | 42 | 1382 | 1382 | 1382 | 0.032905 | 538 | 0.01281 | 1574 | 0.037476 | 1.362 | A04 | MICL0.01421042/DNA
Build-In Floor | Mini Canal | MICL.01421042/DNC | 14 | 210 | 42 | 42 | 1382 | 1382 | 1382 | 0.032905 | 538 | 0.01281 | 1574 | 0.037476 | 1.362 | A04 | MICL0.01421042/DNC
Build-In Floor | Mini Canal | MICL.01421042/DON | 14 | 210 | 42 | 42 | 1325 | 1325 | 1325 | 0.031548 | 515 | 0.012262 | 1509 | 0.035929 | 1.362 | A04 | MICL0.01421042/DON
Build-In Floor | Mini Canal | MICL.01421042/DOV | 14 | 210 | 42 | 42 | 1325 | 1325 | 1325 | 0.031548 | 515 | 0.012262 | 1509 | 0.035929 | 1.362 | A04 | MICL0.01421042/DOV
Build-In Floor | Mini Canal | MICL.01421042/PNC | 14 | 210 | 42 | 42 | 1211 | 1211 | 1211 | 0.028833 | 471 | 0.011214 | 1379 | 0.032833 | 1.362 | A04 | MICL0.01421042/PNC
Build-In Floor | Mini Canal | MICL.01421042/RBL | 14 | 210 | 42 | 42 | 1425 | 1425 | 1425 | 0.033929 | 554 | 0.01319 | 1623 | 0.038643 | 1.362 | A04 | MICL0.01421042/RBL
Build-In Floor | Mini Canal | MICL.01421042/RBN | 14 | 210 | 42 | 42 | 1382 | 1382 | 1382 | 0.032905 | 538 | 0.01281 | 1574 | 0.037476 | 1.362 | A04 | MICL0.01421042/RBN
Build-In Floor | Mini Canal | MICL.01421042/RBR | 14 | 210 | 42 | 42 | 1425 | 1425 | 1425 | 0.033929 | 554 | 0.01319 | 1623 | 0.038643 | 1.362 | A04 | MICL0.01421042/RBR
Build-In Floor | Mini Canal | MICL.01421042/RBV | 14 | 210 | 42 | 42 | 1382 | 1382 | 1382 | 0.032905 | 538 | 0.01281 | 1574 | 0.037476 | 1.362 | A04 | MICL0.01421042/RBV
Build-In Floor | Mini Canal | MICL.01421042/RDB | 14 | 210 | 42 | 42 | 1425 | 1425 | 1425 | 0.033929 | 554 | 0.01319 | 1623 | 0.038643 | 1.362 | A04 | MICL0.01421042/RDB
Build-In Floor | Mini Canal | MICL.01421042/RMN | 14 | 210 | 42 | 42 | 1382 | 1382 | 1382 | 0.032905 | 538 | 0.01281 | 1574 | 0.037476 | 1.362 | A04 | MICL0.01421042/RMN
Build-In Floor | Mini Canal | MICL.01421042/RMV | 14 | 210 | 42 | 42 | 1382 | 1382 | 1382 | 0.032905 | 538 | 0.01281 | 1574 | 0.037476 | 1.362 | A04 | MICL0.01421042/RMV
Build-In Floor | Mini Canal | MICL.01421042/RNA | 14 | 210 | 42 | 42 | 1425 | 1425 | 1425 | 0.033929 | 554 | 0.01319 | 1623 | 0.038643 | 1.362 | A04 | MICL0.01421042/RNA
Build-In Floor | Mini Canal | MICL.01421042/RON | 14 | 210 | 42 | 42 | 1382 | 1382 | 1382 | 0.032905 | 538 | 0.01281 | 1574 | 0.037476 | 1.362 | A04 | MICL0.01421042/RON
Build-In Floor | Mini Canal | MICL.01421042/ROV | 14 | 210 | 42 | 42 | 1382 | 1382 | 1382 | 0.032905 | 538 | 0.01281 | 1574 | 0.037476 | 1.362 | A04 | MICL0.01421042/ROV
Build-In Floor | Mini Canal | MICL.01421042/RSS | 14 | 210 | 42 | 42 | 1368 | 1368 | 1368 | 0.032571 | 532 | 0.012667 | 1558 | 0.037095 | 1.362 | A04 | MICL0.01421042/RSS
Build-In Floor | Mini Canal | MICL.01421042/SBL | 14 | 210 | 42 | 42 | 1425 | 1425 | 1425 | 0.033929 | 554 | 0.01319 | 1623 | 0.038643 | 1.362 | A04 | MICL0.01421042/SBL
Build-In Floor | Mini Canal | MICL.01421042/SBR | 14 | 210 | 42 | 42 | 1425 | 1425 | 1425 | 0.033929 | 554 | 0.01319 | 1623 | 0.038643 | 1.362 | A04 | MICL0.01421042/SBR
Build-In Floor | Mini Canal | MICL.01421042/SDB | 14 | 210 | 42 | 42 | 1425 | 1425 | 1425 | 0.033929 | 554 | 0.01319 | 1623 | 0.038643 | 1.362 | A04 | MICL0.01421042/SDB
Build-In Floor | Mini Canal | MICL.01421042/SNA | 14 | 210 | 42 | 42 | 1425 | 1425 | 1425 | 0.033929 | 554 | 0.01319 | 1623 | 0.038643 | 1.362 | A04 | MICL0.01421042/SNA
Build-In Floor | Mini Canal | MICL.01421042/SNC | 14 | 210 | 42 | 42 | 1425 | 1425 | 1425 | 0.033929 | 554 | 0.01319 | 1623 | 0.038643 | 1.362 | A04 | MICL0.01421042/SNC
Build-In Floor | Mini Canal | MICL.01423014/ANA | 14 | 230 | 14 | 14 | 372 | 372 | 372 | 0.0088571 | 145 | 0.0034524 | 424 | 0.010095 | 1.362 | A04 | MICL0.01423014/ANA
Build-In Floor | Mini Canal | MICL.01423014/DBL | 14 | 230 | 14 | 14 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.01423014/DBL
Build-In Floor | Mini Canal | MICL.01423014/DBN | 14 | 230 | 14 | 14 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01423014/DBN
Build-In Floor | Mini Canal | MICL.01423014/DBR | 14 | 230 | 14 | 14 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.01423014/DBR
Build-In Floor | Mini Canal | MICL.01423014/DBV | 14 | 230 | 14 | 14 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01423014/DBV
Build-In Floor | Mini Canal | MICL.01423014/DDB | 14 | 230 | 14 | 14 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.01423014/DDB
Build-In Floor | Mini Canal | MICL.01423014/DMN | 14 | 230 | 14 | 14 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01423014/DMN
Build-In Floor | Mini Canal | MICL.01423014/DMV | 14 | 230 | 14 | 14 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01423014/DMV
Build-In Floor | Mini Canal | MICL.01423014/DNA | 14 | 230 | 14 | 14 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.01423014/DNA
Build-In Floor | Mini Canal | MICL.01423014/DNC | 14 | 230 | 14 | 14 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.01423014/DNC
Build-In Floor | Mini Canal | MICL.01423014/DON | 14 | 230 | 14 | 14 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01423014/DON
Build-In Floor | Mini Canal | MICL.01423014/DOV | 14 | 230 | 14 | 14 | 461 | 461 | 461 | 0.010976 | 179 | 0.0042619 | 525 | 0.0125 | 1.362 | A04 | MICL0.01423014/DOV
Build-In Floor | Mini Canal | MICL.01423014/RBL | 14 | 230 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.01423014/RBL
Build-In Floor | Mini Canal | MICL.01423014/RBN | 14 | 230 | 14 | 14 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.01423014/RBN
Build-In Floor | Mini Canal | MICL.01423014/RBR | 14 | 230 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.01423014/RBR
Build-In Floor | Mini Canal | MICL.01423014/RBV | 14 | 230 | 14 | 14 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.01423014/RBV
Build-In Floor | Mini Canal | MICL.01423014/RDB | 14 | 230 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.01423014/RDB
Build-In Floor | Mini Canal | MICL.01423014/RMN | 14 | 230 | 14 | 14 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.01423014/RMN
Build-In Floor | Mini Canal | MICL.01423014/RMV | 14 | 230 | 14 | 14 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.01423014/RMV
Build-In Floor | Mini Canal | MICL.01423014/RNA | 14 | 230 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.01423014/RNA
Build-In Floor | Mini Canal | MICL.01423014/RON | 14 | 230 | 14 | 14 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.01423014/RON
Build-In Floor | Mini Canal | MICL.01423014/ROV | 14 | 230 | 14 | 14 | 481 | 481 | 481 | 0.011452 | 187 | 0.0044524 | 548 | 0.013048 | 1.362 | A04 | MICL0.01423014/ROV
Build-In Floor | Mini Canal | MICL.01423014/RSS | 14 | 230 | 14 | 14 | 476 | 476 | 476 | 0.011333 | 185 | 0.0044048 | 542 | 0.012905 | 1.362 | A04 | MICL0.01423014/RSS
Build-In Floor | Mini Canal | MICL.01423014/SBL | 14 | 230 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.01423014/SBL
Build-In Floor | Mini Canal | MICL.01423014/SBR | 14 | 230 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.01423014/SBR
Build-In Floor | Mini Canal | MICL.01423014/SDB | 14 | 230 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.01423014/SDB
Build-In Floor | Mini Canal | MICL.01423014/SNA | 14 | 230 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.01423014/SNA
Build-In Floor | Mini Canal | MICL.01423014/SNC | 14 | 230 | 14 | 14 | 496 | 496 | 496 | 0.01181 | 193 | 0.0045952 | 565 | 0.013452 | 1.362 | A04 | MICL0.01423014/SNC
Build-In Floor | Mini Canal | MICL.01423026/ANA | 14 | 230 | 26 | 26 | 646 | 646 | 646 | 0.015381 | 251 | 0.0059762 | 736 | 0.017524 | 1.362 | A04 | MICL0.01423026/ANA
Build-In Floor | Mini Canal | MICL.01423026/DBL | 14 | 230 | 26 | 26 | 835 | 835 | 835 | 0.019881 | 325 | 0.0077381 | 951 | 0.022643 | 1.362 | A04 | MICL0.01423026/DBL
Build-In Floor | Mini Canal | MICL.01423026/DBN | 14 | 230 | 26 | 26 | 801 | 801 | 801 | 0.019071 | 312 | 0.0074286 | 912 | 0.021714 | 1.362 | A04 | MICL0.01423026/DBN
Build-In Floor | Mini Canal | MICL.01423026/DBR | 14 | 230 | 26 | 26 | 835 | 835 | 835 | 0.019881 | 325 | 0.0077381 | 951 | 0.022643 | 1.362 | A04 | MICL0.01423026/DBR
Build-In Floor | Mini Canal | MICL.01423026/DBV | 14 | 230 | 26 | 26 | 801 | 801 | 801 | 0.019071 | 312 | 0.0074286 | 912 | 0.021714 | 1.362 | A04 | MICL0.01423026/DBV
Build-In Floor | Mini Canal | MICL.01423026/DDB | 14 | 230 | 26 | 26 | 835 | 835 | 835 | 0.019881 | 325 | 0.0077381 | 951 | 0.022643 | 1.362 | A04 | MICL0.01423026/DDB
Build-In Floor | Mini Canal | MICL.01423026/DMN | 14 | 230 | 26 | 26 | 801 | 801 | 801 | 0.019071 | 312 | 0.0074286 | 912 | 0.021714 | 1.362 | A04 | MICL0.01423026/DMN
Build-In Floor | Mini Canal | MICL.01423026/DMV | 14 | 230 | 26 | 26 | 801 | 801 | 801 | 0.019071 | 312 | 0.0074286 | 912 | 0.021714 | 1.362 | A04 | MICL0.01423026/DMV
Build-In Floor | Mini Canal | MICL.01423026/DNA | 14 | 230 | 26 | 26 | 835 | 835 | 835 | 0.019881 | 325 | 0.0077381 | 951 | 0.022643 | 1.362 | A04 | MICL0.01423026/DNA
Build-In Floor | Mini Canal | MICL.01423026/DNC | 14 | 230 | 26 | 26 | 835 | 835 | 835 | 0.019881 | 325 | 0.0077381 | 951 | 0.022643 | 1.362 | A04 | MICL0.01423026/DNC
Build-In Floor | Mini Canal | MICL.01423026/DON | 14 | 230 | 26 | 26 | 801 | 801 | 801 | 0.019071 | 312 | 0.0074286 | 912 | 0.021714 | 1.362 | A04 | MICL0.01423026/DON
Build-In Floor | Mini Canal | MICL.01423026/DOV | 14 | 230 | 26 | 26 | 801 | 801 | 801 | 0.019071 | 312 | 0.0074286 | 912 | 0.021714 | 1.362 | A04 | MICL0.01423026/DOV
Build-In Floor | Mini Canal | MICL.01423026/PNC | 14 | 230 | 26 | 26 | 732 | 732 | 732 | 0.017429 | 285 | 0.0067857 | 834 | 0.019857 | 1.362 | A04 | MICL0.01423026/PNC
Build-In Floor | Mini Canal | MICL.01423026/RBL | 14 | 230 | 26 | 26 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.01423026/RBL
Build-In Floor | Mini Canal | MICL.01423026/RBN | 14 | 230 | 26 | 26 | 835 | 835 | 835 | 0.019881 | 325 | 0.0077381 | 951 | 0.022643 | 1.362 | A04 | MICL0.01423026/RBN
Build-In Floor | Mini Canal | MICL.01423026/RBR | 14 | 230 | 26 | 26 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.01423026/RBR
Build-In Floor | Mini Canal | MICL.01423026/RBV | 14 | 230 | 26 | 26 | 835 | 835 | 835 | 0.019881 | 325 | 0.0077381 | 951 | 0.022643 | 1.362 | A04 | MICL0.01423026/RBV
Build-In Floor | Mini Canal | MICL.01423026/RDB | 14 | 230 | 26 | 26 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.01423026/RDB
Build-In Floor | Mini Canal | MICL.01423026/RMN | 14 | 230 | 26 | 26 | 835 | 835 | 835 | 0.019881 | 325 | 0.0077381 | 951 | 0.022643 | 1.362 | A04 | MICL0.01423026/RMN
Build-In Floor | Mini Canal | MICL.01423026/RMV | 14 | 230 | 26 | 26 | 835 | 835 | 835 | 0.019881 | 325 | 0.0077381 | 951 | 0.022643 | 1.362 | A04 | MICL0.01423026/RMV
Build-In Floor | Mini Canal | MICL.01423026/RNA | 14 | 230 | 26 | 26 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.01423026/RNA
Build-In Floor | Mini Canal | MICL.01423026/RON | 14 | 230 | 26 | 26 | 835 | 835 | 835 | 0.019881 | 325 | 0.0077381 | 951 | 0.022643 | 1.362 | A04 | MICL0.01423026/RON
Build-In Floor | Mini Canal | MICL.01423026/ROV | 14 | 230 | 26 | 26 | 835 | 835 | 835 | 0.019881 | 325 | 0.0077381 | 951 | 0.022643 | 1.362 | A04 | MICL0.01423026/ROV
Build-In Floor | Mini Canal | MICL.01423026/RSS | 14 | 230 | 26 | 26 | 827 | 827 | 827 | 0.01969 | 322 | 0.0076667 | 942 | 0.022429 | 1.362 | A04 | MICL0.01423026/RSS
Build-In Floor | Mini Canal | MICL.01423026/SBL | 14 | 230 | 26 | 26 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.01423026/SBL
Build-In Floor | Mini Canal | MICL.01423026/SBR | 14 | 230 | 26 | 26 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.01423026/SBR
Build-In Floor | Mini Canal | MICL.01423026/SDB | 14 | 230 | 26 | 26 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.01423026/SDB
Build-In Floor | Mini Canal | MICL.01423026/SNA | 14 | 230 | 26 | 26 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.01423026/SNA
Build-In Floor | Mini Canal | MICL.01423026/SNC | 14 | 230 | 26 | 26 | 861 | 861 | 861 | 0.0205 | 335 | 0.0079762 | 981 | 0.023357 | 1.362 | A04 | MICL0.01423026/SNC
Build-In Floor | Mini Canal | MICL.01423034/ANA | 14 | 230 | 34 | 34 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01423034/ANA
Build-In Floor | Mini Canal | MICL.01423034/DBL | 14 | 230 | 34 | 34 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01423034/DBL
Build-In Floor | Mini Canal | MICL.01423034/DBN | 14 | 230 | 34 | 34 | 1093 | 1093 | 1093 | 0.026024 | 425 | 0.010119 | 1245 | 0.029643 | 1.362 | A04 | MICL0.01423034/DBN
Build-In Floor | Mini Canal | MICL.01423034/DBR | 14 | 230 | 34 | 34 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01423034/DBR
Build-In Floor | Mini Canal | MICL.01423034/DBV | 14 | 230 | 34 | 34 | 1093 | 1093 | 1093 | 0.026024 | 425 | 0.010119 | 1245 | 0.029643 | 1.362 | A04 | MICL0.01423034/DBV
Build-In Floor | Mini Canal | MICL.01423034/DDB | 14 | 230 | 34 | 34 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01423034/DDB
Build-In Floor | Mini Canal | MICL.01423034/DMN | 14 | 230 | 34 | 34 | 1093 | 1093 | 1093 | 0.026024 | 425 | 0.010119 | 1245 | 0.029643 | 1.362 | A04 | MICL0.01423034/DMN
Build-In Floor | Mini Canal | MICL.01423034/DMV | 14 | 230 | 34 | 34 | 1093 | 1093 | 1093 | 0.026024 | 425 | 0.010119 | 1245 | 0.029643 | 1.362 | A04 | MICL0.01423034/DMV
Build-In Floor | Mini Canal | MICL.01423034/DNA | 14 | 230 | 34 | 34 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01423034/DNA
Build-In Floor | Mini Canal | MICL.01423034/DNC | 14 | 230 | 34 | 34 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01423034/DNC
Build-In Floor | Mini Canal | MICL.01423034/DON | 14 | 230 | 34 | 34 | 1093 | 1093 | 1093 | 0.026024 | 425 | 0.010119 | 1245 | 0.029643 | 1.362 | A04 | MICL0.01423034/DON
Build-In Floor | Mini Canal | MICL.01423034/DOV | 14 | 230 | 34 | 34 | 1093 | 1093 | 1093 | 0.026024 | 425 | 0.010119 | 1245 | 0.029643 | 1.362 | A04 | MICL0.01423034/DOV
Build-In Floor | Mini Canal | MICL.01423034/PNC | 14 | 230 | 34 | 34 | 999 | 999 | 999 | 0.023786 | 389 | 0.0092619 | 1138 | 0.027095 | 1.362 | A04 | MICL0.01423034/PNC
Build-In Floor | Mini Canal | MICL.01423034/RBL | 14 | 230 | 34 | 34 | 1175 | 1175 | 1175 | 0.027976 | 457 | 0.010881 | 1338 | 0.031857 | 1.362 | A04 | MICL0.01423034/RBL
Build-In Floor | Mini Canal | MICL.01423034/RBN | 14 | 230 | 34 | 34 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01423034/RBN
Build-In Floor | Mini Canal | MICL.01423034/RBR | 14 | 230 | 34 | 34 | 1175 | 1175 | 1175 | 0.027976 | 457 | 0.010881 | 1338 | 0.031857 | 1.362 | A04 | MICL0.01423034/RBR
Build-In Floor | Mini Canal | MICL.01423034/RBV | 14 | 230 | 34 | 34 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01423034/RBV
Build-In Floor | Mini Canal | MICL.01423034/RDB | 14 | 230 | 34 | 34 | 1175 | 1175 | 1175 | 0.027976 | 457 | 0.010881 | 1338 | 0.031857 | 1.362 | A04 | MICL0.01423034/RDB
Build-In Floor | Mini Canal | MICL.01423034/RMN | 14 | 230 | 34 | 34 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01423034/RMN
Build-In Floor | Mini Canal | MICL.01423034/RMV | 14 | 230 | 34 | 34 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01423034/RMV
Build-In Floor | Mini Canal | MICL.01423034/RNA | 14 | 230 | 34 | 34 | 1175 | 1175 | 1175 | 0.027976 | 457 | 0.010881 | 1338 | 0.031857 | 1.362 | A04 | MICL0.01423034/RNA
Build-In Floor | Mini Canal | MICL.01423034/RON | 14 | 230 | 34 | 34 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01423034/RON
Build-In Floor | Mini Canal | MICL.01423034/ROV | 14 | 230 | 34 | 34 | 1140 | 1140 | 1140 | 0.027143 | 443 | 0.010548 | 1298 | 0.030905 | 1.362 | A04 | MICL0.01423034/ROV
Build-In Floor | Mini Canal | MICL.01423034/RSS | 14 | 230 | 34 | 34 | 1128 | 1128 | 1128 | 0.026857 | 439 | 0.010452 | 1285 | 0.030595 | 1.362 | A04 | MICL0.01423034/RSS
Build-In Floor | Mini Canal | MICL.01423034/SBL | 14 | 230 | 34 | 34 | 1175 | 1175 | 1175 | 0.027976 | 457 | 0.010881 | 1338 | 0.031857 | 1.362 | A04 | MICL0.01423034/SBL
Build-In Floor | Mini Canal | MICL.01423034/SBR | 14 | 230 | 34 | 34 | 1175 | 1175 | 1175 | 0.027976 | 457 | 0.010881 | 1338 | 0.031857 | 1.362 | A04 | MICL0.01423034/SBR
Build-In Floor | Mini Canal | MICL.01423034/SDB | 14 | 230 | 34 | 34 | 1175 | 1175 | 1175 | 0.027976 | 457 | 0.010881 | 1338 | 0.031857 | 1.362 | A04 | MICL0.01423034/SDB
Build-In Floor | Mini Canal | MICL.01423034/SNA | 14 | 230 | 34 | 34 | 1175 | 1175 | 1175 | 0.027976 | 457 | 0.010881 | 1338 | 0.031857 | 1.362 | A04 | MICL0.01423034/SNA
Build-In Floor | Mini Canal | MICL.01423034/SNC | 14 | 230 | 34 | 34 | 1175 | 1175 | 1175 | 0.027976 | 457 | 0.010881 | 1338 | 0.031857 | 1.362 | A04 | MICL0.01423034/SNC
Build-In Floor | Mini Canal | MICL.01423042/ANA | 14 | 230 | 42 | 42 | 1187 | 1187 | 1187 | 0.028262 | 462 | 0.011 | 1352 | 0.03219 | 1.362 | A04 | MICL0.01423042/ANA
Build-In Floor | Mini Canal | MICL.01423042/DBL | 14 | 230 | 42 | 42 | 1536 | 1536 | 1536 | 0.036571 | 598 | 0.014238 | 1750 | 0.041667 | 1.362 | A04 | MICL0.01423042/DBL
Build-In Floor | Mini Canal | MICL.01423042/DBN | 14 | 230 | 42 | 42 | 1472 | 1472 | 1472 | 0.035048 | 573 | 0.013643 | 1677 | 0.039929 | 1.362 | A04 | MICL0.01423042/DBN
Build-In Floor | Mini Canal | MICL.01423042/DBR | 14 | 230 | 42 | 42 | 1536 | 1536 | 1536 | 0.036571 | 598 | 0.014238 | 1750 | 0.041667 | 1.362 | A04 | MICL0.01423042/DBR
Build-In Floor | Mini Canal | MICL.01423042/DBV | 14 | 230 | 42 | 42 | 1472 | 1472 | 1472 | 0.035048 | 573 | 0.013643 | 1677 | 0.039929 | 1.362 | A04 | MICL0.01423042/DBV
Build-In Floor | Mini Canal | MICL.01423042/DDB | 14 | 230 | 42 | 42 | 1536 | 1536 | 1536 | 0.036571 | 598 | 0.014238 | 1750 | 0.041667 | 1.362 | A04 | MICL0.01423042/DDB
Build-In Floor | Mini Canal | MICL.01423042/DMN | 14 | 230 | 42 | 42 | 1472 | 1472 | 1472 | 0.035048 | 573 | 0.013643 | 1677 | 0.039929 | 1.362 | A04 | MICL0.01423042/DMN
Build-In Floor | Mini Canal | MICL.01423042/DMV | 14 | 230 | 42 | 42 | 1472 | 1472 | 1472 | 0.035048 | 573 | 0.013643 | 1677 | 0.039929 | 1.362 | A04 | MICL0.01423042/DMV
Build-In Floor | Mini Canal | MICL.01423042/DNA | 14 | 230 | 42 | 42 | 1536 | 1536 | 1536 | 0.036571 | 598 | 0.014238 | 1750 | 0.041667 | 1.362 | A04 | MICL0.01423042/DNA
Build-In Floor | Mini Canal | MICL.01423042/DNC | 14 | 230 | 42 | 42 | 1536 | 1536 | 1536 | 0.036571 | 598 | 0.014238 | 1750 | 0.041667 | 1.362 | A04 | MICL0.01423042/DNC
Build-In Floor | Mini Canal | MICL.01423042/DON | 14 | 230 | 42 | 42 | 1472 | 1472 | 1472 | 0.035048 | 573 | 0.013643 | 1677 | 0.039929 | 1.362 | A04 | MICL0.01423042/DON
Build-In Floor | Mini Canal | MICL.01423042/DOV | 14 | 230 | 42 | 42 | 1472 | 1472 | 1472 | 0.035048 | 573 | 0.013643 | 1677 | 0.039929 | 1.362 | A04 | MICL0.01423042/DOV
Build-In Floor | Mini Canal | MICL.01423042/PNC | 14 | 230 | 42 | 42 | 1346 | 1346 | 1346 | 0.032048 | 524 | 0.012476 | 1533 | 0.0365 | 1.362 | A04 | MICL0.01423042/PNC
Build-In Floor | Mini Canal | MICL.01423042/RBL | 14 | 230 | 42 | 42 | 1583 | 1583 | 1583 | 0.03769 | 616 | 0.014667 | 1803 | 0.042929 | 1.362 | A04 | MICL0.01423042/RBL
Build-In Floor | Mini Canal | MICL.01423042/RBN | 14 | 230 | 42 | 42 | 1536 | 1536 | 1536 | 0.036571 | 598 | 0.014238 | 1750 | 0.041667 | 1.362 | A04 | MICL0.01423042/RBN
Build-In Floor | Mini Canal | MICL.01423042/RBR | 14 | 230 | 42 | 42 | 1583 | 1583 | 1583 | 0.03769 | 616 | 0.014667 | 1803 | 0.042929 | 1.362 | A04 | MICL0.01423042/RBR
Build-In Floor | Mini Canal | MICL.01423042/RBV | 14 | 230 | 42 | 42 | 1536 | 1536 | 1536 | 0.036571 | 598 | 0.014238 | 1750 | 0.041667 | 1.362 | A04 | MICL0.01423042/RBV
Build-In Floor | Mini Canal | MICL.01423042/RDB | 14 | 230 | 42 | 42 | 1583 | 1583 | 1583 | 0.03769 | 616 | 0.014667 | 1803 | 0.042929 | 1.362 | A04 | MICL0.01423042/RDB
Build-In Floor | Mini Canal | MICL.01423042/RMN | 14 | 230 | 42 | 42 | 1536 | 1536 | 1536 | 0.036571 | 598 | 0.014238 | 1750 | 0.041667 | 1.362 | A04 | MICL0.01423042/RMN
Build-In Floor | Mini Canal | MICL.01423042/RMV | 14 | 230 | 42 | 42 | 1536 | 1536 | 1536 | 0.036571 | 598 | 0.014238 | 1750 | 0.041667 | 1.362 | A04 | MICL0.01423042/RMV
Build-In Floor | Mini Canal | MICL.01423042/RNA | 14 | 230 | 42 | 42 | 1583 | 1583 | 1583 | 0.03769 | 616 | 0.014667 | 1803 | 0.042929 | 1.362 | A04 | MICL0.01423042/RNA
Build-In Floor | Mini Canal | MICL.01423042/RON | 14 | 230 | 42 | 42 | 1536 | 1536 | 1536 | 0.036571 | 598 | 0.014238 | 1750 | 0.041667 | 1.362 | A04 | MICL0.01423042/RON
Build-In Floor | Mini Canal | MICL.01423042/ROV | 14 | 230 | 42 | 42 | 1536 | 1536 | 1536 | 0.036571 | 598 | 0.014238 | 1750 | 0.041667 | 1.362 | A04 | MICL0.01423042/ROV
Build-In Floor | Mini Canal | MICL.01423042/RSS | 14 | 230 | 42 | 42 | 1520 | 1520 | 1520 | 0.03619 | 591 | 0.014071 | 1731 | 0.041214 | 1.362 | A04 | MICL0.01423042/RSS
Build-In Floor | Mini Canal | MICL.01423042/SBL | 14 | 230 | 42 | 42 | 1583 | 1583 | 1583 | 0.03769 | 616 | 0.014667 | 1803 | 0.042929 | 1.362 | A04 | MICL0.01423042/SBL
Build-In Floor | Mini Canal | MICL.01423042/SBR | 14 | 230 | 42 | 42 | 1583 | 1583 | 1583 | 0.03769 | 616 | 0.014667 | 1803 | 0.042929 | 1.362 | A04 | MICL0.01423042/SBR
Build-In Floor | Mini Canal | MICL.01423042/SDB | 14 | 230 | 42 | 42 | 1583 | 1583 | 1583 | 0.03769 | 616 | 0.014667 | 1803 | 0.042929 | 1.362 | A04 | MICL0.01423042/SDB
Build-In Floor | Mini Canal | MICL.01423042/SNA | 14 | 230 | 42 | 42 | 1583 | 1583 | 1583 | 0.03769 | 616 | 0.014667 | 1803 | 0.042929 | 1.362 | A04 | MICL0.01423042/SNA
Build-In Floor | Mini Canal | MICL.01423042/SNC | 14 | 230 | 42 | 42 | 1583 | 1583 | 1583 | 0.03769 | 616 | 0.014667 | 1803 | 0.042929 | 1.362 | A04 | MICL0.01423042/SNC
Build-In Floor | Mini Canal | MICL.01425014/ANA | 14 | 250 | 14 | 14 | 410 | 410 | 410 | 0.0097619 | 159 | 0.0037857 | 467 | 0.011119 | 1.362 | A04 | MICL0.01425014/ANA
Build-In Floor | Mini Canal | MICL.01425014/DBL | 14 | 250 | 14 | 14 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01425014/DBL
Build-In Floor | Mini Canal | MICL.01425014/DBN | 14 | 250 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01425014/DBN
Build-In Floor | Mini Canal | MICL.01425014/DBR | 14 | 250 | 14 | 14 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01425014/DBR
Build-In Floor | Mini Canal | MICL.01425014/DBV | 14 | 250 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01425014/DBV
Build-In Floor | Mini Canal | MICL.01425014/DDB | 14 | 250 | 14 | 14 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01425014/DDB
Build-In Floor | Mini Canal | MICL.01425014/DMN | 14 | 250 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01425014/DMN
Build-In Floor | Mini Canal | MICL.01425014/DMV | 14 | 250 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01425014/DMV
Build-In Floor | Mini Canal | MICL.01425014/DNA | 14 | 250 | 14 | 14 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01425014/DNA
Build-In Floor | Mini Canal | MICL.01425014/DNC | 14 | 250 | 14 | 14 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01425014/DNC
Build-In Floor | Mini Canal | MICL.01425014/DON | 14 | 250 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01425014/DON
Build-In Floor | Mini Canal | MICL.01425014/DOV | 14 | 250 | 14 | 14 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01425014/DOV
Build-In Floor | Mini Canal | MICL.01425014/RBL | 14 | 250 | 14 | 14 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01425014/RBL
Build-In Floor | Mini Canal | MICL.01425014/RBN | 14 | 250 | 14 | 14 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01425014/RBN
Build-In Floor | Mini Canal | MICL.01425014/RBR | 14 | 250 | 14 | 14 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01425014/RBR
Build-In Floor | Mini Canal | MICL.01425014/RBV | 14 | 250 | 14 | 14 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01425014/RBV
Build-In Floor | Mini Canal | MICL.01425014/RDB | 14 | 250 | 14 | 14 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01425014/RDB
Build-In Floor | Mini Canal | MICL.01425014/RMN | 14 | 250 | 14 | 14 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01425014/RMN
Build-In Floor | Mini Canal | MICL.01425014/RMV | 14 | 250 | 14 | 14 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01425014/RMV
Build-In Floor | Mini Canal | MICL.01425014/RNA | 14 | 250 | 14 | 14 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01425014/RNA
Build-In Floor | Mini Canal | MICL.01425014/RON | 14 | 250 | 14 | 14 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01425014/RON
Build-In Floor | Mini Canal | MICL.01425014/ROV | 14 | 250 | 14 | 14 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01425014/ROV
Build-In Floor | Mini Canal | MICL.01425014/RSS | 14 | 250 | 14 | 14 | 524 | 524 | 524 | 0.012476 | 204 | 0.0048571 | 597 | 0.014214 | 1.362 | A04 | MICL0.01425014/RSS
Build-In Floor | Mini Canal | MICL.01425014/SBL | 14 | 250 | 14 | 14 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01425014/SBL
Build-In Floor | Mini Canal | MICL.01425014/SBR | 14 | 250 | 14 | 14 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01425014/SBR
Build-In Floor | Mini Canal | MICL.01425014/SDB | 14 | 250 | 14 | 14 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01425014/SDB
Build-In Floor | Mini Canal | MICL.01425014/SNA | 14 | 250 | 14 | 14 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01425014/SNA
Build-In Floor | Mini Canal | MICL.01425014/SNC | 14 | 250 | 14 | 14 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01425014/SNC
Build-In Floor | Mini Canal | MICL.01425026/ANA | 14 | 250 | 26 | 26 | 710 | 710 | 710 | 0.016905 | 276 | 0.0065714 | 809 | 0.019262 | 1.362 | A04 | MICL0.01425026/ANA
Build-In Floor | Mini Canal | MICL.01425026/DBL | 14 | 250 | 26 | 26 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.01425026/DBL
Build-In Floor | Mini Canal | MICL.01425026/DBN | 14 | 250 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01425026/DBN
Build-In Floor | Mini Canal | MICL.01425026/DBR | 14 | 250 | 26 | 26 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.01425026/DBR
Build-In Floor | Mini Canal | MICL.01425026/DBV | 14 | 250 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01425026/DBV
Build-In Floor | Mini Canal | MICL.01425026/DDB | 14 | 250 | 26 | 26 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.01425026/DDB
Build-In Floor | Mini Canal | MICL.01425026/DMN | 14 | 250 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01425026/DMN
Build-In Floor | Mini Canal | MICL.01425026/DMV | 14 | 250 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01425026/DMV
Build-In Floor | Mini Canal | MICL.01425026/DNA | 14 | 250 | 26 | 26 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.01425026/DNA
Build-In Floor | Mini Canal | MICL.01425026/DNC | 14 | 250 | 26 | 26 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.01425026/DNC
Build-In Floor | Mini Canal | MICL.01425026/DON | 14 | 250 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01425026/DON
Build-In Floor | Mini Canal | MICL.01425026/DOV | 14 | 250 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01425026/DOV
Build-In Floor | Mini Canal | MICL.01425026/PNC | 14 | 250 | 26 | 26 | 805 | 805 | 805 | 0.019167 | 313 | 0.0074524 | 917 | 0.021833 | 1.362 | A04 | MICL0.01425026/PNC
Build-In Floor | Mini Canal | MICL.01425026/RBL | 14 | 250 | 26 | 26 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.01425026/RBL
Build-In Floor | Mini Canal | MICL.01425026/RBN | 14 | 250 | 26 | 26 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.01425026/RBN
Build-In Floor | Mini Canal | MICL.01425026/RBR | 14 | 250 | 26 | 26 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.01425026/RBR
Build-In Floor | Mini Canal | MICL.01425026/RBV | 14 | 250 | 26 | 26 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.01425026/RBV
Build-In Floor | Mini Canal | MICL.01425026/RDB | 14 | 250 | 26 | 26 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.01425026/RDB
Build-In Floor | Mini Canal | MICL.01425026/RMN | 14 | 250 | 26 | 26 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.01425026/RMN
Build-In Floor | Mini Canal | MICL.01425026/RMV | 14 | 250 | 26 | 26 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.01425026/RMV
Build-In Floor | Mini Canal | MICL.01425026/RNA | 14 | 250 | 26 | 26 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.01425026/RNA
Build-In Floor | Mini Canal | MICL.01425026/RON | 14 | 250 | 26 | 26 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.01425026/RON
Build-In Floor | Mini Canal | MICL.01425026/ROV | 14 | 250 | 26 | 26 | 919 | 919 | 919 | 0.021881 | 357 | 0.0085 | 1047 | 0.024929 | 1.362 | A04 | MICL0.01425026/ROV
Build-In Floor | Mini Canal | MICL.01425026/RSS | 14 | 250 | 26 | 26 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01425026/RSS
Build-In Floor | Mini Canal | MICL.01425026/SBL | 14 | 250 | 26 | 26 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.01425026/SBL
Build-In Floor | Mini Canal | MICL.01425026/SBR | 14 | 250 | 26 | 26 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.01425026/SBR
Build-In Floor | Mini Canal | MICL.01425026/SDB | 14 | 250 | 26 | 26 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.01425026/SDB
Build-In Floor | Mini Canal | MICL.01425026/SNA | 14 | 250 | 26 | 26 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.01425026/SNA
Build-In Floor | Mini Canal | MICL.01425026/SNC | 14 | 250 | 26 | 26 | 947 | 947 | 947 | 0.022548 | 368 | 0.0087619 | 1079 | 0.02569 | 1.362 | A04 | MICL0.01425026/SNC
Build-In Floor | Mini Canal | MICL.01425034/ANA | 14 | 250 | 34 | 34 | 969 | 969 | 969 | 0.023071 | 377 | 0.0089762 | 1104 | 0.026286 | 1.362 | A04 | MICL0.01425034/ANA
Build-In Floor | Mini Canal | MICL.01425034/DBL | 14 | 250 | 34 | 34 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01425034/DBL
Build-In Floor | Mini Canal | MICL.01425034/DBN | 14 | 250 | 34 | 34 | 1202 | 1202 | 1202 | 0.028619 | 468 | 0.011143 | 1369 | 0.032595 | 1.362 | A04 | MICL0.01425034/DBN
Build-In Floor | Mini Canal | MICL.01425034/DBR | 14 | 250 | 34 | 34 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01425034/DBR
Build-In Floor | Mini Canal | MICL.01425034/DBV | 14 | 250 | 34 | 34 | 1202 | 1202 | 1202 | 0.028619 | 468 | 0.011143 | 1369 | 0.032595 | 1.362 | A04 | MICL0.01425034/DBV
Build-In Floor | Mini Canal | MICL.01425034/DDB | 14 | 250 | 34 | 34 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01425034/DDB
Build-In Floor | Mini Canal | MICL.01425034/DMN | 14 | 250 | 34 | 34 | 1202 | 1202 | 1202 | 0.028619 | 468 | 0.011143 | 1369 | 0.032595 | 1.362 | A04 | MICL0.01425034/DMN
Build-In Floor | Mini Canal | MICL.01425034/DMV | 14 | 250 | 34 | 34 | 1202 | 1202 | 1202 | 0.028619 | 468 | 0.011143 | 1369 | 0.032595 | 1.362 | A04 | MICL0.01425034/DMV
Build-In Floor | Mini Canal | MICL.01425034/DNA | 14 | 250 | 34 | 34 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01425034/DNA
Build-In Floor | Mini Canal | MICL.01425034/DNC | 14 | 250 | 34 | 34 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01425034/DNC
Build-In Floor | Mini Canal | MICL.01425034/DON | 14 | 250 | 34 | 34 | 1202 | 1202 | 1202 | 0.028619 | 468 | 0.011143 | 1369 | 0.032595 | 1.362 | A04 | MICL0.01425034/DON
Build-In Floor | Mini Canal | MICL.01425034/DOV | 14 | 250 | 34 | 34 | 1202 | 1202 | 1202 | 0.028619 | 468 | 0.011143 | 1369 | 0.032595 | 1.362 | A04 | MICL0.01425034/DOV
Build-In Floor | Mini Canal | MICL.01425034/PNC | 14 | 250 | 34 | 34 | 1098 | 1098 | 1098 | 0.026143 | 427 | 0.010167 | 1251 | 0.029786 | 1.362 | A04 | MICL0.01425034/PNC
Build-In Floor | Mini Canal | MICL.01425034/RBL | 14 | 250 | 34 | 34 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01425034/RBL
Build-In Floor | Mini Canal | MICL.01425034/RBN | 14 | 250 | 34 | 34 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01425034/RBN
Build-In Floor | Mini Canal | MICL.01425034/RBR | 14 | 250 | 34 | 34 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01425034/RBR
Build-In Floor | Mini Canal | MICL.01425034/RBV | 14 | 250 | 34 | 34 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01425034/RBV
Build-In Floor | Mini Canal | MICL.01425034/RDB | 14 | 250 | 34 | 34 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01425034/RDB
Build-In Floor | Mini Canal | MICL.01425034/RMN | 14 | 250 | 34 | 34 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01425034/RMN
Build-In Floor | Mini Canal | MICL.01425034/RMV | 14 | 250 | 34 | 34 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01425034/RMV
Build-In Floor | Mini Canal | MICL.01425034/RNA | 14 | 250 | 34 | 34 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01425034/RNA
Build-In Floor | Mini Canal | MICL.01425034/RON | 14 | 250 | 34 | 34 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01425034/RON
Build-In Floor | Mini Canal | MICL.01425034/ROV | 14 | 250 | 34 | 34 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01425034/ROV
Build-In Floor | Mini Canal | MICL.01425034/RSS | 14 | 250 | 34 | 34 | 1240 | 1240 | 1240 | 0.029524 | 482 | 0.011476 | 1412 | 0.033619 | 1.362 | A04 | MICL0.01425034/RSS
Build-In Floor | Mini Canal | MICL.01425034/SBL | 14 | 250 | 34 | 34 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01425034/SBL
Build-In Floor | Mini Canal | MICL.01425034/SBR | 14 | 250 | 34 | 34 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01425034/SBR
Build-In Floor | Mini Canal | MICL.01425034/SDB | 14 | 250 | 34 | 34 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01425034/SDB
Build-In Floor | Mini Canal | MICL.01425034/SNA | 14 | 250 | 34 | 34 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01425034/SNA
Build-In Floor | Mini Canal | MICL.01425034/SNC | 14 | 250 | 34 | 34 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01425034/SNC
Build-In Floor | Mini Canal | MICL.01425042/ANA | 14 | 250 | 42 | 42 | 1307 | 1307 | 1307 | 0.031119 | 508 | 0.012095 | 1489 | 0.035452 | 1.362 | A04 | MICL0.01425042/ANA
Build-In Floor | Mini Canal | MICL.01425042/DBL | 14 | 250 | 42 | 42 | 1690 | 1690 | 1690 | 0.040238 | 657 | 0.015643 | 1925 | 0.045833 | 1.362 | A04 | MICL0.01425042/DBL
Build-In Floor | Mini Canal | MICL.01425042/DBN | 14 | 250 | 42 | 42 | 1620 | 1620 | 1620 | 0.038571 | 630 | 0.015 | 1845 | 0.043929 | 1.362 | A04 | MICL0.01425042/DBN
Build-In Floor | Mini Canal | MICL.01425042/DBR | 14 | 250 | 42 | 42 | 1690 | 1690 | 1690 | 0.040238 | 657 | 0.015643 | 1925 | 0.045833 | 1.362 | A04 | MICL0.01425042/DBR
Build-In Floor | Mini Canal | MICL.01425042/DBV | 14 | 250 | 42 | 42 | 1620 | 1620 | 1620 | 0.038571 | 630 | 0.015 | 1845 | 0.043929 | 1.362 | A04 | MICL0.01425042/DBV
Build-In Floor | Mini Canal | MICL.01425042/DDB | 14 | 250 | 42 | 42 | 1690 | 1690 | 1690 | 0.040238 | 657 | 0.015643 | 1925 | 0.045833 | 1.362 | A04 | MICL0.01425042/DDB
Build-In Floor | Mini Canal | MICL.01425042/DMN | 14 | 250 | 42 | 42 | 1620 | 1620 | 1620 | 0.038571 | 630 | 0.015 | 1845 | 0.043929 | 1.362 | A04 | MICL0.01425042/DMN
Build-In Floor | Mini Canal | MICL.01425042/DMV | 14 | 250 | 42 | 42 | 1620 | 1620 | 1620 | 0.038571 | 630 | 0.015 | 1845 | 0.043929 | 1.362 | A04 | MICL0.01425042/DMV
Build-In Floor | Mini Canal | MICL.01425042/DNA | 14 | 250 | 42 | 42 | 1690 | 1690 | 1690 | 0.040238 | 657 | 0.015643 | 1925 | 0.045833 | 1.362 | A04 | MICL0.01425042/DNA
Build-In Floor | Mini Canal | MICL.01425042/DNC | 14 | 250 | 42 | 42 | 1690 | 1690 | 1690 | 0.040238 | 657 | 0.015643 | 1925 | 0.045833 | 1.362 | A04 | MICL0.01425042/DNC
Build-In Floor | Mini Canal | MICL.01425042/DON | 14 | 250 | 42 | 42 | 1620 | 1620 | 1620 | 0.038571 | 630 | 0.015 | 1845 | 0.043929 | 1.362 | A04 | MICL0.01425042/DON
Build-In Floor | Mini Canal | MICL.01425042/DOV | 14 | 250 | 42 | 42 | 1620 | 1620 | 1620 | 0.038571 | 630 | 0.015 | 1845 | 0.043929 | 1.362 | A04 | MICL0.01425042/DOV
Build-In Floor | Mini Canal | MICL.01425042/PNC | 14 | 250 | 42 | 42 | 1481 | 1481 | 1481 | 0.035262 | 576 | 0.013714 | 1687 | 0.040167 | 1.362 | A04 | MICL0.01425042/PNC
Build-In Floor | Mini Canal | MICL.01425042/RBL | 14 | 250 | 42 | 42 | 1742 | 1742 | 1742 | 0.041476 | 678 | 0.016143 | 1984 | 0.047238 | 1.362 | A04 | MICL0.01425042/RBL
Build-In Floor | Mini Canal | MICL.01425042/RBN | 14 | 250 | 42 | 42 | 1690 | 1690 | 1690 | 0.040238 | 657 | 0.015643 | 1925 | 0.045833 | 1.362 | A04 | MICL0.01425042/RBN
Build-In Floor | Mini Canal | MICL.01425042/RBR | 14 | 250 | 42 | 42 | 1742 | 1742 | 1742 | 0.041476 | 678 | 0.016143 | 1984 | 0.047238 | 1.362 | A04 | MICL0.01425042/RBR
Build-In Floor | Mini Canal | MICL.01425042/RBV | 14 | 250 | 42 | 42 | 1690 | 1690 | 1690 | 0.040238 | 657 | 0.015643 | 1925 | 0.045833 | 1.362 | A04 | MICL0.01425042/RBV
Build-In Floor | Mini Canal | MICL.01425042/RDB | 14 | 250 | 42 | 42 | 1742 | 1742 | 1742 | 0.041476 | 678 | 0.016143 | 1984 | 0.047238 | 1.362 | A04 | MICL0.01425042/RDB
Build-In Floor | Mini Canal | MICL.01425042/RMN | 14 | 250 | 42 | 42 | 1690 | 1690 | 1690 | 0.040238 | 657 | 0.015643 | 1925 | 0.045833 | 1.362 | A04 | MICL0.01425042/RMN
Build-In Floor | Mini Canal | MICL.01425042/RMV | 14 | 250 | 42 | 42 | 1690 | 1690 | 1690 | 0.040238 | 657 | 0.015643 | 1925 | 0.045833 | 1.362 | A04 | MICL0.01425042/RMV
Build-In Floor | Mini Canal | MICL.01425042/RNA | 14 | 250 | 42 | 42 | 1742 | 1742 | 1742 | 0.041476 | 678 | 0.016143 | 1984 | 0.047238 | 1.362 | A04 | MICL0.01425042/RNA
Build-In Floor | Mini Canal | MICL.01425042/RON | 14 | 250 | 42 | 42 | 1690 | 1690 | 1690 | 0.040238 | 657 | 0.015643 | 1925 | 0.045833 | 1.362 | A04 | MICL0.01425042/RON
Build-In Floor | Mini Canal | MICL.01425042/ROV | 14 | 250 | 42 | 42 | 1690 | 1690 | 1690 | 0.040238 | 657 | 0.015643 | 1925 | 0.045833 | 1.362 | A04 | MICL0.01425042/ROV
Build-In Floor | Mini Canal | MICL.01425042/RSS | 14 | 250 | 42 | 42 | 1672 | 1672 | 1672 | 0.03981 | 650 | 0.015476 | 1904 | 0.045333 | 1.362 | A04 | MICL0.01425042/RSS
Build-In Floor | Mini Canal | MICL.01425042/SBL | 14 | 250 | 42 | 42 | 1742 | 1742 | 1742 | 0.041476 | 678 | 0.016143 | 1984 | 0.047238 | 1.362 | A04 | MICL0.01425042/SBL
Build-In Floor | Mini Canal | MICL.01425042/SBR | 14 | 250 | 42 | 42 | 1742 | 1742 | 1742 | 0.041476 | 678 | 0.016143 | 1984 | 0.047238 | 1.362 | A04 | MICL0.01425042/SBR
Build-In Floor | Mini Canal | MICL.01425042/SDB | 14 | 250 | 42 | 42 | 1742 | 1742 | 1742 | 0.041476 | 678 | 0.016143 | 1984 | 0.047238 | 1.362 | A04 | MICL0.01425042/SDB
Build-In Floor | Mini Canal | MICL.01425042/SNA | 14 | 250 | 42 | 42 | 1742 | 1742 | 1742 | 0.041476 | 678 | 0.016143 | 1984 | 0.047238 | 1.362 | A04 | MICL0.01425042/SNA
Build-In Floor | Mini Canal | MICL.01425042/SNC | 14 | 250 | 42 | 42 | 1742 | 1742 | 1742 | 0.041476 | 678 | 0.016143 | 1984 | 0.047238 | 1.362 | A04 | MICL0.01425042/SNC
Build-In Floor | Mini Canal | MICL.01427014/ANA | 14 | 270 | 14 | 14 | 446 | 446 | 446 | 0.010619 | 173 | 0.004119 | 508 | 0.012095 | 1.362 | A04 | MICL0.01427014/ANA
Build-In Floor | Mini Canal | MICL.01427014/DBL | 14 | 270 | 14 | 14 | 577 | 577 | 577 | 0.013738 | 224 | 0.0053333 | 657 | 0.015643 | 1.362 | A04 | MICL0.01427014/DBL
Build-In Floor | Mini Canal | MICL.01427014/DBN | 14 | 270 | 14 | 14 | 553 | 553 | 553 | 0.013167 | 215 | 0.005119 | 630 | 0.015 | 1.362 | A04 | MICL0.01427014/DBN
Build-In Floor | Mini Canal | MICL.01427014/DBR | 14 | 270 | 14 | 14 | 577 | 577 | 577 | 0.013738 | 224 | 0.0053333 | 657 | 0.015643 | 1.362 | A04 | MICL0.01427014/DBR
Build-In Floor | Mini Canal | MICL.01427014/DBV | 14 | 270 | 14 | 14 | 553 | 553 | 553 | 0.013167 | 215 | 0.005119 | 630 | 0.015 | 1.362 | A04 | MICL0.01427014/DBV
Build-In Floor | Mini Canal | MICL.01427014/DDB | 14 | 270 | 14 | 14 | 577 | 577 | 577 | 0.013738 | 224 | 0.0053333 | 657 | 0.015643 | 1.362 | A04 | MICL0.01427014/DDB
Build-In Floor | Mini Canal | MICL.01427014/DMN | 14 | 270 | 14 | 14 | 553 | 553 | 553 | 0.013167 | 215 | 0.005119 | 630 | 0.015 | 1.362 | A04 | MICL0.01427014/DMN
Build-In Floor | Mini Canal | MICL.01427014/DMV | 14 | 270 | 14 | 14 | 553 | 553 | 553 | 0.013167 | 215 | 0.005119 | 630 | 0.015 | 1.362 | A04 | MICL0.01427014/DMV
Build-In Floor | Mini Canal | MICL.01427014/DNA | 14 | 270 | 14 | 14 | 577 | 577 | 577 | 0.013738 | 224 | 0.0053333 | 657 | 0.015643 | 1.362 | A04 | MICL0.01427014/DNA
Build-In Floor | Mini Canal | MICL.01427014/DNC | 14 | 270 | 14 | 14 | 577 | 577 | 577 | 0.013738 | 224 | 0.0053333 | 657 | 0.015643 | 1.362 | A04 | MICL0.01427014/DNC
Build-In Floor | Mini Canal | MICL.01427014/DON | 14 | 270 | 14 | 14 | 553 | 553 | 553 | 0.013167 | 215 | 0.005119 | 630 | 0.015 | 1.362 | A04 | MICL0.01427014/DON
Build-In Floor | Mini Canal | MICL.01427014/DOV | 14 | 270 | 14 | 14 | 553 | 553 | 553 | 0.013167 | 215 | 0.005119 | 630 | 0.015 | 1.362 | A04 | MICL0.01427014/DOV
Build-In Floor | Mini Canal | MICL.01427014/RBL | 14 | 270 | 14 | 14 | 595 | 595 | 595 | 0.014167 | 231 | 0.0055 | 678 | 0.016143 | 1.362 | A04 | MICL0.01427014/RBL
Build-In Floor | Mini Canal | MICL.01427014/RBN | 14 | 270 | 14 | 14 | 577 | 577 | 577 | 0.013738 | 224 | 0.0053333 | 657 | 0.015643 | 1.362 | A04 | MICL0.01427014/RBN
Build-In Floor | Mini Canal | MICL.01427014/RBR | 14 | 270 | 14 | 14 | 595 | 595 | 595 | 0.014167 | 231 | 0.0055 | 678 | 0.016143 | 1.362 | A04 | MICL0.01427014/RBR
Build-In Floor | Mini Canal | MICL.01427014/RBV | 14 | 270 | 14 | 14 | 577 | 577 | 577 | 0.013738 | 224 | 0.0053333 | 657 | 0.015643 | 1.362 | A04 | MICL0.01427014/RBV
Build-In Floor | Mini Canal | MICL.01427014/RDB | 14 | 270 | 14 | 14 | 595 | 595 | 595 | 0.014167 | 231 | 0.0055 | 678 | 0.016143 | 1.362 | A04 | MICL0.01427014/RDB
Build-In Floor | Mini Canal | MICL.01427014/RMN | 14 | 270 | 14 | 14 | 577 | 577 | 577 | 0.013738 | 224 | 0.0053333 | 657 | 0.015643 | 1.362 | A04 | MICL0.01427014/RMN
Build-In Floor | Mini Canal | MICL.01427014/RMV | 14 | 270 | 14 | 14 | 577 | 577 | 577 | 0.013738 | 224 | 0.0053333 | 657 | 0.015643 | 1.362 | A04 | MICL0.01427014/RMV
Build-In Floor | Mini Canal | MICL.01427014/RNA | 14 | 270 | 14 | 14 | 595 | 595 | 595 | 0.014167 | 231 | 0.0055 | 678 | 0.016143 | 1.362 | A04 | MICL0.01427014/RNA
Build-In Floor | Mini Canal | MICL.01427014/RON | 14 | 270 | 14 | 14 | 577 | 577 | 577 | 0.013738 | 224 | 0.0053333 | 657 | 0.015643 | 1.362 | A04 | MICL0.01427014/RON
Build-In Floor | Mini Canal | MICL.01427014/ROV | 14 | 270 | 14 | 14 | 577 | 577 | 577 | 0.013738 | 224 | 0.0053333 | 657 | 0.015643 | 1.362 | A04 | MICL0.01427014/ROV
Build-In Floor | Mini Canal | MICL.01427014/RSS | 14 | 270 | 14 | 14 | 571 | 571 | 571 | 0.013595 | 222 | 0.0052857 | 650 | 0.015476 | 1.362 | A04 | MICL0.01427014/RSS
Build-In Floor | Mini Canal | MICL.01427014/SBL | 14 | 270 | 14 | 14 | 595 | 595 | 595 | 0.014167 | 231 | 0.0055 | 678 | 0.016143 | 1.362 | A04 | MICL0.01427014/SBL
Build-In Floor | Mini Canal | MICL.01427014/SBR | 14 | 270 | 14 | 14 | 595 | 595 | 595 | 0.014167 | 231 | 0.0055 | 678 | 0.016143 | 1.362 | A04 | MICL0.01427014/SBR
Build-In Floor | Mini Canal | MICL.01427014/SDB | 14 | 270 | 14 | 14 | 595 | 595 | 595 | 0.014167 | 231 | 0.0055 | 678 | 0.016143 | 1.362 | A04 | MICL0.01427014/SDB
Build-In Floor | Mini Canal | MICL.01427014/SNA | 14 | 270 | 14 | 14 | 595 | 595 | 595 | 0.014167 | 231 | 0.0055 | 678 | 0.016143 | 1.362 | A04 | MICL0.01427014/SNA
Build-In Floor | Mini Canal | MICL.01427014/SNC | 14 | 270 | 14 | 14 | 595 | 595 | 595 | 0.014167 | 231 | 0.0055 | 678 | 0.016143 | 1.362 | A04 | MICL0.01427014/SNC
Build-In Floor | Mini Canal | MICL.01427026/ANA | 14 | 270 | 26 | 26 | 776 | 776 | 776 | 0.018476 | 302 | 0.0071905 | 884 | 0.021048 | 1.362 | A04 | MICL0.01427026/ANA
Build-In Floor | Mini Canal | MICL.01427026/DBL | 14 | 270 | 26 | 26 | 1003 | 1003 | 1003 | 0.023881 | 390 | 0.0092857 | 1142 | 0.02719 | 1.362 | A04 | MICL0.01427026/DBL
Build-In Floor | Mini Canal | MICL.01427026/DBN | 14 | 270 | 26 | 26 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01427026/DBN
Build-In Floor | Mini Canal | MICL.01427026/DBR | 14 | 270 | 26 | 26 | 1003 | 1003 | 1003 | 0.023881 | 390 | 0.0092857 | 1142 | 0.02719 | 1.362 | A04 | MICL0.01427026/DBR
Build-In Floor | Mini Canal | MICL.01427026/DBV | 14 | 270 | 26 | 26 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01427026/DBV
Build-In Floor | Mini Canal | MICL.01427026/DDB | 14 | 270 | 26 | 26 | 1003 | 1003 | 1003 | 0.023881 | 390 | 0.0092857 | 1142 | 0.02719 | 1.362 | A04 | MICL0.01427026/DDB
Build-In Floor | Mini Canal | MICL.01427026/DMN | 14 | 270 | 26 | 26 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01427026/DMN
Build-In Floor | Mini Canal | MICL.01427026/DMV | 14 | 270 | 26 | 26 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01427026/DMV
Build-In Floor | Mini Canal | MICL.01427026/DNA | 14 | 270 | 26 | 26 | 1003 | 1003 | 1003 | 0.023881 | 390 | 0.0092857 | 1142 | 0.02719 | 1.362 | A04 | MICL0.01427026/DNA
Build-In Floor | Mini Canal | MICL.01427026/DNC | 14 | 270 | 26 | 26 | 1003 | 1003 | 1003 | 0.023881 | 390 | 0.0092857 | 1142 | 0.02719 | 1.362 | A04 | MICL0.01427026/DNC
Build-In Floor | Mini Canal | MICL.01427026/DON | 14 | 270 | 26 | 26 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01427026/DON
Build-In Floor | Mini Canal | MICL.01427026/DOV | 14 | 270 | 26 | 26 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01427026/DOV
Build-In Floor | Mini Canal | MICL.01427026/PNC | 14 | 270 | 26 | 26 | 879 | 879 | 879 | 0.020929 | 342 | 0.0081429 | 1001 | 0.023833 | 1.362 | A04 | MICL0.01427026/PNC
Build-In Floor | Mini Canal | MICL.01427026/RBL | 14 | 270 | 26 | 26 | 1034 | 1034 | 1034 | 0.024619 | 402 | 0.0095714 | 1178 | 0.028048 | 1.362 | A04 | MICL0.01427026/RBL
Build-In Floor | Mini Canal | MICL.01427026/RBN | 14 | 270 | 26 | 26 | 1003 | 1003 | 1003 | 0.023881 | 390 | 0.0092857 | 1142 | 0.02719 | 1.362 | A04 | MICL0.01427026/RBN
Build-In Floor | Mini Canal | MICL.01427026/RBR | 14 | 270 | 26 | 26 | 1034 | 1034 | 1034 | 0.024619 | 402 | 0.0095714 | 1178 | 0.028048 | 1.362 | A04 | MICL0.01427026/RBR
Build-In Floor | Mini Canal | MICL.01427026/RBV | 14 | 270 | 26 | 26 | 1003 | 1003 | 1003 | 0.023881 | 390 | 0.0092857 | 1142 | 0.02719 | 1.362 | A04 | MICL0.01427026/RBV
Build-In Floor | Mini Canal | MICL.01427026/RDB | 14 | 270 | 26 | 26 | 1034 | 1034 | 1034 | 0.024619 | 402 | 0.0095714 | 1178 | 0.028048 | 1.362 | A04 | MICL0.01427026/RDB
Build-In Floor | Mini Canal | MICL.01427026/RMN | 14 | 270 | 26 | 26 | 1003 | 1003 | 1003 | 0.023881 | 390 | 0.0092857 | 1142 | 0.02719 | 1.362 | A04 | MICL0.01427026/RMN
Build-In Floor | Mini Canal | MICL.01427026/RMV | 14 | 270 | 26 | 26 | 1003 | 1003 | 1003 | 0.023881 | 390 | 0.0092857 | 1142 | 0.02719 | 1.362 | A04 | MICL0.01427026/RMV
Build-In Floor | Mini Canal | MICL.01427026/RNA | 14 | 270 | 26 | 26 | 1034 | 1034 | 1034 | 0.024619 | 402 | 0.0095714 | 1178 | 0.028048 | 1.362 | A04 | MICL0.01427026/RNA
Build-In Floor | Mini Canal | MICL.01427026/RON | 14 | 270 | 26 | 26 | 1003 | 1003 | 1003 | 0.023881 | 390 | 0.0092857 | 1142 | 0.02719 | 1.362 | A04 | MICL0.01427026/RON
Build-In Floor | Mini Canal | MICL.01427026/ROV | 14 | 270 | 26 | 26 | 1003 | 1003 | 1003 | 0.023881 | 390 | 0.0092857 | 1142 | 0.02719 | 1.362 | A04 | MICL0.01427026/ROV
Build-In Floor | Mini Canal | MICL.01427026/RSS | 14 | 270 | 26 | 26 | 993 | 993 | 993 | 0.023643 | 386 | 0.0091905 | 1131 | 0.026929 | 1.362 | A04 | MICL0.01427026/RSS
Build-In Floor | Mini Canal | MICL.01427026/SBL | 14 | 270 | 26 | 26 | 1034 | 1034 | 1034 | 0.024619 | 402 | 0.0095714 | 1178 | 0.028048 | 1.362 | A04 | MICL0.01427026/SBL
Build-In Floor | Mini Canal | MICL.01427026/SBR | 14 | 270 | 26 | 26 | 1034 | 1034 | 1034 | 0.024619 | 402 | 0.0095714 | 1178 | 0.028048 | 1.362 | A04 | MICL0.01427026/SBR
Build-In Floor | Mini Canal | MICL.01427026/SDB | 14 | 270 | 26 | 26 | 1034 | 1034 | 1034 | 0.024619 | 402 | 0.0095714 | 1178 | 0.028048 | 1.362 | A04 | MICL0.01427026/SDB
Build-In Floor | Mini Canal | MICL.01427026/SNA | 14 | 270 | 26 | 26 | 1034 | 1034 | 1034 | 0.024619 | 402 | 0.0095714 | 1178 | 0.028048 | 1.362 | A04 | MICL0.01427026/SNA
Build-In Floor | Mini Canal | MICL.01427026/SNC | 14 | 270 | 26 | 26 | 1034 | 1034 | 1034 | 0.024619 | 402 | 0.0095714 | 1178 | 0.028048 | 1.362 | A04 | MICL0.01427026/SNC
Build-In Floor | Mini Canal | MICL.01427034/ANA | 14 | 270 | 34 | 34 | 1057 | 1057 | 1057 | 0.025167 | 411 | 0.0097857 | 1204 | 0.028667 | 1.362 | A04 | MICL0.01427034/ANA
Build-In Floor | Mini Canal | MICL.01427034/DBL | 14 | 270 | 34 | 34 | 1367 | 1367 | 1367 | 0.032548 | 532 | 0.012667 | 1557 | 0.037071 | 1.362 | A04 | MICL0.01427034/DBL
Build-In Floor | Mini Canal | MICL.01427034/DBN | 14 | 270 | 34 | 34 | 1310 | 1310 | 1310 | 0.03119 | 510 | 0.012143 | 1492 | 0.035524 | 1.362 | A04 | MICL0.01427034/DBN
Build-In Floor | Mini Canal | MICL.01427034/DBR | 14 | 270 | 34 | 34 | 1367 | 1367 | 1367 | 0.032548 | 532 | 0.012667 | 1557 | 0.037071 | 1.362 | A04 | MICL0.01427034/DBR
Build-In Floor | Mini Canal | MICL.01427034/DBV | 14 | 270 | 34 | 34 | 1310 | 1310 | 1310 | 0.03119 | 510 | 0.012143 | 1492 | 0.035524 | 1.362 | A04 | MICL0.01427034/DBV
Build-In Floor | Mini Canal | MICL.01427034/DDB | 14 | 270 | 34 | 34 | 1367 | 1367 | 1367 | 0.032548 | 532 | 0.012667 | 1557 | 0.037071 | 1.362 | A04 | MICL0.01427034/DDB
Build-In Floor | Mini Canal | MICL.01427034/DMN | 14 | 270 | 34 | 34 | 1310 | 1310 | 1310 | 0.03119 | 510 | 0.012143 | 1492 | 0.035524 | 1.362 | A04 | MICL0.01427034/DMN
Build-In Floor | Mini Canal | MICL.01427034/DMV | 14 | 270 | 34 | 34 | 1310 | 1310 | 1310 | 0.03119 | 510 | 0.012143 | 1492 | 0.035524 | 1.362 | A04 | MICL0.01427034/DMV
Build-In Floor | Mini Canal | MICL.01427034/DNA | 14 | 270 | 34 | 34 | 1367 | 1367 | 1367 | 0.032548 | 532 | 0.012667 | 1557 | 0.037071 | 1.362 | A04 | MICL0.01427034/DNA
Build-In Floor | Mini Canal | MICL.01427034/DNC | 14 | 270 | 34 | 34 | 1367 | 1367 | 1367 | 0.032548 | 532 | 0.012667 | 1557 | 0.037071 | 1.362 | A04 | MICL0.01427034/DNC
Build-In Floor | Mini Canal | MICL.01427034/DON | 14 | 270 | 34 | 34 | 1310 | 1310 | 1310 | 0.03119 | 510 | 0.012143 | 1492 | 0.035524 | 1.362 | A04 | MICL0.01427034/DON
Build-In Floor | Mini Canal | MICL.01427034/DOV | 14 | 270 | 34 | 34 | 1310 | 1310 | 1310 | 0.03119 | 510 | 0.012143 | 1492 | 0.035524 | 1.362 | A04 | MICL0.01427034/DOV
Build-In Floor | Mini Canal | MICL.01427034/PNC | 14 | 270 | 34 | 34 | 1198 | 1198 | 1198 | 0.028524 | 466 | 0.011095 | 1365 | 0.0325 | 1.362 | A04 | MICL0.01427034/PNC
Build-In Floor | Mini Canal | MICL.01427034/RBL | 14 | 270 | 34 | 34 | 1409 | 1409 | 1409 | 0.033548 | 548 | 0.013048 | 1605 | 0.038214 | 1.362 | A04 | MICL0.01427034/RBL
Build-In Floor | Mini Canal | MICL.01427034/RBN | 14 | 270 | 34 | 34 | 1367 | 1367 | 1367 | 0.032548 | 532 | 0.012667 | 1557 | 0.037071 | 1.362 | A04 | MICL0.01427034/RBN
Build-In Floor | Mini Canal | MICL.01427034/RBR | 14 | 270 | 34 | 34 | 1409 | 1409 | 1409 | 0.033548 | 548 | 0.013048 | 1605 | 0.038214 | 1.362 | A04 | MICL0.01427034/RBR
Build-In Floor | Mini Canal | MICL.01427034/RBV | 14 | 270 | 34 | 34 | 1367 | 1367 | 1367 | 0.032548 | 532 | 0.012667 | 1557 | 0.037071 | 1.362 | A04 | MICL0.01427034/RBV
Build-In Floor | Mini Canal | MICL.01427034/RDB | 14 | 270 | 34 | 34 | 1409 | 1409 | 1409 | 0.033548 | 548 | 0.013048 | 1605 | 0.038214 | 1.362 | A04 | MICL0.01427034/RDB
Build-In Floor | Mini Canal | MICL.01427034/RMN | 14 | 270 | 34 | 34 | 1367 | 1367 | 1367 | 0.032548 | 532 | 0.012667 | 1557 | 0.037071 | 1.362 | A04 | MICL0.01427034/RMN
Build-In Floor | Mini Canal | MICL.01427034/RMV | 14 | 270 | 34 | 34 | 1367 | 1367 | 1367 | 0.032548 | 532 | 0.012667 | 1557 | 0.037071 | 1.362 | A04 | MICL0.01427034/RMV
Build-In Floor | Mini Canal | MICL.01427034/RNA | 14 | 270 | 34 | 34 | 1409 | 1409 | 1409 | 0.033548 | 548 | 0.013048 | 1605 | 0.038214 | 1.362 | A04 | MICL0.01427034/RNA
Build-In Floor | Mini Canal | MICL.01427034/RON | 14 | 270 | 34 | 34 | 1367 | 1367 | 1367 | 0.032548 | 532 | 0.012667 | 1557 | 0.037071 | 1.362 | A04 | MICL0.01427034/RON
Build-In Floor | Mini Canal | MICL.01427034/ROV | 14 | 270 | 34 | 34 | 1367 | 1367 | 1367 | 0.032548 | 532 | 0.012667 | 1557 | 0.037071 | 1.362 | A04 | MICL0.01427034/ROV
Build-In Floor | Mini Canal | MICL.01427034/RSS | 14 | 270 | 34 | 34 | 1353 | 1353 | 1353 | 0.032214 | 526 | 0.012524 | 1541 | 0.03669 | 1.362 | A04 | MICL0.01427034/RSS
Build-In Floor | Mini Canal | MICL.01427034/SBL | 14 | 270 | 34 | 34 | 1409 | 1409 | 1409 | 0.033548 | 548 | 0.013048 | 1605 | 0.038214 | 1.362 | A04 | MICL0.01427034/SBL
Build-In Floor | Mini Canal | MICL.01427034/SBR | 14 | 270 | 34 | 34 | 1409 | 1409 | 1409 | 0.033548 | 548 | 0.013048 | 1605 | 0.038214 | 1.362 | A04 | MICL0.01427034/SBR
Build-In Floor | Mini Canal | MICL.01427034/SDB | 14 | 270 | 34 | 34 | 1409 | 1409 | 1409 | 0.033548 | 548 | 0.013048 | 1605 | 0.038214 | 1.362 | A04 | MICL0.01427034/SDB
Build-In Floor | Mini Canal | MICL.01427034/SNA | 14 | 270 | 34 | 34 | 1409 | 1409 | 1409 | 0.033548 | 548 | 0.013048 | 1605 | 0.038214 | 1.362 | A04 | MICL0.01427034/SNA
Build-In Floor | Mini Canal | MICL.01427034/SNC | 14 | 270 | 34 | 34 | 1409 | 1409 | 1409 | 0.033548 | 548 | 0.013048 | 1605 | 0.038214 | 1.362 | A04 | MICL0.01427034/SNC
Build-In Floor | Mini Canal | MICL.01427042/ANA | 14 | 270 | 42 | 42 | 1425 | 1425 | 1425 | 0.033929 | 554 | 0.01319 | 1623 | 0.038643 | 1.362 | A04 | MICL0.01427042/ANA
Build-In Floor | Mini Canal | MICL.01427042/DBL | 14 | 270 | 42 | 42 | 1843 | 1843 | 1843 | 0.043881 | 717 | 0.017071 | 2099 | 0.049976 | 1.362 | A04 | MICL0.01427042/DBL
Build-In Floor | Mini Canal | MICL.01427042/DBN | 14 | 270 | 42 | 42 | 1767 | 1767 | 1767 | 0.042071 | 687 | 0.016357 | 2013 | 0.047929 | 1.362 | A04 | MICL0.01427042/DBN
Build-In Floor | Mini Canal | MICL.01427042/DBR | 14 | 270 | 42 | 42 | 1843 | 1843 | 1843 | 0.043881 | 717 | 0.017071 | 2099 | 0.049976 | 1.362 | A04 | MICL0.01427042/DBR
Build-In Floor | Mini Canal | MICL.01427042/DBV | 14 | 270 | 42 | 42 | 1767 | 1767 | 1767 | 0.042071 | 687 | 0.016357 | 2013 | 0.047929 | 1.362 | A04 | MICL0.01427042/DBV
Build-In Floor | Mini Canal | MICL.01427042/DDB | 14 | 270 | 42 | 42 | 1843 | 1843 | 1843 | 0.043881 | 717 | 0.017071 | 2099 | 0.049976 | 1.362 | A04 | MICL0.01427042/DDB
Build-In Floor | Mini Canal | MICL.01427042/DMN | 14 | 270 | 42 | 42 | 1767 | 1767 | 1767 | 0.042071 | 687 | 0.016357 | 2013 | 0.047929 | 1.362 | A04 | MICL0.01427042/DMN
Build-In Floor | Mini Canal | MICL.01427042/DMV | 14 | 270 | 42 | 42 | 1767 | 1767 | 1767 | 0.042071 | 687 | 0.016357 | 2013 | 0.047929 | 1.362 | A04 | MICL0.01427042/DMV
Build-In Floor | Mini Canal | MICL.01427042/DNA | 14 | 270 | 42 | 42 | 1843 | 1843 | 1843 | 0.043881 | 717 | 0.017071 | 2099 | 0.049976 | 1.362 | A04 | MICL0.01427042/DNA
Build-In Floor | Mini Canal | MICL.01427042/DNC | 14 | 270 | 42 | 42 | 1843 | 1843 | 1843 | 0.043881 | 717 | 0.017071 | 2099 | 0.049976 | 1.362 | A04 | MICL0.01427042/DNC
Build-In Floor | Mini Canal | MICL.01427042/DON | 14 | 270 | 42 | 42 | 1767 | 1767 | 1767 | 0.042071 | 687 | 0.016357 | 2013 | 0.047929 | 1.362 | A04 | MICL0.01427042/DON
Build-In Floor | Mini Canal | MICL.01427042/DOV | 14 | 270 | 42 | 42 | 1767 | 1767 | 1767 | 0.042071 | 687 | 0.016357 | 2013 | 0.047929 | 1.362 | A04 | MICL0.01427042/DOV
Build-In Floor | Mini Canal | MICL.01427042/PNC | 14 | 270 | 42 | 42 | 1615 | 1615 | 1615 | 0.038452 | 628 | 0.014952 | 1839 | 0.043786 | 1.362 | A04 | MICL0.01427042/PNC
Build-In Floor | Mini Canal | MICL.01427042/RBL | 14 | 270 | 42 | 42 | 1900 | 1900 | 1900 | 0.045238 | 739 | 0.017595 | 2164 | 0.051524 | 1.362 | A04 | MICL0.01427042/RBL
Build-In Floor | Mini Canal | MICL.01427042/RBN | 14 | 270 | 42 | 42 | 1843 | 1843 | 1843 | 0.043881 | 717 | 0.017071 | 2099 | 0.049976 | 1.362 | A04 | MICL0.01427042/RBN
Build-In Floor | Mini Canal | MICL.01427042/RBR | 14 | 270 | 42 | 42 | 1900 | 1900 | 1900 | 0.045238 | 739 | 0.017595 | 2164 | 0.051524 | 1.362 | A04 | MICL0.01427042/RBR
Build-In Floor | Mini Canal | MICL.01427042/RBV | 14 | 270 | 42 | 42 | 1843 | 1843 | 1843 | 0.043881 | 717 | 0.017071 | 2099 | 0.049976 | 1.362 | A04 | MICL0.01427042/RBV
Build-In Floor | Mini Canal | MICL.01427042/RDB | 14 | 270 | 42 | 42 | 1900 | 1900 | 1900 | 0.045238 | 739 | 0.017595 | 2164 | 0.051524 | 1.362 | A04 | MICL0.01427042/RDB
Build-In Floor | Mini Canal | MICL.01427042/RMN | 14 | 270 | 42 | 42 | 1843 | 1843 | 1843 | 0.043881 | 717 | 0.017071 | 2099 | 0.049976 | 1.362 | A04 | MICL0.01427042/RMN
Build-In Floor | Mini Canal | MICL.01427042/RMV | 14 | 270 | 42 | 42 | 1843 | 1843 | 1843 | 0.043881 | 717 | 0.017071 | 2099 | 0.049976 | 1.362 | A04 | MICL0.01427042/RMV
Build-In Floor | Mini Canal | MICL.01427042/RNA | 14 | 270 | 42 | 42 | 1900 | 1900 | 1900 | 0.045238 | 739 | 0.017595 | 2164 | 0.051524 | 1.362 | A04 | MICL0.01427042/RNA
Build-In Floor | Mini Canal | MICL.01427042/RON | 14 | 270 | 42 | 42 | 1843 | 1843 | 1843 | 0.043881 | 717 | 0.017071 | 2099 | 0.049976 | 1.362 | A04 | MICL0.01427042/RON
Build-In Floor | Mini Canal | MICL.01427042/ROV | 14 | 270 | 42 | 42 | 1843 | 1843 | 1843 | 0.043881 | 717 | 0.017071 | 2099 | 0.049976 | 1.362 | A04 | MICL0.01427042/ROV
Build-In Floor | Mini Canal | MICL.01427042/RSS | 14 | 270 | 42 | 42 | 1824 | 1824 | 1824 | 0.043429 | 710 | 0.016905 | 2078 | 0.049476 | 1.362 | A04 | MICL0.01427042/RSS
Build-In Floor | Mini Canal | MICL.01427042/SBL | 14 | 270 | 42 | 42 | 1900 | 1900 | 1900 | 0.045238 | 739 | 0.017595 | 2164 | 0.051524 | 1.362 | A04 | MICL0.01427042/SBL
Build-In Floor | Mini Canal | MICL.01427042/SBR | 14 | 270 | 42 | 42 | 1900 | 1900 | 1900 | 0.045238 | 739 | 0.017595 | 2164 | 0.051524 | 1.362 | A04 | MICL0.01427042/SBR
Build-In Floor | Mini Canal | MICL.01427042/SDB | 14 | 270 | 42 | 42 | 1900 | 1900 | 1900 | 0.045238 | 739 | 0.017595 | 2164 | 0.051524 | 1.362 | A04 | MICL0.01427042/SDB
Build-In Floor | Mini Canal | MICL.01427042/SNA | 14 | 270 | 42 | 42 | 1900 | 1900 | 1900 | 0.045238 | 739 | 0.017595 | 2164 | 0.051524 | 1.362 | A04 | MICL0.01427042/SNA
Build-In Floor | Mini Canal | MICL.01427042/SNC | 14 | 270 | 42 | 42 | 1900 | 1900 | 1900 | 0.045238 | 739 | 0.017595 | 2164 | 0.051524 | 1.362 | A04 | MICL0.01427042/SNC
Build-In Floor | Mini Canal | MICL.01429014/ANA | 14 | 290 | 14 | 14 | 484 | 484 | 484 | 0.011524 | 188 | 0.0044762 | 551 | 0.013119 | 1.362 | A04 | MICL0.01429014/ANA
Build-In Floor | Mini Canal | MICL.01429014/DBL | 14 | 290 | 14 | 14 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01429014/DBL
Build-In Floor | Mini Canal | MICL.01429014/DBN | 14 | 290 | 14 | 14 | 600 | 600 | 600 | 0.014286 | 233 | 0.0055476 | 683 | 0.016262 | 1.362 | A04 | MICL0.01429014/DBN
Build-In Floor | Mini Canal | MICL.01429014/DBR | 14 | 290 | 14 | 14 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01429014/DBR
Build-In Floor | Mini Canal | MICL.01429014/DBV | 14 | 290 | 14 | 14 | 600 | 600 | 600 | 0.014286 | 233 | 0.0055476 | 683 | 0.016262 | 1.362 | A04 | MICL0.01429014/DBV
Build-In Floor | Mini Canal | MICL.01429014/DDB | 14 | 290 | 14 | 14 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01429014/DDB
Build-In Floor | Mini Canal | MICL.01429014/DMN | 14 | 290 | 14 | 14 | 600 | 600 | 600 | 0.014286 | 233 | 0.0055476 | 683 | 0.016262 | 1.362 | A04 | MICL0.01429014/DMN
Build-In Floor | Mini Canal | MICL.01429014/DMV | 14 | 290 | 14 | 14 | 600 | 600 | 600 | 0.014286 | 233 | 0.0055476 | 683 | 0.016262 | 1.362 | A04 | MICL0.01429014/DMV
Build-In Floor | Mini Canal | MICL.01429014/DNA | 14 | 290 | 14 | 14 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01429014/DNA
Build-In Floor | Mini Canal | MICL.01429014/DNC | 14 | 290 | 14 | 14 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01429014/DNC
Build-In Floor | Mini Canal | MICL.01429014/DON | 14 | 290 | 14 | 14 | 600 | 600 | 600 | 0.014286 | 233 | 0.0055476 | 683 | 0.016262 | 1.362 | A04 | MICL0.01429014/DON
Build-In Floor | Mini Canal | MICL.01429014/DOV | 14 | 290 | 14 | 14 | 600 | 600 | 600 | 0.014286 | 233 | 0.0055476 | 683 | 0.016262 | 1.362 | A04 | MICL0.01429014/DOV
Build-In Floor | Mini Canal | MICL.01429014/RBL | 14 | 290 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01429014/RBL
Build-In Floor | Mini Canal | MICL.01429014/RBN | 14 | 290 | 14 | 14 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01429014/RBN
Build-In Floor | Mini Canal | MICL.01429014/RBR | 14 | 290 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01429014/RBR
Build-In Floor | Mini Canal | MICL.01429014/RBV | 14 | 290 | 14 | 14 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01429014/RBV
Build-In Floor | Mini Canal | MICL.01429014/RDB | 14 | 290 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01429014/RDB
Build-In Floor | Mini Canal | MICL.01429014/RMN | 14 | 290 | 14 | 14 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01429014/RMN
Build-In Floor | Mini Canal | MICL.01429014/RMV | 14 | 290 | 14 | 14 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01429014/RMV
Build-In Floor | Mini Canal | MICL.01429014/RNA | 14 | 290 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01429014/RNA
Build-In Floor | Mini Canal | MICL.01429014/RON | 14 | 290 | 14 | 14 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01429014/RON
Build-In Floor | Mini Canal | MICL.01429014/ROV | 14 | 290 | 14 | 14 | 626 | 626 | 626 | 0.014905 | 244 | 0.0058095 | 713 | 0.016976 | 1.362 | A04 | MICL0.01429014/ROV
Build-In Floor | Mini Canal | MICL.01429014/RSS | 14 | 290 | 14 | 14 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.01429014/RSS
Build-In Floor | Mini Canal | MICL.01429014/SBL | 14 | 290 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01429014/SBL
Build-In Floor | Mini Canal | MICL.01429014/SBR | 14 | 290 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01429014/SBR
Build-In Floor | Mini Canal | MICL.01429014/SDB | 14 | 290 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01429014/SDB
Build-In Floor | Mini Canal | MICL.01429014/SNA | 14 | 290 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01429014/SNA
Build-In Floor | Mini Canal | MICL.01429014/SNC | 14 | 290 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01429014/SNC
Build-In Floor | Mini Canal | MICL.01429026/ANA | 14 | 290 | 26 | 26 | 839 | 839 | 839 | 0.019976 | 326 | 0.0077619 | 956 | 0.022762 | 1.362 | A04 | MICL0.01429026/ANA
Build-In Floor | Mini Canal | MICL.01429026/DBL | 14 | 290 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01429026/DBL
Build-In Floor | Mini Canal | MICL.01429026/DBN | 14 | 290 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 405 | 0.0096429 | 1186 | 0.028238 | 1.362 | A04 | MICL0.01429026/DBN
Build-In Floor | Mini Canal | MICL.01429026/DBR | 14 | 290 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01429026/DBR
Build-In Floor | Mini Canal | MICL.01429026/DBV | 14 | 290 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 405 | 0.0096429 | 1186 | 0.028238 | 1.362 | A04 | MICL0.01429026/DBV
Build-In Floor | Mini Canal | MICL.01429026/DDB | 14 | 290 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01429026/DDB
Build-In Floor | Mini Canal | MICL.01429026/DMN | 14 | 290 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 405 | 0.0096429 | 1186 | 0.028238 | 1.362 | A04 | MICL0.01429026/DMN
Build-In Floor | Mini Canal | MICL.01429026/DMV | 14 | 290 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 405 | 0.0096429 | 1186 | 0.028238 | 1.362 | A04 | MICL0.01429026/DMV
Build-In Floor | Mini Canal | MICL.01429026/DNA | 14 | 290 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01429026/DNA
Build-In Floor | Mini Canal | MICL.01429026/DNC | 14 | 290 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01429026/DNC
Build-In Floor | Mini Canal | MICL.01429026/DON | 14 | 290 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 405 | 0.0096429 | 1186 | 0.028238 | 1.362 | A04 | MICL0.01429026/DON
Build-In Floor | Mini Canal | MICL.01429026/DOV | 14 | 290 | 26 | 26 | 1041 | 1041 | 1041 | 0.024786 | 405 | 0.0096429 | 1186 | 0.028238 | 1.362 | A04 | MICL0.01429026/DOV
Build-In Floor | Mini Canal | MICL.01429026/PNC | 14 | 290 | 26 | 26 | 951 | 951 | 951 | 0.022643 | 370 | 0.0088095 | 1083 | 0.025786 | 1.362 | A04 | MICL0.01429026/PNC
Build-In Floor | Mini Canal | MICL.01429026/RBL | 14 | 290 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01429026/RBL
Build-In Floor | Mini Canal | MICL.01429026/RBN | 14 | 290 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01429026/RBN
Build-In Floor | Mini Canal | MICL.01429026/RBR | 14 | 290 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01429026/RBR
Build-In Floor | Mini Canal | MICL.01429026/RBV | 14 | 290 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01429026/RBV
Build-In Floor | Mini Canal | MICL.01429026/RDB | 14 | 290 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01429026/RDB
Build-In Floor | Mini Canal | MICL.01429026/RMN | 14 | 290 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01429026/RMN
Build-In Floor | Mini Canal | MICL.01429026/RMV | 14 | 290 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01429026/RMV
Build-In Floor | Mini Canal | MICL.01429026/RNA | 14 | 290 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01429026/RNA
Build-In Floor | Mini Canal | MICL.01429026/RON | 14 | 290 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01429026/RON
Build-In Floor | Mini Canal | MICL.01429026/ROV | 14 | 290 | 26 | 26 | 1085 | 1085 | 1085 | 0.025833 | 422 | 0.010048 | 1236 | 0.029429 | 1.362 | A04 | MICL0.01429026/ROV
Build-In Floor | Mini Canal | MICL.01429026/RSS | 14 | 290 | 26 | 26 | 1074 | 1074 | 1074 | 0.025571 | 418 | 0.0099524 | 1223 | 0.029119 | 1.362 | A04 | MICL0.01429026/RSS
Build-In Floor | Mini Canal | MICL.01429026/SBL | 14 | 290 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01429026/SBL
Build-In Floor | Mini Canal | MICL.01429026/SBR | 14 | 290 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01429026/SBR
Build-In Floor | Mini Canal | MICL.01429026/SDB | 14 | 290 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01429026/SDB
Build-In Floor | Mini Canal | MICL.01429026/SNA | 14 | 290 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01429026/SNA
Build-In Floor | Mini Canal | MICL.01429026/SNC | 14 | 290 | 26 | 26 | 1119 | 1119 | 1119 | 0.026643 | 435 | 0.010357 | 1275 | 0.030357 | 1.362 | A04 | MICL0.01429026/SNC
Build-In Floor | Mini Canal | MICL.01429034/ANA | 14 | 290 | 34 | 34 | 1145 | 1145 | 1145 | 0.027262 | 445 | 0.010595 | 1304 | 0.031048 | 1.362 | A04 | MICL0.01429034/ANA
Build-In Floor | Mini Canal | MICL.01429034/DBL | 14 | 290 | 34 | 34 | 1481 | 1481 | 1481 | 0.035262 | 576 | 0.013714 | 1687 | 0.040167 | 1.362 | A04 | MICL0.01429034/DBL
Build-In Floor | Mini Canal | MICL.01429034/DBN | 14 | 290 | 34 | 34 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01429034/DBN
Build-In Floor | Mini Canal | MICL.01429034/DBR | 14 | 290 | 34 | 34 | 1481 | 1481 | 1481 | 0.035262 | 576 | 0.013714 | 1687 | 0.040167 | 1.362 | A04 | MICL0.01429034/DBR
Build-In Floor | Mini Canal | MICL.01429034/DBV | 14 | 290 | 34 | 34 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01429034/DBV
Build-In Floor | Mini Canal | MICL.01429034/DDB | 14 | 290 | 34 | 34 | 1481 | 1481 | 1481 | 0.035262 | 576 | 0.013714 | 1687 | 0.040167 | 1.362 | A04 | MICL0.01429034/DDB
Build-In Floor | Mini Canal | MICL.01429034/DMN | 14 | 290 | 34 | 34 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01429034/DMN
Build-In Floor | Mini Canal | MICL.01429034/DMV | 14 | 290 | 34 | 34 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01429034/DMV
Build-In Floor | Mini Canal | MICL.01429034/DNA | 14 | 290 | 34 | 34 | 1481 | 1481 | 1481 | 0.035262 | 576 | 0.013714 | 1687 | 0.040167 | 1.362 | A04 | MICL0.01429034/DNA
Build-In Floor | Mini Canal | MICL.01429034/DNC | 14 | 290 | 34 | 34 | 1481 | 1481 | 1481 | 0.035262 | 576 | 0.013714 | 1687 | 0.040167 | 1.362 | A04 | MICL0.01429034/DNC
Build-In Floor | Mini Canal | MICL.01429034/DON | 14 | 290 | 34 | 34 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01429034/DON
Build-In Floor | Mini Canal | MICL.01429034/DOV | 14 | 290 | 34 | 34 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01429034/DOV
Build-In Floor | Mini Canal | MICL.01429034/PNC | 14 | 290 | 34 | 34 | 1298 | 1298 | 1298 | 0.030905 | 505 | 0.012024 | 1478 | 0.03519 | 1.362 | A04 | MICL0.01429034/PNC
Build-In Floor | Mini Canal | MICL.01429034/RBL | 14 | 290 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 594 | 0.014143 | 1739 | 0.041405 | 1.362 | A04 | MICL0.01429034/RBL
Build-In Floor | Mini Canal | MICL.01429034/RBN | 14 | 290 | 34 | 34 | 1481 | 1481 | 1481 | 0.035262 | 576 | 0.013714 | 1687 | 0.040167 | 1.362 | A04 | MICL0.01429034/RBN
Build-In Floor | Mini Canal | MICL.01429034/RBR | 14 | 290 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 594 | 0.014143 | 1739 | 0.041405 | 1.362 | A04 | MICL0.01429034/RBR
Build-In Floor | Mini Canal | MICL.01429034/RBV | 14 | 290 | 34 | 34 | 1481 | 1481 | 1481 | 0.035262 | 576 | 0.013714 | 1687 | 0.040167 | 1.362 | A04 | MICL0.01429034/RBV
Build-In Floor | Mini Canal | MICL.01429034/RDB | 14 | 290 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 594 | 0.014143 | 1739 | 0.041405 | 1.362 | A04 | MICL0.01429034/RDB
Build-In Floor | Mini Canal | MICL.01429034/RMN | 14 | 290 | 34 | 34 | 1481 | 1481 | 1481 | 0.035262 | 576 | 0.013714 | 1687 | 0.040167 | 1.362 | A04 | MICL0.01429034/RMN
Build-In Floor | Mini Canal | MICL.01429034/RMV | 14 | 290 | 34 | 34 | 1481 | 1481 | 1481 | 0.035262 | 576 | 0.013714 | 1687 | 0.040167 | 1.362 | A04 | MICL0.01429034/RMV
Build-In Floor | Mini Canal | MICL.01429034/RNA | 14 | 290 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 594 | 0.014143 | 1739 | 0.041405 | 1.362 | A04 | MICL0.01429034/RNA
Build-In Floor | Mini Canal | MICL.01429034/RON | 14 | 290 | 34 | 34 | 1481 | 1481 | 1481 | 0.035262 | 576 | 0.013714 | 1687 | 0.040167 | 1.362 | A04 | MICL0.01429034/RON
Build-In Floor | Mini Canal | MICL.01429034/ROV | 14 | 290 | 34 | 34 | 1481 | 1481 | 1481 | 0.035262 | 576 | 0.013714 | 1687 | 0.040167 | 1.362 | A04 | MICL0.01429034/ROV
Build-In Floor | Mini Canal | MICL.01429034/RSS | 14 | 290 | 34 | 34 | 1466 | 1466 | 1466 | 0.034905 | 570 | 0.013571 | 1670 | 0.039762 | 1.362 | A04 | MICL0.01429034/RSS
Build-In Floor | Mini Canal | MICL.01429034/SBL | 14 | 290 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 594 | 0.014143 | 1739 | 0.041405 | 1.362 | A04 | MICL0.01429034/SBL
Build-In Floor | Mini Canal | MICL.01429034/SBR | 14 | 290 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 594 | 0.014143 | 1739 | 0.041405 | 1.362 | A04 | MICL0.01429034/SBR
Build-In Floor | Mini Canal | MICL.01429034/SDB | 14 | 290 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 594 | 0.014143 | 1739 | 0.041405 | 1.362 | A04 | MICL0.01429034/SDB
Build-In Floor | Mini Canal | MICL.01429034/SNA | 14 | 290 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 594 | 0.014143 | 1739 | 0.041405 | 1.362 | A04 | MICL0.01429034/SNA
Build-In Floor | Mini Canal | MICL.01429034/SNC | 14 | 290 | 34 | 34 | 1527 | 1527 | 1527 | 0.036357 | 594 | 0.014143 | 1739 | 0.041405 | 1.362 | A04 | MICL0.01429034/SNC
Build-In Floor | Mini Canal | MICL.01429042/ANA | 14 | 290 | 42 | 42 | 1544 | 1544 | 1544 | 0.036762 | 601 | 0.01431 | 1759 | 0.041881 | 1.362 | A04 | MICL0.01429042/ANA
Build-In Floor | Mini Canal | MICL.01429042/DBL | 14 | 290 | 42 | 42 | 1996 | 1996 | 1996 | 0.047524 | 776 | 0.018476 | 2273 | 0.054119 | 1.362 | A04 | MICL0.01429042/DBL
Build-In Floor | Mini Canal | MICL.01429042/DBN | 14 | 290 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01429042/DBN
Build-In Floor | Mini Canal | MICL.01429042/DBR | 14 | 290 | 42 | 42 | 1996 | 1996 | 1996 | 0.047524 | 776 | 0.018476 | 2273 | 0.054119 | 1.362 | A04 | MICL0.01429042/DBR
Build-In Floor | Mini Canal | MICL.01429042/DBV | 14 | 290 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01429042/DBV
Build-In Floor | Mini Canal | MICL.01429042/DDB | 14 | 290 | 42 | 42 | 1996 | 1996 | 1996 | 0.047524 | 776 | 0.018476 | 2273 | 0.054119 | 1.362 | A04 | MICL0.01429042/DDB
Build-In Floor | Mini Canal | MICL.01429042/DMN | 14 | 290 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01429042/DMN
Build-In Floor | Mini Canal | MICL.01429042/DMV | 14 | 290 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01429042/DMV
Build-In Floor | Mini Canal | MICL.01429042/DNA | 14 | 290 | 42 | 42 | 1996 | 1996 | 1996 | 0.047524 | 776 | 0.018476 | 2273 | 0.054119 | 1.362 | A04 | MICL0.01429042/DNA
Build-In Floor | Mini Canal | MICL.01429042/DNC | 14 | 290 | 42 | 42 | 1996 | 1996 | 1996 | 0.047524 | 776 | 0.018476 | 2273 | 0.054119 | 1.362 | A04 | MICL0.01429042/DNC
Build-In Floor | Mini Canal | MICL.01429042/DON | 14 | 290 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01429042/DON
Build-In Floor | Mini Canal | MICL.01429042/DOV | 14 | 290 | 42 | 42 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01429042/DOV
Build-In Floor | Mini Canal | MICL.01429042/PNC | 14 | 290 | 42 | 42 | 1749 | 1749 | 1749 | 0.041643 | 680 | 0.01619 | 1992 | 0.047429 | 1.362 | A04 | MICL0.01429042/PNC
Build-In Floor | Mini Canal | MICL.01429042/RBL | 14 | 290 | 42 | 42 | 2058 | 2058 | 2058 | 0.049 | 801 | 0.019071 | 2344 | 0.05581 | 1.362 | A04 | MICL0.01429042/RBL
Build-In Floor | Mini Canal | MICL.01429042/RBN | 14 | 290 | 42 | 42 | 1996 | 1996 | 1996 | 0.047524 | 776 | 0.018476 | 2273 | 0.054119 | 1.362 | A04 | MICL0.01429042/RBN
Build-In Floor | Mini Canal | MICL.01429042/RBR | 14 | 290 | 42 | 42 | 2058 | 2058 | 2058 | 0.049 | 801 | 0.019071 | 2344 | 0.05581 | 1.362 | A04 | MICL0.01429042/RBR
Build-In Floor | Mini Canal | MICL.01429042/RBV | 14 | 290 | 42 | 42 | 1996 | 1996 | 1996 | 0.047524 | 776 | 0.018476 | 2273 | 0.054119 | 1.362 | A04 | MICL0.01429042/RBV
Build-In Floor | Mini Canal | MICL.01429042/RDB | 14 | 290 | 42 | 42 | 2058 | 2058 | 2058 | 0.049 | 801 | 0.019071 | 2344 | 0.05581 | 1.362 | A04 | MICL0.01429042/RDB
Build-In Floor | Mini Canal | MICL.01429042/RMN | 14 | 290 | 42 | 42 | 1996 | 1996 | 1996 | 0.047524 | 776 | 0.018476 | 2273 | 0.054119 | 1.362 | A04 | MICL0.01429042/RMN
Build-In Floor | Mini Canal | MICL.01429042/RMV | 14 | 290 | 42 | 42 | 1996 | 1996 | 1996 | 0.047524 | 776 | 0.018476 | 2273 | 0.054119 | 1.362 | A04 | MICL0.01429042/RMV
Build-In Floor | Mini Canal | MICL.01429042/RNA | 14 | 290 | 42 | 42 | 2058 | 2058 | 2058 | 0.049 | 801 | 0.019071 | 2344 | 0.05581 | 1.362 | A04 | MICL0.01429042/RNA
Build-In Floor | Mini Canal | MICL.01429042/RON | 14 | 290 | 42 | 42 | 1996 | 1996 | 1996 | 0.047524 | 776 | 0.018476 | 2273 | 0.054119 | 1.362 | A04 | MICL0.01429042/RON
Build-In Floor | Mini Canal | MICL.01429042/ROV | 14 | 290 | 42 | 42 | 1996 | 1996 | 1996 | 0.047524 | 776 | 0.018476 | 2273 | 0.054119 | 1.362 | A04 | MICL0.01429042/ROV
Build-In Floor | Mini Canal | MICL.01429042/RSS | 14 | 290 | 42 | 42 | 1976 | 1976 | 1976 | 0.047048 | 769 | 0.01831 | 2251 | 0.053595 | 1.362 | A04 | MICL0.01429042/RSS
Build-In Floor | Mini Canal | MICL.01429042/SBL | 14 | 290 | 42 | 42 | 2058 | 2058 | 2058 | 0.049 | 801 | 0.019071 | 2344 | 0.05581 | 1.362 | A04 | MICL0.01429042/SBL
Build-In Floor | Mini Canal | MICL.01429042/SBR | 14 | 290 | 42 | 42 | 2058 | 2058 | 2058 | 0.049 | 801 | 0.019071 | 2344 | 0.05581 | 1.362 | A04 | MICL0.01429042/SBR
Build-In Floor | Mini Canal | MICL.01429042/SDB | 14 | 290 | 42 | 42 | 2058 | 2058 | 2058 | 0.049 | 801 | 0.019071 | 2344 | 0.05581 | 1.362 | A04 | MICL0.01429042/SDB
Build-In Floor | Mini Canal | MICL.01429042/SNA | 14 | 290 | 42 | 42 | 2058 | 2058 | 2058 | 0.049 | 801 | 0.019071 | 2344 | 0.05581 | 1.362 | A04 | MICL0.01429042/SNA
Build-In Floor | Mini Canal | MICL.01429042/SNC | 14 | 290 | 42 | 42 | 2058 | 2058 | 2058 | 0.049 | 801 | 0.019071 | 2344 | 0.05581 | 1.362 | A04 | MICL0.01429042/SNC
Build-In Floor | Mini Canal | MICL.01431014/ANA | 14 | 310 | 14 | 14 | 521 | 521 | 521 | 0.012405 | 203 | 0.0048333 | 593 | 0.014119 | 1.362 | A04 | MICL0.01431014/ANA
Build-In Floor | Mini Canal | MICL.01431014/DBL | 14 | 310 | 14 | 14 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01431014/DBL
Build-In Floor | Mini Canal | MICL.01431014/DBN | 14 | 310 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01431014/DBN
Build-In Floor | Mini Canal | MICL.01431014/DBR | 14 | 310 | 14 | 14 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01431014/DBR
Build-In Floor | Mini Canal | MICL.01431014/DBV | 14 | 310 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01431014/DBV
Build-In Floor | Mini Canal | MICL.01431014/DDB | 14 | 310 | 14 | 14 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01431014/DDB
Build-In Floor | Mini Canal | MICL.01431014/DMN | 14 | 310 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01431014/DMN
Build-In Floor | Mini Canal | MICL.01431014/DMV | 14 | 310 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01431014/DMV
Build-In Floor | Mini Canal | MICL.01431014/DNA | 14 | 310 | 14 | 14 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01431014/DNA
Build-In Floor | Mini Canal | MICL.01431014/DNC | 14 | 310 | 14 | 14 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01431014/DNC
Build-In Floor | Mini Canal | MICL.01431014/DON | 14 | 310 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01431014/DON
Build-In Floor | Mini Canal | MICL.01431014/DOV | 14 | 310 | 14 | 14 | 645 | 645 | 645 | 0.015357 | 251 | 0.0059762 | 735 | 0.0175 | 1.362 | A04 | MICL0.01431014/DOV
Build-In Floor | Mini Canal | MICL.01431014/RBL | 14 | 310 | 14 | 14 | 694 | 694 | 694 | 0.016524 | 270 | 0.0064286 | 790 | 0.01881 | 1.362 | A04 | MICL0.01431014/RBL
Build-In Floor | Mini Canal | MICL.01431014/RBN | 14 | 310 | 14 | 14 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01431014/RBN
Build-In Floor | Mini Canal | MICL.01431014/RBR | 14 | 310 | 14 | 14 | 694 | 694 | 694 | 0.016524 | 270 | 0.0064286 | 790 | 0.01881 | 1.362 | A04 | MICL0.01431014/RBR
Build-In Floor | Mini Canal | MICL.01431014/RBV | 14 | 310 | 14 | 14 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01431014/RBV
Build-In Floor | Mini Canal | MICL.01431014/RDB | 14 | 310 | 14 | 14 | 694 | 694 | 694 | 0.016524 | 270 | 0.0064286 | 790 | 0.01881 | 1.362 | A04 | MICL0.01431014/RDB
Build-In Floor | Mini Canal | MICL.01431014/RMN | 14 | 310 | 14 | 14 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01431014/RMN
Build-In Floor | Mini Canal | MICL.01431014/RMV | 14 | 310 | 14 | 14 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01431014/RMV
Build-In Floor | Mini Canal | MICL.01431014/RNA | 14 | 310 | 14 | 14 | 694 | 694 | 694 | 0.016524 | 270 | 0.0064286 | 790 | 0.01881 | 1.362 | A04 | MICL0.01431014/RNA
Build-In Floor | Mini Canal | MICL.01431014/RON | 14 | 310 | 14 | 14 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01431014/RON
Build-In Floor | Mini Canal | MICL.01431014/ROV | 14 | 310 | 14 | 14 | 673 | 673 | 673 | 0.016024 | 262 | 0.0062381 | 767 | 0.018262 | 1.362 | A04 | MICL0.01431014/ROV
Build-In Floor | Mini Canal | MICL.01431014/RSS | 14 | 310 | 14 | 14 | 666 | 666 | 666 | 0.015857 | 259 | 0.0061667 | 759 | 0.018071 | 1.362 | A04 | MICL0.01431014/RSS
Build-In Floor | Mini Canal | MICL.01431014/SBL | 14 | 310 | 14 | 14 | 694 | 694 | 694 | 0.016524 | 270 | 0.0064286 | 790 | 0.01881 | 1.362 | A04 | MICL0.01431014/SBL
Build-In Floor | Mini Canal | MICL.01431014/SBR | 14 | 310 | 14 | 14 | 694 | 694 | 694 | 0.016524 | 270 | 0.0064286 | 790 | 0.01881 | 1.362 | A04 | MICL0.01431014/SBR
Build-In Floor | Mini Canal | MICL.01431014/SDB | 14 | 310 | 14 | 14 | 694 | 694 | 694 | 0.016524 | 270 | 0.0064286 | 790 | 0.01881 | 1.362 | A04 | MICL0.01431014/SDB
Build-In Floor | Mini Canal | MICL.01431014/SNA | 14 | 310 | 14 | 14 | 694 | 694 | 694 | 0.016524 | 270 | 0.0064286 | 790 | 0.01881 | 1.362 | A04 | MICL0.01431014/SNA
Build-In Floor | Mini Canal | MICL.01431014/SNC | 14 | 310 | 14 | 14 | 694 | 694 | 694 | 0.016524 | 270 | 0.0064286 | 790 | 0.01881 | 1.362 | A04 | MICL0.01431014/SNC
Build-In Floor | Mini Canal | MICL.01431026/ANA | 14 | 310 | 26 | 26 | 905 | 905 | 905 | 0.021548 | 352 | 0.008381 | 1031 | 0.024548 | 1.362 | A04 | MICL0.01431026/ANA
Build-In Floor | Mini Canal | MICL.01431026/DBL | 14 | 310 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01431026/DBL
Build-In Floor | Mini Canal | MICL.01431026/DBN | 14 | 310 | 26 | 26 | 1122 | 1122 | 1122 | 0.026714 | 436 | 0.010381 | 1278 | 0.030429 | 1.362 | A04 | MICL0.01431026/DBN
Build-In Floor | Mini Canal | MICL.01431026/DBR | 14 | 310 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01431026/DBR
Build-In Floor | Mini Canal | MICL.01431026/DBV | 14 | 310 | 26 | 26 | 1122 | 1122 | 1122 | 0.026714 | 436 | 0.010381 | 1278 | 0.030429 | 1.362 | A04 | MICL0.01431026/DBV
Build-In Floor | Mini Canal | MICL.01431026/DDB | 14 | 310 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01431026/DDB
Build-In Floor | Mini Canal | MICL.01431026/DMN | 14 | 310 | 26 | 26 | 1122 | 1122 | 1122 | 0.026714 | 436 | 0.010381 | 1278 | 0.030429 | 1.362 | A04 | MICL0.01431026/DMN
Build-In Floor | Mini Canal | MICL.01431026/DMV | 14 | 310 | 26 | 26 | 1122 | 1122 | 1122 | 0.026714 | 436 | 0.010381 | 1278 | 0.030429 | 1.362 | A04 | MICL0.01431026/DMV
Build-In Floor | Mini Canal | MICL.01431026/DNA | 14 | 310 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01431026/DNA
Build-In Floor | Mini Canal | MICL.01431026/DNC | 14 | 310 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01431026/DNC
Build-In Floor | Mini Canal | MICL.01431026/DON | 14 | 310 | 26 | 26 | 1122 | 1122 | 1122 | 0.026714 | 436 | 0.010381 | 1278 | 0.030429 | 1.362 | A04 | MICL0.01431026/DON
Build-In Floor | Mini Canal | MICL.01431026/DOV | 14 | 310 | 26 | 26 | 1122 | 1122 | 1122 | 0.026714 | 436 | 0.010381 | 1278 | 0.030429 | 1.362 | A04 | MICL0.01431026/DOV
Build-In Floor | Mini Canal | MICL.01431026/PNC | 14 | 310 | 26 | 26 | 1025 | 1025 | 1025 | 0.024405 | 399 | 0.0095 | 1167 | 0.027786 | 1.362 | A04 | MICL0.01431026/PNC
Build-In Floor | Mini Canal | MICL.01431026/RBL | 14 | 310 | 26 | 26 | 1206 | 1206 | 1206 | 0.028714 | 469 | 0.011167 | 1374 | 0.032714 | 1.362 | A04 | MICL0.01431026/RBL
Build-In Floor | Mini Canal | MICL.01431026/RBN | 14 | 310 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01431026/RBN
Build-In Floor | Mini Canal | MICL.01431026/RBR | 14 | 310 | 26 | 26 | 1206 | 1206 | 1206 | 0.028714 | 469 | 0.011167 | 1374 | 0.032714 | 1.362 | A04 | MICL0.01431026/RBR
Build-In Floor | Mini Canal | MICL.01431026/RBV | 14 | 310 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01431026/RBV
Build-In Floor | Mini Canal | MICL.01431026/RDB | 14 | 310 | 26 | 26 | 1206 | 1206 | 1206 | 0.028714 | 469 | 0.011167 | 1374 | 0.032714 | 1.362 | A04 | MICL0.01431026/RDB
Build-In Floor | Mini Canal | MICL.01431026/RMN | 14 | 310 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01431026/RMN
Build-In Floor | Mini Canal | MICL.01431026/RMV | 14 | 310 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01431026/RMV
Build-In Floor | Mini Canal | MICL.01431026/RNA | 14 | 310 | 26 | 26 | 1206 | 1206 | 1206 | 0.028714 | 469 | 0.011167 | 1374 | 0.032714 | 1.362 | A04 | MICL0.01431026/RNA
Build-In Floor | Mini Canal | MICL.01431026/RON | 14 | 310 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01431026/RON
Build-In Floor | Mini Canal | MICL.01431026/ROV | 14 | 310 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01431026/ROV
Build-In Floor | Mini Canal | MICL.01431026/RSS | 14 | 310 | 26 | 26 | 1158 | 1158 | 1158 | 0.027571 | 450 | 0.010714 | 1319 | 0.031405 | 1.362 | A04 | MICL0.01431026/RSS
Build-In Floor | Mini Canal | MICL.01431026/SBL | 14 | 310 | 26 | 26 | 1206 | 1206 | 1206 | 0.028714 | 469 | 0.011167 | 1374 | 0.032714 | 1.362 | A04 | MICL0.01431026/SBL
Build-In Floor | Mini Canal | MICL.01431026/SBR | 14 | 310 | 26 | 26 | 1206 | 1206 | 1206 | 0.028714 | 469 | 0.011167 | 1374 | 0.032714 | 1.362 | A04 | MICL0.01431026/SBR
Build-In Floor | Mini Canal | MICL.01431026/SDB | 14 | 310 | 26 | 26 | 1206 | 1206 | 1206 | 0.028714 | 469 | 0.011167 | 1374 | 0.032714 | 1.362 | A04 | MICL0.01431026/SDB
Build-In Floor | Mini Canal | MICL.01431026/SNA | 14 | 310 | 26 | 26 | 1206 | 1206 | 1206 | 0.028714 | 469 | 0.011167 | 1374 | 0.032714 | 1.362 | A04 | MICL0.01431026/SNA
Build-In Floor | Mini Canal | MICL.01431026/SNC | 14 | 310 | 26 | 26 | 1206 | 1206 | 1206 | 0.028714 | 469 | 0.011167 | 1374 | 0.032714 | 1.362 | A04 | MICL0.01431026/SNC
Build-In Floor | Mini Canal | MICL.01431034/ANA | 14 | 310 | 34 | 34 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01431034/ANA
Build-In Floor | Mini Canal | MICL.01431034/DBL | 14 | 310 | 34 | 34 | 1595 | 1595 | 1595 | 0.037976 | 620 | 0.014762 | 1817 | 0.043262 | 1.362 | A04 | MICL0.01431034/DBL
Build-In Floor | Mini Canal | MICL.01431034/DBN | 14 | 310 | 34 | 34 | 1529 | 1529 | 1529 | 0.036405 | 595 | 0.014167 | 1742 | 0.041476 | 1.362 | A04 | MICL0.01431034/DBN
Build-In Floor | Mini Canal | MICL.01431034/DBR | 14 | 310 | 34 | 34 | 1595 | 1595 | 1595 | 0.037976 | 620 | 0.014762 | 1817 | 0.043262 | 1.362 | A04 | MICL0.01431034/DBR
Build-In Floor | Mini Canal | MICL.01431034/DBV | 14 | 310 | 34 | 34 | 1529 | 1529 | 1529 | 0.036405 | 595 | 0.014167 | 1742 | 0.041476 | 1.362 | A04 | MICL0.01431034/DBV
Build-In Floor | Mini Canal | MICL.01431034/DDB | 14 | 310 | 34 | 34 | 1595 | 1595 | 1595 | 0.037976 | 620 | 0.014762 | 1817 | 0.043262 | 1.362 | A04 | MICL0.01431034/DDB
Build-In Floor | Mini Canal | MICL.01431034/DMN | 14 | 310 | 34 | 34 | 1529 | 1529 | 1529 | 0.036405 | 595 | 0.014167 | 1742 | 0.041476 | 1.362 | A04 | MICL0.01431034/DMN
Build-In Floor | Mini Canal | MICL.01431034/DMV | 14 | 310 | 34 | 34 | 1529 | 1529 | 1529 | 0.036405 | 595 | 0.014167 | 1742 | 0.041476 | 1.362 | A04 | MICL0.01431034/DMV
Build-In Floor | Mini Canal | MICL.01431034/DNA | 14 | 310 | 34 | 34 | 1595 | 1595 | 1595 | 0.037976 | 620 | 0.014762 | 1817 | 0.043262 | 1.362 | A04 | MICL0.01431034/DNA
Build-In Floor | Mini Canal | MICL.01431034/DNC | 14 | 310 | 34 | 34 | 1595 | 1595 | 1595 | 0.037976 | 620 | 0.014762 | 1817 | 0.043262 | 1.362 | A04 | MICL0.01431034/DNC
Build-In Floor | Mini Canal | MICL.01431034/DON | 14 | 310 | 34 | 34 | 1529 | 1529 | 1529 | 0.036405 | 595 | 0.014167 | 1742 | 0.041476 | 1.362 | A04 | MICL0.01431034/DON
Build-In Floor | Mini Canal | MICL.01431034/DOV | 14 | 310 | 34 | 34 | 1529 | 1529 | 1529 | 0.036405 | 595 | 0.014167 | 1742 | 0.041476 | 1.362 | A04 | MICL0.01431034/DOV
Build-In Floor | Mini Canal | MICL.01431034/PNC | 14 | 310 | 34 | 34 | 1397 | 1397 | 1397 | 0.033262 | 543 | 0.012929 | 1591 | 0.037881 | 1.362 | A04 | MICL0.01431034/PNC
Build-In Floor | Mini Canal | MICL.01431034/RBL | 14 | 310 | 34 | 34 | 1644 | 1644 | 1644 | 0.039143 | 640 | 0.015238 | 1873 | 0.044595 | 1.362 | A04 | MICL0.01431034/RBL
Build-In Floor | Mini Canal | MICL.01431034/RBN | 14 | 310 | 34 | 34 | 1595 | 1595 | 1595 | 0.037976 | 620 | 0.014762 | 1817 | 0.043262 | 1.362 | A04 | MICL0.01431034/RBN
Build-In Floor | Mini Canal | MICL.01431034/RBR | 14 | 310 | 34 | 34 | 1644 | 1644 | 1644 | 0.039143 | 640 | 0.015238 | 1873 | 0.044595 | 1.362 | A04 | MICL0.01431034/RBR
Build-In Floor | Mini Canal | MICL.01431034/RBV | 14 | 310 | 34 | 34 | 1595 | 1595 | 1595 | 0.037976 | 620 | 0.014762 | 1817 | 0.043262 | 1.362 | A04 | MICL0.01431034/RBV
Build-In Floor | Mini Canal | MICL.01431034/RDB | 14 | 310 | 34 | 34 | 1644 | 1644 | 1644 | 0.039143 | 640 | 0.015238 | 1873 | 0.044595 | 1.362 | A04 | MICL0.01431034/RDB
Build-In Floor | Mini Canal | MICL.01431034/RMN | 14 | 310 | 34 | 34 | 1595 | 1595 | 1595 | 0.037976 | 620 | 0.014762 | 1817 | 0.043262 | 1.362 | A04 | MICL0.01431034/RMN
Build-In Floor | Mini Canal | MICL.01431034/RMV | 14 | 310 | 34 | 34 | 1595 | 1595 | 1595 | 0.037976 | 620 | 0.014762 | 1817 | 0.043262 | 1.362 | A04 | MICL0.01431034/RMV
Build-In Floor | Mini Canal | MICL.01431034/RNA | 14 | 310 | 34 | 34 | 1644 | 1644 | 1644 | 0.039143 | 640 | 0.015238 | 1873 | 0.044595 | 1.362 | A04 | MICL0.01431034/RNA
Build-In Floor | Mini Canal | MICL.01431034/RON | 14 | 310 | 34 | 34 | 1595 | 1595 | 1595 | 0.037976 | 620 | 0.014762 | 1817 | 0.043262 | 1.362 | A04 | MICL0.01431034/RON
Build-In Floor | Mini Canal | MICL.01431034/ROV | 14 | 310 | 34 | 34 | 1595 | 1595 | 1595 | 0.037976 | 620 | 0.014762 | 1817 | 0.043262 | 1.362 | A04 | MICL0.01431034/ROV
Build-In Floor | Mini Canal | MICL.01431034/RSS | 14 | 310 | 34 | 34 | 1578 | 1578 | 1578 | 0.037571 | 614 | 0.014619 | 1797 | 0.042786 | 1.362 | A04 | MICL0.01431034/RSS
Build-In Floor | Mini Canal | MICL.01431034/SBL | 14 | 310 | 34 | 34 | 1644 | 1644 | 1644 | 0.039143 | 640 | 0.015238 | 1873 | 0.044595 | 1.362 | A04 | MICL0.01431034/SBL
Build-In Floor | Mini Canal | MICL.01431034/SBR | 14 | 310 | 34 | 34 | 1644 | 1644 | 1644 | 0.039143 | 640 | 0.015238 | 1873 | 0.044595 | 1.362 | A04 | MICL0.01431034/SBR
Build-In Floor | Mini Canal | MICL.01431034/SDB | 14 | 310 | 34 | 34 | 1644 | 1644 | 1644 | 0.039143 | 640 | 0.015238 | 1873 | 0.044595 | 1.362 | A04 | MICL0.01431034/SDB
Build-In Floor | Mini Canal | MICL.01431034/SNA | 14 | 310 | 34 | 34 | 1644 | 1644 | 1644 | 0.039143 | 640 | 0.015238 | 1873 | 0.044595 | 1.362 | A04 | MICL0.01431034/SNA
Build-In Floor | Mini Canal | MICL.01431034/SNC | 14 | 310 | 34 | 34 | 1644 | 1644 | 1644 | 0.039143 | 640 | 0.015238 | 1873 | 0.044595 | 1.362 | A04 | MICL0.01431034/SNC
Build-In Floor | Mini Canal | MICL.01431042/ANA | 14 | 310 | 42 | 42 | 1663 | 1663 | 1663 | 0.039595 | 647 | 0.015405 | 1894 | 0.045095 | 1.362 | A04 | MICL0.01431042/ANA
Build-In Floor | Mini Canal | MICL.01431042/DBL | 14 | 310 | 42 | 42 | 2150 | 2150 | 2150 | 0.05119 | 836 | 0.019905 | 2449 | 0.05831 | 1.362 | A04 | MICL0.01431042/DBL
Build-In Floor | Mini Canal | MICL.01431042/DBN | 14 | 310 | 42 | 42 | 2062 | 2062 | 2062 | 0.049095 | 802 | 0.019095 | 2349 | 0.055929 | 1.362 | A04 | MICL0.01431042/DBN
Build-In Floor | Mini Canal | MICL.01431042/DBR | 14 | 310 | 42 | 42 | 2150 | 2150 | 2150 | 0.05119 | 836 | 0.019905 | 2449 | 0.05831 | 1.362 | A04 | MICL0.01431042/DBR
Build-In Floor | Mini Canal | MICL.01431042/DBV | 14 | 310 | 42 | 42 | 2062 | 2062 | 2062 | 0.049095 | 802 | 0.019095 | 2349 | 0.055929 | 1.362 | A04 | MICL0.01431042/DBV
Build-In Floor | Mini Canal | MICL.01431042/DDB | 14 | 310 | 42 | 42 | 2150 | 2150 | 2150 | 0.05119 | 836 | 0.019905 | 2449 | 0.05831 | 1.362 | A04 | MICL0.01431042/DDB
Build-In Floor | Mini Canal | MICL.01431042/DMN | 14 | 310 | 42 | 42 | 2062 | 2062 | 2062 | 0.049095 | 802 | 0.019095 | 2349 | 0.055929 | 1.362 | A04 | MICL0.01431042/DMN
Build-In Floor | Mini Canal | MICL.01431042/DMV | 14 | 310 | 42 | 42 | 2062 | 2062 | 2062 | 0.049095 | 802 | 0.019095 | 2349 | 0.055929 | 1.362 | A04 | MICL0.01431042/DMV
Build-In Floor | Mini Canal | MICL.01431042/DNA | 14 | 310 | 42 | 42 | 2150 | 2150 | 2150 | 0.05119 | 836 | 0.019905 | 2449 | 0.05831 | 1.362 | A04 | MICL0.01431042/DNA
Build-In Floor | Mini Canal | MICL.01431042/DNC | 14 | 310 | 42 | 42 | 2150 | 2150 | 2150 | 0.05119 | 836 | 0.019905 | 2449 | 0.05831 | 1.362 | A04 | MICL0.01431042/DNC
Build-In Floor | Mini Canal | MICL.01431042/DON | 14 | 310 | 42 | 42 | 2062 | 2062 | 2062 | 0.049095 | 802 | 0.019095 | 2349 | 0.055929 | 1.362 | A04 | MICL0.01431042/DON
Build-In Floor | Mini Canal | MICL.01431042/DOV | 14 | 310 | 42 | 42 | 2062 | 2062 | 2062 | 0.049095 | 802 | 0.019095 | 2349 | 0.055929 | 1.362 | A04 | MICL0.01431042/DOV
Build-In Floor | Mini Canal | MICL.01431042/PNC | 14 | 310 | 42 | 42 | 1884 | 1884 | 1884 | 0.044857 | 733 | 0.017452 | 2146 | 0.051095 | 1.362 | A04 | MICL0.01431042/PNC
Build-In Floor | Mini Canal | MICL.01431042/RBL | 14 | 310 | 42 | 42 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01431042/RBL
Build-In Floor | Mini Canal | MICL.01431042/RBN | 14 | 310 | 42 | 42 | 2150 | 2150 | 2150 | 0.05119 | 836 | 0.019905 | 2449 | 0.05831 | 1.362 | A04 | MICL0.01431042/RBN
Build-In Floor | Mini Canal | MICL.01431042/RBR | 14 | 310 | 42 | 42 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01431042/RBR
Build-In Floor | Mini Canal | MICL.01431042/RBV | 14 | 310 | 42 | 42 | 2150 | 2150 | 2150 | 0.05119 | 836 | 0.019905 | 2449 | 0.05831 | 1.362 | A04 | MICL0.01431042/RBV
Build-In Floor | Mini Canal | MICL.01431042/RDB | 14 | 310 | 42 | 42 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01431042/RDB
Build-In Floor | Mini Canal | MICL.01431042/RMN | 14 | 310 | 42 | 42 | 2150 | 2150 | 2150 | 0.05119 | 836 | 0.019905 | 2449 | 0.05831 | 1.362 | A04 | MICL0.01431042/RMN
Build-In Floor | Mini Canal | MICL.01431042/RMV | 14 | 310 | 42 | 42 | 2150 | 2150 | 2150 | 0.05119 | 836 | 0.019905 | 2449 | 0.05831 | 1.362 | A04 | MICL0.01431042/RMV
Build-In Floor | Mini Canal | MICL.01431042/RNA | 14 | 310 | 42 | 42 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01431042/RNA
Build-In Floor | Mini Canal | MICL.01431042/RON | 14 | 310 | 42 | 42 | 2150 | 2150 | 2150 | 0.05119 | 836 | 0.019905 | 2449 | 0.05831 | 1.362 | A04 | MICL0.01431042/RON
Build-In Floor | Mini Canal | MICL.01431042/ROV | 14 | 310 | 42 | 42 | 2150 | 2150 | 2150 | 0.05119 | 836 | 0.019905 | 2449 | 0.05831 | 1.362 | A04 | MICL0.01431042/ROV
Build-In Floor | Mini Canal | MICL.01431042/RSS | 14 | 310 | 42 | 42 | 2128 | 2128 | 2128 | 0.050667 | 828 | 0.019714 | 2424 | 0.057714 | 1.362 | A04 | MICL0.01431042/RSS
Build-In Floor | Mini Canal | MICL.01431042/SBL | 14 | 310 | 42 | 42 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01431042/SBL
Build-In Floor | Mini Canal | MICL.01431042/SBR | 14 | 310 | 42 | 42 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01431042/SBR
Build-In Floor | Mini Canal | MICL.01431042/SDB | 14 | 310 | 42 | 42 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01431042/SDB
Build-In Floor | Mini Canal | MICL.01431042/SNA | 14 | 310 | 42 | 42 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01431042/SNA
Build-In Floor | Mini Canal | MICL.01431042/SNC | 14 | 310 | 42 | 42 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01431042/SNC
Build-In Floor | Mini Canal | MICL.01433014/ANA | 14 | 330 | 14 | 14 | 558 | 558 | 558 | 0.013286 | 217 | 0.0051667 | 636 | 0.015143 | 1.362 | A04 | MICL0.01433014/ANA
Build-In Floor | Mini Canal | MICL.01433014/DBL | 14 | 330 | 14 | 14 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.01433014/DBL
Build-In Floor | Mini Canal | MICL.01433014/DBN | 14 | 330 | 14 | 14 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01433014/DBN
Build-In Floor | Mini Canal | MICL.01433014/DBR | 14 | 330 | 14 | 14 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.01433014/DBR
Build-In Floor | Mini Canal | MICL.01433014/DBV | 14 | 330 | 14 | 14 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01433014/DBV
Build-In Floor | Mini Canal | MICL.01433014/DDB | 14 | 330 | 14 | 14 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.01433014/DDB
Build-In Floor | Mini Canal | MICL.01433014/DMN | 14 | 330 | 14 | 14 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01433014/DMN
Build-In Floor | Mini Canal | MICL.01433014/DMV | 14 | 330 | 14 | 14 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01433014/DMV
Build-In Floor | Mini Canal | MICL.01433014/DNA | 14 | 330 | 14 | 14 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.01433014/DNA
Build-In Floor | Mini Canal | MICL.01433014/DNC | 14 | 330 | 14 | 14 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.01433014/DNC
Build-In Floor | Mini Canal | MICL.01433014/DON | 14 | 330 | 14 | 14 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01433014/DON
Build-In Floor | Mini Canal | MICL.01433014/DOV | 14 | 330 | 14 | 14 | 692 | 692 | 692 | 0.016476 | 269 | 0.0064048 | 788 | 0.018762 | 1.362 | A04 | MICL0.01433014/DOV
Build-In Floor | Mini Canal | MICL.01433014/RBL | 14 | 330 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.01433014/RBL
Build-In Floor | Mini Canal | MICL.01433014/RBN | 14 | 330 | 14 | 14 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.01433014/RBN
Build-In Floor | Mini Canal | MICL.01433014/RBR | 14 | 330 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.01433014/RBR
Build-In Floor | Mini Canal | MICL.01433014/RBV | 14 | 330 | 14 | 14 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.01433014/RBV
Build-In Floor | Mini Canal | MICL.01433014/RDB | 14 | 330 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.01433014/RDB
Build-In Floor | Mini Canal | MICL.01433014/RMN | 14 | 330 | 14 | 14 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.01433014/RMN
Build-In Floor | Mini Canal | MICL.01433014/RMV | 14 | 330 | 14 | 14 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.01433014/RMV
Build-In Floor | Mini Canal | MICL.01433014/RNA | 14 | 330 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.01433014/RNA
Build-In Floor | Mini Canal | MICL.01433014/RON | 14 | 330 | 14 | 14 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.01433014/RON
Build-In Floor | Mini Canal | MICL.01433014/ROV | 14 | 330 | 14 | 14 | 722 | 722 | 722 | 0.01719 | 281 | 0.0066905 | 822 | 0.019571 | 1.362 | A04 | MICL0.01433014/ROV
Build-In Floor | Mini Canal | MICL.01433014/RSS | 14 | 330 | 14 | 14 | 714 | 714 | 714 | 0.017 | 278 | 0.006619 | 813 | 0.019357 | 1.362 | A04 | MICL0.01433014/RSS
Build-In Floor | Mini Canal | MICL.01433014/SBL | 14 | 330 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.01433014/SBL
Build-In Floor | Mini Canal | MICL.01433014/SBR | 14 | 330 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.01433014/SBR
Build-In Floor | Mini Canal | MICL.01433014/SDB | 14 | 330 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.01433014/SDB
Build-In Floor | Mini Canal | MICL.01433014/SNA | 14 | 330 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.01433014/SNA
Build-In Floor | Mini Canal | MICL.01433014/SNC | 14 | 330 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.01433014/SNC
Build-In Floor | Mini Canal | MICL.01433026/ANA | 14 | 330 | 26 | 26 | 969 | 969 | 969 | 0.023071 | 377 | 0.0089762 | 1104 | 0.026286 | 1.362 | A04 | MICL0.01433026/ANA
Build-In Floor | Mini Canal | MICL.01433026/DBL | 14 | 330 | 26 | 26 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01433026/DBL
Build-In Floor | Mini Canal | MICL.01433026/DBN | 14 | 330 | 26 | 26 | 1202 | 1202 | 1202 | 0.028619 | 468 | 0.011143 | 1369 | 0.032595 | 1.362 | A04 | MICL0.01433026/DBN
Build-In Floor | Mini Canal | MICL.01433026/DBR | 14 | 330 | 26 | 26 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01433026/DBR
Build-In Floor | Mini Canal | MICL.01433026/DBV | 14 | 330 | 26 | 26 | 1202 | 1202 | 1202 | 0.028619 | 468 | 0.011143 | 1369 | 0.032595 | 1.362 | A04 | MICL0.01433026/DBV
Build-In Floor | Mini Canal | MICL.01433026/DDB | 14 | 330 | 26 | 26 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01433026/DDB
Build-In Floor | Mini Canal | MICL.01433026/DMN | 14 | 330 | 26 | 26 | 1202 | 1202 | 1202 | 0.028619 | 468 | 0.011143 | 1369 | 0.032595 | 1.362 | A04 | MICL0.01433026/DMN
Build-In Floor | Mini Canal | MICL.01433026/DMV | 14 | 330 | 26 | 26 | 1202 | 1202 | 1202 | 0.028619 | 468 | 0.011143 | 1369 | 0.032595 | 1.362 | A04 | MICL0.01433026/DMV
Build-In Floor | Mini Canal | MICL.01433026/DNA | 14 | 330 | 26 | 26 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01433026/DNA
Build-In Floor | Mini Canal | MICL.01433026/DNC | 14 | 330 | 26 | 26 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01433026/DNC
Build-In Floor | Mini Canal | MICL.01433026/DON | 14 | 330 | 26 | 26 | 1202 | 1202 | 1202 | 0.028619 | 468 | 0.011143 | 1369 | 0.032595 | 1.362 | A04 | MICL0.01433026/DON
Build-In Floor | Mini Canal | MICL.01433026/DOV | 14 | 330 | 26 | 26 | 1202 | 1202 | 1202 | 0.028619 | 468 | 0.011143 | 1369 | 0.032595 | 1.362 | A04 | MICL0.01433026/DOV
Build-In Floor | Mini Canal | MICL.01433026/PNC | 14 | 330 | 26 | 26 | 1098 | 1098 | 1098 | 0.026143 | 427 | 0.010167 | 1251 | 0.029786 | 1.362 | A04 | MICL0.01433026/PNC
Build-In Floor | Mini Canal | MICL.01433026/RBL | 14 | 330 | 26 | 26 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01433026/RBL
Build-In Floor | Mini Canal | MICL.01433026/RBN | 14 | 330 | 26 | 26 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01433026/RBN
Build-In Floor | Mini Canal | MICL.01433026/RBR | 14 | 330 | 26 | 26 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01433026/RBR
Build-In Floor | Mini Canal | MICL.01433026/RBV | 14 | 330 | 26 | 26 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01433026/RBV
Build-In Floor | Mini Canal | MICL.01433026/RDB | 14 | 330 | 26 | 26 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01433026/RDB
Build-In Floor | Mini Canal | MICL.01433026/RMN | 14 | 330 | 26 | 26 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01433026/RMN
Build-In Floor | Mini Canal | MICL.01433026/RMV | 14 | 330 | 26 | 26 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01433026/RMV
Build-In Floor | Mini Canal | MICL.01433026/RNA | 14 | 330 | 26 | 26 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01433026/RNA
Build-In Floor | Mini Canal | MICL.01433026/RON | 14 | 330 | 26 | 26 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01433026/RON
Build-In Floor | Mini Canal | MICL.01433026/ROV | 14 | 330 | 26 | 26 | 1253 | 1253 | 1253 | 0.029833 | 487 | 0.011595 | 1427 | 0.033976 | 1.362 | A04 | MICL0.01433026/ROV
Build-In Floor | Mini Canal | MICL.01433026/RSS | 14 | 330 | 26 | 26 | 1240 | 1240 | 1240 | 0.029524 | 482 | 0.011476 | 1412 | 0.033619 | 1.362 | A04 | MICL0.01433026/RSS
Build-In Floor | Mini Canal | MICL.01433026/SBL | 14 | 330 | 26 | 26 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01433026/SBL
Build-In Floor | Mini Canal | MICL.01433026/SBR | 14 | 330 | 26 | 26 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01433026/SBR
Build-In Floor | Mini Canal | MICL.01433026/SDB | 14 | 330 | 26 | 26 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01433026/SDB
Build-In Floor | Mini Canal | MICL.01433026/SNA | 14 | 330 | 26 | 26 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01433026/SNA
Build-In Floor | Mini Canal | MICL.01433026/SNC | 14 | 330 | 26 | 26 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01433026/SNC
Build-In Floor | Mini Canal | MICL.01433034/ANA | 14 | 330 | 34 | 34 | 1322 | 1322 | 1322 | 0.031476 | 514 | 0.012238 | 1506 | 0.035857 | 1.362 | A04 | MICL0.01433034/ANA
Build-In Floor | Mini Canal | MICL.01433034/DBL | 14 | 330 | 34 | 34 | 1709 | 1709 | 1709 | 0.04069 | 665 | 0.015833 | 1947 | 0.046357 | 1.362 | A04 | MICL0.01433034/DBL
Build-In Floor | Mini Canal | MICL.01433034/DBN | 14 | 330 | 34 | 34 | 1639 | 1639 | 1639 | 0.039024 | 638 | 0.01519 | 1867 | 0.044452 | 1.362 | A04 | MICL0.01433034/DBN
Build-In Floor | Mini Canal | MICL.01433034/DBR | 14 | 330 | 34 | 34 | 1709 | 1709 | 1709 | 0.04069 | 665 | 0.015833 | 1947 | 0.046357 | 1.362 | A04 | MICL0.01433034/DBR
Build-In Floor | Mini Canal | MICL.01433034/DBV | 14 | 330 | 34 | 34 | 1639 | 1639 | 1639 | 0.039024 | 638 | 0.01519 | 1867 | 0.044452 | 1.362 | A04 | MICL0.01433034/DBV
Build-In Floor | Mini Canal | MICL.01433034/DDB | 14 | 330 | 34 | 34 | 1709 | 1709 | 1709 | 0.04069 | 665 | 0.015833 | 1947 | 0.046357 | 1.362 | A04 | MICL0.01433034/DDB
Build-In Floor | Mini Canal | MICL.01433034/DMN | 14 | 330 | 34 | 34 | 1639 | 1639 | 1639 | 0.039024 | 638 | 0.01519 | 1867 | 0.044452 | 1.362 | A04 | MICL0.01433034/DMN
Build-In Floor | Mini Canal | MICL.01433034/DMV | 14 | 330 | 34 | 34 | 1639 | 1639 | 1639 | 0.039024 | 638 | 0.01519 | 1867 | 0.044452 | 1.362 | A04 | MICL0.01433034/DMV
Build-In Floor | Mini Canal | MICL.01433034/DNA | 14 | 330 | 34 | 34 | 1709 | 1709 | 1709 | 0.04069 | 665 | 0.015833 | 1947 | 0.046357 | 1.362 | A04 | MICL0.01433034/DNA
Build-In Floor | Mini Canal | MICL.01433034/DNC | 14 | 330 | 34 | 34 | 1709 | 1709 | 1709 | 0.04069 | 665 | 0.015833 | 1947 | 0.046357 | 1.362 | A04 | MICL0.01433034/DNC
Build-In Floor | Mini Canal | MICL.01433034/DON | 14 | 330 | 34 | 34 | 1639 | 1639 | 1639 | 0.039024 | 638 | 0.01519 | 1867 | 0.044452 | 1.362 | A04 | MICL0.01433034/DON
Build-In Floor | Mini Canal | MICL.01433034/DOV | 14 | 330 | 34 | 34 | 1639 | 1639 | 1639 | 0.039024 | 638 | 0.01519 | 1867 | 0.044452 | 1.362 | A04 | MICL0.01433034/DOV
Build-In Floor | Mini Canal | MICL.01433034/PNC | 14 | 330 | 34 | 34 | 1498 | 1498 | 1498 | 0.035667 | 583 | 0.013881 | 1706 | 0.040619 | 1.362 | A04 | MICL0.01433034/PNC
Build-In Floor | Mini Canal | MICL.01433034/RBL | 14 | 330 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01433034/RBL
Build-In Floor | Mini Canal | MICL.01433034/RBN | 14 | 330 | 34 | 34 | 1709 | 1709 | 1709 | 0.04069 | 665 | 0.015833 | 1947 | 0.046357 | 1.362 | A04 | MICL0.01433034/RBN
Build-In Floor | Mini Canal | MICL.01433034/RBR | 14 | 330 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01433034/RBR
Build-In Floor | Mini Canal | MICL.01433034/RBV | 14 | 330 | 34 | 34 | 1709 | 1709 | 1709 | 0.04069 | 665 | 0.015833 | 1947 | 0.046357 | 1.362 | A04 | MICL0.01433034/RBV
Build-In Floor | Mini Canal | MICL.01433034/RDB | 14 | 330 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01433034/RDB
Build-In Floor | Mini Canal | MICL.01433034/RMN | 14 | 330 | 34 | 34 | 1709 | 1709 | 1709 | 0.04069 | 665 | 0.015833 | 1947 | 0.046357 | 1.362 | A04 | MICL0.01433034/RMN
Build-In Floor | Mini Canal | MICL.01433034/RMV | 14 | 330 | 34 | 34 | 1709 | 1709 | 1709 | 0.04069 | 665 | 0.015833 | 1947 | 0.046357 | 1.362 | A04 | MICL0.01433034/RMV
Build-In Floor | Mini Canal | MICL.01433034/RNA | 14 | 330 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01433034/RNA
Build-In Floor | Mini Canal | MICL.01433034/RON | 14 | 330 | 34 | 34 | 1709 | 1709 | 1709 | 0.04069 | 665 | 0.015833 | 1947 | 0.046357 | 1.362 | A04 | MICL0.01433034/RON
Build-In Floor | Mini Canal | MICL.01433034/ROV | 14 | 330 | 34 | 34 | 1709 | 1709 | 1709 | 0.04069 | 665 | 0.015833 | 1947 | 0.046357 | 1.362 | A04 | MICL0.01433034/ROV
Build-In Floor | Mini Canal | MICL.01433034/RSS | 14 | 330 | 34 | 34 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.01433034/RSS
Build-In Floor | Mini Canal | MICL.01433034/SBL | 14 | 330 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01433034/SBL
Build-In Floor | Mini Canal | MICL.01433034/SBR | 14 | 330 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01433034/SBR
Build-In Floor | Mini Canal | MICL.01433034/SDB | 14 | 330 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01433034/SDB
Build-In Floor | Mini Canal | MICL.01433034/SNA | 14 | 330 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01433034/SNA
Build-In Floor | Mini Canal | MICL.01433034/SNC | 14 | 330 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01433034/SNC
Build-In Floor | Mini Canal | MICL.01433042/ANA | 14 | 330 | 42 | 42 | 1781 | 1781 | 1781 | 0.042405 | 693 | 0.0165 | 2029 | 0.04831 | 1.362 | A04 | MICL0.01433042/ANA
Build-In Floor | Mini Canal | MICL.01433042/DBL | 14 | 330 | 42 | 42 | 2304 | 2304 | 2304 | 0.054857 | 896 | 0.021333 | 2624 | 0.062476 | 1.362 | A04 | MICL0.01433042/DBL
Build-In Floor | Mini Canal | MICL.01433042/DBN | 14 | 330 | 42 | 42 | 2209 | 2209 | 2209 | 0.052595 | 859 | 0.020452 | 2516 | 0.059905 | 1.362 | A04 | MICL0.01433042/DBN
Build-In Floor | Mini Canal | MICL.01433042/DBR | 14 | 330 | 42 | 42 | 2304 | 2304 | 2304 | 0.054857 | 896 | 0.021333 | 2624 | 0.062476 | 1.362 | A04 | MICL0.01433042/DBR
Build-In Floor | Mini Canal | MICL.01433042/DBV | 14 | 330 | 42 | 42 | 2209 | 2209 | 2209 | 0.052595 | 859 | 0.020452 | 2516 | 0.059905 | 1.362 | A04 | MICL0.01433042/DBV
Build-In Floor | Mini Canal | MICL.01433042/DDB | 14 | 330 | 42 | 42 | 2304 | 2304 | 2304 | 0.054857 | 896 | 0.021333 | 2624 | 0.062476 | 1.362 | A04 | MICL0.01433042/DDB
Build-In Floor | Mini Canal | MICL.01433042/DMN | 14 | 330 | 42 | 42 | 2209 | 2209 | 2209 | 0.052595 | 859 | 0.020452 | 2516 | 0.059905 | 1.362 | A04 | MICL0.01433042/DMN
Build-In Floor | Mini Canal | MICL.01433042/DMV | 14 | 330 | 42 | 42 | 2209 | 2209 | 2209 | 0.052595 | 859 | 0.020452 | 2516 | 0.059905 | 1.362 | A04 | MICL0.01433042/DMV
Build-In Floor | Mini Canal | MICL.01433042/DNA | 14 | 330 | 42 | 42 | 2304 | 2304 | 2304 | 0.054857 | 896 | 0.021333 | 2624 | 0.062476 | 1.362 | A04 | MICL0.01433042/DNA
Build-In Floor | Mini Canal | MICL.01433042/DNC | 14 | 330 | 42 | 42 | 2304 | 2304 | 2304 | 0.054857 | 896 | 0.021333 | 2624 | 0.062476 | 1.362 | A04 | MICL0.01433042/DNC
Build-In Floor | Mini Canal | MICL.01433042/DON | 14 | 330 | 42 | 42 | 2209 | 2209 | 2209 | 0.052595 | 859 | 0.020452 | 2516 | 0.059905 | 1.362 | A04 | MICL0.01433042/DON
Build-In Floor | Mini Canal | MICL.01433042/DOV | 14 | 330 | 42 | 42 | 2209 | 2209 | 2209 | 0.052595 | 859 | 0.020452 | 2516 | 0.059905 | 1.362 | A04 | MICL0.01433042/DOV
Build-In Floor | Mini Canal | MICL.01433042/PNC | 14 | 330 | 42 | 42 | 2019 | 2019 | 2019 | 0.048071 | 785 | 0.01869 | 2300 | 0.054762 | 1.362 | A04 | MICL0.01433042/PNC
Build-In Floor | Mini Canal | MICL.01433042/RBL | 14 | 330 | 42 | 42 | 2375 | 2375 | 2375 | 0.056548 | 924 | 0.022 | 2705 | 0.064405 | 1.362 | A04 | MICL0.01433042/RBL
Build-In Floor | Mini Canal | MICL.01433042/RBN | 14 | 330 | 42 | 42 | 2304 | 2304 | 2304 | 0.054857 | 896 | 0.021333 | 2624 | 0.062476 | 1.362 | A04 | MICL0.01433042/RBN
Build-In Floor | Mini Canal | MICL.01433042/RBR | 14 | 330 | 42 | 42 | 2375 | 2375 | 2375 | 0.056548 | 924 | 0.022 | 2705 | 0.064405 | 1.362 | A04 | MICL0.01433042/RBR
Build-In Floor | Mini Canal | MICL.01433042/RBV | 14 | 330 | 42 | 42 | 2304 | 2304 | 2304 | 0.054857 | 896 | 0.021333 | 2624 | 0.062476 | 1.362 | A04 | MICL0.01433042/RBV
Build-In Floor | Mini Canal | MICL.01433042/RDB | 14 | 330 | 42 | 42 | 2375 | 2375 | 2375 | 0.056548 | 924 | 0.022 | 2705 | 0.064405 | 1.362 | A04 | MICL0.01433042/RDB
Build-In Floor | Mini Canal | MICL.01433042/RMN | 14 | 330 | 42 | 42 | 2304 | 2304 | 2304 | 0.054857 | 896 | 0.021333 | 2624 | 0.062476 | 1.362 | A04 | MICL0.01433042/RMN
Build-In Floor | Mini Canal | MICL.01433042/RMV | 14 | 330 | 42 | 42 | 2304 | 2304 | 2304 | 0.054857 | 896 | 0.021333 | 2624 | 0.062476 | 1.362 | A04 | MICL0.01433042/RMV
Build-In Floor | Mini Canal | MICL.01433042/RNA | 14 | 330 | 42 | 42 | 2375 | 2375 | 2375 | 0.056548 | 924 | 0.022 | 2705 | 0.064405 | 1.362 | A04 | MICL0.01433042/RNA
Build-In Floor | Mini Canal | MICL.01433042/RON | 14 | 330 | 42 | 42 | 2304 | 2304 | 2304 | 0.054857 | 896 | 0.021333 | 2624 | 0.062476 | 1.362 | A04 | MICL0.01433042/RON
Build-In Floor | Mini Canal | MICL.01433042/ROV | 14 | 330 | 42 | 42 | 2304 | 2304 | 2304 | 0.054857 | 896 | 0.021333 | 2624 | 0.062476 | 1.362 | A04 | MICL0.01433042/ROV
Build-In Floor | Mini Canal | MICL.01433042/RSS | 14 | 330 | 42 | 42 | 2280 | 2280 | 2280 | 0.054286 | 887 | 0.021119 | 2597 | 0.061833 | 1.362 | A04 | MICL0.01433042/RSS
Build-In Floor | Mini Canal | MICL.01433042/SBL | 14 | 330 | 42 | 42 | 2375 | 2375 | 2375 | 0.056548 | 924 | 0.022 | 2705 | 0.064405 | 1.362 | A04 | MICL0.01433042/SBL
Build-In Floor | Mini Canal | MICL.01433042/SBR | 14 | 330 | 42 | 42 | 2375 | 2375 | 2375 | 0.056548 | 924 | 0.022 | 2705 | 0.064405 | 1.362 | A04 | MICL0.01433042/SBR
Build-In Floor | Mini Canal | MICL.01433042/SDB | 14 | 330 | 42 | 42 | 2375 | 2375 | 2375 | 0.056548 | 924 | 0.022 | 2705 | 0.064405 | 1.362 | A04 | MICL0.01433042/SDB
Build-In Floor | Mini Canal | MICL.01433042/SNA | 14 | 330 | 42 | 42 | 2375 | 2375 | 2375 | 0.056548 | 924 | 0.022 | 2705 | 0.064405 | 1.362 | A04 | MICL0.01433042/SNA
Build-In Floor | Mini Canal | MICL.01433042/SNC | 14 | 330 | 42 | 42 | 2375 | 2375 | 2375 | 0.056548 | 924 | 0.022 | 2705 | 0.064405 | 1.362 | A04 | MICL0.01433042/SNC
Build-In Floor | Mini Canal | MICL.01435014/ANA | 14 | 350 | 14 | 14 | 596 | 596 | 596 | 0.01419 | 232 | 0.0055238 | 679 | 0.016167 | 1.362 | A04 | MICL0.01435014/ANA
Build-In Floor | Mini Canal | MICL.01435014/DBL | 14 | 350 | 14 | 14 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01435014/DBL
Build-In Floor | Mini Canal | MICL.01435014/DBN | 14 | 350 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.01435014/DBN
Build-In Floor | Mini Canal | MICL.01435014/DBR | 14 | 350 | 14 | 14 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01435014/DBR
Build-In Floor | Mini Canal | MICL.01435014/DBV | 14 | 350 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.01435014/DBV
Build-In Floor | Mini Canal | MICL.01435014/DDB | 14 | 350 | 14 | 14 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01435014/DDB
Build-In Floor | Mini Canal | MICL.01435014/DMN | 14 | 350 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.01435014/DMN
Build-In Floor | Mini Canal | MICL.01435014/DMV | 14 | 350 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.01435014/DMV
Build-In Floor | Mini Canal | MICL.01435014/DNA | 14 | 350 | 14 | 14 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01435014/DNA
Build-In Floor | Mini Canal | MICL.01435014/DNC | 14 | 350 | 14 | 14 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01435014/DNC
Build-In Floor | Mini Canal | MICL.01435014/DON | 14 | 350 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.01435014/DON
Build-In Floor | Mini Canal | MICL.01435014/DOV | 14 | 350 | 14 | 14 | 738 | 738 | 738 | 0.017571 | 287 | 0.0068333 | 841 | 0.020024 | 1.362 | A04 | MICL0.01435014/DOV
Build-In Floor | Mini Canal | MICL.01435014/RBL | 14 | 350 | 14 | 14 | 794 | 794 | 794 | 0.018905 | 309 | 0.0073571 | 904 | 0.021524 | 1.362 | A04 | MICL0.01435014/RBL
Build-In Floor | Mini Canal | MICL.01435014/RBN | 14 | 350 | 14 | 14 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01435014/RBN
Build-In Floor | Mini Canal | MICL.01435014/RBR | 14 | 350 | 14 | 14 | 794 | 794 | 794 | 0.018905 | 309 | 0.0073571 | 904 | 0.021524 | 1.362 | A04 | MICL0.01435014/RBR
Build-In Floor | Mini Canal | MICL.01435014/RBV | 14 | 350 | 14 | 14 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01435014/RBV
Build-In Floor | Mini Canal | MICL.01435014/RDB | 14 | 350 | 14 | 14 | 794 | 794 | 794 | 0.018905 | 309 | 0.0073571 | 904 | 0.021524 | 1.362 | A04 | MICL0.01435014/RDB
Build-In Floor | Mini Canal | MICL.01435014/RMN | 14 | 350 | 14 | 14 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01435014/RMN
Build-In Floor | Mini Canal | MICL.01435014/RMV | 14 | 350 | 14 | 14 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01435014/RMV
Build-In Floor | Mini Canal | MICL.01435014/RNA | 14 | 350 | 14 | 14 | 794 | 794 | 794 | 0.018905 | 309 | 0.0073571 | 904 | 0.021524 | 1.362 | A04 | MICL0.01435014/RNA
Build-In Floor | Mini Canal | MICL.01435014/RON | 14 | 350 | 14 | 14 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01435014/RON
Build-In Floor | Mini Canal | MICL.01435014/ROV | 14 | 350 | 14 | 14 | 770 | 770 | 770 | 0.018333 | 300 | 0.0071429 | 877 | 0.020881 | 1.362 | A04 | MICL0.01435014/ROV
Build-In Floor | Mini Canal | MICL.01435014/RSS | 14 | 350 | 14 | 14 | 762 | 762 | 762 | 0.018143 | 296 | 0.0070476 | 868 | 0.020667 | 1.362 | A04 | MICL0.01435014/RSS
Build-In Floor | Mini Canal | MICL.01435014/SBL | 14 | 350 | 14 | 14 | 794 | 794 | 794 | 0.018905 | 309 | 0.0073571 | 904 | 0.021524 | 1.362 | A04 | MICL0.01435014/SBL
Build-In Floor | Mini Canal | MICL.01435014/SBR | 14 | 350 | 14 | 14 | 794 | 794 | 794 | 0.018905 | 309 | 0.0073571 | 904 | 0.021524 | 1.362 | A04 | MICL0.01435014/SBR
Build-In Floor | Mini Canal | MICL.01435014/SDB | 14 | 350 | 14 | 14 | 794 | 794 | 794 | 0.018905 | 309 | 0.0073571 | 904 | 0.021524 | 1.362 | A04 | MICL0.01435014/SDB
Build-In Floor | Mini Canal | MICL.01435014/SNA | 14 | 350 | 14 | 14 | 794 | 794 | 794 | 0.018905 | 309 | 0.0073571 | 904 | 0.021524 | 1.362 | A04 | MICL0.01435014/SNA
Build-In Floor | Mini Canal | MICL.01435014/SNC | 14 | 350 | 14 | 14 | 794 | 794 | 794 | 0.018905 | 309 | 0.0073571 | 904 | 0.021524 | 1.362 | A04 | MICL0.01435014/SNC
Build-In Floor | Mini Canal | MICL.01435026/ANA | 14 | 350 | 26 | 26 | 1033 | 1033 | 1033 | 0.024595 | 402 | 0.0095714 | 1177 | 0.028024 | 1.362 | A04 | MICL0.01435026/ANA
Build-In Floor | Mini Canal | MICL.01435026/DBL | 14 | 350 | 26 | 26 | 1336 | 1336 | 1336 | 0.03181 | 520 | 0.012381 | 1522 | 0.036238 | 1.362 | A04 | MICL0.01435026/DBL
Build-In Floor | Mini Canal | MICL.01435026/DBN | 14 | 350 | 26 | 26 | 1281 | 1281 | 1281 | 0.0305 | 498 | 0.011857 | 1459 | 0.034738 | 1.362 | A04 | MICL0.01435026/DBN
Build-In Floor | Mini Canal | MICL.01435026/DBR | 14 | 350 | 26 | 26 | 1336 | 1336 | 1336 | 0.03181 | 520 | 0.012381 | 1522 | 0.036238 | 1.362 | A04 | MICL0.01435026/DBR
Build-In Floor | Mini Canal | MICL.01435026/DBV | 14 | 350 | 26 | 26 | 1281 | 1281 | 1281 | 0.0305 | 498 | 0.011857 | 1459 | 0.034738 | 1.362 | A04 | MICL0.01435026/DBV
Build-In Floor | Mini Canal | MICL.01435026/DDB | 14 | 350 | 26 | 26 | 1336 | 1336 | 1336 | 0.03181 | 520 | 0.012381 | 1522 | 0.036238 | 1.362 | A04 | MICL0.01435026/DDB
Build-In Floor | Mini Canal | MICL.01435026/DMN | 14 | 350 | 26 | 26 | 1281 | 1281 | 1281 | 0.0305 | 498 | 0.011857 | 1459 | 0.034738 | 1.362 | A04 | MICL0.01435026/DMN
Build-In Floor | Mini Canal | MICL.01435026/DMV | 14 | 350 | 26 | 26 | 1281 | 1281 | 1281 | 0.0305 | 498 | 0.011857 | 1459 | 0.034738 | 1.362 | A04 | MICL0.01435026/DMV
Build-In Floor | Mini Canal | MICL.01435026/DNA | 14 | 350 | 26 | 26 | 1336 | 1336 | 1336 | 0.03181 | 520 | 0.012381 | 1522 | 0.036238 | 1.362 | A04 | MICL0.01435026/DNA
Build-In Floor | Mini Canal | MICL.01435026/DNC | 14 | 350 | 26 | 26 | 1336 | 1336 | 1336 | 0.03181 | 520 | 0.012381 | 1522 | 0.036238 | 1.362 | A04 | MICL0.01435026/DNC
Build-In Floor | Mini Canal | MICL.01435026/DON | 14 | 350 | 26 | 26 | 1281 | 1281 | 1281 | 0.0305 | 498 | 0.011857 | 1459 | 0.034738 | 1.362 | A04 | MICL0.01435026/DON
Build-In Floor | Mini Canal | MICL.01435026/DOV | 14 | 350 | 26 | 26 | 1281 | 1281 | 1281 | 0.0305 | 498 | 0.011857 | 1459 | 0.034738 | 1.362 | A04 | MICL0.01435026/DOV
Build-In Floor | Mini Canal | MICL.01435026/PNC | 14 | 350 | 26 | 26 | 1170 | 1170 | 1170 | 0.027857 | 455 | 0.010833 | 1333 | 0.031738 | 1.362 | A04 | MICL0.01435026/PNC
Build-In Floor | Mini Canal | MICL.01435026/RBL | 14 | 350 | 26 | 26 | 1377 | 1377 | 1377 | 0.032786 | 536 | 0.012762 | 1568 | 0.037333 | 1.362 | A04 | MICL0.01435026/RBL
Build-In Floor | Mini Canal | MICL.01435026/RBN | 14 | 350 | 26 | 26 | 1336 | 1336 | 1336 | 0.03181 | 520 | 0.012381 | 1522 | 0.036238 | 1.362 | A04 | MICL0.01435026/RBN
Build-In Floor | Mini Canal | MICL.01435026/RBR | 14 | 350 | 26 | 26 | 1377 | 1377 | 1377 | 0.032786 | 536 | 0.012762 | 1568 | 0.037333 | 1.362 | A04 | MICL0.01435026/RBR
Build-In Floor | Mini Canal | MICL.01435026/RBV | 14 | 350 | 26 | 26 | 1336 | 1336 | 1336 | 0.03181 | 520 | 0.012381 | 1522 | 0.036238 | 1.362 | A04 | MICL0.01435026/RBV
Build-In Floor | Mini Canal | MICL.01435026/RDB | 14 | 350 | 26 | 26 | 1377 | 1377 | 1377 | 0.032786 | 536 | 0.012762 | 1568 | 0.037333 | 1.362 | A04 | MICL0.01435026/RDB
Build-In Floor | Mini Canal | MICL.01435026/RMN | 14 | 350 | 26 | 26 | 1336 | 1336 | 1336 | 0.03181 | 520 | 0.012381 | 1522 | 0.036238 | 1.362 | A04 | MICL0.01435026/RMN
Build-In Floor | Mini Canal | MICL.01435026/RMV | 14 | 350 | 26 | 26 | 1336 | 1336 | 1336 | 0.03181 | 520 | 0.012381 | 1522 | 0.036238 | 1.362 | A04 | MICL0.01435026/RMV
Build-In Floor | Mini Canal | MICL.01435026/RNA | 14 | 350 | 26 | 26 | 1377 | 1377 | 1377 | 0.032786 | 536 | 0.012762 | 1568 | 0.037333 | 1.362 | A04 | MICL0.01435026/RNA
Build-In Floor | Mini Canal | MICL.01435026/RON | 14 | 350 | 26 | 26 | 1336 | 1336 | 1336 | 0.03181 | 520 | 0.012381 | 1522 | 0.036238 | 1.362 | A04 | MICL0.01435026/RON
Build-In Floor | Mini Canal | MICL.01435026/ROV | 14 | 350 | 26 | 26 | 1336 | 1336 | 1336 | 0.03181 | 520 | 0.012381 | 1522 | 0.036238 | 1.362 | A04 | MICL0.01435026/ROV
Build-In Floor | Mini Canal | MICL.01435026/RSS | 14 | 350 | 26 | 26 | 1322 | 1322 | 1322 | 0.031476 | 514 | 0.012238 | 1506 | 0.035857 | 1.362 | A04 | MICL0.01435026/RSS
Build-In Floor | Mini Canal | MICL.01435026/SBL | 14 | 350 | 26 | 26 | 1377 | 1377 | 1377 | 0.032786 | 536 | 0.012762 | 1568 | 0.037333 | 1.362 | A04 | MICL0.01435026/SBL
Build-In Floor | Mini Canal | MICL.01435026/SBR | 14 | 350 | 26 | 26 | 1377 | 1377 | 1377 | 0.032786 | 536 | 0.012762 | 1568 | 0.037333 | 1.362 | A04 | MICL0.01435026/SBR
Build-In Floor | Mini Canal | MICL.01435026/SDB | 14 | 350 | 26 | 26 | 1377 | 1377 | 1377 | 0.032786 | 536 | 0.012762 | 1568 | 0.037333 | 1.362 | A04 | MICL0.01435026/SDB
Build-In Floor | Mini Canal | MICL.01435026/SNA | 14 | 350 | 26 | 26 | 1377 | 1377 | 1377 | 0.032786 | 536 | 0.012762 | 1568 | 0.037333 | 1.362 | A04 | MICL0.01435026/SNA
Build-In Floor | Mini Canal | MICL.01435026/SNC | 14 | 350 | 26 | 26 | 1377 | 1377 | 1377 | 0.032786 | 536 | 0.012762 | 1568 | 0.037333 | 1.362 | A04 | MICL0.01435026/SNC
Build-In Floor | Mini Canal | MICL.01435034/ANA | 14 | 350 | 34 | 34 | 1410 | 1410 | 1410 | 0.033571 | 548 | 0.013048 | 1606 | 0.038238 | 1.362 | A04 | MICL0.01435034/ANA
Build-In Floor | Mini Canal | MICL.01435034/DBL | 14 | 350 | 34 | 34 | 1824 | 1824 | 1824 | 0.043429 | 710 | 0.016905 | 2078 | 0.049476 | 1.362 | A04 | MICL0.01435034/DBL
Build-In Floor | Mini Canal | MICL.01435034/DBN | 14 | 350 | 34 | 34 | 1748 | 1748 | 1748 | 0.041619 | 680 | 0.01619 | 1991 | 0.047405 | 1.362 | A04 | MICL0.01435034/DBN
Build-In Floor | Mini Canal | MICL.01435034/DBR | 14 | 350 | 34 | 34 | 1824 | 1824 | 1824 | 0.043429 | 710 | 0.016905 | 2078 | 0.049476 | 1.362 | A04 | MICL0.01435034/DBR
Build-In Floor | Mini Canal | MICL.01435034/DBV | 14 | 350 | 34 | 34 | 1748 | 1748 | 1748 | 0.041619 | 680 | 0.01619 | 1991 | 0.047405 | 1.362 | A04 | MICL0.01435034/DBV
Build-In Floor | Mini Canal | MICL.01435034/DDB | 14 | 350 | 34 | 34 | 1824 | 1824 | 1824 | 0.043429 | 710 | 0.016905 | 2078 | 0.049476 | 1.362 | A04 | MICL0.01435034/DDB
Build-In Floor | Mini Canal | MICL.01435034/DMN | 14 | 350 | 34 | 34 | 1748 | 1748 | 1748 | 0.041619 | 680 | 0.01619 | 1991 | 0.047405 | 1.362 | A04 | MICL0.01435034/DMN
Build-In Floor | Mini Canal | MICL.01435034/DMV | 14 | 350 | 34 | 34 | 1748 | 1748 | 1748 | 0.041619 | 680 | 0.01619 | 1991 | 0.047405 | 1.362 | A04 | MICL0.01435034/DMV
Build-In Floor | Mini Canal | MICL.01435034/DNA | 14 | 350 | 34 | 34 | 1824 | 1824 | 1824 | 0.043429 | 710 | 0.016905 | 2078 | 0.049476 | 1.362 | A04 | MICL0.01435034/DNA
Build-In Floor | Mini Canal | MICL.01435034/DNC | 14 | 350 | 34 | 34 | 1824 | 1824 | 1824 | 0.043429 | 710 | 0.016905 | 2078 | 0.049476 | 1.362 | A04 | MICL0.01435034/DNC
Build-In Floor | Mini Canal | MICL.01435034/DON | 14 | 350 | 34 | 34 | 1748 | 1748 | 1748 | 0.041619 | 680 | 0.01619 | 1991 | 0.047405 | 1.362 | A04 | MICL0.01435034/DON
Build-In Floor | Mini Canal | MICL.01435034/DOV | 14 | 350 | 34 | 34 | 1748 | 1748 | 1748 | 0.041619 | 680 | 0.01619 | 1991 | 0.047405 | 1.362 | A04 | MICL0.01435034/DOV
Build-In Floor | Mini Canal | MICL.01435034/PNC | 14 | 350 | 34 | 34 | 1598 | 1598 | 1598 | 0.038048 | 622 | 0.01481 | 1820 | 0.043333 | 1.362 | A04 | MICL0.01435034/PNC
Build-In Floor | Mini Canal | MICL.01435034/RBL | 14 | 350 | 34 | 34 | 1880 | 1880 | 1880 | 0.044762 | 731 | 0.017405 | 2141 | 0.050976 | 1.362 | A04 | MICL0.01435034/RBL
Build-In Floor | Mini Canal | MICL.01435034/RBN | 14 | 350 | 34 | 34 | 1824 | 1824 | 1824 | 0.043429 | 710 | 0.016905 | 2078 | 0.049476 | 1.362 | A04 | MICL0.01435034/RBN
Build-In Floor | Mini Canal | MICL.01435034/RBR | 14 | 350 | 34 | 34 | 1880 | 1880 | 1880 | 0.044762 | 731 | 0.017405 | 2141 | 0.050976 | 1.362 | A04 | MICL0.01435034/RBR
Build-In Floor | Mini Canal | MICL.01435034/RBV | 14 | 350 | 34 | 34 | 1824 | 1824 | 1824 | 0.043429 | 710 | 0.016905 | 2078 | 0.049476 | 1.362 | A04 | MICL0.01435034/RBV
Build-In Floor | Mini Canal | MICL.01435034/RDB | 14 | 350 | 34 | 34 | 1880 | 1880 | 1880 | 0.044762 | 731 | 0.017405 | 2141 | 0.050976 | 1.362 | A04 | MICL0.01435034/RDB
Build-In Floor | Mini Canal | MICL.01435034/RMN | 14 | 350 | 34 | 34 | 1824 | 1824 | 1824 | 0.043429 | 710 | 0.016905 | 2078 | 0.049476 | 1.362 | A04 | MICL0.01435034/RMN
Build-In Floor | Mini Canal | MICL.01435034/RMV | 14 | 350 | 34 | 34 | 1824 | 1824 | 1824 | 0.043429 | 710 | 0.016905 | 2078 | 0.049476 | 1.362 | A04 | MICL0.01435034/RMV
Build-In Floor | Mini Canal | MICL.01435034/RNA | 14 | 350 | 34 | 34 | 1880 | 1880 | 1880 | 0.044762 | 731 | 0.017405 | 2141 | 0.050976 | 1.362 | A04 | MICL0.01435034/RNA
Build-In Floor | Mini Canal | MICL.01435034/RON | 14 | 350 | 34 | 34 | 1824 | 1824 | 1824 | 0.043429 | 710 | 0.016905 | 2078 | 0.049476 | 1.362 | A04 | MICL0.01435034/RON
Build-In Floor | Mini Canal | MICL.01435034/ROV | 14 | 350 | 34 | 34 | 1824 | 1824 | 1824 | 0.043429 | 710 | 0.016905 | 2078 | 0.049476 | 1.362 | A04 | MICL0.01435034/ROV
Build-In Floor | Mini Canal | MICL.01435034/RSS | 14 | 350 | 34 | 34 | 1805 | 1805 | 1805 | 0.042976 | 702 | 0.016714 | 2056 | 0.048952 | 1.362 | A04 | MICL0.01435034/RSS
Build-In Floor | Mini Canal | MICL.01435034/SBL | 14 | 350 | 34 | 34 | 1880 | 1880 | 1880 | 0.044762 | 731 | 0.017405 | 2141 | 0.050976 | 1.362 | A04 | MICL0.01435034/SBL
Build-In Floor | Mini Canal | MICL.01435034/SBR | 14 | 350 | 34 | 34 | 1880 | 1880 | 1880 | 0.044762 | 731 | 0.017405 | 2141 | 0.050976 | 1.362 | A04 | MICL0.01435034/SBR
Build-In Floor | Mini Canal | MICL.01435034/SDB | 14 | 350 | 34 | 34 | 1880 | 1880 | 1880 | 0.044762 | 731 | 0.017405 | 2141 | 0.050976 | 1.362 | A04 | MICL0.01435034/SDB
Build-In Floor | Mini Canal | MICL.01435034/SNA | 14 | 350 | 34 | 34 | 1880 | 1880 | 1880 | 0.044762 | 731 | 0.017405 | 2141 | 0.050976 | 1.362 | A04 | MICL0.01435034/SNA
Build-In Floor | Mini Canal | MICL.01435034/SNC | 14 | 350 | 34 | 34 | 1880 | 1880 | 1880 | 0.044762 | 731 | 0.017405 | 2141 | 0.050976 | 1.362 | A04 | MICL0.01435034/SNC
Build-In Floor | Mini Canal | MICL.01435042/ANA | 14 | 350 | 42 | 42 | 1900 | 1900 | 1900 | 0.045238 | 739 | 0.017595 | 2164 | 0.051524 | 1.362 | A04 | MICL0.01435042/ANA
Build-In Floor | Mini Canal | MICL.01435042/DBL | 14 | 350 | 42 | 42 | 2457 | 2457 | 2457 | 0.0585 | 956 | 0.022762 | 2799 | 0.066643 | 1.362 | A04 | MICL0.01435042/DBL
Build-In Floor | Mini Canal | MICL.01435042/DBN | 14 | 350 | 42 | 42 | 2356 | 2356 | 2356 | 0.056095 | 916 | 0.02181 | 2683 | 0.063881 | 1.362 | A04 | MICL0.01435042/DBN
Build-In Floor | Mini Canal | MICL.01435042/DBR | 14 | 350 | 42 | 42 | 2457 | 2457 | 2457 | 0.0585 | 956 | 0.022762 | 2799 | 0.066643 | 1.362 | A04 | MICL0.01435042/DBR
Build-In Floor | Mini Canal | MICL.01435042/DBV | 14 | 350 | 42 | 42 | 2356 | 2356 | 2356 | 0.056095 | 916 | 0.02181 | 2683 | 0.063881 | 1.362 | A04 | MICL0.01435042/DBV
Build-In Floor | Mini Canal | MICL.01435042/DDB | 14 | 350 | 42 | 42 | 2457 | 2457 | 2457 | 0.0585 | 956 | 0.022762 | 2799 | 0.066643 | 1.362 | A04 | MICL0.01435042/DDB
Build-In Floor | Mini Canal | MICL.01435042/DMN | 14 | 350 | 42 | 42 | 2356 | 2356 | 2356 | 0.056095 | 916 | 0.02181 | 2683 | 0.063881 | 1.362 | A04 | MICL0.01435042/DMN
Build-In Floor | Mini Canal | MICL.01435042/DMV | 14 | 350 | 42 | 42 | 2356 | 2356 | 2356 | 0.056095 | 916 | 0.02181 | 2683 | 0.063881 | 1.362 | A04 | MICL0.01435042/DMV
Build-In Floor | Mini Canal | MICL.01435042/DNA | 14 | 350 | 42 | 42 | 2457 | 2457 | 2457 | 0.0585 | 956 | 0.022762 | 2799 | 0.066643 | 1.362 | A04 | MICL0.01435042/DNA
Build-In Floor | Mini Canal | MICL.01435042/DNC | 14 | 350 | 42 | 42 | 2457 | 2457 | 2457 | 0.0585 | 956 | 0.022762 | 2799 | 0.066643 | 1.362 | A04 | MICL0.01435042/DNC
Build-In Floor | Mini Canal | MICL.01435042/DON | 14 | 350 | 42 | 42 | 2356 | 2356 | 2356 | 0.056095 | 916 | 0.02181 | 2683 | 0.063881 | 1.362 | A04 | MICL0.01435042/DON
Build-In Floor | Mini Canal | MICL.01435042/DOV | 14 | 350 | 42 | 42 | 2356 | 2356 | 2356 | 0.056095 | 916 | 0.02181 | 2683 | 0.063881 | 1.362 | A04 | MICL0.01435042/DOV
Build-In Floor | Mini Canal | MICL.01435042/PNC | 14 | 350 | 42 | 42 | 2153 | 2153 | 2153 | 0.051262 | 838 | 0.019952 | 2452 | 0.058381 | 1.362 | A04 | MICL0.01435042/PNC
Build-In Floor | Mini Canal | MICL.01435042/RBL | 14 | 350 | 42 | 42 | 2533 | 2533 | 2533 | 0.06031 | 985 | 0.023452 | 2885 | 0.06869 | 1.362 | A04 | MICL0.01435042/RBL
Build-In Floor | Mini Canal | MICL.01435042/RBN | 14 | 350 | 42 | 42 | 2457 | 2457 | 2457 | 0.0585 | 956 | 0.022762 | 2799 | 0.066643 | 1.362 | A04 | MICL0.01435042/RBN
Build-In Floor | Mini Canal | MICL.01435042/RBR | 14 | 350 | 42 | 42 | 2533 | 2533 | 2533 | 0.06031 | 985 | 0.023452 | 2885 | 0.06869 | 1.362 | A04 | MICL0.01435042/RBR
Build-In Floor | Mini Canal | MICL.01435042/RBV | 14 | 350 | 42 | 42 | 2457 | 2457 | 2457 | 0.0585 | 956 | 0.022762 | 2799 | 0.066643 | 1.362 | A04 | MICL0.01435042/RBV
Build-In Floor | Mini Canal | MICL.01435042/RDB | 14 | 350 | 42 | 42 | 2533 | 2533 | 2533 | 0.06031 | 985 | 0.023452 | 2885 | 0.06869 | 1.362 | A04 | MICL0.01435042/RDB
Build-In Floor | Mini Canal | MICL.01435042/RMN | 14 | 350 | 42 | 42 | 2457 | 2457 | 2457 | 0.0585 | 956 | 0.022762 | 2799 | 0.066643 | 1.362 | A04 | MICL0.01435042/RMN
Build-In Floor | Mini Canal | MICL.01435042/RMV | 14 | 350 | 42 | 42 | 2457 | 2457 | 2457 | 0.0585 | 956 | 0.022762 | 2799 | 0.066643 | 1.362 | A04 | MICL0.01435042/RMV
Build-In Floor | Mini Canal | MICL.01435042/RNA | 14 | 350 | 42 | 42 | 2533 | 2533 | 2533 | 0.06031 | 985 | 0.023452 | 2885 | 0.06869 | 1.362 | A04 | MICL0.01435042/RNA
Build-In Floor | Mini Canal | MICL.01435042/RON | 14 | 350 | 42 | 42 | 2457 | 2457 | 2457 | 0.0585 | 956 | 0.022762 | 2799 | 0.066643 | 1.362 | A04 | MICL0.01435042/RON
Build-In Floor | Mini Canal | MICL.01435042/ROV | 14 | 350 | 42 | 42 | 2457 | 2457 | 2457 | 0.0585 | 956 | 0.022762 | 2799 | 0.066643 | 1.362 | A04 | MICL0.01435042/ROV
Build-In Floor | Mini Canal | MICL.01435042/RSS | 14 | 350 | 42 | 42 | 2432 | 2432 | 2432 | 0.057905 | 946 | 0.022524 | 2770 | 0.065952 | 1.362 | A04 | MICL0.01435042/RSS
Build-In Floor | Mini Canal | MICL.01435042/SBL | 14 | 350 | 42 | 42 | 2533 | 2533 | 2533 | 0.06031 | 985 | 0.023452 | 2885 | 0.06869 | 1.362 | A04 | MICL0.01435042/SBL
Build-In Floor | Mini Canal | MICL.01435042/SBR | 14 | 350 | 42 | 42 | 2533 | 2533 | 2533 | 0.06031 | 985 | 0.023452 | 2885 | 0.06869 | 1.362 | A04 | MICL0.01435042/SBR
Build-In Floor | Mini Canal | MICL.01435042/SDB | 14 | 350 | 42 | 42 | 2533 | 2533 | 2533 | 0.06031 | 985 | 0.023452 | 2885 | 0.06869 | 1.362 | A04 | MICL0.01435042/SDB
Build-In Floor | Mini Canal | MICL.01435042/SNA | 14 | 350 | 42 | 42 | 2533 | 2533 | 2533 | 0.06031 | 985 | 0.023452 | 2885 | 0.06869 | 1.362 | A04 | MICL0.01435042/SNA
Build-In Floor | Mini Canal | MICL.01435042/SNC | 14 | 350 | 42 | 42 | 2533 | 2533 | 2533 | 0.06031 | 985 | 0.023452 | 2885 | 0.06869 | 1.362 | A04 | MICL0.01435042/SNC
Build-In Floor | Mini Canal | MICL.01437014/ANA | 14 | 370 | 14 | 14 | 632 | 632 | 632 | 0.015048 | 246 | 0.0058571 | 720 | 0.017143 | 1.362 | A04 | MICL0.01437014/ANA
Build-In Floor | Mini Canal | MICL.01437014/DBL | 14 | 370 | 14 | 14 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01437014/DBL
Build-In Floor | Mini Canal | MICL.01437014/DBN | 14 | 370 | 14 | 14 | 784 | 784 | 784 | 0.018667 | 305 | 0.0072619 | 893 | 0.021262 | 1.362 | A04 | MICL0.01437014/DBN
Build-In Floor | Mini Canal | MICL.01437014/DBR | 14 | 370 | 14 | 14 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01437014/DBR
Build-In Floor | Mini Canal | MICL.01437014/DBV | 14 | 370 | 14 | 14 | 784 | 784 | 784 | 0.018667 | 305 | 0.0072619 | 893 | 0.021262 | 1.362 | A04 | MICL0.01437014/DBV
Build-In Floor | Mini Canal | MICL.01437014/DDB | 14 | 370 | 14 | 14 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01437014/DDB
Build-In Floor | Mini Canal | MICL.01437014/DMN | 14 | 370 | 14 | 14 | 784 | 784 | 784 | 0.018667 | 305 | 0.0072619 | 893 | 0.021262 | 1.362 | A04 | MICL0.01437014/DMN
Build-In Floor | Mini Canal | MICL.01437014/DMV | 14 | 370 | 14 | 14 | 784 | 784 | 784 | 0.018667 | 305 | 0.0072619 | 893 | 0.021262 | 1.362 | A04 | MICL0.01437014/DMV
Build-In Floor | Mini Canal | MICL.01437014/DNA | 14 | 370 | 14 | 14 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01437014/DNA
Build-In Floor | Mini Canal | MICL.01437014/DNC | 14 | 370 | 14 | 14 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01437014/DNC
Build-In Floor | Mini Canal | MICL.01437014/DON | 14 | 370 | 14 | 14 | 784 | 784 | 784 | 0.018667 | 305 | 0.0072619 | 893 | 0.021262 | 1.362 | A04 | MICL0.01437014/DON
Build-In Floor | Mini Canal | MICL.01437014/DOV | 14 | 370 | 14 | 14 | 784 | 784 | 784 | 0.018667 | 305 | 0.0072619 | 893 | 0.021262 | 1.362 | A04 | MICL0.01437014/DOV
Build-In Floor | Mini Canal | MICL.01437014/RBL | 14 | 370 | 14 | 14 | 843 | 843 | 843 | 0.020071 | 328 | 0.0078095 | 960 | 0.022857 | 1.362 | A04 | MICL0.01437014/RBL
Build-In Floor | Mini Canal | MICL.01437014/RBN | 14 | 370 | 14 | 14 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01437014/RBN
Build-In Floor | Mini Canal | MICL.01437014/RBR | 14 | 370 | 14 | 14 | 843 | 843 | 843 | 0.020071 | 328 | 0.0078095 | 960 | 0.022857 | 1.362 | A04 | MICL0.01437014/RBR
Build-In Floor | Mini Canal | MICL.01437014/RBV | 14 | 370 | 14 | 14 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01437014/RBV
Build-In Floor | Mini Canal | MICL.01437014/RDB | 14 | 370 | 14 | 14 | 843 | 843 | 843 | 0.020071 | 328 | 0.0078095 | 960 | 0.022857 | 1.362 | A04 | MICL0.01437014/RDB
Build-In Floor | Mini Canal | MICL.01437014/RMN | 14 | 370 | 14 | 14 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01437014/RMN
Build-In Floor | Mini Canal | MICL.01437014/RMV | 14 | 370 | 14 | 14 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01437014/RMV
Build-In Floor | Mini Canal | MICL.01437014/RNA | 14 | 370 | 14 | 14 | 843 | 843 | 843 | 0.020071 | 328 | 0.0078095 | 960 | 0.022857 | 1.362 | A04 | MICL0.01437014/RNA
Build-In Floor | Mini Canal | MICL.01437014/RON | 14 | 370 | 14 | 14 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01437014/RON
Build-In Floor | Mini Canal | MICL.01437014/ROV | 14 | 370 | 14 | 14 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01437014/ROV
Build-In Floor | Mini Canal | MICL.01437014/RSS | 14 | 370 | 14 | 14 | 809 | 809 | 809 | 0.019262 | 315 | 0.0075 | 921 | 0.021929 | 1.362 | A04 | MICL0.01437014/RSS
Build-In Floor | Mini Canal | MICL.01437014/SBL | 14 | 370 | 14 | 14 | 843 | 843 | 843 | 0.020071 | 328 | 0.0078095 | 960 | 0.022857 | 1.362 | A04 | MICL0.01437014/SBL
Build-In Floor | Mini Canal | MICL.01437014/SBR | 14 | 370 | 14 | 14 | 843 | 843 | 843 | 0.020071 | 328 | 0.0078095 | 960 | 0.022857 | 1.362 | A04 | MICL0.01437014/SBR
Build-In Floor | Mini Canal | MICL.01437014/SDB | 14 | 370 | 14 | 14 | 843 | 843 | 843 | 0.020071 | 328 | 0.0078095 | 960 | 0.022857 | 1.362 | A04 | MICL0.01437014/SDB
Build-In Floor | Mini Canal | MICL.01437014/SNA | 14 | 370 | 14 | 14 | 843 | 843 | 843 | 0.020071 | 328 | 0.0078095 | 960 | 0.022857 | 1.362 | A04 | MICL0.01437014/SNA
Build-In Floor | Mini Canal | MICL.01437014/SNC | 14 | 370 | 14 | 14 | 843 | 843 | 843 | 0.020071 | 328 | 0.0078095 | 960 | 0.022857 | 1.362 | A04 | MICL0.01437014/SNC
Build-In Floor | Mini Canal | MICL.01437026/ANA | 14 | 370 | 26 | 26 | 1098 | 1098 | 1098 | 0.026143 | 427 | 0.010167 | 1251 | 0.029786 | 1.362 | A04 | MICL0.01437026/ANA
Build-In Floor | Mini Canal | MICL.01437026/DBL | 14 | 370 | 26 | 26 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01437026/DBL
Build-In Floor | Mini Canal | MICL.01437026/DBN | 14 | 370 | 26 | 26 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01437026/DBN
Build-In Floor | Mini Canal | MICL.01437026/DBR | 14 | 370 | 26 | 26 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01437026/DBR
Build-In Floor | Mini Canal | MICL.01437026/DBV | 14 | 370 | 26 | 26 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01437026/DBV
Build-In Floor | Mini Canal | MICL.01437026/DDB | 14 | 370 | 26 | 26 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01437026/DDB
Build-In Floor | Mini Canal | MICL.01437026/DMN | 14 | 370 | 26 | 26 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01437026/DMN
Build-In Floor | Mini Canal | MICL.01437026/DMV | 14 | 370 | 26 | 26 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01437026/DMV
Build-In Floor | Mini Canal | MICL.01437026/DNA | 14 | 370 | 26 | 26 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01437026/DNA
Build-In Floor | Mini Canal | MICL.01437026/DNC | 14 | 370 | 26 | 26 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01437026/DNC
Build-In Floor | Mini Canal | MICL.01437026/DON | 14 | 370 | 26 | 26 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01437026/DON
Build-In Floor | Mini Canal | MICL.01437026/DOV | 14 | 370 | 26 | 26 | 1362 | 1362 | 1362 | 0.032429 | 530 | 0.012619 | 1551 | 0.036929 | 1.362 | A04 | MICL0.01437026/DOV
Build-In Floor | Mini Canal | MICL.01437026/PNC | 14 | 370 | 26 | 26 | 1244 | 1244 | 1244 | 0.029619 | 484 | 0.011524 | 1417 | 0.033738 | 1.362 | A04 | MICL0.01437026/PNC
Build-In Floor | Mini Canal | MICL.01437026/RBL | 14 | 370 | 26 | 26 | 1464 | 1464 | 1464 | 0.034857 | 569 | 0.013548 | 1667 | 0.03969 | 1.362 | A04 | MICL0.01437026/RBL
Build-In Floor | Mini Canal | MICL.01437026/RBN | 14 | 370 | 26 | 26 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01437026/RBN
Build-In Floor | Mini Canal | MICL.01437026/RBR | 14 | 370 | 26 | 26 | 1464 | 1464 | 1464 | 0.034857 | 569 | 0.013548 | 1667 | 0.03969 | 1.362 | A04 | MICL0.01437026/RBR
Build-In Floor | Mini Canal | MICL.01437026/RBV | 14 | 370 | 26 | 26 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01437026/RBV
Build-In Floor | Mini Canal | MICL.01437026/RDB | 14 | 370 | 26 | 26 | 1464 | 1464 | 1464 | 0.034857 | 569 | 0.013548 | 1667 | 0.03969 | 1.362 | A04 | MICL0.01437026/RDB
Build-In Floor | Mini Canal | MICL.01437026/RMN | 14 | 370 | 26 | 26 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01437026/RMN
Build-In Floor | Mini Canal | MICL.01437026/RMV | 14 | 370 | 26 | 26 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01437026/RMV
Build-In Floor | Mini Canal | MICL.01437026/RNA | 14 | 370 | 26 | 26 | 1464 | 1464 | 1464 | 0.034857 | 569 | 0.013548 | 1667 | 0.03969 | 1.362 | A04 | MICL0.01437026/RNA
Build-In Floor | Mini Canal | MICL.01437026/RON | 14 | 370 | 26 | 26 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01437026/RON
Build-In Floor | Mini Canal | MICL.01437026/ROV | 14 | 370 | 26 | 26 | 1420 | 1420 | 1420 | 0.03381 | 552 | 0.013143 | 1617 | 0.0385 | 1.362 | A04 | MICL0.01437026/ROV
Build-In Floor | Mini Canal | MICL.01437026/RSS | 14 | 370 | 26 | 26 | 1405 | 1405 | 1405 | 0.033452 | 547 | 0.013024 | 1600 | 0.038095 | 1.362 | A04 | MICL0.01437026/RSS
Build-In Floor | Mini Canal | MICL.01437026/SBL | 14 | 370 | 26 | 26 | 1464 | 1464 | 1464 | 0.034857 | 569 | 0.013548 | 1667 | 0.03969 | 1.362 | A04 | MICL0.01437026/SBL
Build-In Floor | Mini Canal | MICL.01437026/SBR | 14 | 370 | 26 | 26 | 1464 | 1464 | 1464 | 0.034857 | 569 | 0.013548 | 1667 | 0.03969 | 1.362 | A04 | MICL0.01437026/SBR
Build-In Floor | Mini Canal | MICL.01437026/SDB | 14 | 370 | 26 | 26 | 1464 | 1464 | 1464 | 0.034857 | 569 | 0.013548 | 1667 | 0.03969 | 1.362 | A04 | MICL0.01437026/SDB
Build-In Floor | Mini Canal | MICL.01437026/SNA | 14 | 370 | 26 | 26 | 1464 | 1464 | 1464 | 0.034857 | 569 | 0.013548 | 1667 | 0.03969 | 1.362 | A04 | MICL0.01437026/SNA
Build-In Floor | Mini Canal | MICL.01437026/SNC | 14 | 370 | 26 | 26 | 1464 | 1464 | 1464 | 0.034857 | 569 | 0.013548 | 1667 | 0.03969 | 1.362 | A04 | MICL0.01437026/SNC
Build-In Floor | Mini Canal | MICL.01437034/ANA | 14 | 370 | 34 | 34 | 1498 | 1498 | 1498 | 0.035667 | 583 | 0.013881 | 1706 | 0.040619 | 1.362 | A04 | MICL0.01437034/ANA
Build-In Floor | Mini Canal | MICL.01437034/DBL | 14 | 370 | 34 | 34 | 1937 | 1937 | 1937 | 0.046119 | 753 | 0.017929 | 2206 | 0.052524 | 1.362 | A04 | MICL0.01437034/DBL
Build-In Floor | Mini Canal | MICL.01437034/DBN | 14 | 370 | 34 | 34 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01437034/DBN
Build-In Floor | Mini Canal | MICL.01437034/DBR | 14 | 370 | 34 | 34 | 1937 | 1937 | 1937 | 0.046119 | 753 | 0.017929 | 2206 | 0.052524 | 1.362 | A04 | MICL0.01437034/DBR
Build-In Floor | Mini Canal | MICL.01437034/DBV | 14 | 370 | 34 | 34 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01437034/DBV
Build-In Floor | Mini Canal | MICL.01437034/DDB | 14 | 370 | 34 | 34 | 1937 | 1937 | 1937 | 0.046119 | 753 | 0.017929 | 2206 | 0.052524 | 1.362 | A04 | MICL0.01437034/DDB
Build-In Floor | Mini Canal | MICL.01437034/DMN | 14 | 370 | 34 | 34 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01437034/DMN
Build-In Floor | Mini Canal | MICL.01437034/DMV | 14 | 370 | 34 | 34 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01437034/DMV
Build-In Floor | Mini Canal | MICL.01437034/DNA | 14 | 370 | 34 | 34 | 1937 | 1937 | 1937 | 0.046119 | 753 | 0.017929 | 2206 | 0.052524 | 1.362 | A04 | MICL0.01437034/DNA
Build-In Floor | Mini Canal | MICL.01437034/DNC | 14 | 370 | 34 | 34 | 1937 | 1937 | 1937 | 0.046119 | 753 | 0.017929 | 2206 | 0.052524 | 1.362 | A04 | MICL0.01437034/DNC
Build-In Floor | Mini Canal | MICL.01437034/DON | 14 | 370 | 34 | 34 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01437034/DON
Build-In Floor | Mini Canal | MICL.01437034/DOV | 14 | 370 | 34 | 34 | 1857 | 1857 | 1857 | 0.044214 | 722 | 0.01719 | 2115 | 0.050357 | 1.362 | A04 | MICL0.01437034/DOV
Build-In Floor | Mini Canal | MICL.01437034/PNC | 14 | 370 | 34 | 34 | 1697 | 1697 | 1697 | 0.040405 | 660 | 0.015714 | 1933 | 0.046024 | 1.362 | A04 | MICL0.01437034/PNC
Build-In Floor | Mini Canal | MICL.01437034/RBL | 14 | 370 | 34 | 34 | 1997 | 1997 | 1997 | 0.047548 | 777 | 0.0185 | 2275 | 0.054167 | 1.362 | A04 | MICL0.01437034/RBL
Build-In Floor | Mini Canal | MICL.01437034/RBN | 14 | 370 | 34 | 34 | 1937 | 1937 | 1937 | 0.046119 | 753 | 0.017929 | 2206 | 0.052524 | 1.362 | A04 | MICL0.01437034/RBN
Build-In Floor | Mini Canal | MICL.01437034/RBR | 14 | 370 | 34 | 34 | 1997 | 1997 | 1997 | 0.047548 | 777 | 0.0185 | 2275 | 0.054167 | 1.362 | A04 | MICL0.01437034/RBR
Build-In Floor | Mini Canal | MICL.01437034/RBV | 14 | 370 | 34 | 34 | 1937 | 1937 | 1937 | 0.046119 | 753 | 0.017929 | 2206 | 0.052524 | 1.362 | A04 | MICL0.01437034/RBV
Build-In Floor | Mini Canal | MICL.01437034/RDB | 14 | 370 | 34 | 34 | 1997 | 1997 | 1997 | 0.047548 | 777 | 0.0185 | 2275 | 0.054167 | 1.362 | A04 | MICL0.01437034/RDB
Build-In Floor | Mini Canal | MICL.01437034/RMN | 14 | 370 | 34 | 34 | 1937 | 1937 | 1937 | 0.046119 | 753 | 0.017929 | 2206 | 0.052524 | 1.362 | A04 | MICL0.01437034/RMN
Build-In Floor | Mini Canal | MICL.01437034/RMV | 14 | 370 | 34 | 34 | 1937 | 1937 | 1937 | 0.046119 | 753 | 0.017929 | 2206 | 0.052524 | 1.362 | A04 | MICL0.01437034/RMV
Build-In Floor | Mini Canal | MICL.01437034/RNA | 14 | 370 | 34 | 34 | 1997 | 1997 | 1997 | 0.047548 | 777 | 0.0185 | 2275 | 0.054167 | 1.362 | A04 | MICL0.01437034/RNA
Build-In Floor | Mini Canal | MICL.01437034/RON | 14 | 370 | 34 | 34 | 1937 | 1937 | 1937 | 0.046119 | 753 | 0.017929 | 2206 | 0.052524 | 1.362 | A04 | MICL0.01437034/RON
Build-In Floor | Mini Canal | MICL.01437034/ROV | 14 | 370 | 34 | 34 | 1937 | 1937 | 1937 | 0.046119 | 753 | 0.017929 | 2206 | 0.052524 | 1.362 | A04 | MICL0.01437034/ROV
Build-In Floor | Mini Canal | MICL.01437034/RSS | 14 | 370 | 34 | 34 | 1917 | 1917 | 1917 | 0.045643 | 746 | 0.017762 | 2183 | 0.051976 | 1.362 | A04 | MICL0.01437034/RSS
Build-In Floor | Mini Canal | MICL.01437034/SBL | 14 | 370 | 34 | 34 | 1997 | 1997 | 1997 | 0.047548 | 777 | 0.0185 | 2275 | 0.054167 | 1.362 | A04 | MICL0.01437034/SBL
Build-In Floor | Mini Canal | MICL.01437034/SBR | 14 | 370 | 34 | 34 | 1997 | 1997 | 1997 | 0.047548 | 777 | 0.0185 | 2275 | 0.054167 | 1.362 | A04 | MICL0.01437034/SBR
Build-In Floor | Mini Canal | MICL.01437034/SDB | 14 | 370 | 34 | 34 | 1997 | 1997 | 1997 | 0.047548 | 777 | 0.0185 | 2275 | 0.054167 | 1.362 | A04 | MICL0.01437034/SDB
Build-In Floor | Mini Canal | MICL.01437034/SNA | 14 | 370 | 34 | 34 | 1997 | 1997 | 1997 | 0.047548 | 777 | 0.0185 | 2275 | 0.054167 | 1.362 | A04 | MICL0.01437034/SNA
Build-In Floor | Mini Canal | MICL.01437034/SNC | 14 | 370 | 34 | 34 | 1997 | 1997 | 1997 | 0.047548 | 777 | 0.0185 | 2275 | 0.054167 | 1.362 | A04 | MICL0.01437034/SNC
Build-In Floor | Mini Canal | MICL.01437042/ANA | 14 | 370 | 42 | 42 | 2019 | 2019 | 2019 | 0.048071 | 785 | 0.01869 | 2300 | 0.054762 | 1.362 | A04 | MICL0.01437042/ANA
Build-In Floor | Mini Canal | MICL.01437042/DBL | 14 | 370 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01437042/DBL
Build-In Floor | Mini Canal | MICL.01437042/DBN | 14 | 370 | 42 | 42 | 2504 | 2504 | 2504 | 0.059619 | 974 | 0.02319 | 2852 | 0.067905 | 1.362 | A04 | MICL0.01437042/DBN
Build-In Floor | Mini Canal | MICL.01437042/DBR | 14 | 370 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01437042/DBR
Build-In Floor | Mini Canal | MICL.01437042/DBV | 14 | 370 | 42 | 42 | 2504 | 2504 | 2504 | 0.059619 | 974 | 0.02319 | 2852 | 0.067905 | 1.362 | A04 | MICL0.01437042/DBV
Build-In Floor | Mini Canal | MICL.01437042/DDB | 14 | 370 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01437042/DDB
Build-In Floor | Mini Canal | MICL.01437042/DMN | 14 | 370 | 42 | 42 | 2504 | 2504 | 2504 | 0.059619 | 974 | 0.02319 | 2852 | 0.067905 | 1.362 | A04 | MICL0.01437042/DMN
Build-In Floor | Mini Canal | MICL.01437042/DMV | 14 | 370 | 42 | 42 | 2504 | 2504 | 2504 | 0.059619 | 974 | 0.02319 | 2852 | 0.067905 | 1.362 | A04 | MICL0.01437042/DMV
Build-In Floor | Mini Canal | MICL.01437042/DNA | 14 | 370 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01437042/DNA
Build-In Floor | Mini Canal | MICL.01437042/DNC | 14 | 370 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01437042/DNC
Build-In Floor | Mini Canal | MICL.01437042/DON | 14 | 370 | 42 | 42 | 2504 | 2504 | 2504 | 0.059619 | 974 | 0.02319 | 2852 | 0.067905 | 1.362 | A04 | MICL0.01437042/DON
Build-In Floor | Mini Canal | MICL.01437042/DOV | 14 | 370 | 42 | 42 | 2504 | 2504 | 2504 | 0.059619 | 974 | 0.02319 | 2852 | 0.067905 | 1.362 | A04 | MICL0.01437042/DOV
Build-In Floor | Mini Canal | MICL.01437042/PNC | 14 | 370 | 42 | 42 | 2288 | 2288 | 2288 | 0.054476 | 890 | 0.02119 | 2606 | 0.062048 | 1.362 | A04 | MICL0.01437042/PNC
Build-In Floor | Mini Canal | MICL.01437042/RBL | 14 | 370 | 42 | 42 | 2692 | 2692 | 2692 | 0.064095 | 1047 | 0.024929 | 3066 | 0.073 | 1.362 | A04 | MICL0.01437042/RBL
Build-In Floor | Mini Canal | MICL.01437042/RBN | 14 | 370 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01437042/RBN
Build-In Floor | Mini Canal | MICL.01437042/RBR | 14 | 370 | 42 | 42 | 2692 | 2692 | 2692 | 0.064095 | 1047 | 0.024929 | 3066 | 0.073 | 1.362 | A04 | MICL0.01437042/RBR
Build-In Floor | Mini Canal | MICL.01437042/RBV | 14 | 370 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01437042/RBV
Build-In Floor | Mini Canal | MICL.01437042/RDB | 14 | 370 | 42 | 42 | 2692 | 2692 | 2692 | 0.064095 | 1047 | 0.024929 | 3066 | 0.073 | 1.362 | A04 | MICL0.01437042/RDB
Build-In Floor | Mini Canal | MICL.01437042/RMN | 14 | 370 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01437042/RMN
Build-In Floor | Mini Canal | MICL.01437042/RMV | 14 | 370 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01437042/RMV
Build-In Floor | Mini Canal | MICL.01437042/RNA | 14 | 370 | 42 | 42 | 2692 | 2692 | 2692 | 0.064095 | 1047 | 0.024929 | 3066 | 0.073 | 1.362 | A04 | MICL0.01437042/RNA
Build-In Floor | Mini Canal | MICL.01437042/RON | 14 | 370 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01437042/RON
Build-In Floor | Mini Canal | MICL.01437042/ROV | 14 | 370 | 42 | 42 | 2611 | 2611 | 2611 | 0.062167 | 1016 | 0.02419 | 2974 | 0.07081 | 1.362 | A04 | MICL0.01437042/ROV
Build-In Floor | Mini Canal | MICL.01437042/RSS | 14 | 370 | 42 | 42 | 2584 | 2584 | 2584 | 0.061524 | 1005 | 0.023929 | 2943 | 0.070071 | 1.362 | A04 | MICL0.01437042/RSS
Build-In Floor | Mini Canal | MICL.01437042/SBL | 14 | 370 | 42 | 42 | 2692 | 2692 | 2692 | 0.064095 | 1047 | 0.024929 | 3066 | 0.073 | 1.362 | A04 | MICL0.01437042/SBL
Build-In Floor | Mini Canal | MICL.01437042/SBR | 14 | 370 | 42 | 42 | 2692 | 2692 | 2692 | 0.064095 | 1047 | 0.024929 | 3066 | 0.073 | 1.362 | A04 | MICL0.01437042/SBR
Build-In Floor | Mini Canal | MICL.01437042/SDB | 14 | 370 | 42 | 42 | 2692 | 2692 | 2692 | 0.064095 | 1047 | 0.024929 | 3066 | 0.073 | 1.362 | A04 | MICL0.01437042/SDB
Build-In Floor | Mini Canal | MICL.01437042/SNA | 14 | 370 | 42 | 42 | 2692 | 2692 | 2692 | 0.064095 | 1047 | 0.024929 | 3066 | 0.073 | 1.362 | A04 | MICL0.01437042/SNA
Build-In Floor | Mini Canal | MICL.01437042/SNC | 14 | 370 | 42 | 42 | 2692 | 2692 | 2692 | 0.064095 | 1047 | 0.024929 | 3066 | 0.073 | 1.362 | A04 | MICL0.01437042/SNC
Build-In Floor | Mini Canal | MICL.01439014/ANA | 14 | 390 | 14 | 14 | 670 | 670 | 670 | 0.015952 | 261 | 0.0062143 | 763 | 0.018167 | 1.362 | A04 | MICL0.01439014/ANA
Build-In Floor | Mini Canal | MICL.01439014/DBL | 14 | 390 | 14 | 14 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01439014/DBL
Build-In Floor | Mini Canal | MICL.01439014/DBN | 14 | 390 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01439014/DBN
Build-In Floor | Mini Canal | MICL.01439014/DBR | 14 | 390 | 14 | 14 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01439014/DBR
Build-In Floor | Mini Canal | MICL.01439014/DBV | 14 | 390 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01439014/DBV
Build-In Floor | Mini Canal | MICL.01439014/DDB | 14 | 390 | 14 | 14 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01439014/DDB
Build-In Floor | Mini Canal | MICL.01439014/DMN | 14 | 390 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01439014/DMN
Build-In Floor | Mini Canal | MICL.01439014/DMV | 14 | 390 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01439014/DMV
Build-In Floor | Mini Canal | MICL.01439014/DNA | 14 | 390 | 14 | 14 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01439014/DNA
Build-In Floor | Mini Canal | MICL.01439014/DNC | 14 | 390 | 14 | 14 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01439014/DNC
Build-In Floor | Mini Canal | MICL.01439014/DON | 14 | 390 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01439014/DON
Build-In Floor | Mini Canal | MICL.01439014/DOV | 14 | 390 | 14 | 14 | 830 | 830 | 830 | 0.019762 | 323 | 0.0076905 | 945 | 0.0225 | 1.362 | A04 | MICL0.01439014/DOV
Build-In Floor | Mini Canal | MICL.01439014/RBL | 14 | 390 | 14 | 14 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01439014/RBL
Build-In Floor | Mini Canal | MICL.01439014/RBN | 14 | 390 | 14 | 14 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01439014/RBN
Build-In Floor | Mini Canal | MICL.01439014/RBR | 14 | 390 | 14 | 14 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01439014/RBR
Build-In Floor | Mini Canal | MICL.01439014/RBV | 14 | 390 | 14 | 14 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01439014/RBV
Build-In Floor | Mini Canal | MICL.01439014/RDB | 14 | 390 | 14 | 14 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01439014/RDB
Build-In Floor | Mini Canal | MICL.01439014/RMN | 14 | 390 | 14 | 14 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01439014/RMN
Build-In Floor | Mini Canal | MICL.01439014/RMV | 14 | 390 | 14 | 14 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01439014/RMV
Build-In Floor | Mini Canal | MICL.01439014/RNA | 14 | 390 | 14 | 14 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01439014/RNA
Build-In Floor | Mini Canal | MICL.01439014/RON | 14 | 390 | 14 | 14 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01439014/RON
Build-In Floor | Mini Canal | MICL.01439014/ROV | 14 | 390 | 14 | 14 | 866 | 866 | 866 | 0.020619 | 337 | 0.0080238 | 986 | 0.023476 | 1.362 | A04 | MICL0.01439014/ROV
Build-In Floor | Mini Canal | MICL.01439014/RSS | 14 | 390 | 14 | 14 | 857 | 857 | 857 | 0.020405 | 333 | 0.0079286 | 976 | 0.023238 | 1.362 | A04 | MICL0.01439014/RSS
Build-In Floor | Mini Canal | MICL.01439014/SBL | 14 | 390 | 14 | 14 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01439014/SBL
Build-In Floor | Mini Canal | MICL.01439014/SBR | 14 | 390 | 14 | 14 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01439014/SBR
Build-In Floor | Mini Canal | MICL.01439014/SDB | 14 | 390 | 14 | 14 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01439014/SDB
Build-In Floor | Mini Canal | MICL.01439014/SNA | 14 | 390 | 14 | 14 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01439014/SNA
Build-In Floor | Mini Canal | MICL.01439014/SNC | 14 | 390 | 14 | 14 | 893 | 893 | 893 | 0.021262 | 347 | 0.0082619 | 1017 | 0.024214 | 1.362 | A04 | MICL0.01439014/SNC
Build-In Floor | Mini Canal | MICL.01439026/ANA | 14 | 390 | 26 | 26 | 1163 | 1163 | 1163 | 0.02769 | 452 | 0.010762 | 1325 | 0.031548 | 1.362 | A04 | MICL0.01439026/ANA
Build-In Floor | Mini Canal | MICL.01439026/DBL | 14 | 390 | 26 | 26 | 1504 | 1504 | 1504 | 0.03581 | 585 | 0.013929 | 1713 | 0.040786 | 1.362 | A04 | MICL0.01439026/DBL
Build-In Floor | Mini Canal | MICL.01439026/DBN | 14 | 390 | 26 | 26 | 1442 | 1442 | 1442 | 0.034333 | 561 | 0.013357 | 1642 | 0.039095 | 1.362 | A04 | MICL0.01439026/DBN
Build-In Floor | Mini Canal | MICL.01439026/DBR | 14 | 390 | 26 | 26 | 1504 | 1504 | 1504 | 0.03581 | 585 | 0.013929 | 1713 | 0.040786 | 1.362 | A04 | MICL0.01439026/DBR
Build-In Floor | Mini Canal | MICL.01439026/DBV | 14 | 390 | 26 | 26 | 1442 | 1442 | 1442 | 0.034333 | 561 | 0.013357 | 1642 | 0.039095 | 1.362 | A04 | MICL0.01439026/DBV
Build-In Floor | Mini Canal | MICL.01439026/DDB | 14 | 390 | 26 | 26 | 1504 | 1504 | 1504 | 0.03581 | 585 | 0.013929 | 1713 | 0.040786 | 1.362 | A04 | MICL0.01439026/DDB
Build-In Floor | Mini Canal | MICL.01439026/DMN | 14 | 390 | 26 | 26 | 1442 | 1442 | 1442 | 0.034333 | 561 | 0.013357 | 1642 | 0.039095 | 1.362 | A04 | MICL0.01439026/DMN
Build-In Floor | Mini Canal | MICL.01439026/DMV | 14 | 390 | 26 | 26 | 1442 | 1442 | 1442 | 0.034333 | 561 | 0.013357 | 1642 | 0.039095 | 1.362 | A04 | MICL0.01439026/DMV
Build-In Floor | Mini Canal | MICL.01439026/DNA | 14 | 390 | 26 | 26 | 1504 | 1504 | 1504 | 0.03581 | 585 | 0.013929 | 1713 | 0.040786 | 1.362 | A04 | MICL0.01439026/DNA
Build-In Floor | Mini Canal | MICL.01439026/DNC | 14 | 390 | 26 | 26 | 1504 | 1504 | 1504 | 0.03581 | 585 | 0.013929 | 1713 | 0.040786 | 1.362 | A04 | MICL0.01439026/DNC
Build-In Floor | Mini Canal | MICL.01439026/DON | 14 | 390 | 26 | 26 | 1442 | 1442 | 1442 | 0.034333 | 561 | 0.013357 | 1642 | 0.039095 | 1.362 | A04 | MICL0.01439026/DON
Build-In Floor | Mini Canal | MICL.01439026/DOV | 14 | 390 | 26 | 26 | 1442 | 1442 | 1442 | 0.034333 | 561 | 0.013357 | 1642 | 0.039095 | 1.362 | A04 | MICL0.01439026/DOV
Build-In Floor | Mini Canal | MICL.01439026/PNC | 14 | 390 | 26 | 26 | 1318 | 1318 | 1318 | 0.031381 | 513 | 0.012214 | 1501 | 0.035738 | 1.362 | A04 | MICL0.01439026/PNC
Build-In Floor | Mini Canal | MICL.01439026/RBL | 14 | 390 | 26 | 26 | 1550 | 1550 | 1550 | 0.036905 | 603 | 0.014357 | 1765 | 0.042024 | 1.362 | A04 | MICL0.01439026/RBL
Build-In Floor | Mini Canal | MICL.01439026/RBN | 14 | 390 | 26 | 26 | 1504 | 1504 | 1504 | 0.03581 | 585 | 0.013929 | 1713 | 0.040786 | 1.362 | A04 | MICL0.01439026/RBN
Build-In Floor | Mini Canal | MICL.01439026/RBR | 14 | 390 | 26 | 26 | 1550 | 1550 | 1550 | 0.036905 | 603 | 0.014357 | 1765 | 0.042024 | 1.362 | A04 | MICL0.01439026/RBR
Build-In Floor | Mini Canal | MICL.01439026/RBV | 14 | 390 | 26 | 26 | 1504 | 1504 | 1504 | 0.03581 | 585 | 0.013929 | 1713 | 0.040786 | 1.362 | A04 | MICL0.01439026/RBV
Build-In Floor | Mini Canal | MICL.01439026/RDB | 14 | 390 | 26 | 26 | 1550 | 1550 | 1550 | 0.036905 | 603 | 0.014357 | 1765 | 0.042024 | 1.362 | A04 | MICL0.01439026/RDB
Build-In Floor | Mini Canal | MICL.01439026/RMN | 14 | 390 | 26 | 26 | 1504 | 1504 | 1504 | 0.03581 | 585 | 0.013929 | 1713 | 0.040786 | 1.362 | A04 | MICL0.01439026/RMN
Build-In Floor | Mini Canal | MICL.01439026/RMV | 14 | 390 | 26 | 26 | 1504 | 1504 | 1504 | 0.03581 | 585 | 0.013929 | 1713 | 0.040786 | 1.362 | A04 | MICL0.01439026/RMV
Build-In Floor | Mini Canal | MICL.01439026/RNA | 14 | 390 | 26 | 26 | 1550 | 1550 | 1550 | 0.036905 | 603 | 0.014357 | 1765 | 0.042024 | 1.362 | A04 | MICL0.01439026/RNA
Build-In Floor | Mini Canal | MICL.01439026/RON | 14 | 390 | 26 | 26 | 1504 | 1504 | 1504 | 0.03581 | 585 | 0.013929 | 1713 | 0.040786 | 1.362 | A04 | MICL0.01439026/RON
Build-In Floor | Mini Canal | MICL.01439026/ROV | 14 | 390 | 26 | 26 | 1504 | 1504 | 1504 | 0.03581 | 585 | 0.013929 | 1713 | 0.040786 | 1.362 | A04 | MICL0.01439026/ROV
Build-In Floor | Mini Canal | MICL.01439026/RSS | 14 | 390 | 26 | 26 | 1488 | 1488 | 1488 | 0.035429 | 579 | 0.013786 | 1695 | 0.040357 | 1.362 | A04 | MICL0.01439026/RSS
Build-In Floor | Mini Canal | MICL.01439026/SBL | 14 | 390 | 26 | 26 | 1550 | 1550 | 1550 | 0.036905 | 603 | 0.014357 | 1765 | 0.042024 | 1.362 | A04 | MICL0.01439026/SBL
Build-In Floor | Mini Canal | MICL.01439026/SBR | 14 | 390 | 26 | 26 | 1550 | 1550 | 1550 | 0.036905 | 603 | 0.014357 | 1765 | 0.042024 | 1.362 | A04 | MICL0.01439026/SBR
Build-In Floor | Mini Canal | MICL.01439026/SDB | 14 | 390 | 26 | 26 | 1550 | 1550 | 1550 | 0.036905 | 603 | 0.014357 | 1765 | 0.042024 | 1.362 | A04 | MICL0.01439026/SDB
Build-In Floor | Mini Canal | MICL.01439026/SNA | 14 | 390 | 26 | 26 | 1550 | 1550 | 1550 | 0.036905 | 603 | 0.014357 | 1765 | 0.042024 | 1.362 | A04 | MICL0.01439026/SNA
Build-In Floor | Mini Canal | MICL.01439026/SNC | 14 | 390 | 26 | 26 | 1550 | 1550 | 1550 | 0.036905 | 603 | 0.014357 | 1765 | 0.042024 | 1.362 | A04 | MICL0.01439026/SNC
Build-In Floor | Mini Canal | MICL.01439034/ANA | 14 | 390 | 34 | 34 | 1586 | 1586 | 1586 | 0.037762 | 617 | 0.01469 | 1806 | 0.043 | 1.362 | A04 | MICL0.01439034/ANA
Build-In Floor | Mini Canal | MICL.01439034/DBL | 14 | 390 | 34 | 34 | 2052 | 2052 | 2052 | 0.048857 | 798 | 0.019 | 2337 | 0.055643 | 1.362 | A04 | MICL0.01439034/DBL
Build-In Floor | Mini Canal | MICL.01439034/DBN | 14 | 390 | 34 | 34 | 1967 | 1967 | 1967 | 0.046833 | 765 | 0.018214 | 2240 | 0.053333 | 1.362 | A04 | MICL0.01439034/DBN
Build-In Floor | Mini Canal | MICL.01439034/DBR | 14 | 390 | 34 | 34 | 2052 | 2052 | 2052 | 0.048857 | 798 | 0.019 | 2337 | 0.055643 | 1.362 | A04 | MICL0.01439034/DBR
Build-In Floor | Mini Canal | MICL.01439034/DBV | 14 | 390 | 34 | 34 | 1967 | 1967 | 1967 | 0.046833 | 765 | 0.018214 | 2240 | 0.053333 | 1.362 | A04 | MICL0.01439034/DBV
Build-In Floor | Mini Canal | MICL.01439034/DDB | 14 | 390 | 34 | 34 | 2052 | 2052 | 2052 | 0.048857 | 798 | 0.019 | 2337 | 0.055643 | 1.362 | A04 | MICL0.01439034/DDB
Build-In Floor | Mini Canal | MICL.01439034/DMN | 14 | 390 | 34 | 34 | 1967 | 1967 | 1967 | 0.046833 | 765 | 0.018214 | 2240 | 0.053333 | 1.362 | A04 | MICL0.01439034/DMN
Build-In Floor | Mini Canal | MICL.01439034/DMV | 14 | 390 | 34 | 34 | 1967 | 1967 | 1967 | 0.046833 | 765 | 0.018214 | 2240 | 0.053333 | 1.362 | A04 | MICL0.01439034/DMV
Build-In Floor | Mini Canal | MICL.01439034/DNA | 14 | 390 | 34 | 34 | 2052 | 2052 | 2052 | 0.048857 | 798 | 0.019 | 2337 | 0.055643 | 1.362 | A04 | MICL0.01439034/DNA
Build-In Floor | Mini Canal | MICL.01439034/DNC | 14 | 390 | 34 | 34 | 2052 | 2052 | 2052 | 0.048857 | 798 | 0.019 | 2337 | 0.055643 | 1.362 | A04 | MICL0.01439034/DNC
Build-In Floor | Mini Canal | MICL.01439034/DON | 14 | 390 | 34 | 34 | 1967 | 1967 | 1967 | 0.046833 | 765 | 0.018214 | 2240 | 0.053333 | 1.362 | A04 | MICL0.01439034/DON
Build-In Floor | Mini Canal | MICL.01439034/DOV | 14 | 390 | 34 | 34 | 1967 | 1967 | 1967 | 0.046833 | 765 | 0.018214 | 2240 | 0.053333 | 1.362 | A04 | MICL0.01439034/DOV
Build-In Floor | Mini Canal | MICL.01439034/PNC | 14 | 390 | 34 | 34 | 1798 | 1798 | 1798 | 0.04281 | 699 | 0.016643 | 2048 | 0.048762 | 1.362 | A04 | MICL0.01439034/PNC
Build-In Floor | Mini Canal | MICL.01439034/RBL | 14 | 390 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 823 | 0.019595 | 2409 | 0.057357 | 1.362 | A04 | MICL0.01439034/RBL
Build-In Floor | Mini Canal | MICL.01439034/RBN | 14 | 390 | 34 | 34 | 2052 | 2052 | 2052 | 0.048857 | 798 | 0.019 | 2337 | 0.055643 | 1.362 | A04 | MICL0.01439034/RBN
Build-In Floor | Mini Canal | MICL.01439034/RBR | 14 | 390 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 823 | 0.019595 | 2409 | 0.057357 | 1.362 | A04 | MICL0.01439034/RBR
Build-In Floor | Mini Canal | MICL.01439034/RBV | 14 | 390 | 34 | 34 | 2052 | 2052 | 2052 | 0.048857 | 798 | 0.019 | 2337 | 0.055643 | 1.362 | A04 | MICL0.01439034/RBV
Build-In Floor | Mini Canal | MICL.01439034/RDB | 14 | 390 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 823 | 0.019595 | 2409 | 0.057357 | 1.362 | A04 | MICL0.01439034/RDB
Build-In Floor | Mini Canal | MICL.01439034/RMN | 14 | 390 | 34 | 34 | 2052 | 2052 | 2052 | 0.048857 | 798 | 0.019 | 2337 | 0.055643 | 1.362 | A04 | MICL0.01439034/RMN
Build-In Floor | Mini Canal | MICL.01439034/RMV | 14 | 390 | 34 | 34 | 2052 | 2052 | 2052 | 0.048857 | 798 | 0.019 | 2337 | 0.055643 | 1.362 | A04 | MICL0.01439034/RMV
Build-In Floor | Mini Canal | MICL.01439034/RNA | 14 | 390 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 823 | 0.019595 | 2409 | 0.057357 | 1.362 | A04 | MICL0.01439034/RNA
Build-In Floor | Mini Canal | MICL.01439034/RON | 14 | 390 | 34 | 34 | 2052 | 2052 | 2052 | 0.048857 | 798 | 0.019 | 2337 | 0.055643 | 1.362 | A04 | MICL0.01439034/RON
Build-In Floor | Mini Canal | MICL.01439034/ROV | 14 | 390 | 34 | 34 | 2052 | 2052 | 2052 | 0.048857 | 798 | 0.019 | 2337 | 0.055643 | 1.362 | A04 | MICL0.01439034/ROV
Build-In Floor | Mini Canal | MICL.01439034/RSS | 14 | 390 | 34 | 34 | 2030 | 2030 | 2030 | 0.048333 | 790 | 0.01881 | 2312 | 0.055048 | 1.362 | A04 | MICL0.01439034/RSS
Build-In Floor | Mini Canal | MICL.01439034/SBL | 14 | 390 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 823 | 0.019595 | 2409 | 0.057357 | 1.362 | A04 | MICL0.01439034/SBL
Build-In Floor | Mini Canal | MICL.01439034/SBR | 14 | 390 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 823 | 0.019595 | 2409 | 0.057357 | 1.362 | A04 | MICL0.01439034/SBR
Build-In Floor | Mini Canal | MICL.01439034/SDB | 14 | 390 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 823 | 0.019595 | 2409 | 0.057357 | 1.362 | A04 | MICL0.01439034/SDB
Build-In Floor | Mini Canal | MICL.01439034/SNA | 14 | 390 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 823 | 0.019595 | 2409 | 0.057357 | 1.362 | A04 | MICL0.01439034/SNA
Build-In Floor | Mini Canal | MICL.01439034/SNC | 14 | 390 | 34 | 34 | 2115 | 2115 | 2115 | 0.050357 | 823 | 0.019595 | 2409 | 0.057357 | 1.362 | A04 | MICL0.01439034/SNC
Build-In Floor | Mini Canal | MICL.01439042/ANA | 14 | 390 | 42 | 42 | 2138 | 2138 | 2138 | 0.050905 | 832 | 0.01981 | 2435 | 0.057976 | 1.362 | A04 | MICL0.01439042/ANA
Build-In Floor | Mini Canal | MICL.01439042/DBL | 14 | 390 | 42 | 42 | 2764 | 2764 | 2764 | 0.06581 | 1075 | 0.025595 | 3148 | 0.074952 | 1.362 | A04 | MICL0.01439042/DBL
Build-In Floor | Mini Canal | MICL.01439042/DBN | 14 | 390 | 42 | 42 | 2650 | 2650 | 2650 | 0.063095 | 1031 | 0.024548 | 3018 | 0.071857 | 1.362 | A04 | MICL0.01439042/DBN
Build-In Floor | Mini Canal | MICL.01439042/DBR | 14 | 390 | 42 | 42 | 2764 | 2764 | 2764 | 0.06581 | 1075 | 0.025595 | 3148 | 0.074952 | 1.362 | A04 | MICL0.01439042/DBR
Build-In Floor | Mini Canal | MICL.01439042/DBV | 14 | 390 | 42 | 42 | 2650 | 2650 | 2650 | 0.063095 | 1031 | 0.024548 | 3018 | 0.071857 | 1.362 | A04 | MICL0.01439042/DBV
Build-In Floor | Mini Canal | MICL.01439042/DDB | 14 | 390 | 42 | 42 | 2764 | 2764 | 2764 | 0.06581 | 1075 | 0.025595 | 3148 | 0.074952 | 1.362 | A04 | MICL0.01439042/DDB
Build-In Floor | Mini Canal | MICL.01439042/DMN | 14 | 390 | 42 | 42 | 2650 | 2650 | 2650 | 0.063095 | 1031 | 0.024548 | 3018 | 0.071857 | 1.362 | A04 | MICL0.01439042/DMN
Build-In Floor | Mini Canal | MICL.01439042/DMV | 14 | 390 | 42 | 42 | 2650 | 2650 | 2650 | 0.063095 | 1031 | 0.024548 | 3018 | 0.071857 | 1.362 | A04 | MICL0.01439042/DMV
Build-In Floor | Mini Canal | MICL.01439042/DNA | 14 | 390 | 42 | 42 | 2764 | 2764 | 2764 | 0.06581 | 1075 | 0.025595 | 3148 | 0.074952 | 1.362 | A04 | MICL0.01439042/DNA
Build-In Floor | Mini Canal | MICL.01439042/DNC | 14 | 390 | 42 | 42 | 2764 | 2764 | 2764 | 0.06581 | 1075 | 0.025595 | 3148 | 0.074952 | 1.362 | A04 | MICL0.01439042/DNC
Build-In Floor | Mini Canal | MICL.01439042/DON | 14 | 390 | 42 | 42 | 2650 | 2650 | 2650 | 0.063095 | 1031 | 0.024548 | 3018 | 0.071857 | 1.362 | A04 | MICL0.01439042/DON
Build-In Floor | Mini Canal | MICL.01439042/DOV | 14 | 390 | 42 | 42 | 2650 | 2650 | 2650 | 0.063095 | 1031 | 0.024548 | 3018 | 0.071857 | 1.362 | A04 | MICL0.01439042/DOV
Build-In Floor | Mini Canal | MICL.01439042/PNC | 14 | 390 | 42 | 42 | 2423 | 2423 | 2423 | 0.05769 | 943 | 0.022452 | 2760 | 0.065714 | 1.362 | A04 | MICL0.01439042/PNC
Build-In Floor | Mini Canal | MICL.01439042/RBL | 14 | 390 | 42 | 42 | 2850 | 2850 | 2850 | 0.067857 | 1109 | 0.026405 | 3246 | 0.077286 | 1.362 | A04 | MICL0.01439042/RBL
Build-In Floor | Mini Canal | MICL.01439042/RBN | 14 | 390 | 42 | 42 | 2764 | 2764 | 2764 | 0.06581 | 1075 | 0.025595 | 3148 | 0.074952 | 1.362 | A04 | MICL0.01439042/RBN
Build-In Floor | Mini Canal | MICL.01439042/RBR | 14 | 390 | 42 | 42 | 2850 | 2850 | 2850 | 0.067857 | 1109 | 0.026405 | 3246 | 0.077286 | 1.362 | A04 | MICL0.01439042/RBR
Build-In Floor | Mini Canal | MICL.01439042/RBV | 14 | 390 | 42 | 42 | 2764 | 2764 | 2764 | 0.06581 | 1075 | 0.025595 | 3148 | 0.074952 | 1.362 | A04 | MICL0.01439042/RBV
Build-In Floor | Mini Canal | MICL.01439042/RDB | 14 | 390 | 42 | 42 | 2850 | 2850 | 2850 | 0.067857 | 1109 | 0.026405 | 3246 | 0.077286 | 1.362 | A04 | MICL0.01439042/RDB
Build-In Floor | Mini Canal | MICL.01439042/RMN | 14 | 390 | 42 | 42 | 2764 | 2764 | 2764 | 0.06581 | 1075 | 0.025595 | 3148 | 0.074952 | 1.362 | A04 | MICL0.01439042/RMN
Build-In Floor | Mini Canal | MICL.01439042/RMV | 14 | 390 | 42 | 42 | 2764 | 2764 | 2764 | 0.06581 | 1075 | 0.025595 | 3148 | 0.074952 | 1.362 | A04 | MICL0.01439042/RMV
Build-In Floor | Mini Canal | MICL.01439042/RNA | 14 | 390 | 42 | 42 | 2850 | 2850 | 2850 | 0.067857 | 1109 | 0.026405 | 3246 | 0.077286 | 1.362 | A04 | MICL0.01439042/RNA
Build-In Floor | Mini Canal | MICL.01439042/RON | 14 | 390 | 42 | 42 | 2764 | 2764 | 2764 | 0.06581 | 1075 | 0.025595 | 3148 | 0.074952 | 1.362 | A04 | MICL0.01439042/RON
Build-In Floor | Mini Canal | MICL.01439042/ROV | 14 | 390 | 42 | 42 | 2764 | 2764 | 2764 | 0.06581 | 1075 | 0.025595 | 3148 | 0.074952 | 1.362 | A04 | MICL0.01439042/ROV
Build-In Floor | Mini Canal | MICL.01439042/RSS | 14 | 390 | 42 | 42 | 2736 | 2736 | 2736 | 0.065143 | 1064 | 0.025333 | 3116 | 0.07419 | 1.362 | A04 | MICL0.01439042/RSS
Build-In Floor | Mini Canal | MICL.01439042/SBL | 14 | 390 | 42 | 42 | 2850 | 2850 | 2850 | 0.067857 | 1109 | 0.026405 | 3246 | 0.077286 | 1.362 | A04 | MICL0.01439042/SBL
Build-In Floor | Mini Canal | MICL.01439042/SBR | 14 | 390 | 42 | 42 | 2850 | 2850 | 2850 | 0.067857 | 1109 | 0.026405 | 3246 | 0.077286 | 1.362 | A04 | MICL0.01439042/SBR
Build-In Floor | Mini Canal | MICL.01439042/SDB | 14 | 390 | 42 | 42 | 2850 | 2850 | 2850 | 0.067857 | 1109 | 0.026405 | 3246 | 0.077286 | 1.362 | A04 | MICL0.01439042/SDB
Build-In Floor | Mini Canal | MICL.01439042/SNA | 14 | 390 | 42 | 42 | 2850 | 2850 | 2850 | 0.067857 | 1109 | 0.026405 | 3246 | 0.077286 | 1.362 | A04 | MICL0.01439042/SNA
Build-In Floor | Mini Canal | MICL.01439042/SNC | 14 | 390 | 42 | 42 | 2850 | 2850 | 2850 | 0.067857 | 1109 | 0.026405 | 3246 | 0.077286 | 1.362 | A04 | MICL0.01439042/SNC
Build-In Floor | Mini Canal | MICL.01441014/ANA | 14 | 410 | 14 | 14 | 707 | 707 | 707 | 0.016833 | 275 | 0.0065476 | 805 | 0.019167 | 1.362 | A04 | MICL0.01441014/ANA
Build-In Floor | Mini Canal | MICL.01441014/DBL | 14 | 410 | 14 | 14 | 914 | 914 | 914 | 0.021762 | 356 | 0.0084762 | 1041 | 0.024786 | 1.362 | A04 | MICL0.01441014/DBL
Build-In Floor | Mini Canal | MICL.01441014/DBN | 14 | 410 | 14 | 14 | 876 | 876 | 876 | 0.020857 | 341 | 0.008119 | 998 | 0.023762 | 1.362 | A04 | MICL0.01441014/DBN
Build-In Floor | Mini Canal | MICL.01441014/DBR | 14 | 410 | 14 | 14 | 914 | 914 | 914 | 0.021762 | 356 | 0.0084762 | 1041 | 0.024786 | 1.362 | A04 | MICL0.01441014/DBR
Build-In Floor | Mini Canal | MICL.01441014/DBV | 14 | 410 | 14 | 14 | 876 | 876 | 876 | 0.020857 | 341 | 0.008119 | 998 | 0.023762 | 1.362 | A04 | MICL0.01441014/DBV
Build-In Floor | Mini Canal | MICL.01441014/DDB | 14 | 410 | 14 | 14 | 914 | 914 | 914 | 0.021762 | 356 | 0.0084762 | 1041 | 0.024786 | 1.362 | A04 | MICL0.01441014/DDB
Build-In Floor | Mini Canal | MICL.01441014/DMN | 14 | 410 | 14 | 14 | 876 | 876 | 876 | 0.020857 | 341 | 0.008119 | 998 | 0.023762 | 1.362 | A04 | MICL0.01441014/DMN
Build-In Floor | Mini Canal | MICL.01441014/DMV | 14 | 410 | 14 | 14 | 876 | 876 | 876 | 0.020857 | 341 | 0.008119 | 998 | 0.023762 | 1.362 | A04 | MICL0.01441014/DMV
Build-In Floor | Mini Canal | MICL.01441014/DNA | 14 | 410 | 14 | 14 | 914 | 914 | 914 | 0.021762 | 356 | 0.0084762 | 1041 | 0.024786 | 1.362 | A04 | MICL0.01441014/DNA
Build-In Floor | Mini Canal | MICL.01441014/DNC | 14 | 410 | 14 | 14 | 914 | 914 | 914 | 0.021762 | 356 | 0.0084762 | 1041 | 0.024786 | 1.362 | A04 | MICL0.01441014/DNC
Build-In Floor | Mini Canal | MICL.01441014/DON | 14 | 410 | 14 | 14 | 876 | 876 | 876 | 0.020857 | 341 | 0.008119 | 998 | 0.023762 | 1.362 | A04 | MICL0.01441014/DON
Build-In Floor | Mini Canal | MICL.01441014/DOV | 14 | 410 | 14 | 14 | 876 | 876 | 876 | 0.020857 | 341 | 0.008119 | 998 | 0.023762 | 1.362 | A04 | MICL0.01441014/DOV
Build-In Floor | Mini Canal | MICL.01441014/RBL | 14 | 410 | 14 | 14 | 942 | 942 | 942 | 0.022429 | 366 | 0.0087143 | 1073 | 0.025548 | 1.362 | A04 | MICL0.01441014/RBL
Build-In Floor | Mini Canal | MICL.01441014/RBN | 14 | 410 | 14 | 14 | 914 | 914 | 914 | 0.021762 | 356 | 0.0084762 | 1041 | 0.024786 | 1.362 | A04 | MICL0.01441014/RBN
Build-In Floor | Mini Canal | MICL.01441014/RBR | 14 | 410 | 14 | 14 | 942 | 942 | 942 | 0.022429 | 366 | 0.0087143 | 1073 | 0.025548 | 1.362 | A04 | MICL0.01441014/RBR
Build-In Floor | Mini Canal | MICL.01441014/RBV | 14 | 410 | 14 | 14 | 914 | 914 | 914 | 0.021762 | 356 | 0.0084762 | 1041 | 0.024786 | 1.362 | A04 | MICL0.01441014/RBV
Build-In Floor | Mini Canal | MICL.01441014/RDB | 14 | 410 | 14 | 14 | 942 | 942 | 942 | 0.022429 | 366 | 0.0087143 | 1073 | 0.025548 | 1.362 | A04 | MICL0.01441014/RDB
Build-In Floor | Mini Canal | MICL.01441014/RMN | 14 | 410 | 14 | 14 | 914 | 914 | 914 | 0.021762 | 356 | 0.0084762 | 1041 | 0.024786 | 1.362 | A04 | MICL0.01441014/RMN
Build-In Floor | Mini Canal | MICL.01441014/RMV | 14 | 410 | 14 | 14 | 914 | 914 | 914 | 0.021762 | 356 | 0.0084762 | 1041 | 0.024786 | 1.362 | A04 | MICL0.01441014/RMV
Build-In Floor | Mini Canal | MICL.01441014/RNA | 14 | 410 | 14 | 14 | 942 | 942 | 942 | 0.022429 | 366 | 0.0087143 | 1073 | 0.025548 | 1.362 | A04 | MICL0.01441014/RNA
Build-In Floor | Mini Canal | MICL.01441014/RON | 14 | 410 | 14 | 14 | 914 | 914 | 914 | 0.021762 | 356 | 0.0084762 | 1041 | 0.024786 | 1.362 | A04 | MICL0.01441014/RON
Build-In Floor | Mini Canal | MICL.01441014/ROV | 14 | 410 | 14 | 14 | 914 | 914 | 914 | 0.021762 | 356 | 0.0084762 | 1041 | 0.024786 | 1.362 | A04 | MICL0.01441014/ROV
Build-In Floor | Mini Canal | MICL.01441014/RSS | 14 | 410 | 14 | 14 | 904 | 904 | 904 | 0.021524 | 352 | 0.008381 | 1030 | 0.024524 | 1.362 | A04 | MICL0.01441014/RSS
Build-In Floor | Mini Canal | MICL.01441014/SBL | 14 | 410 | 14 | 14 | 942 | 942 | 942 | 0.022429 | 366 | 0.0087143 | 1073 | 0.025548 | 1.362 | A04 | MICL0.01441014/SBL
Build-In Floor | Mini Canal | MICL.01441014/SBR | 14 | 410 | 14 | 14 | 942 | 942 | 942 | 0.022429 | 366 | 0.0087143 | 1073 | 0.025548 | 1.362 | A04 | MICL0.01441014/SBR
Build-In Floor | Mini Canal | MICL.01441014/SDB | 14 | 410 | 14 | 14 | 942 | 942 | 942 | 0.022429 | 366 | 0.0087143 | 1073 | 0.025548 | 1.362 | A04 | MICL0.01441014/SDB
Build-In Floor | Mini Canal | MICL.01441014/SNA | 14 | 410 | 14 | 14 | 942 | 942 | 942 | 0.022429 | 366 | 0.0087143 | 1073 | 0.025548 | 1.362 | A04 | MICL0.01441014/SNA
Build-In Floor | Mini Canal | MICL.01441014/SNC | 14 | 410 | 14 | 14 | 942 | 942 | 942 | 0.022429 | 366 | 0.0087143 | 1073 | 0.025548 | 1.362 | A04 | MICL0.01441014/SNC
Build-In Floor | Mini Canal | MICL.01441026/ANA | 14 | 410 | 26 | 26 | 1227 | 1227 | 1227 | 0.029214 | 477 | 0.011357 | 1398 | 0.033286 | 1.362 | A04 | MICL0.01441026/ANA
Build-In Floor | Mini Canal | MICL.01441026/DBL | 14 | 410 | 26 | 26 | 1587 | 1587 | 1587 | 0.037786 | 617 | 0.01469 | 1808 | 0.043048 | 1.362 | A04 | MICL0.01441026/DBL
Build-In Floor | Mini Canal | MICL.01441026/DBN | 14 | 410 | 26 | 26 | 1521 | 1521 | 1521 | 0.036214 | 592 | 0.014095 | 1732 | 0.041238 | 1.362 | A04 | MICL0.01441026/DBN
Build-In Floor | Mini Canal | MICL.01441026/DBR | 14 | 410 | 26 | 26 | 1587 | 1587 | 1587 | 0.037786 | 617 | 0.01469 | 1808 | 0.043048 | 1.362 | A04 | MICL0.01441026/DBR
Build-In Floor | Mini Canal | MICL.01441026/DBV | 14 | 410 | 26 | 26 | 1521 | 1521 | 1521 | 0.036214 | 592 | 0.014095 | 1732 | 0.041238 | 1.362 | A04 | MICL0.01441026/DBV
Build-In Floor | Mini Canal | MICL.01441026/DDB | 14 | 410 | 26 | 26 | 1587 | 1587 | 1587 | 0.037786 | 617 | 0.01469 | 1808 | 0.043048 | 1.362 | A04 | MICL0.01441026/DDB
Build-In Floor | Mini Canal | MICL.01441026/DMN | 14 | 410 | 26 | 26 | 1521 | 1521 | 1521 | 0.036214 | 592 | 0.014095 | 1732 | 0.041238 | 1.362 | A04 | MICL0.01441026/DMN
Build-In Floor | Mini Canal | MICL.01441026/DMV | 14 | 410 | 26 | 26 | 1521 | 1521 | 1521 | 0.036214 | 592 | 0.014095 | 1732 | 0.041238 | 1.362 | A04 | MICL0.01441026/DMV
Build-In Floor | Mini Canal | MICL.01441026/DNA | 14 | 410 | 26 | 26 | 1587 | 1587 | 1587 | 0.037786 | 617 | 0.01469 | 1808 | 0.043048 | 1.362 | A04 | MICL0.01441026/DNA
Build-In Floor | Mini Canal | MICL.01441026/DNC | 14 | 410 | 26 | 26 | 1587 | 1587 | 1587 | 0.037786 | 617 | 0.01469 | 1808 | 0.043048 | 1.362 | A04 | MICL0.01441026/DNC
Build-In Floor | Mini Canal | MICL.01441026/DON | 14 | 410 | 26 | 26 | 1521 | 1521 | 1521 | 0.036214 | 592 | 0.014095 | 1732 | 0.041238 | 1.362 | A04 | MICL0.01441026/DON
Build-In Floor | Mini Canal | MICL.01441026/DOV | 14 | 410 | 26 | 26 | 1521 | 1521 | 1521 | 0.036214 | 592 | 0.014095 | 1732 | 0.041238 | 1.362 | A04 | MICL0.01441026/DOV
Build-In Floor | Mini Canal | MICL.01441026/PNC | 14 | 410 | 26 | 26 | 1391 | 1391 | 1391 | 0.033119 | 541 | 0.012881 | 1584 | 0.037714 | 1.362 | A04 | MICL0.01441026/PNC
Build-In Floor | Mini Canal | MICL.01441026/RBL | 14 | 410 | 26 | 26 | 1636 | 1636 | 1636 | 0.038952 | 636 | 0.015143 | 1863 | 0.044357 | 1.362 | A04 | MICL0.01441026/RBL
Build-In Floor | Mini Canal | MICL.01441026/RBN | 14 | 410 | 26 | 26 | 1587 | 1587 | 1587 | 0.037786 | 617 | 0.01469 | 1808 | 0.043048 | 1.362 | A04 | MICL0.01441026/RBN
Build-In Floor | Mini Canal | MICL.01441026/RBR | 14 | 410 | 26 | 26 | 1636 | 1636 | 1636 | 0.038952 | 636 | 0.015143 | 1863 | 0.044357 | 1.362 | A04 | MICL0.01441026/RBR
Build-In Floor | Mini Canal | MICL.01441026/RBV | 14 | 410 | 26 | 26 | 1587 | 1587 | 1587 | 0.037786 | 617 | 0.01469 | 1808 | 0.043048 | 1.362 | A04 | MICL0.01441026/RBV
Build-In Floor | Mini Canal | MICL.01441026/RDB | 14 | 410 | 26 | 26 | 1636 | 1636 | 1636 | 0.038952 | 636 | 0.015143 | 1863 | 0.044357 | 1.362 | A04 | MICL0.01441026/RDB
Build-In Floor | Mini Canal | MICL.01441026/RMN | 14 | 410 | 26 | 26 | 1587 | 1587 | 1587 | 0.037786 | 617 | 0.01469 | 1808 | 0.043048 | 1.362 | A04 | MICL0.01441026/RMN
Build-In Floor | Mini Canal | MICL.01441026/RMV | 14 | 410 | 26 | 26 | 1587 | 1587 | 1587 | 0.037786 | 617 | 0.01469 | 1808 | 0.043048 | 1.362 | A04 | MICL0.01441026/RMV
Build-In Floor | Mini Canal | MICL.01441026/RNA | 14 | 410 | 26 | 26 | 1636 | 1636 | 1636 | 0.038952 | 636 | 0.015143 | 1863 | 0.044357 | 1.362 | A04 | MICL0.01441026/RNA
Build-In Floor | Mini Canal | MICL.01441026/RON | 14 | 410 | 26 | 26 | 1587 | 1587 | 1587 | 0.037786 | 617 | 0.01469 | 1808 | 0.043048 | 1.362 | A04 | MICL0.01441026/RON
Build-In Floor | Mini Canal | MICL.01441026/ROV | 14 | 410 | 26 | 26 | 1587 | 1587 | 1587 | 0.037786 | 617 | 0.01469 | 1808 | 0.043048 | 1.362 | A04 | MICL0.01441026/ROV
Build-In Floor | Mini Canal | MICL.01441026/RSS | 14 | 410 | 26 | 26 | 1571 | 1571 | 1571 | 0.037405 | 611 | 0.014548 | 1789 | 0.042595 | 1.362 | A04 | MICL0.01441026/RSS
Build-In Floor | Mini Canal | MICL.01441026/SBL | 14 | 410 | 26 | 26 | 1636 | 1636 | 1636 | 0.038952 | 636 | 0.015143 | 1863 | 0.044357 | 1.362 | A04 | MICL0.01441026/SBL
Build-In Floor | Mini Canal | MICL.01441026/SBR | 14 | 410 | 26 | 26 | 1636 | 1636 | 1636 | 0.038952 | 636 | 0.015143 | 1863 | 0.044357 | 1.362 | A04 | MICL0.01441026/SBR
Build-In Floor | Mini Canal | MICL.01441026/SDB | 14 | 410 | 26 | 26 | 1636 | 1636 | 1636 | 0.038952 | 636 | 0.015143 | 1863 | 0.044357 | 1.362 | A04 | MICL0.01441026/SDB
Build-In Floor | Mini Canal | MICL.01441026/SNA | 14 | 410 | 26 | 26 | 1636 | 1636 | 1636 | 0.038952 | 636 | 0.015143 | 1863 | 0.044357 | 1.362 | A04 | MICL0.01441026/SNA
Build-In Floor | Mini Canal | MICL.01441026/SNC | 14 | 410 | 26 | 26 | 1636 | 1636 | 1636 | 0.038952 | 636 | 0.015143 | 1863 | 0.044357 | 1.362 | A04 | MICL0.01441026/SNC
Build-In Floor | Mini Canal | MICL.01441034/ANA | 14 | 410 | 34 | 34 | 1674 | 1674 | 1674 | 0.039857 | 651 | 0.0155 | 1907 | 0.045405 | 1.362 | A04 | MICL0.01441034/ANA
Build-In Floor | Mini Canal | MICL.01441034/DBL | 14 | 410 | 34 | 34 | 2165 | 2165 | 2165 | 0.051548 | 842 | 0.020048 | 2466 | 0.058714 | 1.362 | A04 | MICL0.01441034/DBL
Build-In Floor | Mini Canal | MICL.01441034/DBN | 14 | 410 | 34 | 34 | 2076 | 2076 | 2076 | 0.049429 | 808 | 0.019238 | 2365 | 0.05631 | 1.362 | A04 | MICL0.01441034/DBN
Build-In Floor | Mini Canal | MICL.01441034/DBR | 14 | 410 | 34 | 34 | 2165 | 2165 | 2165 | 0.051548 | 842 | 0.020048 | 2466 | 0.058714 | 1.362 | A04 | MICL0.01441034/DBR
Build-In Floor | Mini Canal | MICL.01441034/DBV | 14 | 410 | 34 | 34 | 2076 | 2076 | 2076 | 0.049429 | 808 | 0.019238 | 2365 | 0.05631 | 1.362 | A04 | MICL0.01441034/DBV
Build-In Floor | Mini Canal | MICL.01441034/DDB | 14 | 410 | 34 | 34 | 2165 | 2165 | 2165 | 0.051548 | 842 | 0.020048 | 2466 | 0.058714 | 1.362 | A04 | MICL0.01441034/DDB
Build-In Floor | Mini Canal | MICL.01441034/DMN | 14 | 410 | 34 | 34 | 2076 | 2076 | 2076 | 0.049429 | 808 | 0.019238 | 2365 | 0.05631 | 1.362 | A04 | MICL0.01441034/DMN
Build-In Floor | Mini Canal | MICL.01441034/DMV | 14 | 410 | 34 | 34 | 2076 | 2076 | 2076 | 0.049429 | 808 | 0.019238 | 2365 | 0.05631 | 1.362 | A04 | MICL0.01441034/DMV
Build-In Floor | Mini Canal | MICL.01441034/DNA | 14 | 410 | 34 | 34 | 2165 | 2165 | 2165 | 0.051548 | 842 | 0.020048 | 2466 | 0.058714 | 1.362 | A04 | MICL0.01441034/DNA
Build-In Floor | Mini Canal | MICL.01441034/DNC | 14 | 410 | 34 | 34 | 2165 | 2165 | 2165 | 0.051548 | 842 | 0.020048 | 2466 | 0.058714 | 1.362 | A04 | MICL0.01441034/DNC
Build-In Floor | Mini Canal | MICL.01441034/DON | 14 | 410 | 34 | 34 | 2076 | 2076 | 2076 | 0.049429 | 808 | 0.019238 | 2365 | 0.05631 | 1.362 | A04 | MICL0.01441034/DON
Build-In Floor | Mini Canal | MICL.01441034/DOV | 14 | 410 | 34 | 34 | 2076 | 2076 | 2076 | 0.049429 | 808 | 0.019238 | 2365 | 0.05631 | 1.362 | A04 | MICL0.01441034/DOV
Build-In Floor | Mini Canal | MICL.01441034/PNC | 14 | 410 | 34 | 34 | 1897 | 1897 | 1897 | 0.045167 | 738 | 0.017571 | 2161 | 0.051452 | 1.362 | A04 | MICL0.01441034/PNC
Build-In Floor | Mini Canal | MICL.01441034/RBL | 14 | 410 | 34 | 34 | 2232 | 2232 | 2232 | 0.053143 | 868 | 0.020667 | 2542 | 0.060524 | 1.362 | A04 | MICL0.01441034/RBL
Build-In Floor | Mini Canal | MICL.01441034/RBN | 14 | 410 | 34 | 34 | 2165 | 2165 | 2165 | 0.051548 | 842 | 0.020048 | 2466 | 0.058714 | 1.362 | A04 | MICL0.01441034/RBN
Build-In Floor | Mini Canal | MICL.01441034/RBR | 14 | 410 | 34 | 34 | 2232 | 2232 | 2232 | 0.053143 | 868 | 0.020667 | 2542 | 0.060524 | 1.362 | A04 | MICL0.01441034/RBR
Build-In Floor | Mini Canal | MICL.01441034/RBV | 14 | 410 | 34 | 34 | 2165 | 2165 | 2165 | 0.051548 | 842 | 0.020048 | 2466 | 0.058714 | 1.362 | A04 | MICL0.01441034/RBV
Build-In Floor | Mini Canal | MICL.01441034/RDB | 14 | 410 | 34 | 34 | 2232 | 2232 | 2232 | 0.053143 | 868 | 0.020667 | 2542 | 0.060524 | 1.362 | A04 | MICL0.01441034/RDB
Build-In Floor | Mini Canal | MICL.01441034/RMN | 14 | 410 | 34 | 34 | 2165 | 2165 | 2165 | 0.051548 | 842 | 0.020048 | 2466 | 0.058714 | 1.362 | A04 | MICL0.01441034/RMN
Build-In Floor | Mini Canal | MICL.01441034/RMV | 14 | 410 | 34 | 34 | 2165 | 2165 | 2165 | 0.051548 | 842 | 0.020048 | 2466 | 0.058714 | 1.362 | A04 | MICL0.01441034/RMV
Build-In Floor | Mini Canal | MICL.01441034/RNA | 14 | 410 | 34 | 34 | 2232 | 2232 | 2232 | 0.053143 | 868 | 0.020667 | 2542 | 0.060524 | 1.362 | A04 | MICL0.01441034/RNA
Build-In Floor | Mini Canal | MICL.01441034/RON | 14 | 410 | 34 | 34 | 2165 | 2165 | 2165 | 0.051548 | 842 | 0.020048 | 2466 | 0.058714 | 1.362 | A04 | MICL0.01441034/RON
Build-In Floor | Mini Canal | MICL.01441034/ROV | 14 | 410 | 34 | 34 | 2165 | 2165 | 2165 | 0.051548 | 842 | 0.020048 | 2466 | 0.058714 | 1.362 | A04 | MICL0.01441034/ROV
Build-In Floor | Mini Canal | MICL.01441034/RSS | 14 | 410 | 34 | 34 | 2143 | 2143 | 2143 | 0.051024 | 834 | 0.019857 | 2441 | 0.058119 | 1.362 | A04 | MICL0.01441034/RSS
Build-In Floor | Mini Canal | MICL.01441034/SBL | 14 | 410 | 34 | 34 | 2232 | 2232 | 2232 | 0.053143 | 868 | 0.020667 | 2542 | 0.060524 | 1.362 | A04 | MICL0.01441034/SBL
Build-In Floor | Mini Canal | MICL.01441034/SBR | 14 | 410 | 34 | 34 | 2232 | 2232 | 2232 | 0.053143 | 868 | 0.020667 | 2542 | 0.060524 | 1.362 | A04 | MICL0.01441034/SBR
Build-In Floor | Mini Canal | MICL.01441034/SDB | 14 | 410 | 34 | 34 | 2232 | 2232 | 2232 | 0.053143 | 868 | 0.020667 | 2542 | 0.060524 | 1.362 | A04 | MICL0.01441034/SDB
Build-In Floor | Mini Canal | MICL.01441034/SNA | 14 | 410 | 34 | 34 | 2232 | 2232 | 2232 | 0.053143 | 868 | 0.020667 | 2542 | 0.060524 | 1.362 | A04 | MICL0.01441034/SNA
Build-In Floor | Mini Canal | MICL.01441034/SNC | 14 | 410 | 34 | 34 | 2232 | 2232 | 2232 | 0.053143 | 868 | 0.020667 | 2542 | 0.060524 | 1.362 | A04 | MICL0.01441034/SNC
Build-In Floor | Mini Canal | MICL.01441042/ANA | 14 | 410 | 42 | 42 | 2256 | 2256 | 2256 | 0.053714 | 878 | 0.020905 | 2570 | 0.06119 | 1.362 | A04 | MICL0.01441042/ANA
Build-In Floor | Mini Canal | MICL.01441042/DBL | 14 | 410 | 42 | 42 | 2918 | 2918 | 2918 | 0.069476 | 1135 | 0.027024 | 3324 | 0.079143 | 1.362 | A04 | MICL0.01441042/DBL
Build-In Floor | Mini Canal | MICL.01441042/DBN | 14 | 410 | 42 | 42 | 2797 | 2797 | 2797 | 0.066595 | 1088 | 0.025905 | 3186 | 0.075857 | 1.362 | A04 | MICL0.01441042/DBN
Build-In Floor | Mini Canal | MICL.01441042/DBR | 14 | 410 | 42 | 42 | 2918 | 2918 | 2918 | 0.069476 | 1135 | 0.027024 | 3324 | 0.079143 | 1.362 | A04 | MICL0.01441042/DBR
Build-In Floor | Mini Canal | MICL.01441042/DBV | 14 | 410 | 42 | 42 | 2797 | 2797 | 2797 | 0.066595 | 1088 | 0.025905 | 3186 | 0.075857 | 1.362 | A04 | MICL0.01441042/DBV
Build-In Floor | Mini Canal | MICL.01441042/DDB | 14 | 410 | 42 | 42 | 2918 | 2918 | 2918 | 0.069476 | 1135 | 0.027024 | 3324 | 0.079143 | 1.362 | A04 | MICL0.01441042/DDB
Build-In Floor | Mini Canal | MICL.01441042/DMN | 14 | 410 | 42 | 42 | 2797 | 2797 | 2797 | 0.066595 | 1088 | 0.025905 | 3186 | 0.075857 | 1.362 | A04 | MICL0.01441042/DMN
Build-In Floor | Mini Canal | MICL.01441042/DMV | 14 | 410 | 42 | 42 | 2797 | 2797 | 2797 | 0.066595 | 1088 | 0.025905 | 3186 | 0.075857 | 1.362 | A04 | MICL0.01441042/DMV
Build-In Floor | Mini Canal | MICL.01441042/DNA | 14 | 410 | 42 | 42 | 2918 | 2918 | 2918 | 0.069476 | 1135 | 0.027024 | 3324 | 0.079143 | 1.362 | A04 | MICL0.01441042/DNA
Build-In Floor | Mini Canal | MICL.01441042/DNC | 14 | 410 | 42 | 42 | 2918 | 2918 | 2918 | 0.069476 | 1135 | 0.027024 | 3324 | 0.079143 | 1.362 | A04 | MICL0.01441042/DNC
Build-In Floor | Mini Canal | MICL.01441042/DON | 14 | 410 | 42 | 42 | 2797 | 2797 | 2797 | 0.066595 | 1088 | 0.025905 | 3186 | 0.075857 | 1.362 | A04 | MICL0.01441042/DON
Build-In Floor | Mini Canal | MICL.01441042/DOV | 14 | 410 | 42 | 42 | 2797 | 2797 | 2797 | 0.066595 | 1088 | 0.025905 | 3186 | 0.075857 | 1.362 | A04 | MICL0.01441042/DOV
Build-In Floor | Mini Canal | MICL.01441042/PNC | 14 | 410 | 42 | 42 | 2557 | 2557 | 2557 | 0.060881 | 995 | 0.02369 | 2912 | 0.069333 | 1.362 | A04 | MICL0.01441042/PNC
Build-In Floor | Mini Canal | MICL.01441042/RBL | 14 | 410 | 42 | 42 | 3008 | 3008 | 3008 | 0.071619 | 1170 | 0.027857 | 3426 | 0.081571 | 1.362 | A04 | MICL0.01441042/RBL
Build-In Floor | Mini Canal | MICL.01441042/RBN | 14 | 410 | 42 | 42 | 2918 | 2918 | 2918 | 0.069476 | 1135 | 0.027024 | 3324 | 0.079143 | 1.362 | A04 | MICL0.01441042/RBN
Build-In Floor | Mini Canal | MICL.01441042/RBR | 14 | 410 | 42 | 42 | 3008 | 3008 | 3008 | 0.071619 | 1170 | 0.027857 | 3426 | 0.081571 | 1.362 | A04 | MICL0.01441042/RBR
Build-In Floor | Mini Canal | MICL.01441042/RBV | 14 | 410 | 42 | 42 | 2918 | 2918 | 2918 | 0.069476 | 1135 | 0.027024 | 3324 | 0.079143 | 1.362 | A04 | MICL0.01441042/RBV
Build-In Floor | Mini Canal | MICL.01441042/RDB | 14 | 410 | 42 | 42 | 3008 | 3008 | 3008 | 0.071619 | 1170 | 0.027857 | 3426 | 0.081571 | 1.362 | A04 | MICL0.01441042/RDB
Build-In Floor | Mini Canal | MICL.01441042/RMN | 14 | 410 | 42 | 42 | 2918 | 2918 | 2918 | 0.069476 | 1135 | 0.027024 | 3324 | 0.079143 | 1.362 | A04 | MICL0.01441042/RMN
Build-In Floor | Mini Canal | MICL.01441042/RMV | 14 | 410 | 42 | 42 | 2918 | 2918 | 2918 | 0.069476 | 1135 | 0.027024 | 3324 | 0.079143 | 1.362 | A04 | MICL0.01441042/RMV
Build-In Floor | Mini Canal | MICL.01441042/RNA | 14 | 410 | 42 | 42 | 3008 | 3008 | 3008 | 0.071619 | 1170 | 0.027857 | 3426 | 0.081571 | 1.362 | A04 | MICL0.01441042/RNA
Build-In Floor | Mini Canal | MICL.01441042/RON | 14 | 410 | 42 | 42 | 2918 | 2918 | 2918 | 0.069476 | 1135 | 0.027024 | 3324 | 0.079143 | 1.362 | A04 | MICL0.01441042/RON
Build-In Floor | Mini Canal | MICL.01441042/ROV | 14 | 410 | 42 | 42 | 2918 | 2918 | 2918 | 0.069476 | 1135 | 0.027024 | 3324 | 0.079143 | 1.362 | A04 | MICL0.01441042/ROV
Build-In Floor | Mini Canal | MICL.01441042/RSS | 14 | 410 | 42 | 42 | 2888 | 2888 | 2888 | 0.068762 | 1123 | 0.026738 | 3289 | 0.07831 | 1.362 | A04 | MICL0.01441042/RSS
Build-In Floor | Mini Canal | MICL.01441042/SBL | 14 | 410 | 42 | 42 | 3008 | 3008 | 3008 | 0.071619 | 1170 | 0.027857 | 3426 | 0.081571 | 1.362 | A04 | MICL0.01441042/SBL
Build-In Floor | Mini Canal | MICL.01441042/SBR | 14 | 410 | 42 | 42 | 3008 | 3008 | 3008 | 0.071619 | 1170 | 0.027857 | 3426 | 0.081571 | 1.362 | A04 | MICL0.01441042/SBR
Build-In Floor | Mini Canal | MICL.01441042/SDB | 14 | 410 | 42 | 42 | 3008 | 3008 | 3008 | 0.071619 | 1170 | 0.027857 | 3426 | 0.081571 | 1.362 | A04 | MICL0.01441042/SDB
Build-In Floor | Mini Canal | MICL.01441042/SNA | 14 | 410 | 42 | 42 | 3008 | 3008 | 3008 | 0.071619 | 1170 | 0.027857 | 3426 | 0.081571 | 1.362 | A04 | MICL0.01441042/SNA
Build-In Floor | Mini Canal | MICL.01441042/SNC | 14 | 410 | 42 | 42 | 3008 | 3008 | 3008 | 0.071619 | 1170 | 0.027857 | 3426 | 0.081571 | 1.362 | A04 | MICL0.01441042/SNC
Build-In Floor | Mini Canal | MICL.01443014/ANA | 14 | 430 | 14 | 14 | 744 | 744 | 744 | 0.017714 | 289 | 0.006881 | 847 | 0.020167 | 1.362 | A04 | MICL0.01443014/ANA
Build-In Floor | Mini Canal | MICL.01443014/DBL | 14 | 430 | 14 | 14 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01443014/DBL
Build-In Floor | Mini Canal | MICL.01443014/DBN | 14 | 430 | 14 | 14 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.01443014/DBN
Build-In Floor | Mini Canal | MICL.01443014/DBR | 14 | 430 | 14 | 14 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01443014/DBR
Build-In Floor | Mini Canal | MICL.01443014/DBV | 14 | 430 | 14 | 14 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.01443014/DBV
Build-In Floor | Mini Canal | MICL.01443014/DDB | 14 | 430 | 14 | 14 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01443014/DDB
Build-In Floor | Mini Canal | MICL.01443014/DMN | 14 | 430 | 14 | 14 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.01443014/DMN
Build-In Floor | Mini Canal | MICL.01443014/DMV | 14 | 430 | 14 | 14 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.01443014/DMV
Build-In Floor | Mini Canal | MICL.01443014/DNA | 14 | 430 | 14 | 14 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01443014/DNA
Build-In Floor | Mini Canal | MICL.01443014/DNC | 14 | 430 | 14 | 14 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01443014/DNC
Build-In Floor | Mini Canal | MICL.01443014/DON | 14 | 430 | 14 | 14 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.01443014/DON
Build-In Floor | Mini Canal | MICL.01443014/DOV | 14 | 430 | 14 | 14 | 923 | 923 | 923 | 0.021976 | 359 | 0.0085476 | 1051 | 0.025024 | 1.362 | A04 | MICL0.01443014/DOV
Build-In Floor | Mini Canal | MICL.01443014/RBL | 14 | 430 | 14 | 14 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.01443014/RBL
Build-In Floor | Mini Canal | MICL.01443014/RBN | 14 | 430 | 14 | 14 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01443014/RBN
Build-In Floor | Mini Canal | MICL.01443014/RBR | 14 | 430 | 14 | 14 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.01443014/RBR
Build-In Floor | Mini Canal | MICL.01443014/RBV | 14 | 430 | 14 | 14 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01443014/RBV
Build-In Floor | Mini Canal | MICL.01443014/RDB | 14 | 430 | 14 | 14 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.01443014/RDB
Build-In Floor | Mini Canal | MICL.01443014/RMN | 14 | 430 | 14 | 14 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01443014/RMN
Build-In Floor | Mini Canal | MICL.01443014/RMV | 14 | 430 | 14 | 14 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01443014/RMV
Build-In Floor | Mini Canal | MICL.01443014/RNA | 14 | 430 | 14 | 14 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.01443014/RNA
Build-In Floor | Mini Canal | MICL.01443014/RON | 14 | 430 | 14 | 14 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01443014/RON
Build-In Floor | Mini Canal | MICL.01443014/ROV | 14 | 430 | 14 | 14 | 962 | 962 | 962 | 0.022905 | 374 | 0.0089048 | 1096 | 0.026095 | 1.362 | A04 | MICL0.01443014/ROV
Build-In Floor | Mini Canal | MICL.01443014/RSS | 14 | 430 | 14 | 14 | 952 | 952 | 952 | 0.022667 | 370 | 0.0088095 | 1084 | 0.02581 | 1.362 | A04 | MICL0.01443014/RSS
Build-In Floor | Mini Canal | MICL.01443014/SBL | 14 | 430 | 14 | 14 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.01443014/SBL
Build-In Floor | Mini Canal | MICL.01443014/SBR | 14 | 430 | 14 | 14 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.01443014/SBR
Build-In Floor | Mini Canal | MICL.01443014/SDB | 14 | 430 | 14 | 14 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.01443014/SDB
Build-In Floor | Mini Canal | MICL.01443014/SNA | 14 | 430 | 14 | 14 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.01443014/SNA
Build-In Floor | Mini Canal | MICL.01443014/SNC | 14 | 430 | 14 | 14 | 992 | 992 | 992 | 0.023619 | 386 | 0.0091905 | 1130 | 0.026905 | 1.362 | A04 | MICL0.01443014/SNC
Build-In Floor | Mini Canal | MICL.01443026/ANA | 14 | 430 | 26 | 26 | 1292 | 1292 | 1292 | 0.030762 | 503 | 0.011976 | 1472 | 0.035048 | 1.362 | A04 | MICL0.01443026/ANA
Build-In Floor | Mini Canal | MICL.01443026/DBL | 14 | 430 | 26 | 26 | 1670 | 1670 | 1670 | 0.039762 | 650 | 0.015476 | 1902 | 0.045286 | 1.362 | A04 | MICL0.01443026/DBL
Build-In Floor | Mini Canal | MICL.01443026/DBN | 14 | 430 | 26 | 26 | 1601 | 1601 | 1601 | 0.038119 | 623 | 0.014833 | 1824 | 0.043429 | 1.362 | A04 | MICL0.01443026/DBN
Build-In Floor | Mini Canal | MICL.01443026/DBR | 14 | 430 | 26 | 26 | 1670 | 1670 | 1670 | 0.039762 | 650 | 0.015476 | 1902 | 0.045286 | 1.362 | A04 | MICL0.01443026/DBR
Build-In Floor | Mini Canal | MICL.01443026/DBV | 14 | 430 | 26 | 26 | 1601 | 1601 | 1601 | 0.038119 | 623 | 0.014833 | 1824 | 0.043429 | 1.362 | A04 | MICL0.01443026/DBV
Build-In Floor | Mini Canal | MICL.01443026/DDB | 14 | 430 | 26 | 26 | 1670 | 1670 | 1670 | 0.039762 | 650 | 0.015476 | 1902 | 0.045286 | 1.362 | A04 | MICL0.01443026/DDB
Build-In Floor | Mini Canal | MICL.01443026/DMN | 14 | 430 | 26 | 26 | 1601 | 1601 | 1601 | 0.038119 | 623 | 0.014833 | 1824 | 0.043429 | 1.362 | A04 | MICL0.01443026/DMN
Build-In Floor | Mini Canal | MICL.01443026/DMV | 14 | 430 | 26 | 26 | 1601 | 1601 | 1601 | 0.038119 | 623 | 0.014833 | 1824 | 0.043429 | 1.362 | A04 | MICL0.01443026/DMV
Build-In Floor | Mini Canal | MICL.01443026/DNA | 14 | 430 | 26 | 26 | 1670 | 1670 | 1670 | 0.039762 | 650 | 0.015476 | 1902 | 0.045286 | 1.362 | A04 | MICL0.01443026/DNA
Build-In Floor | Mini Canal | MICL.01443026/DNC | 14 | 430 | 26 | 26 | 1670 | 1670 | 1670 | 0.039762 | 650 | 0.015476 | 1902 | 0.045286 | 1.362 | A04 | MICL0.01443026/DNC
Build-In Floor | Mini Canal | MICL.01443026/DON | 14 | 430 | 26 | 26 | 1601 | 1601 | 1601 | 0.038119 | 623 | 0.014833 | 1824 | 0.043429 | 1.362 | A04 | MICL0.01443026/DON
Build-In Floor | Mini Canal | MICL.01443026/DOV | 14 | 430 | 26 | 26 | 1601 | 1601 | 1601 | 0.038119 | 623 | 0.014833 | 1824 | 0.043429 | 1.362 | A04 | MICL0.01443026/DOV
Build-In Floor | Mini Canal | MICL.01443026/PNC | 14 | 430 | 26 | 26 | 1464 | 1464 | 1464 | 0.034857 | 569 | 0.013548 | 1667 | 0.03969 | 1.362 | A04 | MICL0.01443026/PNC
Build-In Floor | Mini Canal | MICL.01443026/RBL | 14 | 430 | 26 | 26 | 1722 | 1722 | 1722 | 0.041 | 670 | 0.015952 | 1961 | 0.04669 | 1.362 | A04 | MICL0.01443026/RBL
Build-In Floor | Mini Canal | MICL.01443026/RBN | 14 | 430 | 26 | 26 | 1670 | 1670 | 1670 | 0.039762 | 650 | 0.015476 | 1902 | 0.045286 | 1.362 | A04 | MICL0.01443026/RBN
Build-In Floor | Mini Canal | MICL.01443026/RBR | 14 | 430 | 26 | 26 | 1722 | 1722 | 1722 | 0.041 | 670 | 0.015952 | 1961 | 0.04669 | 1.362 | A04 | MICL0.01443026/RBR
Build-In Floor | Mini Canal | MICL.01443026/RBV | 14 | 430 | 26 | 26 | 1670 | 1670 | 1670 | 0.039762 | 650 | 0.015476 | 1902 | 0.045286 | 1.362 | A04 | MICL0.01443026/RBV
Build-In Floor | Mini Canal | MICL.01443026/RDB | 14 | 430 | 26 | 26 | 1722 | 1722 | 1722 | 0.041 | 670 | 0.015952 | 1961 | 0.04669 | 1.362 | A04 | MICL0.01443026/RDB
Build-In Floor | Mini Canal | MICL.01443026/RMN | 14 | 430 | 26 | 26 | 1670 | 1670 | 1670 | 0.039762 | 650 | 0.015476 | 1902 | 0.045286 | 1.362 | A04 | MICL0.01443026/RMN
Build-In Floor | Mini Canal | MICL.01443026/RMV | 14 | 430 | 26 | 26 | 1670 | 1670 | 1670 | 0.039762 | 650 | 0.015476 | 1902 | 0.045286 | 1.362 | A04 | MICL0.01443026/RMV
Build-In Floor | Mini Canal | MICL.01443026/RNA | 14 | 430 | 26 | 26 | 1722 | 1722 | 1722 | 0.041 | 670 | 0.015952 | 1961 | 0.04669 | 1.362 | A04 | MICL0.01443026/RNA
Build-In Floor | Mini Canal | MICL.01443026/RON | 14 | 430 | 26 | 26 | 1670 | 1670 | 1670 | 0.039762 | 650 | 0.015476 | 1902 | 0.045286 | 1.362 | A04 | MICL0.01443026/RON
Build-In Floor | Mini Canal | MICL.01443026/ROV | 14 | 430 | 26 | 26 | 1670 | 1670 | 1670 | 0.039762 | 650 | 0.015476 | 1902 | 0.045286 | 1.362 | A04 | MICL0.01443026/ROV
Build-In Floor | Mini Canal | MICL.01443026/RSS | 14 | 430 | 26 | 26 | 1653 | 1653 | 1653 | 0.039357 | 643 | 0.01531 | 1883 | 0.044833 | 1.362 | A04 | MICL0.01443026/RSS
Build-In Floor | Mini Canal | MICL.01443026/SBL | 14 | 430 | 26 | 26 | 1722 | 1722 | 1722 | 0.041 | 670 | 0.015952 | 1961 | 0.04669 | 1.362 | A04 | MICL0.01443026/SBL
Build-In Floor | Mini Canal | MICL.01443026/SBR | 14 | 430 | 26 | 26 | 1722 | 1722 | 1722 | 0.041 | 670 | 0.015952 | 1961 | 0.04669 | 1.362 | A04 | MICL0.01443026/SBR
Build-In Floor | Mini Canal | MICL.01443026/SDB | 14 | 430 | 26 | 26 | 1722 | 1722 | 1722 | 0.041 | 670 | 0.015952 | 1961 | 0.04669 | 1.362 | A04 | MICL0.01443026/SDB
Build-In Floor | Mini Canal | MICL.01443026/SNA | 14 | 430 | 26 | 26 | 1722 | 1722 | 1722 | 0.041 | 670 | 0.015952 | 1961 | 0.04669 | 1.362 | A04 | MICL0.01443026/SNA
Build-In Floor | Mini Canal | MICL.01443026/SNC | 14 | 430 | 26 | 26 | 1722 | 1722 | 1722 | 0.041 | 670 | 0.015952 | 1961 | 0.04669 | 1.362 | A04 | MICL0.01443026/SNC
Build-In Floor | Mini Canal | MICL.01443034/ANA | 14 | 430 | 34 | 34 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01443034/ANA
Build-In Floor | Mini Canal | MICL.01443034/DBL | 14 | 430 | 34 | 34 | 2279 | 2279 | 2279 | 0.054262 | 887 | 0.021119 | 2596 | 0.06181 | 1.362 | A04 | MICL0.01443034/DBL
Build-In Floor | Mini Canal | MICL.01443034/DBN | 14 | 430 | 34 | 34 | 2185 | 2185 | 2185 | 0.052024 | 850 | 0.020238 | 2489 | 0.059262 | 1.362 | A04 | MICL0.01443034/DBN
Build-In Floor | Mini Canal | MICL.01443034/DBR | 14 | 430 | 34 | 34 | 2279 | 2279 | 2279 | 0.054262 | 887 | 0.021119 | 2596 | 0.06181 | 1.362 | A04 | MICL0.01443034/DBR
Build-In Floor | Mini Canal | MICL.01443034/DBV | 14 | 430 | 34 | 34 | 2185 | 2185 | 2185 | 0.052024 | 850 | 0.020238 | 2489 | 0.059262 | 1.362 | A04 | MICL0.01443034/DBV
Build-In Floor | Mini Canal | MICL.01443034/DDB | 14 | 430 | 34 | 34 | 2279 | 2279 | 2279 | 0.054262 | 887 | 0.021119 | 2596 | 0.06181 | 1.362 | A04 | MICL0.01443034/DDB
Build-In Floor | Mini Canal | MICL.01443034/DMN | 14 | 430 | 34 | 34 | 2185 | 2185 | 2185 | 0.052024 | 850 | 0.020238 | 2489 | 0.059262 | 1.362 | A04 | MICL0.01443034/DMN
Build-In Floor | Mini Canal | MICL.01443034/DMV | 14 | 430 | 34 | 34 | 2185 | 2185 | 2185 | 0.052024 | 850 | 0.020238 | 2489 | 0.059262 | 1.362 | A04 | MICL0.01443034/DMV
Build-In Floor | Mini Canal | MICL.01443034/DNA | 14 | 430 | 34 | 34 | 2279 | 2279 | 2279 | 0.054262 | 887 | 0.021119 | 2596 | 0.06181 | 1.362 | A04 | MICL0.01443034/DNA
Build-In Floor | Mini Canal | MICL.01443034/DNC | 14 | 430 | 34 | 34 | 2279 | 2279 | 2279 | 0.054262 | 887 | 0.021119 | 2596 | 0.06181 | 1.362 | A04 | MICL0.01443034/DNC
Build-In Floor | Mini Canal | MICL.01443034/DON | 14 | 430 | 34 | 34 | 2185 | 2185 | 2185 | 0.052024 | 850 | 0.020238 | 2489 | 0.059262 | 1.362 | A04 | MICL0.01443034/DON
Build-In Floor | Mini Canal | MICL.01443034/DOV | 14 | 430 | 34 | 34 | 2185 | 2185 | 2185 | 0.052024 | 850 | 0.020238 | 2489 | 0.059262 | 1.362 | A04 | MICL0.01443034/DOV
Build-In Floor | Mini Canal | MICL.01443034/PNC | 14 | 430 | 34 | 34 | 1997 | 1997 | 1997 | 0.047548 | 777 | 0.0185 | 2275 | 0.054167 | 1.362 | A04 | MICL0.01443034/PNC
Build-In Floor | Mini Canal | MICL.01443034/RBL | 14 | 430 | 34 | 34 | 2349 | 2349 | 2349 | 0.055929 | 914 | 0.021762 | 2676 | 0.063714 | 1.362 | A04 | MICL0.01443034/RBL
Build-In Floor | Mini Canal | MICL.01443034/RBN | 14 | 430 | 34 | 34 | 2279 | 2279 | 2279 | 0.054262 | 887 | 0.021119 | 2596 | 0.06181 | 1.362 | A04 | MICL0.01443034/RBN
Build-In Floor | Mini Canal | MICL.01443034/RBR | 14 | 430 | 34 | 34 | 2349 | 2349 | 2349 | 0.055929 | 914 | 0.021762 | 2676 | 0.063714 | 1.362 | A04 | MICL0.01443034/RBR
Build-In Floor | Mini Canal | MICL.01443034/RBV | 14 | 430 | 34 | 34 | 2279 | 2279 | 2279 | 0.054262 | 887 | 0.021119 | 2596 | 0.06181 | 1.362 | A04 | MICL0.01443034/RBV
Build-In Floor | Mini Canal | MICL.01443034/RDB | 14 | 430 | 34 | 34 | 2349 | 2349 | 2349 | 0.055929 | 914 | 0.021762 | 2676 | 0.063714 | 1.362 | A04 | MICL0.01443034/RDB
Build-In Floor | Mini Canal | MICL.01443034/RMN | 14 | 430 | 34 | 34 | 2279 | 2279 | 2279 | 0.054262 | 887 | 0.021119 | 2596 | 0.06181 | 1.362 | A04 | MICL0.01443034/RMN
Build-In Floor | Mini Canal | MICL.01443034/RMV | 14 | 430 | 34 | 34 | 2279 | 2279 | 2279 | 0.054262 | 887 | 0.021119 | 2596 | 0.06181 | 1.362 | A04 | MICL0.01443034/RMV
Build-In Floor | Mini Canal | MICL.01443034/RNA | 14 | 430 | 34 | 34 | 2349 | 2349 | 2349 | 0.055929 | 914 | 0.021762 | 2676 | 0.063714 | 1.362 | A04 | MICL0.01443034/RNA
Build-In Floor | Mini Canal | MICL.01443034/RON | 14 | 430 | 34 | 34 | 2279 | 2279 | 2279 | 0.054262 | 887 | 0.021119 | 2596 | 0.06181 | 1.362 | A04 | MICL0.01443034/RON
Build-In Floor | Mini Canal | MICL.01443034/ROV | 14 | 430 | 34 | 34 | 2279 | 2279 | 2279 | 0.054262 | 887 | 0.021119 | 2596 | 0.06181 | 1.362 | A04 | MICL0.01443034/ROV
Build-In Floor | Mini Canal | MICL.01443034/RSS | 14 | 430 | 34 | 34 | 2255 | 2255 | 2255 | 0.05369 | 877 | 0.020881 | 2568 | 0.061143 | 1.362 | A04 | MICL0.01443034/RSS
Build-In Floor | Mini Canal | MICL.01443034/SBL | 14 | 430 | 34 | 34 | 2349 | 2349 | 2349 | 0.055929 | 914 | 0.021762 | 2676 | 0.063714 | 1.362 | A04 | MICL0.01443034/SBL
Build-In Floor | Mini Canal | MICL.01443034/SBR | 14 | 430 | 34 | 34 | 2349 | 2349 | 2349 | 0.055929 | 914 | 0.021762 | 2676 | 0.063714 | 1.362 | A04 | MICL0.01443034/SBR
Build-In Floor | Mini Canal | MICL.01443034/SDB | 14 | 430 | 34 | 34 | 2349 | 2349 | 2349 | 0.055929 | 914 | 0.021762 | 2676 | 0.063714 | 1.362 | A04 | MICL0.01443034/SDB
Build-In Floor | Mini Canal | MICL.01443034/SNA | 14 | 430 | 34 | 34 | 2349 | 2349 | 2349 | 0.055929 | 914 | 0.021762 | 2676 | 0.063714 | 1.362 | A04 | MICL0.01443034/SNA
Build-In Floor | Mini Canal | MICL.01443034/SNC | 14 | 430 | 34 | 34 | 2349 | 2349 | 2349 | 0.055929 | 914 | 0.021762 | 2676 | 0.063714 | 1.362 | A04 | MICL0.01443034/SNC
Build-In Floor | Mini Canal | MICL.01443042/ANA | 14 | 430 | 42 | 42 | 2375 | 2375 | 2375 | 0.056548 | 924 | 0.022 | 2705 | 0.064405 | 1.362 | A04 | MICL0.01443042/ANA
Build-In Floor | Mini Canal | MICL.01443042/DBL | 14 | 430 | 42 | 42 | 3072 | 3072 | 3072 | 0.073143 | 1195 | 0.028452 | 3499 | 0.08331 | 1.362 | A04 | MICL0.01443042/DBL
Build-In Floor | Mini Canal | MICL.01443042/DBN | 14 | 430 | 42 | 42 | 2945 | 2945 | 2945 | 0.070119 | 1146 | 0.027286 | 3354 | 0.079857 | 1.362 | A04 | MICL0.01443042/DBN
Build-In Floor | Mini Canal | MICL.01443042/DBR | 14 | 430 | 42 | 42 | 3072 | 3072 | 3072 | 0.073143 | 1195 | 0.028452 | 3499 | 0.08331 | 1.362 | A04 | MICL0.01443042/DBR
Build-In Floor | Mini Canal | MICL.01443042/DBV | 14 | 430 | 42 | 42 | 2945 | 2945 | 2945 | 0.070119 | 1146 | 0.027286 | 3354 | 0.079857 | 1.362 | A04 | MICL0.01443042/DBV
Build-In Floor | Mini Canal | MICL.01443042/DDB | 14 | 430 | 42 | 42 | 3072 | 3072 | 3072 | 0.073143 | 1195 | 0.028452 | 3499 | 0.08331 | 1.362 | A04 | MICL0.01443042/DDB
Build-In Floor | Mini Canal | MICL.01443042/DMN | 14 | 430 | 42 | 42 | 2945 | 2945 | 2945 | 0.070119 | 1146 | 0.027286 | 3354 | 0.079857 | 1.362 | A04 | MICL0.01443042/DMN
Build-In Floor | Mini Canal | MICL.01443042/DMV | 14 | 430 | 42 | 42 | 2945 | 2945 | 2945 | 0.070119 | 1146 | 0.027286 | 3354 | 0.079857 | 1.362 | A04 | MICL0.01443042/DMV
Build-In Floor | Mini Canal | MICL.01443042/DNA | 14 | 430 | 42 | 42 | 3072 | 3072 | 3072 | 0.073143 | 1195 | 0.028452 | 3499 | 0.08331 | 1.362 | A04 | MICL0.01443042/DNA
Build-In Floor | Mini Canal | MICL.01443042/DNC | 14 | 430 | 42 | 42 | 3072 | 3072 | 3072 | 0.073143 | 1195 | 0.028452 | 3499 | 0.08331 | 1.362 | A04 | MICL0.01443042/DNC
Build-In Floor | Mini Canal | MICL.01443042/DON | 14 | 430 | 42 | 42 | 2945 | 2945 | 2945 | 0.070119 | 1146 | 0.027286 | 3354 | 0.079857 | 1.362 | A04 | MICL0.01443042/DON
Build-In Floor | Mini Canal | MICL.01443042/DOV | 14 | 430 | 42 | 42 | 2945 | 2945 | 2945 | 0.070119 | 1146 | 0.027286 | 3354 | 0.079857 | 1.362 | A04 | MICL0.01443042/DOV
Build-In Floor | Mini Canal | MICL.01443042/PNC | 14 | 430 | 42 | 42 | 2692 | 2692 | 2692 | 0.064095 | 1047 | 0.024929 | 3066 | 0.073 | 1.362 | A04 | MICL0.01443042/PNC
Build-In Floor | Mini Canal | MICL.01443042/RBL | 14 | 430 | 42 | 42 | 3167 | 3167 | 3167 | 0.075405 | 1232 | 0.029333 | 3607 | 0.085881 | 1.362 | A04 | MICL0.01443042/RBL
Build-In Floor | Mini Canal | MICL.01443042/RBN | 14 | 430 | 42 | 42 | 3072 | 3072 | 3072 | 0.073143 | 1195 | 0.028452 | 3499 | 0.08331 | 1.362 | A04 | MICL0.01443042/RBN
Build-In Floor | Mini Canal | MICL.01443042/RBR | 14 | 430 | 42 | 42 | 3167 | 3167 | 3167 | 0.075405 | 1232 | 0.029333 | 3607 | 0.085881 | 1.362 | A04 | MICL0.01443042/RBR
Build-In Floor | Mini Canal | MICL.01443042/RBV | 14 | 430 | 42 | 42 | 3072 | 3072 | 3072 | 0.073143 | 1195 | 0.028452 | 3499 | 0.08331 | 1.362 | A04 | MICL0.01443042/RBV
Build-In Floor | Mini Canal | MICL.01443042/RDB | 14 | 430 | 42 | 42 | 3167 | 3167 | 3167 | 0.075405 | 1232 | 0.029333 | 3607 | 0.085881 | 1.362 | A04 | MICL0.01443042/RDB
Build-In Floor | Mini Canal | MICL.01443042/RMN | 14 | 430 | 42 | 42 | 3072 | 3072 | 3072 | 0.073143 | 1195 | 0.028452 | 3499 | 0.08331 | 1.362 | A04 | MICL0.01443042/RMN
Build-In Floor | Mini Canal | MICL.01443042/RMV | 14 | 430 | 42 | 42 | 3072 | 3072 | 3072 | 0.073143 | 1195 | 0.028452 | 3499 | 0.08331 | 1.362 | A04 | MICL0.01443042/RMV
Build-In Floor | Mini Canal | MICL.01443042/RNA | 14 | 430 | 42 | 42 | 3167 | 3167 | 3167 | 0.075405 | 1232 | 0.029333 | 3607 | 0.085881 | 1.362 | A04 | MICL0.01443042/RNA
Build-In Floor | Mini Canal | MICL.01443042/RON | 14 | 430 | 42 | 42 | 3072 | 3072 | 3072 | 0.073143 | 1195 | 0.028452 | 3499 | 0.08331 | 1.362 | A04 | MICL0.01443042/RON
Build-In Floor | Mini Canal | MICL.01443042/ROV | 14 | 430 | 42 | 42 | 3072 | 3072 | 3072 | 0.073143 | 1195 | 0.028452 | 3499 | 0.08331 | 1.362 | A04 | MICL0.01443042/ROV
Build-In Floor | Mini Canal | MICL.01443042/RSS | 14 | 430 | 42 | 42 | 3040 | 3040 | 3040 | 0.072381 | 1183 | 0.028167 | 3463 | 0.082452 | 1.362 | A04 | MICL0.01443042/RSS
Build-In Floor | Mini Canal | MICL.01443042/SBL | 14 | 430 | 42 | 42 | 3167 | 3167 | 3167 | 0.075405 | 1232 | 0.029333 | 3607 | 0.085881 | 1.362 | A04 | MICL0.01443042/SBL
Build-In Floor | Mini Canal | MICL.01443042/SBR | 14 | 430 | 42 | 42 | 3167 | 3167 | 3167 | 0.075405 | 1232 | 0.029333 | 3607 | 0.085881 | 1.362 | A04 | MICL0.01443042/SBR
Build-In Floor | Mini Canal | MICL.01443042/SDB | 14 | 430 | 42 | 42 | 3167 | 3167 | 3167 | 0.075405 | 1232 | 0.029333 | 3607 | 0.085881 | 1.362 | A04 | MICL0.01443042/SDB
Build-In Floor | Mini Canal | MICL.01443042/SNA | 14 | 430 | 42 | 42 | 3167 | 3167 | 3167 | 0.075405 | 1232 | 0.029333 | 3607 | 0.085881 | 1.362 | A04 | MICL0.01443042/SNA
Build-In Floor | Mini Canal | MICL.01443042/SNC | 14 | 430 | 42 | 42 | 3167 | 3167 | 3167 | 0.075405 | 1232 | 0.029333 | 3607 | 0.085881 | 1.362 | A04 | MICL0.01443042/SNC
Build-In Floor | Mini Canal | MICL.01445014/ANA | 14 | 450 | 14 | 14 | 782 | 782 | 782 | 0.018619 | 304 | 0.0072381 | 891 | 0.021214 | 1.362 | A04 | MICL0.01445014/ANA
Build-In Floor | Mini Canal | MICL.01445014/DBL | 14 | 450 | 14 | 14 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01445014/DBL
Build-In Floor | Mini Canal | MICL.01445014/DBN | 14 | 450 | 14 | 14 | 969 | 969 | 969 | 0.023071 | 377 | 0.0089762 | 1104 | 0.026286 | 1.362 | A04 | MICL0.01445014/DBN
Build-In Floor | Mini Canal | MICL.01445014/DBR | 14 | 450 | 14 | 14 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01445014/DBR
Build-In Floor | Mini Canal | MICL.01445014/DBV | 14 | 450 | 14 | 14 | 969 | 969 | 969 | 0.023071 | 377 | 0.0089762 | 1104 | 0.026286 | 1.362 | A04 | MICL0.01445014/DBV
Build-In Floor | Mini Canal | MICL.01445014/DDB | 14 | 450 | 14 | 14 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01445014/DDB
Build-In Floor | Mini Canal | MICL.01445014/DMN | 14 | 450 | 14 | 14 | 969 | 969 | 969 | 0.023071 | 377 | 0.0089762 | 1104 | 0.026286 | 1.362 | A04 | MICL0.01445014/DMN
Build-In Floor | Mini Canal | MICL.01445014/DMV | 14 | 450 | 14 | 14 | 969 | 969 | 969 | 0.023071 | 377 | 0.0089762 | 1104 | 0.026286 | 1.362 | A04 | MICL0.01445014/DMV
Build-In Floor | Mini Canal | MICL.01445014/DNA | 14 | 450 | 14 | 14 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01445014/DNA
Build-In Floor | Mini Canal | MICL.01445014/DNC | 14 | 450 | 14 | 14 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01445014/DNC
Build-In Floor | Mini Canal | MICL.01445014/DON | 14 | 450 | 14 | 14 | 969 | 969 | 969 | 0.023071 | 377 | 0.0089762 | 1104 | 0.026286 | 1.362 | A04 | MICL0.01445014/DON
Build-In Floor | Mini Canal | MICL.01445014/DOV | 14 | 450 | 14 | 14 | 969 | 969 | 969 | 0.023071 | 377 | 0.0089762 | 1104 | 0.026286 | 1.362 | A04 | MICL0.01445014/DOV
Build-In Floor | Mini Canal | MICL.01445014/RBL | 14 | 450 | 14 | 14 | 1042 | 1042 | 1042 | 0.02481 | 405 | 0.0096429 | 1187 | 0.028262 | 1.362 | A04 | MICL0.01445014/RBL
Build-In Floor | Mini Canal | MICL.01445014/RBN | 14 | 450 | 14 | 14 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01445014/RBN
Build-In Floor | Mini Canal | MICL.01445014/RBR | 14 | 450 | 14 | 14 | 1042 | 1042 | 1042 | 0.02481 | 405 | 0.0096429 | 1187 | 0.028262 | 1.362 | A04 | MICL0.01445014/RBR
Build-In Floor | Mini Canal | MICL.01445014/RBV | 14 | 450 | 14 | 14 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01445014/RBV
Build-In Floor | Mini Canal | MICL.01445014/RDB | 14 | 450 | 14 | 14 | 1042 | 1042 | 1042 | 0.02481 | 405 | 0.0096429 | 1187 | 0.028262 | 1.362 | A04 | MICL0.01445014/RDB
Build-In Floor | Mini Canal | MICL.01445014/RMN | 14 | 450 | 14 | 14 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01445014/RMN
Build-In Floor | Mini Canal | MICL.01445014/RMV | 14 | 450 | 14 | 14 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01445014/RMV
Build-In Floor | Mini Canal | MICL.01445014/RNA | 14 | 450 | 14 | 14 | 1042 | 1042 | 1042 | 0.02481 | 405 | 0.0096429 | 1187 | 0.028262 | 1.362 | A04 | MICL0.01445014/RNA
Build-In Floor | Mini Canal | MICL.01445014/RON | 14 | 450 | 14 | 14 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01445014/RON
Build-In Floor | Mini Canal | MICL.01445014/ROV | 14 | 450 | 14 | 14 | 1011 | 1011 | 1011 | 0.024071 | 393 | 0.0093571 | 1152 | 0.027429 | 1.362 | A04 | MICL0.01445014/ROV
Build-In Floor | Mini Canal | MICL.01445014/RSS | 14 | 450 | 14 | 14 | 1000 | 1000 | 1000 | 0.02381 | 389 | 0.0092619 | 1139 | 0.027119 | 1.362 | A04 | MICL0.01445014/RSS
Build-In Floor | Mini Canal | MICL.01445014/SBL | 14 | 450 | 14 | 14 | 1042 | 1042 | 1042 | 0.02481 | 405 | 0.0096429 | 1187 | 0.028262 | 1.362 | A04 | MICL0.01445014/SBL
Build-In Floor | Mini Canal | MICL.01445014/SBR | 14 | 450 | 14 | 14 | 1042 | 1042 | 1042 | 0.02481 | 405 | 0.0096429 | 1187 | 0.028262 | 1.362 | A04 | MICL0.01445014/SBR
Build-In Floor | Mini Canal | MICL.01445014/SDB | 14 | 450 | 14 | 14 | 1042 | 1042 | 1042 | 0.02481 | 405 | 0.0096429 | 1187 | 0.028262 | 1.362 | A04 | MICL0.01445014/SDB
Build-In Floor | Mini Canal | MICL.01445014/SNA | 14 | 450 | 14 | 14 | 1042 | 1042 | 1042 | 0.02481 | 405 | 0.0096429 | 1187 | 0.028262 | 1.362 | A04 | MICL0.01445014/SNA
Build-In Floor | Mini Canal | MICL.01445014/SNC | 14 | 450 | 14 | 14 | 1042 | 1042 | 1042 | 0.02481 | 405 | 0.0096429 | 1187 | 0.028262 | 1.362 | A04 | MICL0.01445014/SNC
Build-In Floor | Mini Canal | MICL.01445026/ANA | 14 | 450 | 26 | 26 | 1356 | 1356 | 1356 | 0.032286 | 527 | 0.012548 | 1544 | 0.036762 | 1.362 | A04 | MICL0.01445026/ANA
Build-In Floor | Mini Canal | MICL.01445026/DBL | 14 | 450 | 26 | 26 | 1754 | 1754 | 1754 | 0.041762 | 682 | 0.016238 | 1998 | 0.047571 | 1.362 | A04 | MICL0.01445026/DBL
Build-In Floor | Mini Canal | MICL.01445026/DBN | 14 | 450 | 26 | 26 | 1681 | 1681 | 1681 | 0.040024 | 654 | 0.015571 | 1915 | 0.045595 | 1.362 | A04 | MICL0.01445026/DBN
Build-In Floor | Mini Canal | MICL.01445026/DBR | 14 | 450 | 26 | 26 | 1754 | 1754 | 1754 | 0.041762 | 682 | 0.016238 | 1998 | 0.047571 | 1.362 | A04 | MICL0.01445026/DBR
Build-In Floor | Mini Canal | MICL.01445026/DBV | 14 | 450 | 26 | 26 | 1681 | 1681 | 1681 | 0.040024 | 654 | 0.015571 | 1915 | 0.045595 | 1.362 | A04 | MICL0.01445026/DBV
Build-In Floor | Mini Canal | MICL.01445026/DDB | 14 | 450 | 26 | 26 | 1754 | 1754 | 1754 | 0.041762 | 682 | 0.016238 | 1998 | 0.047571 | 1.362 | A04 | MICL0.01445026/DDB
Build-In Floor | Mini Canal | MICL.01445026/DMN | 14 | 450 | 26 | 26 | 1681 | 1681 | 1681 | 0.040024 | 654 | 0.015571 | 1915 | 0.045595 | 1.362 | A04 | MICL0.01445026/DMN
Build-In Floor | Mini Canal | MICL.01445026/DMV | 14 | 450 | 26 | 26 | 1681 | 1681 | 1681 | 0.040024 | 654 | 0.015571 | 1915 | 0.045595 | 1.362 | A04 | MICL0.01445026/DMV
Build-In Floor | Mini Canal | MICL.01445026/DNA | 14 | 450 | 26 | 26 | 1754 | 1754 | 1754 | 0.041762 | 682 | 0.016238 | 1998 | 0.047571 | 1.362 | A04 | MICL0.01445026/DNA
Build-In Floor | Mini Canal | MICL.01445026/DNC | 14 | 450 | 26 | 26 | 1754 | 1754 | 1754 | 0.041762 | 682 | 0.016238 | 1998 | 0.047571 | 1.362 | A04 | MICL0.01445026/DNC
Build-In Floor | Mini Canal | MICL.01445026/DON | 14 | 450 | 26 | 26 | 1681 | 1681 | 1681 | 0.040024 | 654 | 0.015571 | 1915 | 0.045595 | 1.362 | A04 | MICL0.01445026/DON
Build-In Floor | Mini Canal | MICL.01445026/DOV | 14 | 450 | 26 | 26 | 1681 | 1681 | 1681 | 0.040024 | 654 | 0.015571 | 1915 | 0.045595 | 1.362 | A04 | MICL0.01445026/DOV
Build-In Floor | Mini Canal | MICL.01445026/PNC | 14 | 450 | 26 | 26 | 1537 | 1537 | 1537 | 0.036595 | 598 | 0.014238 | 1751 | 0.04169 | 1.362 | A04 | MICL0.01445026/PNC
Build-In Floor | Mini Canal | MICL.01445026/RBL | 14 | 450 | 26 | 26 | 1808 | 1808 | 1808 | 0.043048 | 703 | 0.016738 | 2059 | 0.049024 | 1.362 | A04 | MICL0.01445026/RBL
Build-In Floor | Mini Canal | MICL.01445026/RBN | 14 | 450 | 26 | 26 | 1754 | 1754 | 1754 | 0.041762 | 682 | 0.016238 | 1998 | 0.047571 | 1.362 | A04 | MICL0.01445026/RBN
Build-In Floor | Mini Canal | MICL.01445026/RBR | 14 | 450 | 26 | 26 | 1808 | 1808 | 1808 | 0.043048 | 703 | 0.016738 | 2059 | 0.049024 | 1.362 | A04 | MICL0.01445026/RBR
Build-In Floor | Mini Canal | MICL.01445026/RBV | 14 | 450 | 26 | 26 | 1754 | 1754 | 1754 | 0.041762 | 682 | 0.016238 | 1998 | 0.047571 | 1.362 | A04 | MICL0.01445026/RBV
Build-In Floor | Mini Canal | MICL.01445026/RDB | 14 | 450 | 26 | 26 | 1808 | 1808 | 1808 | 0.043048 | 703 | 0.016738 | 2059 | 0.049024 | 1.362 | A04 | MICL0.01445026/RDB
Build-In Floor | Mini Canal | MICL.01445026/RMN | 14 | 450 | 26 | 26 | 1754 | 1754 | 1754 | 0.041762 | 682 | 0.016238 | 1998 | 0.047571 | 1.362 | A04 | MICL0.01445026/RMN
Build-In Floor | Mini Canal | MICL.01445026/RMV | 14 | 450 | 26 | 26 | 1754 | 1754 | 1754 | 0.041762 | 682 | 0.016238 | 1998 | 0.047571 | 1.362 | A04 | MICL0.01445026/RMV
Build-In Floor | Mini Canal | MICL.01445026/RNA | 14 | 450 | 26 | 26 | 1808 | 1808 | 1808 | 0.043048 | 703 | 0.016738 | 2059 | 0.049024 | 1.362 | A04 | MICL0.01445026/RNA
Build-In Floor | Mini Canal | MICL.01445026/RON | 14 | 450 | 26 | 26 | 1754 | 1754 | 1754 | 0.041762 | 682 | 0.016238 | 1998 | 0.047571 | 1.362 | A04 | MICL0.01445026/RON
Build-In Floor | Mini Canal | MICL.01445026/ROV | 14 | 450 | 26 | 26 | 1754 | 1754 | 1754 | 0.041762 | 682 | 0.016238 | 1998 | 0.047571 | 1.362 | A04 | MICL0.01445026/ROV
Build-In Floor | Mini Canal | MICL.01445026/RSS | 14 | 450 | 26 | 26 | 1736 | 1736 | 1736 | 0.041333 | 675 | 0.016071 | 1977 | 0.047071 | 1.362 | A04 | MICL0.01445026/RSS
Build-In Floor | Mini Canal | MICL.01445026/SBL | 14 | 450 | 26 | 26 | 1808 | 1808 | 1808 | 0.043048 | 703 | 0.016738 | 2059 | 0.049024 | 1.362 | A04 | MICL0.01445026/SBL
Build-In Floor | Mini Canal | MICL.01445026/SBR | 14 | 450 | 26 | 26 | 1808 | 1808 | 1808 | 0.043048 | 703 | 0.016738 | 2059 | 0.049024 | 1.362 | A04 | MICL0.01445026/SBR
Build-In Floor | Mini Canal | MICL.01445026/SDB | 14 | 450 | 26 | 26 | 1808 | 1808 | 1808 | 0.043048 | 703 | 0.016738 | 2059 | 0.049024 | 1.362 | A04 | MICL0.01445026/SDB
Build-In Floor | Mini Canal | MICL.01445026/SNA | 14 | 450 | 26 | 26 | 1808 | 1808 | 1808 | 0.043048 | 703 | 0.016738 | 2059 | 0.049024 | 1.362 | A04 | MICL0.01445026/SNA
Build-In Floor | Mini Canal | MICL.01445026/SNC | 14 | 450 | 26 | 26 | 1808 | 1808 | 1808 | 0.043048 | 703 | 0.016738 | 2059 | 0.049024 | 1.362 | A04 | MICL0.01445026/SNC
Build-In Floor | Mini Canal | MICL.01445034/ANA | 14 | 450 | 34 | 34 | 1850 | 1850 | 1850 | 0.044048 | 720 | 0.017143 | 2107 | 0.050167 | 1.362 | A04 | MICL0.01445034/ANA
Build-In Floor | Mini Canal | MICL.01445034/DBL | 14 | 450 | 34 | 34 | 2393 | 2393 | 2393 | 0.056976 | 931 | 0.022167 | 2726 | 0.064905 | 1.362 | A04 | MICL0.01445034/DBL
Build-In Floor | Mini Canal | MICL.01445034/DBN | 14 | 450 | 34 | 34 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01445034/DBN
Build-In Floor | Mini Canal | MICL.01445034/DBR | 14 | 450 | 34 | 34 | 2393 | 2393 | 2393 | 0.056976 | 931 | 0.022167 | 2726 | 0.064905 | 1.362 | A04 | MICL0.01445034/DBR
Build-In Floor | Mini Canal | MICL.01445034/DBV | 14 | 450 | 34 | 34 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01445034/DBV
Build-In Floor | Mini Canal | MICL.01445034/DDB | 14 | 450 | 34 | 34 | 2393 | 2393 | 2393 | 0.056976 | 931 | 0.022167 | 2726 | 0.064905 | 1.362 | A04 | MICL0.01445034/DDB
Build-In Floor | Mini Canal | MICL.01445034/DMN | 14 | 450 | 34 | 34 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01445034/DMN
Build-In Floor | Mini Canal | MICL.01445034/DMV | 14 | 450 | 34 | 34 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01445034/DMV
Build-In Floor | Mini Canal | MICL.01445034/DNA | 14 | 450 | 34 | 34 | 2393 | 2393 | 2393 | 0.056976 | 931 | 0.022167 | 2726 | 0.064905 | 1.362 | A04 | MICL0.01445034/DNA
Build-In Floor | Mini Canal | MICL.01445034/DNC | 14 | 450 | 34 | 34 | 2393 | 2393 | 2393 | 0.056976 | 931 | 0.022167 | 2726 | 0.064905 | 1.362 | A04 | MICL0.01445034/DNC
Build-In Floor | Mini Canal | MICL.01445034/DON | 14 | 450 | 34 | 34 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01445034/DON
Build-In Floor | Mini Canal | MICL.01445034/DOV | 14 | 450 | 34 | 34 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01445034/DOV
Build-In Floor | Mini Canal | MICL.01445034/PNC | 14 | 450 | 34 | 34 | 2097 | 2097 | 2097 | 0.049929 | 816 | 0.019429 | 2388 | 0.056857 | 1.362 | A04 | MICL0.01445034/PNC
Build-In Floor | Mini Canal | MICL.01445034/RBL | 14 | 450 | 34 | 34 | 2467 | 2467 | 2467 | 0.058738 | 960 | 0.022857 | 2810 | 0.066905 | 1.362 | A04 | MICL0.01445034/RBL
Build-In Floor | Mini Canal | MICL.01445034/RBN | 14 | 450 | 34 | 34 | 2393 | 2393 | 2393 | 0.056976 | 931 | 0.022167 | 2726 | 0.064905 | 1.362 | A04 | MICL0.01445034/RBN
Build-In Floor | Mini Canal | MICL.01445034/RBR | 14 | 450 | 34 | 34 | 2467 | 2467 | 2467 | 0.058738 | 960 | 0.022857 | 2810 | 0.066905 | 1.362 | A04 | MICL0.01445034/RBR
Build-In Floor | Mini Canal | MICL.01445034/RBV | 14 | 450 | 34 | 34 | 2393 | 2393 | 2393 | 0.056976 | 931 | 0.022167 | 2726 | 0.064905 | 1.362 | A04 | MICL0.01445034/RBV
Build-In Floor | Mini Canal | MICL.01445034/RDB | 14 | 450 | 34 | 34 | 2467 | 2467 | 2467 | 0.058738 | 960 | 0.022857 | 2810 | 0.066905 | 1.362 | A04 | MICL0.01445034/RDB
Build-In Floor | Mini Canal | MICL.01445034/RMN | 14 | 450 | 34 | 34 | 2393 | 2393 | 2393 | 0.056976 | 931 | 0.022167 | 2726 | 0.064905 | 1.362 | A04 | MICL0.01445034/RMN
Build-In Floor | Mini Canal | MICL.01445034/RMV | 14 | 450 | 34 | 34 | 2393 | 2393 | 2393 | 0.056976 | 931 | 0.022167 | 2726 | 0.064905 | 1.362 | A04 | MICL0.01445034/RMV
Build-In Floor | Mini Canal | MICL.01445034/RNA | 14 | 450 | 34 | 34 | 2467 | 2467 | 2467 | 0.058738 | 960 | 0.022857 | 2810 | 0.066905 | 1.362 | A04 | MICL0.01445034/RNA
Build-In Floor | Mini Canal | MICL.01445034/RON | 14 | 450 | 34 | 34 | 2393 | 2393 | 2393 | 0.056976 | 931 | 0.022167 | 2726 | 0.064905 | 1.362 | A04 | MICL0.01445034/RON
Build-In Floor | Mini Canal | MICL.01445034/ROV | 14 | 450 | 34 | 34 | 2393 | 2393 | 2393 | 0.056976 | 931 | 0.022167 | 2726 | 0.064905 | 1.362 | A04 | MICL0.01445034/ROV
Build-In Floor | Mini Canal | MICL.01445034/RSS | 14 | 450 | 34 | 34 | 2368 | 2368 | 2368 | 0.056381 | 921 | 0.021929 | 2697 | 0.064214 | 1.362 | A04 | MICL0.01445034/RSS
Build-In Floor | Mini Canal | MICL.01445034/SBL | 14 | 450 | 34 | 34 | 2467 | 2467 | 2467 | 0.058738 | 960 | 0.022857 | 2810 | 0.066905 | 1.362 | A04 | MICL0.01445034/SBL
Build-In Floor | Mini Canal | MICL.01445034/SBR | 14 | 450 | 34 | 34 | 2467 | 2467 | 2467 | 0.058738 | 960 | 0.022857 | 2810 | 0.066905 | 1.362 | A04 | MICL0.01445034/SBR
Build-In Floor | Mini Canal | MICL.01445034/SDB | 14 | 450 | 34 | 34 | 2467 | 2467 | 2467 | 0.058738 | 960 | 0.022857 | 2810 | 0.066905 | 1.362 | A04 | MICL0.01445034/SDB
Build-In Floor | Mini Canal | MICL.01445034/SNA | 14 | 450 | 34 | 34 | 2467 | 2467 | 2467 | 0.058738 | 960 | 0.022857 | 2810 | 0.066905 | 1.362 | A04 | MICL0.01445034/SNA
Build-In Floor | Mini Canal | MICL.01445034/SNC | 14 | 450 | 34 | 34 | 2467 | 2467 | 2467 | 0.058738 | 960 | 0.022857 | 2810 | 0.066905 | 1.362 | A04 | MICL0.01445034/SNC
Build-In Floor | Mini Canal | MICL.01445042/ANA | 14 | 450 | 42 | 42 | 2494 | 2494 | 2494 | 0.059381 | 970 | 0.023095 | 2841 | 0.067643 | 1.362 | A04 | MICL0.01445042/ANA
Build-In Floor | Mini Canal | MICL.01445042/DBL | 14 | 450 | 42 | 42 | 3225 | 3225 | 3225 | 0.076786 | 1255 | 0.029881 | 3673 | 0.087452 | 1.362 | A04 | MICL0.01445042/DBL
Build-In Floor | Mini Canal | MICL.01445042/DBN | 14 | 450 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01445042/DBN
Build-In Floor | Mini Canal | MICL.01445042/DBR | 14 | 450 | 42 | 42 | 3225 | 3225 | 3225 | 0.076786 | 1255 | 0.029881 | 3673 | 0.087452 | 1.362 | A04 | MICL0.01445042/DBR
Build-In Floor | Mini Canal | MICL.01445042/DBV | 14 | 450 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01445042/DBV
Build-In Floor | Mini Canal | MICL.01445042/DDB | 14 | 450 | 42 | 42 | 3225 | 3225 | 3225 | 0.076786 | 1255 | 0.029881 | 3673 | 0.087452 | 1.362 | A04 | MICL0.01445042/DDB
Build-In Floor | Mini Canal | MICL.01445042/DMN | 14 | 450 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01445042/DMN
Build-In Floor | Mini Canal | MICL.01445042/DMV | 14 | 450 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01445042/DMV
Build-In Floor | Mini Canal | MICL.01445042/DNA | 14 | 450 | 42 | 42 | 3225 | 3225 | 3225 | 0.076786 | 1255 | 0.029881 | 3673 | 0.087452 | 1.362 | A04 | MICL0.01445042/DNA
Build-In Floor | Mini Canal | MICL.01445042/DNC | 14 | 450 | 42 | 42 | 3225 | 3225 | 3225 | 0.076786 | 1255 | 0.029881 | 3673 | 0.087452 | 1.362 | A04 | MICL0.01445042/DNC
Build-In Floor | Mini Canal | MICL.01445042/DON | 14 | 450 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01445042/DON
Build-In Floor | Mini Canal | MICL.01445042/DOV | 14 | 450 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01445042/DOV
Build-In Floor | Mini Canal | MICL.01445042/PNC | 14 | 450 | 42 | 42 | 2826 | 2826 | 2826 | 0.067286 | 1099 | 0.026167 | 3219 | 0.076643 | 1.362 | A04 | MICL0.01445042/PNC
Build-In Floor | Mini Canal | MICL.01445042/RBL | 14 | 450 | 42 | 42 | 3325 | 3325 | 3325 | 0.079167 | 1293 | 0.030786 | 3787 | 0.090167 | 1.362 | A04 | MICL0.01445042/RBL
Build-In Floor | Mini Canal | MICL.01445042/RBN | 14 | 450 | 42 | 42 | 3225 | 3225 | 3225 | 0.076786 | 1255 | 0.029881 | 3673 | 0.087452 | 1.362 | A04 | MICL0.01445042/RBN
Build-In Floor | Mini Canal | MICL.01445042/RBR | 14 | 450 | 42 | 42 | 3325 | 3325 | 3325 | 0.079167 | 1293 | 0.030786 | 3787 | 0.090167 | 1.362 | A04 | MICL0.01445042/RBR
Build-In Floor | Mini Canal | MICL.01445042/RBV | 14 | 450 | 42 | 42 | 3225 | 3225 | 3225 | 0.076786 | 1255 | 0.029881 | 3673 | 0.087452 | 1.362 | A04 | MICL0.01445042/RBV
Build-In Floor | Mini Canal | MICL.01445042/RDB | 14 | 450 | 42 | 42 | 3325 | 3325 | 3325 | 0.079167 | 1293 | 0.030786 | 3787 | 0.090167 | 1.362 | A04 | MICL0.01445042/RDB
Build-In Floor | Mini Canal | MICL.01445042/RMN | 14 | 450 | 42 | 42 | 3225 | 3225 | 3225 | 0.076786 | 1255 | 0.029881 | 3673 | 0.087452 | 1.362 | A04 | MICL0.01445042/RMN
Build-In Floor | Mini Canal | MICL.01445042/RMV | 14 | 450 | 42 | 42 | 3225 | 3225 | 3225 | 0.076786 | 1255 | 0.029881 | 3673 | 0.087452 | 1.362 | A04 | MICL0.01445042/RMV
Build-In Floor | Mini Canal | MICL.01445042/RNA | 14 | 450 | 42 | 42 | 3325 | 3325 | 3325 | 0.079167 | 1293 | 0.030786 | 3787 | 0.090167 | 1.362 | A04 | MICL0.01445042/RNA
Build-In Floor | Mini Canal | MICL.01445042/RON | 14 | 450 | 42 | 42 | 3225 | 3225 | 3225 | 0.076786 | 1255 | 0.029881 | 3673 | 0.087452 | 1.362 | A04 | MICL0.01445042/RON
Build-In Floor | Mini Canal | MICL.01445042/ROV | 14 | 450 | 42 | 42 | 3225 | 3225 | 3225 | 0.076786 | 1255 | 0.029881 | 3673 | 0.087452 | 1.362 | A04 | MICL0.01445042/ROV
Build-In Floor | Mini Canal | MICL.01445042/RSS | 14 | 450 | 42 | 42 | 3192 | 3192 | 3192 | 0.076 | 1242 | 0.029571 | 3636 | 0.086571 | 1.362 | A04 | MICL0.01445042/RSS
Build-In Floor | Mini Canal | MICL.01445042/SBL | 14 | 450 | 42 | 42 | 3325 | 3325 | 3325 | 0.079167 | 1293 | 0.030786 | 3787 | 0.090167 | 1.362 | A04 | MICL0.01445042/SBL
Build-In Floor | Mini Canal | MICL.01445042/SBR | 14 | 450 | 42 | 42 | 3325 | 3325 | 3325 | 0.079167 | 1293 | 0.030786 | 3787 | 0.090167 | 1.362 | A04 | MICL0.01445042/SBR
Build-In Floor | Mini Canal | MICL.01445042/SDB | 14 | 450 | 42 | 42 | 3325 | 3325 | 3325 | 0.079167 | 1293 | 0.030786 | 3787 | 0.090167 | 1.362 | A04 | MICL0.01445042/SDB
Build-In Floor | Mini Canal | MICL.01445042/SNA | 14 | 450 | 42 | 42 | 3325 | 3325 | 3325 | 0.079167 | 1293 | 0.030786 | 3787 | 0.090167 | 1.362 | A04 | MICL0.01445042/SNA
Build-In Floor | Mini Canal | MICL.01445042/SNC | 14 | 450 | 42 | 42 | 3325 | 3325 | 3325 | 0.079167 | 1293 | 0.030786 | 3787 | 0.090167 | 1.362 | A04 | MICL0.01445042/SNC
Build-In Floor | Mini Canal | MICL.01447014/ANA | 14 | 470 | 14 | 14 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01447014/ANA
Build-In Floor | Mini Canal | MICL.01447014/DBL | 14 | 470 | 14 | 14 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01447014/DBL
Build-In Floor | Mini Canal | MICL.01447014/DBN | 14 | 470 | 14 | 14 | 1015 | 1015 | 1015 | 0.024167 | 395 | 0.0094048 | 1156 | 0.027524 | 1.362 | A04 | MICL0.01447014/DBN
Build-In Floor | Mini Canal | MICL.01447014/DBR | 14 | 470 | 14 | 14 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01447014/DBR
Build-In Floor | Mini Canal | MICL.01447014/DBV | 14 | 470 | 14 | 14 | 1015 | 1015 | 1015 | 0.024167 | 395 | 0.0094048 | 1156 | 0.027524 | 1.362 | A04 | MICL0.01447014/DBV
Build-In Floor | Mini Canal | MICL.01447014/DDB | 14 | 470 | 14 | 14 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01447014/DDB
Build-In Floor | Mini Canal | MICL.01447014/DMN | 14 | 470 | 14 | 14 | 1015 | 1015 | 1015 | 0.024167 | 395 | 0.0094048 | 1156 | 0.027524 | 1.362 | A04 | MICL0.01447014/DMN
Build-In Floor | Mini Canal | MICL.01447014/DMV | 14 | 470 | 14 | 14 | 1015 | 1015 | 1015 | 0.024167 | 395 | 0.0094048 | 1156 | 0.027524 | 1.362 | A04 | MICL0.01447014/DMV
Build-In Floor | Mini Canal | MICL.01447014/DNA | 14 | 470 | 14 | 14 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01447014/DNA
Build-In Floor | Mini Canal | MICL.01447014/DNC | 14 | 470 | 14 | 14 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01447014/DNC
Build-In Floor | Mini Canal | MICL.01447014/DON | 14 | 470 | 14 | 14 | 1015 | 1015 | 1015 | 0.024167 | 395 | 0.0094048 | 1156 | 0.027524 | 1.362 | A04 | MICL0.01447014/DON
Build-In Floor | Mini Canal | MICL.01447014/DOV | 14 | 470 | 14 | 14 | 1015 | 1015 | 1015 | 0.024167 | 395 | 0.0094048 | 1156 | 0.027524 | 1.362 | A04 | MICL0.01447014/DOV
Build-In Floor | Mini Canal | MICL.01447014/RBL | 14 | 470 | 14 | 14 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01447014/RBL
Build-In Floor | Mini Canal | MICL.01447014/RBN | 14 | 470 | 14 | 14 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01447014/RBN
Build-In Floor | Mini Canal | MICL.01447014/RBR | 14 | 470 | 14 | 14 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01447014/RBR
Build-In Floor | Mini Canal | MICL.01447014/RBV | 14 | 470 | 14 | 14 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01447014/RBV
Build-In Floor | Mini Canal | MICL.01447014/RDB | 14 | 470 | 14 | 14 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01447014/RDB
Build-In Floor | Mini Canal | MICL.01447014/RMN | 14 | 470 | 14 | 14 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01447014/RMN
Build-In Floor | Mini Canal | MICL.01447014/RMV | 14 | 470 | 14 | 14 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01447014/RMV
Build-In Floor | Mini Canal | MICL.01447014/RNA | 14 | 470 | 14 | 14 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01447014/RNA
Build-In Floor | Mini Canal | MICL.01447014/RON | 14 | 470 | 14 | 14 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01447014/RON
Build-In Floor | Mini Canal | MICL.01447014/ROV | 14 | 470 | 14 | 14 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01447014/ROV
Build-In Floor | Mini Canal | MICL.01447014/RSS | 14 | 470 | 14 | 14 | 1047 | 1047 | 1047 | 0.024929 | 407 | 0.0096905 | 1193 | 0.028405 | 1.362 | A04 | MICL0.01447014/RSS
Build-In Floor | Mini Canal | MICL.01447014/SBL | 14 | 470 | 14 | 14 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01447014/SBL
Build-In Floor | Mini Canal | MICL.01447014/SBR | 14 | 470 | 14 | 14 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01447014/SBR
Build-In Floor | Mini Canal | MICL.01447014/SDB | 14 | 470 | 14 | 14 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01447014/SDB
Build-In Floor | Mini Canal | MICL.01447014/SNA | 14 | 470 | 14 | 14 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01447014/SNA
Build-In Floor | Mini Canal | MICL.01447014/SNC | 14 | 470 | 14 | 14 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01447014/SNC
Build-In Floor | Mini Canal | MICL.01447026/ANA | 14 | 470 | 26 | 26 | 1421 | 1421 | 1421 | 0.033833 | 553 | 0.013167 | 1619 | 0.038548 | 1.362 | A04 | MICL0.01447026/ANA
Build-In Floor | Mini Canal | MICL.01447026/DBL | 14 | 470 | 26 | 26 | 1838 | 1838 | 1838 | 0.043762 | 715 | 0.017024 | 2093 | 0.049833 | 1.362 | A04 | MICL0.01447026/DBL
Build-In Floor | Mini Canal | MICL.01447026/DBN | 14 | 470 | 26 | 26 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01447026/DBN
Build-In Floor | Mini Canal | MICL.01447026/DBR | 14 | 470 | 26 | 26 | 1838 | 1838 | 1838 | 0.043762 | 715 | 0.017024 | 2093 | 0.049833 | 1.362 | A04 | MICL0.01447026/DBR
Build-In Floor | Mini Canal | MICL.01447026/DBV | 14 | 470 | 26 | 26 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01447026/DBV
Build-In Floor | Mini Canal | MICL.01447026/DDB | 14 | 470 | 26 | 26 | 1838 | 1838 | 1838 | 0.043762 | 715 | 0.017024 | 2093 | 0.049833 | 1.362 | A04 | MICL0.01447026/DDB
Build-In Floor | Mini Canal | MICL.01447026/DMN | 14 | 470 | 26 | 26 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01447026/DMN
Build-In Floor | Mini Canal | MICL.01447026/DMV | 14 | 470 | 26 | 26 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01447026/DMV
Build-In Floor | Mini Canal | MICL.01447026/DNA | 14 | 470 | 26 | 26 | 1838 | 1838 | 1838 | 0.043762 | 715 | 0.017024 | 2093 | 0.049833 | 1.362 | A04 | MICL0.01447026/DNA
Build-In Floor | Mini Canal | MICL.01447026/DNC | 14 | 470 | 26 | 26 | 1838 | 1838 | 1838 | 0.043762 | 715 | 0.017024 | 2093 | 0.049833 | 1.362 | A04 | MICL0.01447026/DNC
Build-In Floor | Mini Canal | MICL.01447026/DON | 14 | 470 | 26 | 26 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01447026/DON
Build-In Floor | Mini Canal | MICL.01447026/DOV | 14 | 470 | 26 | 26 | 1762 | 1762 | 1762 | 0.041952 | 685 | 0.01631 | 2007 | 0.047786 | 1.362 | A04 | MICL0.01447026/DOV
Build-In Floor | Mini Canal | MICL.01447026/PNC | 14 | 470 | 26 | 26 | 1611 | 1611 | 1611 | 0.038357 | 627 | 0.014929 | 1835 | 0.04369 | 1.362 | A04 | MICL0.01447026/PNC
Build-In Floor | Mini Canal | MICL.01447026/RBL | 14 | 470 | 26 | 26 | 1895 | 1895 | 1895 | 0.045119 | 737 | 0.017548 | 2158 | 0.051381 | 1.362 | A04 | MICL0.01447026/RBL
Build-In Floor | Mini Canal | MICL.01447026/RBN | 14 | 470 | 26 | 26 | 1838 | 1838 | 1838 | 0.043762 | 715 | 0.017024 | 2093 | 0.049833 | 1.362 | A04 | MICL0.01447026/RBN
Build-In Floor | Mini Canal | MICL.01447026/RBR | 14 | 470 | 26 | 26 | 1895 | 1895 | 1895 | 0.045119 | 737 | 0.017548 | 2158 | 0.051381 | 1.362 | A04 | MICL0.01447026/RBR
Build-In Floor | Mini Canal | MICL.01447026/RBV | 14 | 470 | 26 | 26 | 1838 | 1838 | 1838 | 0.043762 | 715 | 0.017024 | 2093 | 0.049833 | 1.362 | A04 | MICL0.01447026/RBV
Build-In Floor | Mini Canal | MICL.01447026/RDB | 14 | 470 | 26 | 26 | 1895 | 1895 | 1895 | 0.045119 | 737 | 0.017548 | 2158 | 0.051381 | 1.362 | A04 | MICL0.01447026/RDB
Build-In Floor | Mini Canal | MICL.01447026/RMN | 14 | 470 | 26 | 26 | 1838 | 1838 | 1838 | 0.043762 | 715 | 0.017024 | 2093 | 0.049833 | 1.362 | A04 | MICL0.01447026/RMN
Build-In Floor | Mini Canal | MICL.01447026/RMV | 14 | 470 | 26 | 26 | 1838 | 1838 | 1838 | 0.043762 | 715 | 0.017024 | 2093 | 0.049833 | 1.362 | A04 | MICL0.01447026/RMV
Build-In Floor | Mini Canal | MICL.01447026/RNA | 14 | 470 | 26 | 26 | 1895 | 1895 | 1895 | 0.045119 | 737 | 0.017548 | 2158 | 0.051381 | 1.362 | A04 | MICL0.01447026/RNA
Build-In Floor | Mini Canal | MICL.01447026/RON | 14 | 470 | 26 | 26 | 1838 | 1838 | 1838 | 0.043762 | 715 | 0.017024 | 2093 | 0.049833 | 1.362 | A04 | MICL0.01447026/RON
Build-In Floor | Mini Canal | MICL.01447026/ROV | 14 | 470 | 26 | 26 | 1838 | 1838 | 1838 | 0.043762 | 715 | 0.017024 | 2093 | 0.049833 | 1.362 | A04 | MICL0.01447026/ROV
Build-In Floor | Mini Canal | MICL.01447026/RSS | 14 | 470 | 26 | 26 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01447026/RSS
Build-In Floor | Mini Canal | MICL.01447026/SBL | 14 | 470 | 26 | 26 | 1895 | 1895 | 1895 | 0.045119 | 737 | 0.017548 | 2158 | 0.051381 | 1.362 | A04 | MICL0.01447026/SBL
Build-In Floor | Mini Canal | MICL.01447026/SBR | 14 | 470 | 26 | 26 | 1895 | 1895 | 1895 | 0.045119 | 737 | 0.017548 | 2158 | 0.051381 | 1.362 | A04 | MICL0.01447026/SBR
Build-In Floor | Mini Canal | MICL.01447026/SDB | 14 | 470 | 26 | 26 | 1895 | 1895 | 1895 | 0.045119 | 737 | 0.017548 | 2158 | 0.051381 | 1.362 | A04 | MICL0.01447026/SDB
Build-In Floor | Mini Canal | MICL.01447026/SNA | 14 | 470 | 26 | 26 | 1895 | 1895 | 1895 | 0.045119 | 737 | 0.017548 | 2158 | 0.051381 | 1.362 | A04 | MICL0.01447026/SNA
Build-In Floor | Mini Canal | MICL.01447026/SNC | 14 | 470 | 26 | 26 | 1895 | 1895 | 1895 | 0.045119 | 737 | 0.017548 | 2158 | 0.051381 | 1.362 | A04 | MICL0.01447026/SNC
Build-In Floor | Mini Canal | MICL.01447034/ANA | 14 | 470 | 34 | 34 | 1938 | 1938 | 1938 | 0.046143 | 754 | 0.017952 | 2207 | 0.052548 | 1.362 | A04 | MICL0.01447034/ANA
Build-In Floor | Mini Canal | MICL.01447034/DBL | 14 | 470 | 34 | 34 | 2506 | 2506 | 2506 | 0.059667 | 975 | 0.023214 | 2854 | 0.067952 | 1.362 | A04 | MICL0.01447034/DBL
Build-In Floor | Mini Canal | MICL.01447034/DBN | 14 | 470 | 34 | 34 | 2403 | 2403 | 2403 | 0.057214 | 935 | 0.022262 | 2737 | 0.065167 | 1.362 | A04 | MICL0.01447034/DBN
Build-In Floor | Mini Canal | MICL.01447034/DBR | 14 | 470 | 34 | 34 | 2506 | 2506 | 2506 | 0.059667 | 975 | 0.023214 | 2854 | 0.067952 | 1.362 | A04 | MICL0.01447034/DBR
Build-In Floor | Mini Canal | MICL.01447034/DBV | 14 | 470 | 34 | 34 | 2403 | 2403 | 2403 | 0.057214 | 935 | 0.022262 | 2737 | 0.065167 | 1.362 | A04 | MICL0.01447034/DBV
Build-In Floor | Mini Canal | MICL.01447034/DDB | 14 | 470 | 34 | 34 | 2506 | 2506 | 2506 | 0.059667 | 975 | 0.023214 | 2854 | 0.067952 | 1.362 | A04 | MICL0.01447034/DDB
Build-In Floor | Mini Canal | MICL.01447034/DMN | 14 | 470 | 34 | 34 | 2403 | 2403 | 2403 | 0.057214 | 935 | 0.022262 | 2737 | 0.065167 | 1.362 | A04 | MICL0.01447034/DMN
Build-In Floor | Mini Canal | MICL.01447034/DMV | 14 | 470 | 34 | 34 | 2403 | 2403 | 2403 | 0.057214 | 935 | 0.022262 | 2737 | 0.065167 | 1.362 | A04 | MICL0.01447034/DMV
Build-In Floor | Mini Canal | MICL.01447034/DNA | 14 | 470 | 34 | 34 | 2506 | 2506 | 2506 | 0.059667 | 975 | 0.023214 | 2854 | 0.067952 | 1.362 | A04 | MICL0.01447034/DNA
Build-In Floor | Mini Canal | MICL.01447034/DNC | 14 | 470 | 34 | 34 | 2506 | 2506 | 2506 | 0.059667 | 975 | 0.023214 | 2854 | 0.067952 | 1.362 | A04 | MICL0.01447034/DNC
Build-In Floor | Mini Canal | MICL.01447034/DON | 14 | 470 | 34 | 34 | 2403 | 2403 | 2403 | 0.057214 | 935 | 0.022262 | 2737 | 0.065167 | 1.362 | A04 | MICL0.01447034/DON
Build-In Floor | Mini Canal | MICL.01447034/DOV | 14 | 470 | 34 | 34 | 2403 | 2403 | 2403 | 0.057214 | 935 | 0.022262 | 2737 | 0.065167 | 1.362 | A04 | MICL0.01447034/DOV
Build-In Floor | Mini Canal | MICL.01447034/PNC | 14 | 470 | 34 | 34 | 2196 | 2196 | 2196 | 0.052286 | 854 | 0.020333 | 2501 | 0.059548 | 1.362 | A04 | MICL0.01447034/PNC
Build-In Floor | Mini Canal | MICL.01447034/RBL | 14 | 470 | 34 | 34 | 2584 | 2584 | 2584 | 0.061524 | 1005 | 0.023929 | 2943 | 0.070071 | 1.362 | A04 | MICL0.01447034/RBL
Build-In Floor | Mini Canal | MICL.01447034/RBN | 14 | 470 | 34 | 34 | 2506 | 2506 | 2506 | 0.059667 | 975 | 0.023214 | 2854 | 0.067952 | 1.362 | A04 | MICL0.01447034/RBN
Build-In Floor | Mini Canal | MICL.01447034/RBR | 14 | 470 | 34 | 34 | 2584 | 2584 | 2584 | 0.061524 | 1005 | 0.023929 | 2943 | 0.070071 | 1.362 | A04 | MICL0.01447034/RBR
Build-In Floor | Mini Canal | MICL.01447034/RBV | 14 | 470 | 34 | 34 | 2506 | 2506 | 2506 | 0.059667 | 975 | 0.023214 | 2854 | 0.067952 | 1.362 | A04 | MICL0.01447034/RBV
Build-In Floor | Mini Canal | MICL.01447034/RDB | 14 | 470 | 34 | 34 | 2584 | 2584 | 2584 | 0.061524 | 1005 | 0.023929 | 2943 | 0.070071 | 1.362 | A04 | MICL0.01447034/RDB
Build-In Floor | Mini Canal | MICL.01447034/RMN | 14 | 470 | 34 | 34 | 2506 | 2506 | 2506 | 0.059667 | 975 | 0.023214 | 2854 | 0.067952 | 1.362 | A04 | MICL0.01447034/RMN
Build-In Floor | Mini Canal | MICL.01447034/RMV | 14 | 470 | 34 | 34 | 2506 | 2506 | 2506 | 0.059667 | 975 | 0.023214 | 2854 | 0.067952 | 1.362 | A04 | MICL0.01447034/RMV
Build-In Floor | Mini Canal | MICL.01447034/RNA | 14 | 470 | 34 | 34 | 2584 | 2584 | 2584 | 0.061524 | 1005 | 0.023929 | 2943 | 0.070071 | 1.362 | A04 | MICL0.01447034/RNA
Build-In Floor | Mini Canal | MICL.01447034/RON | 14 | 470 | 34 | 34 | 2506 | 2506 | 2506 | 0.059667 | 975 | 0.023214 | 2854 | 0.067952 | 1.362 | A04 | MICL0.01447034/RON
Build-In Floor | Mini Canal | MICL.01447034/ROV | 14 | 470 | 34 | 34 | 2506 | 2506 | 2506 | 0.059667 | 975 | 0.023214 | 2854 | 0.067952 | 1.362 | A04 | MICL0.01447034/ROV
Build-In Floor | Mini Canal | MICL.01447034/RSS | 14 | 470 | 34 | 34 | 2481 | 2481 | 2481 | 0.059071 | 965 | 0.022976 | 2826 | 0.067286 | 1.362 | A04 | MICL0.01447034/RSS
Build-In Floor | Mini Canal | MICL.01447034/SBL | 14 | 470 | 34 | 34 | 2584 | 2584 | 2584 | 0.061524 | 1005 | 0.023929 | 2943 | 0.070071 | 1.362 | A04 | MICL0.01447034/SBL
Build-In Floor | Mini Canal | MICL.01447034/SBR | 14 | 470 | 34 | 34 | 2584 | 2584 | 2584 | 0.061524 | 1005 | 0.023929 | 2943 | 0.070071 | 1.362 | A04 | MICL0.01447034/SBR
Build-In Floor | Mini Canal | MICL.01447034/SDB | 14 | 470 | 34 | 34 | 2584 | 2584 | 2584 | 0.061524 | 1005 | 0.023929 | 2943 | 0.070071 | 1.362 | A04 | MICL0.01447034/SDB
Build-In Floor | Mini Canal | MICL.01447034/SNA | 14 | 470 | 34 | 34 | 2584 | 2584 | 2584 | 0.061524 | 1005 | 0.023929 | 2943 | 0.070071 | 1.362 | A04 | MICL0.01447034/SNA
Build-In Floor | Mini Canal | MICL.01447034/SNC | 14 | 470 | 34 | 34 | 2584 | 2584 | 2584 | 0.061524 | 1005 | 0.023929 | 2943 | 0.070071 | 1.362 | A04 | MICL0.01447034/SNC
Build-In Floor | Mini Canal | MICL.01447042/ANA | 14 | 470 | 42 | 42 | 2612 | 2612 | 2612 | 0.06219 | 1016 | 0.02419 | 2975 | 0.070833 | 1.362 | A04 | MICL0.01447042/ANA
Build-In Floor | Mini Canal | MICL.01447042/DBL | 14 | 470 | 42 | 42 | 3379 | 3379 | 3379 | 0.080452 | 1314 | 0.031286 | 3849 | 0.091643 | 1.362 | A04 | MICL0.01447042/DBL
Build-In Floor | Mini Canal | MICL.01447042/DBN | 14 | 470 | 42 | 42 | 3239 | 3239 | 3239 | 0.077119 | 1260 | 0.03 | 3689 | 0.087833 | 1.362 | A04 | MICL0.01447042/DBN
Build-In Floor | Mini Canal | MICL.01447042/DBR | 14 | 470 | 42 | 42 | 3379 | 3379 | 3379 | 0.080452 | 1314 | 0.031286 | 3849 | 0.091643 | 1.362 | A04 | MICL0.01447042/DBR
Build-In Floor | Mini Canal | MICL.01447042/DBV | 14 | 470 | 42 | 42 | 3239 | 3239 | 3239 | 0.077119 | 1260 | 0.03 | 3689 | 0.087833 | 1.362 | A04 | MICL0.01447042/DBV
Build-In Floor | Mini Canal | MICL.01447042/DDB | 14 | 470 | 42 | 42 | 3379 | 3379 | 3379 | 0.080452 | 1314 | 0.031286 | 3849 | 0.091643 | 1.362 | A04 | MICL0.01447042/DDB
Build-In Floor | Mini Canal | MICL.01447042/DMN | 14 | 470 | 42 | 42 | 3239 | 3239 | 3239 | 0.077119 | 1260 | 0.03 | 3689 | 0.087833 | 1.362 | A04 | MICL0.01447042/DMN
Build-In Floor | Mini Canal | MICL.01447042/DMV | 14 | 470 | 42 | 42 | 3239 | 3239 | 3239 | 0.077119 | 1260 | 0.03 | 3689 | 0.087833 | 1.362 | A04 | MICL0.01447042/DMV
Build-In Floor | Mini Canal | MICL.01447042/DNA | 14 | 470 | 42 | 42 | 3379 | 3379 | 3379 | 0.080452 | 1314 | 0.031286 | 3849 | 0.091643 | 1.362 | A04 | MICL0.01447042/DNA
Build-In Floor | Mini Canal | MICL.01447042/DNC | 14 | 470 | 42 | 42 | 3379 | 3379 | 3379 | 0.080452 | 1314 | 0.031286 | 3849 | 0.091643 | 1.362 | A04 | MICL0.01447042/DNC
Build-In Floor | Mini Canal | MICL.01447042/DON | 14 | 470 | 42 | 42 | 3239 | 3239 | 3239 | 0.077119 | 1260 | 0.03 | 3689 | 0.087833 | 1.362 | A04 | MICL0.01447042/DON
Build-In Floor | Mini Canal | MICL.01447042/DOV | 14 | 470 | 42 | 42 | 3239 | 3239 | 3239 | 0.077119 | 1260 | 0.03 | 3689 | 0.087833 | 1.362 | A04 | MICL0.01447042/DOV
Build-In Floor | Mini Canal | MICL.01447042/PNC | 14 | 470 | 42 | 42 | 2961 | 2961 | 2961 | 0.0705 | 1152 | 0.027429 | 3373 | 0.08031 | 1.362 | A04 | MICL0.01447042/PNC
Build-In Floor | Mini Canal | MICL.01447042/RBL | 14 | 470 | 42 | 42 | 3483 | 3483 | 3483 | 0.082929 | 1355 | 0.032262 | 3967 | 0.094452 | 1.362 | A04 | MICL0.01447042/RBL
Build-In Floor | Mini Canal | MICL.01447042/RBN | 14 | 470 | 42 | 42 | 3379 | 3379 | 3379 | 0.080452 | 1314 | 0.031286 | 3849 | 0.091643 | 1.362 | A04 | MICL0.01447042/RBN
Build-In Floor | Mini Canal | MICL.01447042/RBR | 14 | 470 | 42 | 42 | 3483 | 3483 | 3483 | 0.082929 | 1355 | 0.032262 | 3967 | 0.094452 | 1.362 | A04 | MICL0.01447042/RBR
Build-In Floor | Mini Canal | MICL.01447042/RBV | 14 | 470 | 42 | 42 | 3379 | 3379 | 3379 | 0.080452 | 1314 | 0.031286 | 3849 | 0.091643 | 1.362 | A04 | MICL0.01447042/RBV
Build-In Floor | Mini Canal | MICL.01447042/RDB | 14 | 470 | 42 | 42 | 3483 | 3483 | 3483 | 0.082929 | 1355 | 0.032262 | 3967 | 0.094452 | 1.362 | A04 | MICL0.01447042/RDB
Build-In Floor | Mini Canal | MICL.01447042/RMN | 14 | 470 | 42 | 42 | 3379 | 3379 | 3379 | 0.080452 | 1314 | 0.031286 | 3849 | 0.091643 | 1.362 | A04 | MICL0.01447042/RMN
Build-In Floor | Mini Canal | MICL.01447042/RMV | 14 | 470 | 42 | 42 | 3379 | 3379 | 3379 | 0.080452 | 1314 | 0.031286 | 3849 | 0.091643 | 1.362 | A04 | MICL0.01447042/RMV
Build-In Floor | Mini Canal | MICL.01447042/RNA | 14 | 470 | 42 | 42 | 3483 | 3483 | 3483 | 0.082929 | 1355 | 0.032262 | 3967 | 0.094452 | 1.362 | A04 | MICL0.01447042/RNA
Build-In Floor | Mini Canal | MICL.01447042/RON | 14 | 470 | 42 | 42 | 3379 | 3379 | 3379 | 0.080452 | 1314 | 0.031286 | 3849 | 0.091643 | 1.362 | A04 | MICL0.01447042/RON
Build-In Floor | Mini Canal | MICL.01447042/ROV | 14 | 470 | 42 | 42 | 3379 | 3379 | 3379 | 0.080452 | 1314 | 0.031286 | 3849 | 0.091643 | 1.362 | A04 | MICL0.01447042/ROV
Build-In Floor | Mini Canal | MICL.01447042/RSS | 14 | 470 | 42 | 42 | 3344 | 3344 | 3344 | 0.079619 | 1301 | 0.030976 | 3809 | 0.09069 | 1.362 | A04 | MICL0.01447042/RSS
Build-In Floor | Mini Canal | MICL.01447042/SBL | 14 | 470 | 42 | 42 | 3483 | 3483 | 3483 | 0.082929 | 1355 | 0.032262 | 3967 | 0.094452 | 1.362 | A04 | MICL0.01447042/SBL
Build-In Floor | Mini Canal | MICL.01447042/SBR | 14 | 470 | 42 | 42 | 3483 | 3483 | 3483 | 0.082929 | 1355 | 0.032262 | 3967 | 0.094452 | 1.362 | A04 | MICL0.01447042/SBR
Build-In Floor | Mini Canal | MICL.01447042/SDB | 14 | 470 | 42 | 42 | 3483 | 3483 | 3483 | 0.082929 | 1355 | 0.032262 | 3967 | 0.094452 | 1.362 | A04 | MICL0.01447042/SDB
Build-In Floor | Mini Canal | MICL.01447042/SNA | 14 | 470 | 42 | 42 | 3483 | 3483 | 3483 | 0.082929 | 1355 | 0.032262 | 3967 | 0.094452 | 1.362 | A04 | MICL0.01447042/SNA
Build-In Floor | Mini Canal | MICL.01447042/SNC | 14 | 470 | 42 | 42 | 3483 | 3483 | 3483 | 0.082929 | 1355 | 0.032262 | 3967 | 0.094452 | 1.362 | A04 | MICL0.01447042/SNC
Build-In Floor | Mini Canal | MICL.01449014/ANA | 14 | 490 | 14 | 14 | 856 | 856 | 856 | 0.020381 | 333 | 0.0079286 | 975 | 0.023214 | 1.362 | A04 | MICL0.01449014/ANA
Build-In Floor | Mini Canal | MICL.01449014/DBL | 14 | 490 | 14 | 14 | 1107 | 1107 | 1107 | 0.026357 | 431 | 0.010262 | 1261 | 0.030024 | 1.362 | A04 | MICL0.01449014/DBL
Build-In Floor | Mini Canal | MICL.01449014/DBN | 14 | 490 | 14 | 14 | 1061 | 1061 | 1061 | 0.025262 | 413 | 0.0098333 | 1208 | 0.028762 | 1.362 | A04 | MICL0.01449014/DBN
Build-In Floor | Mini Canal | MICL.01449014/DBR | 14 | 490 | 14 | 14 | 1107 | 1107 | 1107 | 0.026357 | 431 | 0.010262 | 1261 | 0.030024 | 1.362 | A04 | MICL0.01449014/DBR
Build-In Floor | Mini Canal | MICL.01449014/DBV | 14 | 490 | 14 | 14 | 1061 | 1061 | 1061 | 0.025262 | 413 | 0.0098333 | 1208 | 0.028762 | 1.362 | A04 | MICL0.01449014/DBV
Build-In Floor | Mini Canal | MICL.01449014/DDB | 14 | 490 | 14 | 14 | 1107 | 1107 | 1107 | 0.026357 | 431 | 0.010262 | 1261 | 0.030024 | 1.362 | A04 | MICL0.01449014/DDB
Build-In Floor | Mini Canal | MICL.01449014/DMN | 14 | 490 | 14 | 14 | 1061 | 1061 | 1061 | 0.025262 | 413 | 0.0098333 | 1208 | 0.028762 | 1.362 | A04 | MICL0.01449014/DMN
Build-In Floor | Mini Canal | MICL.01449014/DMV | 14 | 490 | 14 | 14 | 1061 | 1061 | 1061 | 0.025262 | 413 | 0.0098333 | 1208 | 0.028762 | 1.362 | A04 | MICL0.01449014/DMV
Build-In Floor | Mini Canal | MICL.01449014/DNA | 14 | 490 | 14 | 14 | 1107 | 1107 | 1107 | 0.026357 | 431 | 0.010262 | 1261 | 0.030024 | 1.362 | A04 | MICL0.01449014/DNA
Build-In Floor | Mini Canal | MICL.01449014/DNC | 14 | 490 | 14 | 14 | 1107 | 1107 | 1107 | 0.026357 | 431 | 0.010262 | 1261 | 0.030024 | 1.362 | A04 | MICL0.01449014/DNC
Build-In Floor | Mini Canal | MICL.01449014/DON | 14 | 490 | 14 | 14 | 1061 | 1061 | 1061 | 0.025262 | 413 | 0.0098333 | 1208 | 0.028762 | 1.362 | A04 | MICL0.01449014/DON
Build-In Floor | Mini Canal | MICL.01449014/DOV | 14 | 490 | 14 | 14 | 1061 | 1061 | 1061 | 0.025262 | 413 | 0.0098333 | 1208 | 0.028762 | 1.362 | A04 | MICL0.01449014/DOV
Build-In Floor | Mini Canal | MICL.01449014/RBL | 14 | 490 | 14 | 14 | 1141 | 1141 | 1141 | 0.027167 | 444 | 0.010571 | 1300 | 0.030952 | 1.362 | A04 | MICL0.01449014/RBL
Build-In Floor | Mini Canal | MICL.01449014/RBN | 14 | 490 | 14 | 14 | 1107 | 1107 | 1107 | 0.026357 | 431 | 0.010262 | 1261 | 0.030024 | 1.362 | A04 | MICL0.01449014/RBN
Build-In Floor | Mini Canal | MICL.01449014/RBR | 14 | 490 | 14 | 14 | 1141 | 1141 | 1141 | 0.027167 | 444 | 0.010571 | 1300 | 0.030952 | 1.362 | A04 | MICL0.01449014/RBR
Build-In Floor | Mini Canal | MICL.01449014/RBV | 14 | 490 | 14 | 14 | 1107 | 1107 | 1107 | 0.026357 | 431 | 0.010262 | 1261 | 0.030024 | 1.362 | A04 | MICL0.01449014/RBV
Build-In Floor | Mini Canal | MICL.01449014/RDB | 14 | 490 | 14 | 14 | 1141 | 1141 | 1141 | 0.027167 | 444 | 0.010571 | 1300 | 0.030952 | 1.362 | A04 | MICL0.01449014/RDB
Build-In Floor | Mini Canal | MICL.01449014/RMN | 14 | 490 | 14 | 14 | 1107 | 1107 | 1107 | 0.026357 | 431 | 0.010262 | 1261 | 0.030024 | 1.362 | A04 | MICL0.01449014/RMN
Build-In Floor | Mini Canal | MICL.01449014/RMV | 14 | 490 | 14 | 14 | 1107 | 1107 | 1107 | 0.026357 | 431 | 0.010262 | 1261 | 0.030024 | 1.362 | A04 | MICL0.01449014/RMV
Build-In Floor | Mini Canal | MICL.01449014/RNA | 14 | 490 | 14 | 14 | 1141 | 1141 | 1141 | 0.027167 | 444 | 0.010571 | 1300 | 0.030952 | 1.362 | A04 | MICL0.01449014/RNA
Build-In Floor | Mini Canal | MICL.01449014/RON | 14 | 490 | 14 | 14 | 1107 | 1107 | 1107 | 0.026357 | 431 | 0.010262 | 1261 | 0.030024 | 1.362 | A04 | MICL0.01449014/RON
Build-In Floor | Mini Canal | MICL.01449014/ROV | 14 | 490 | 14 | 14 | 1107 | 1107 | 1107 | 0.026357 | 431 | 0.010262 | 1261 | 0.030024 | 1.362 | A04 | MICL0.01449014/ROV
Build-In Floor | Mini Canal | MICL.01449014/RSS | 14 | 490 | 14 | 14 | 1095 | 1095 | 1095 | 0.026071 | 426 | 0.010143 | 1247 | 0.02969 | 1.362 | A04 | MICL0.01449014/RSS
Build-In Floor | Mini Canal | MICL.01449014/SBL | 14 | 490 | 14 | 14 | 1141 | 1141 | 1141 | 0.027167 | 444 | 0.010571 | 1300 | 0.030952 | 1.362 | A04 | MICL0.01449014/SBL
Build-In Floor | Mini Canal | MICL.01449014/SBR | 14 | 490 | 14 | 14 | 1141 | 1141 | 1141 | 0.027167 | 444 | 0.010571 | 1300 | 0.030952 | 1.362 | A04 | MICL0.01449014/SBR
Build-In Floor | Mini Canal | MICL.01449014/SDB | 14 | 490 | 14 | 14 | 1141 | 1141 | 1141 | 0.027167 | 444 | 0.010571 | 1300 | 0.030952 | 1.362 | A04 | MICL0.01449014/SDB
Build-In Floor | Mini Canal | MICL.01449014/SNA | 14 | 490 | 14 | 14 | 1141 | 1141 | 1141 | 0.027167 | 444 | 0.010571 | 1300 | 0.030952 | 1.362 | A04 | MICL0.01449014/SNA
Build-In Floor | Mini Canal | MICL.01449014/SNC | 14 | 490 | 14 | 14 | 1141 | 1141 | 1141 | 0.027167 | 444 | 0.010571 | 1300 | 0.030952 | 1.362 | A04 | MICL0.01449014/SNC
Build-In Floor | Mini Canal | MICL.01449026/ANA | 14 | 490 | 26 | 26 | 1485 | 1485 | 1485 | 0.035357 | 578 | 0.013762 | 1691 | 0.040262 | 1.362 | A04 | MICL0.01449026/ANA
Build-In Floor | Mini Canal | MICL.01449026/DBL | 14 | 490 | 26 | 26 | 1921 | 1921 | 1921 | 0.045738 | 747 | 0.017786 | 2188 | 0.052095 | 1.362 | A04 | MICL0.01449026/DBL
Build-In Floor | Mini Canal | MICL.01449026/DBN | 14 | 490 | 26 | 26 | 1841 | 1841 | 1841 | 0.043833 | 716 | 0.017048 | 2097 | 0.049929 | 1.362 | A04 | MICL0.01449026/DBN
Build-In Floor | Mini Canal | MICL.01449026/DBR | 14 | 490 | 26 | 26 | 1921 | 1921 | 1921 | 0.045738 | 747 | 0.017786 | 2188 | 0.052095 | 1.362 | A04 | MICL0.01449026/DBR
Build-In Floor | Mini Canal | MICL.01449026/DBV | 14 | 490 | 26 | 26 | 1841 | 1841 | 1841 | 0.043833 | 716 | 0.017048 | 2097 | 0.049929 | 1.362 | A04 | MICL0.01449026/DBV
Build-In Floor | Mini Canal | MICL.01449026/DDB | 14 | 490 | 26 | 26 | 1921 | 1921 | 1921 | 0.045738 | 747 | 0.017786 | 2188 | 0.052095 | 1.362 | A04 | MICL0.01449026/DDB
Build-In Floor | Mini Canal | MICL.01449026/DMN | 14 | 490 | 26 | 26 | 1841 | 1841 | 1841 | 0.043833 | 716 | 0.017048 | 2097 | 0.049929 | 1.362 | A04 | MICL0.01449026/DMN
Build-In Floor | Mini Canal | MICL.01449026/DMV | 14 | 490 | 26 | 26 | 1841 | 1841 | 1841 | 0.043833 | 716 | 0.017048 | 2097 | 0.049929 | 1.362 | A04 | MICL0.01449026/DMV
Build-In Floor | Mini Canal | MICL.01449026/DNA | 14 | 490 | 26 | 26 | 1921 | 1921 | 1921 | 0.045738 | 747 | 0.017786 | 2188 | 0.052095 | 1.362 | A04 | MICL0.01449026/DNA
Build-In Floor | Mini Canal | MICL.01449026/DNC | 14 | 490 | 26 | 26 | 1921 | 1921 | 1921 | 0.045738 | 747 | 0.017786 | 2188 | 0.052095 | 1.362 | A04 | MICL0.01449026/DNC
Build-In Floor | Mini Canal | MICL.01449026/DON | 14 | 490 | 26 | 26 | 1841 | 1841 | 1841 | 0.043833 | 716 | 0.017048 | 2097 | 0.049929 | 1.362 | A04 | MICL0.01449026/DON
Build-In Floor | Mini Canal | MICL.01449026/DOV | 14 | 490 | 26 | 26 | 1841 | 1841 | 1841 | 0.043833 | 716 | 0.017048 | 2097 | 0.049929 | 1.362 | A04 | MICL0.01449026/DOV
Build-In Floor | Mini Canal | MICL.01449026/PNC | 14 | 490 | 26 | 26 | 1683 | 1683 | 1683 | 0.040071 | 655 | 0.015595 | 1917 | 0.045643 | 1.362 | A04 | MICL0.01449026/PNC
Build-In Floor | Mini Canal | MICL.01449026/RBL | 14 | 490 | 26 | 26 | 1980 | 1980 | 1980 | 0.047143 | 770 | 0.018333 | 2255 | 0.05369 | 1.362 | A04 | MICL0.01449026/RBL
Build-In Floor | Mini Canal | MICL.01449026/RBN | 14 | 490 | 26 | 26 | 1921 | 1921 | 1921 | 0.045738 | 747 | 0.017786 | 2188 | 0.052095 | 1.362 | A04 | MICL0.01449026/RBN
Build-In Floor | Mini Canal | MICL.01449026/RBR | 14 | 490 | 26 | 26 | 1980 | 1980 | 1980 | 0.047143 | 770 | 0.018333 | 2255 | 0.05369 | 1.362 | A04 | MICL0.01449026/RBR
Build-In Floor | Mini Canal | MICL.01449026/RBV | 14 | 490 | 26 | 26 | 1921 | 1921 | 1921 | 0.045738 | 747 | 0.017786 | 2188 | 0.052095 | 1.362 | A04 | MICL0.01449026/RBV
Build-In Floor | Mini Canal | MICL.01449026/RDB | 14 | 490 | 26 | 26 | 1980 | 1980 | 1980 | 0.047143 | 770 | 0.018333 | 2255 | 0.05369 | 1.362 | A04 | MICL0.01449026/RDB
Build-In Floor | Mini Canal | MICL.01449026/RMN | 14 | 490 | 26 | 26 | 1921 | 1921 | 1921 | 0.045738 | 747 | 0.017786 | 2188 | 0.052095 | 1.362 | A04 | MICL0.01449026/RMN
Build-In Floor | Mini Canal | MICL.01449026/RMV | 14 | 490 | 26 | 26 | 1921 | 1921 | 1921 | 0.045738 | 747 | 0.017786 | 2188 | 0.052095 | 1.362 | A04 | MICL0.01449026/RMV
Build-In Floor | Mini Canal | MICL.01449026/RNA | 14 | 490 | 26 | 26 | 1980 | 1980 | 1980 | 0.047143 | 770 | 0.018333 | 2255 | 0.05369 | 1.362 | A04 | MICL0.01449026/RNA
Build-In Floor | Mini Canal | MICL.01449026/RON | 14 | 490 | 26 | 26 | 1921 | 1921 | 1921 | 0.045738 | 747 | 0.017786 | 2188 | 0.052095 | 1.362 | A04 | MICL0.01449026/RON
Build-In Floor | Mini Canal | MICL.01449026/ROV | 14 | 490 | 26 | 26 | 1921 | 1921 | 1921 | 0.045738 | 747 | 0.017786 | 2188 | 0.052095 | 1.362 | A04 | MICL0.01449026/ROV
Build-In Floor | Mini Canal | MICL.01449026/RSS | 14 | 490 | 26 | 26 | 1901 | 1901 | 1901 | 0.045262 | 739 | 0.017595 | 2165 | 0.051548 | 1.362 | A04 | MICL0.01449026/RSS
Build-In Floor | Mini Canal | MICL.01449026/SBL | 14 | 490 | 26 | 26 | 1980 | 1980 | 1980 | 0.047143 | 770 | 0.018333 | 2255 | 0.05369 | 1.362 | A04 | MICL0.01449026/SBL
Build-In Floor | Mini Canal | MICL.01449026/SBR | 14 | 490 | 26 | 26 | 1980 | 1980 | 1980 | 0.047143 | 770 | 0.018333 | 2255 | 0.05369 | 1.362 | A04 | MICL0.01449026/SBR
Build-In Floor | Mini Canal | MICL.01449026/SDB | 14 | 490 | 26 | 26 | 1980 | 1980 | 1980 | 0.047143 | 770 | 0.018333 | 2255 | 0.05369 | 1.362 | A04 | MICL0.01449026/SDB
Build-In Floor | Mini Canal | MICL.01449026/SNA | 14 | 490 | 26 | 26 | 1980 | 1980 | 1980 | 0.047143 | 770 | 0.018333 | 2255 | 0.05369 | 1.362 | A04 | MICL0.01449026/SNA
Build-In Floor | Mini Canal | MICL.01449026/SNC | 14 | 490 | 26 | 26 | 1980 | 1980 | 1980 | 0.047143 | 770 | 0.018333 | 2255 | 0.05369 | 1.362 | A04 | MICL0.01449026/SNC
Build-In Floor | Mini Canal | MICL.01449034/ANA | 14 | 490 | 34 | 34 | 2027 | 2027 | 2027 | 0.048262 | 789 | 0.018786 | 2309 | 0.054976 | 1.362 | A04 | MICL0.01449034/ANA
Build-In Floor | Mini Canal | MICL.01449034/DBL | 14 | 490 | 34 | 34 | 2621 | 2621 | 2621 | 0.062405 | 1020 | 0.024286 | 2985 | 0.071071 | 1.362 | A04 | MICL0.01449034/DBL
Build-In Floor | Mini Canal | MICL.01449034/DBN | 14 | 490 | 34 | 34 | 2513 | 2513 | 2513 | 0.059833 | 978 | 0.023286 | 2862 | 0.068143 | 1.362 | A04 | MICL0.01449034/DBN
Build-In Floor | Mini Canal | MICL.01449034/DBR | 14 | 490 | 34 | 34 | 2621 | 2621 | 2621 | 0.062405 | 1020 | 0.024286 | 2985 | 0.071071 | 1.362 | A04 | MICL0.01449034/DBR
Build-In Floor | Mini Canal | MICL.01449034/DBV | 14 | 490 | 34 | 34 | 2513 | 2513 | 2513 | 0.059833 | 978 | 0.023286 | 2862 | 0.068143 | 1.362 | A04 | MICL0.01449034/DBV
Build-In Floor | Mini Canal | MICL.01449034/DDB | 14 | 490 | 34 | 34 | 2621 | 2621 | 2621 | 0.062405 | 1020 | 0.024286 | 2985 | 0.071071 | 1.362 | A04 | MICL0.01449034/DDB
Build-In Floor | Mini Canal | MICL.01449034/DMN | 14 | 490 | 34 | 34 | 2513 | 2513 | 2513 | 0.059833 | 978 | 0.023286 | 2862 | 0.068143 | 1.362 | A04 | MICL0.01449034/DMN
Build-In Floor | Mini Canal | MICL.01449034/DMV | 14 | 490 | 34 | 34 | 2513 | 2513 | 2513 | 0.059833 | 978 | 0.023286 | 2862 | 0.068143 | 1.362 | A04 | MICL0.01449034/DMV
Build-In Floor | Mini Canal | MICL.01449034/DNA | 14 | 490 | 34 | 34 | 2621 | 2621 | 2621 | 0.062405 | 1020 | 0.024286 | 2985 | 0.071071 | 1.362 | A04 | MICL0.01449034/DNA
Build-In Floor | Mini Canal | MICL.01449034/DNC | 14 | 490 | 34 | 34 | 2621 | 2621 | 2621 | 0.062405 | 1020 | 0.024286 | 2985 | 0.071071 | 1.362 | A04 | MICL0.01449034/DNC
Build-In Floor | Mini Canal | MICL.01449034/DON | 14 | 490 | 34 | 34 | 2513 | 2513 | 2513 | 0.059833 | 978 | 0.023286 | 2862 | 0.068143 | 1.362 | A04 | MICL0.01449034/DON
Build-In Floor | Mini Canal | MICL.01449034/DOV | 14 | 490 | 34 | 34 | 2513 | 2513 | 2513 | 0.059833 | 978 | 0.023286 | 2862 | 0.068143 | 1.362 | A04 | MICL0.01449034/DOV
Build-In Floor | Mini Canal | MICL.01449034/PNC | 14 | 490 | 34 | 34 | 2297 | 2297 | 2297 | 0.05469 | 894 | 0.021286 | 2616 | 0.062286 | 1.362 | A04 | MICL0.01449034/PNC
Build-In Floor | Mini Canal | MICL.01449034/RBL | 14 | 490 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1051 | 0.025024 | 3078 | 0.073286 | 1.362 | A04 | MICL0.01449034/RBL
Build-In Floor | Mini Canal | MICL.01449034/RBN | 14 | 490 | 34 | 34 | 2621 | 2621 | 2621 | 0.062405 | 1020 | 0.024286 | 2985 | 0.071071 | 1.362 | A04 | MICL0.01449034/RBN
Build-In Floor | Mini Canal | MICL.01449034/RBR | 14 | 490 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1051 | 0.025024 | 3078 | 0.073286 | 1.362 | A04 | MICL0.01449034/RBR
Build-In Floor | Mini Canal | MICL.01449034/RBV | 14 | 490 | 34 | 34 | 2621 | 2621 | 2621 | 0.062405 | 1020 | 0.024286 | 2985 | 0.071071 | 1.362 | A04 | MICL0.01449034/RBV
Build-In Floor | Mini Canal | MICL.01449034/RDB | 14 | 490 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1051 | 0.025024 | 3078 | 0.073286 | 1.362 | A04 | MICL0.01449034/RDB
Build-In Floor | Mini Canal | MICL.01449034/RMN | 14 | 490 | 34 | 34 | 2621 | 2621 | 2621 | 0.062405 | 1020 | 0.024286 | 2985 | 0.071071 | 1.362 | A04 | MICL0.01449034/RMN
Build-In Floor | Mini Canal | MICL.01449034/RMV | 14 | 490 | 34 | 34 | 2621 | 2621 | 2621 | 0.062405 | 1020 | 0.024286 | 2985 | 0.071071 | 1.362 | A04 | MICL0.01449034/RMV
Build-In Floor | Mini Canal | MICL.01449034/RNA | 14 | 490 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1051 | 0.025024 | 3078 | 0.073286 | 1.362 | A04 | MICL0.01449034/RNA
Build-In Floor | Mini Canal | MICL.01449034/RON | 14 | 490 | 34 | 34 | 2621 | 2621 | 2621 | 0.062405 | 1020 | 0.024286 | 2985 | 0.071071 | 1.362 | A04 | MICL0.01449034/RON
Build-In Floor | Mini Canal | MICL.01449034/ROV | 14 | 490 | 34 | 34 | 2621 | 2621 | 2621 | 0.062405 | 1020 | 0.024286 | 2985 | 0.071071 | 1.362 | A04 | MICL0.01449034/ROV
Build-In Floor | Mini Canal | MICL.01449034/RSS | 14 | 490 | 34 | 34 | 2594 | 2594 | 2594 | 0.061762 | 1009 | 0.024024 | 2955 | 0.070357 | 1.362 | A04 | MICL0.01449034/RSS
Build-In Floor | Mini Canal | MICL.01449034/SBL | 14 | 490 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1051 | 0.025024 | 3078 | 0.073286 | 1.362 | A04 | MICL0.01449034/SBL
Build-In Floor | Mini Canal | MICL.01449034/SBR | 14 | 490 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1051 | 0.025024 | 3078 | 0.073286 | 1.362 | A04 | MICL0.01449034/SBR
Build-In Floor | Mini Canal | MICL.01449034/SDB | 14 | 490 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1051 | 0.025024 | 3078 | 0.073286 | 1.362 | A04 | MICL0.01449034/SDB
Build-In Floor | Mini Canal | MICL.01449034/SNA | 14 | 490 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1051 | 0.025024 | 3078 | 0.073286 | 1.362 | A04 | MICL0.01449034/SNA
Build-In Floor | Mini Canal | MICL.01449034/SNC | 14 | 490 | 34 | 34 | 2702 | 2702 | 2702 | 0.064333 | 1051 | 0.025024 | 3078 | 0.073286 | 1.362 | A04 | MICL0.01449034/SNC
Build-In Floor | Mini Canal | MICL.01449042/ANA | 14 | 490 | 42 | 42 | 2732 | 2732 | 2732 | 0.065048 | 1063 | 0.02531 | 3112 | 0.074095 | 1.362 | A04 | MICL0.01449042/ANA
Build-In Floor | Mini Canal | MICL.01449042/DBL | 14 | 490 | 42 | 42 | 3533 | 3533 | 3533 | 0.084119 | 1374 | 0.032714 | 4024 | 0.09581 | 1.362 | A04 | MICL0.01449042/DBL
Build-In Floor | Mini Canal | MICL.01449042/DBN | 14 | 490 | 42 | 42 | 3387 | 3387 | 3387 | 0.080643 | 1318 | 0.031381 | 3858 | 0.091857 | 1.362 | A04 | MICL0.01449042/DBN
Build-In Floor | Mini Canal | MICL.01449042/DBR | 14 | 490 | 42 | 42 | 3533 | 3533 | 3533 | 0.084119 | 1374 | 0.032714 | 4024 | 0.09581 | 1.362 | A04 | MICL0.01449042/DBR
Build-In Floor | Mini Canal | MICL.01449042/DBV | 14 | 490 | 42 | 42 | 3387 | 3387 | 3387 | 0.080643 | 1318 | 0.031381 | 3858 | 0.091857 | 1.362 | A04 | MICL0.01449042/DBV
Build-In Floor | Mini Canal | MICL.01449042/DDB | 14 | 490 | 42 | 42 | 3533 | 3533 | 3533 | 0.084119 | 1374 | 0.032714 | 4024 | 0.09581 | 1.362 | A04 | MICL0.01449042/DDB
Build-In Floor | Mini Canal | MICL.01449042/DMN | 14 | 490 | 42 | 42 | 3387 | 3387 | 3387 | 0.080643 | 1318 | 0.031381 | 3858 | 0.091857 | 1.362 | A04 | MICL0.01449042/DMN
Build-In Floor | Mini Canal | MICL.01449042/DMV | 14 | 490 | 42 | 42 | 3387 | 3387 | 3387 | 0.080643 | 1318 | 0.031381 | 3858 | 0.091857 | 1.362 | A04 | MICL0.01449042/DMV
Build-In Floor | Mini Canal | MICL.01449042/DNA | 14 | 490 | 42 | 42 | 3533 | 3533 | 3533 | 0.084119 | 1374 | 0.032714 | 4024 | 0.09581 | 1.362 | A04 | MICL0.01449042/DNA
Build-In Floor | Mini Canal | MICL.01449042/DNC | 14 | 490 | 42 | 42 | 3533 | 3533 | 3533 | 0.084119 | 1374 | 0.032714 | 4024 | 0.09581 | 1.362 | A04 | MICL0.01449042/DNC
Build-In Floor | Mini Canal | MICL.01449042/DON | 14 | 490 | 42 | 42 | 3387 | 3387 | 3387 | 0.080643 | 1318 | 0.031381 | 3858 | 0.091857 | 1.362 | A04 | MICL0.01449042/DON
Build-In Floor | Mini Canal | MICL.01449042/DOV | 14 | 490 | 42 | 42 | 3387 | 3387 | 3387 | 0.080643 | 1318 | 0.031381 | 3858 | 0.091857 | 1.362 | A04 | MICL0.01449042/DOV
Build-In Floor | Mini Canal | MICL.01449042/PNC | 14 | 490 | 42 | 42 | 3096 | 3096 | 3096 | 0.073714 | 1204 | 0.028667 | 3526 | 0.083952 | 1.362 | A04 | MICL0.01449042/PNC
Build-In Floor | Mini Canal | MICL.01449042/RBL | 14 | 490 | 42 | 42 | 3642 | 3642 | 3642 | 0.086714 | 1417 | 0.033738 | 4148 | 0.098762 | 1.362 | A04 | MICL0.01449042/RBL
Build-In Floor | Mini Canal | MICL.01449042/RBN | 14 | 490 | 42 | 42 | 3533 | 3533 | 3533 | 0.084119 | 1374 | 0.032714 | 4024 | 0.09581 | 1.362 | A04 | MICL0.01449042/RBN
Build-In Floor | Mini Canal | MICL.01449042/RBR | 14 | 490 | 42 | 42 | 3642 | 3642 | 3642 | 0.086714 | 1417 | 0.033738 | 4148 | 0.098762 | 1.362 | A04 | MICL0.01449042/RBR
Build-In Floor | Mini Canal | MICL.01449042/RBV | 14 | 490 | 42 | 42 | 3533 | 3533 | 3533 | 0.084119 | 1374 | 0.032714 | 4024 | 0.09581 | 1.362 | A04 | MICL0.01449042/RBV
Build-In Floor | Mini Canal | MICL.01449042/RDB | 14 | 490 | 42 | 42 | 3642 | 3642 | 3642 | 0.086714 | 1417 | 0.033738 | 4148 | 0.098762 | 1.362 | A04 | MICL0.01449042/RDB
Build-In Floor | Mini Canal | MICL.01449042/RMN | 14 | 490 | 42 | 42 | 3533 | 3533 | 3533 | 0.084119 | 1374 | 0.032714 | 4024 | 0.09581 | 1.362 | A04 | MICL0.01449042/RMN
Build-In Floor | Mini Canal | MICL.01449042/RMV | 14 | 490 | 42 | 42 | 3533 | 3533 | 3533 | 0.084119 | 1374 | 0.032714 | 4024 | 0.09581 | 1.362 | A04 | MICL0.01449042/RMV
Build-In Floor | Mini Canal | MICL.01449042/RNA | 14 | 490 | 42 | 42 | 3642 | 3642 | 3642 | 0.086714 | 1417 | 0.033738 | 4148 | 0.098762 | 1.362 | A04 | MICL0.01449042/RNA
Build-In Floor | Mini Canal | MICL.01449042/RON | 14 | 490 | 42 | 42 | 3533 | 3533 | 3533 | 0.084119 | 1374 | 0.032714 | 4024 | 0.09581 | 1.362 | A04 | MICL0.01449042/RON
Build-In Floor | Mini Canal | MICL.01449042/ROV | 14 | 490 | 42 | 42 | 3533 | 3533 | 3533 | 0.084119 | 1374 | 0.032714 | 4024 | 0.09581 | 1.362 | A04 | MICL0.01449042/ROV
Build-In Floor | Mini Canal | MICL.01449042/RSS | 14 | 490 | 42 | 42 | 3496 | 3496 | 3496 | 0.083238 | 1360 | 0.032381 | 3982 | 0.09481 | 1.362 | A04 | MICL0.01449042/RSS
Build-In Floor | Mini Canal | MICL.01449042/SBL | 14 | 490 | 42 | 42 | 3642 | 3642 | 3642 | 0.086714 | 1417 | 0.033738 | 4148 | 0.098762 | 1.362 | A04 | MICL0.01449042/SBL
Build-In Floor | Mini Canal | MICL.01449042/SBR | 14 | 490 | 42 | 42 | 3642 | 3642 | 3642 | 0.086714 | 1417 | 0.033738 | 4148 | 0.098762 | 1.362 | A04 | MICL0.01449042/SBR
Build-In Floor | Mini Canal | MICL.01449042/SDB | 14 | 490 | 42 | 42 | 3642 | 3642 | 3642 | 0.086714 | 1417 | 0.033738 | 4148 | 0.098762 | 1.362 | A04 | MICL0.01449042/SDB
Build-In Floor | Mini Canal | MICL.01449042/SNA | 14 | 490 | 42 | 42 | 3642 | 3642 | 3642 | 0.086714 | 1417 | 0.033738 | 4148 | 0.098762 | 1.362 | A04 | MICL0.01449042/SNA
Build-In Floor | Mini Canal | MICL.01449042/SNC | 14 | 490 | 42 | 42 | 3642 | 3642 | 3642 | 0.086714 | 1417 | 0.033738 | 4148 | 0.098762 | 1.362 | A04 | MICL0.01449042/SNC
Build-In Floor | Mini Canal | MICL.01907026/ANA | 19 | 70 | 26 | 26 | 147 | 147 | 147 | 0.0035 | 57 | 0.0013571 | 167 | 0.0039762 | 1.362 | A04 | MICL0.01907026/ANA
Build-In Floor | Mini Canal | MICL.01907026/DBL | 19 | 70 | 26 | 26 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.01907026/DBL
Build-In Floor | Mini Canal | MICL.01907026/DBN | 19 | 70 | 26 | 26 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01907026/DBN
Build-In Floor | Mini Canal | MICL.01907026/DBR | 19 | 70 | 26 | 26 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.01907026/DBR
Build-In Floor | Mini Canal | MICL.01907026/DBV | 19 | 70 | 26 | 26 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01907026/DBV
Build-In Floor | Mini Canal | MICL.01907026/DDB | 19 | 70 | 26 | 26 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.01907026/DDB
Build-In Floor | Mini Canal | MICL.01907026/DMN | 19 | 70 | 26 | 26 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01907026/DMN
Build-In Floor | Mini Canal | MICL.01907026/DMV | 19 | 70 | 26 | 26 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01907026/DMV
Build-In Floor | Mini Canal | MICL.01907026/DNA | 19 | 70 | 26 | 26 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.01907026/DNA
Build-In Floor | Mini Canal | MICL.01907026/DNC | 19 | 70 | 26 | 26 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.01907026/DNC
Build-In Floor | Mini Canal | MICL.01907026/DON | 19 | 70 | 26 | 26 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01907026/DON
Build-In Floor | Mini Canal | MICL.01907026/DOV | 19 | 70 | 26 | 26 | 182 | 182 | 182 | 0.0043333 | 71 | 0.0016905 | 207 | 0.0049286 | 1.362 | A04 | MICL0.01907026/DOV
Build-In Floor | Mini Canal | MICL.01907026/PNC | 19 | 70 | 26 | 26 | 167 | 167 | 167 | 0.0039762 | 65 | 0.0015476 | 190 | 0.0045238 | 1.362 | A04 | MICL0.01907026/PNC
Build-In Floor | Mini Canal | MICL.01907026/RBL | 19 | 70 | 26 | 26 | 196 | 196 | 196 | 0.0046667 | 76 | 0.0018095 | 223 | 0.0053095 | 1.362 | A04 | MICL0.01907026/RBL
Build-In Floor | Mini Canal | MICL.01907026/RBN | 19 | 70 | 26 | 26 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.01907026/RBN
Build-In Floor | Mini Canal | MICL.01907026/RBR | 19 | 70 | 26 | 26 | 196 | 196 | 196 | 0.0046667 | 76 | 0.0018095 | 223 | 0.0053095 | 1.362 | A04 | MICL0.01907026/RBR
Build-In Floor | Mini Canal | MICL.01907026/RBV | 19 | 70 | 26 | 26 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.01907026/RBV
Build-In Floor | Mini Canal | MICL.01907026/RDB | 19 | 70 | 26 | 26 | 196 | 196 | 196 | 0.0046667 | 76 | 0.0018095 | 223 | 0.0053095 | 1.362 | A04 | MICL0.01907026/RDB
Build-In Floor | Mini Canal | MICL.01907026/RMN | 19 | 70 | 26 | 26 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.01907026/RMN
Build-In Floor | Mini Canal | MICL.01907026/RMV | 19 | 70 | 26 | 26 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.01907026/RMV
Build-In Floor | Mini Canal | MICL.01907026/RNA | 19 | 70 | 26 | 26 | 196 | 196 | 196 | 0.0046667 | 76 | 0.0018095 | 223 | 0.0053095 | 1.362 | A04 | MICL0.01907026/RNA
Build-In Floor | Mini Canal | MICL.01907026/RON | 19 | 70 | 26 | 26 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.01907026/RON
Build-In Floor | Mini Canal | MICL.01907026/ROV | 19 | 70 | 26 | 26 | 190 | 190 | 190 | 0.0045238 | 74 | 0.0017619 | 216 | 0.0051429 | 1.362 | A04 | MICL0.01907026/ROV
Build-In Floor | Mini Canal | MICL.01907026/RSS | 19 | 70 | 26 | 26 | 188 | 188 | 188 | 0.0044762 | 73 | 0.0017381 | 214 | 0.0050952 | 1.362 | A04 | MICL0.01907026/RSS
Build-In Floor | Mini Canal | MICL.01907026/SBL | 19 | 70 | 26 | 26 | 196 | 196 | 196 | 0.0046667 | 76 | 0.0018095 | 223 | 0.0053095 | 1.362 | A04 | MICL0.01907026/SBL
Build-In Floor | Mini Canal | MICL.01907026/SBR | 19 | 70 | 26 | 26 | 196 | 196 | 196 | 0.0046667 | 76 | 0.0018095 | 223 | 0.0053095 | 1.362 | A04 | MICL0.01907026/SBR
Build-In Floor | Mini Canal | MICL.01907026/SDB | 19 | 70 | 26 | 26 | 196 | 196 | 196 | 0.0046667 | 76 | 0.0018095 | 223 | 0.0053095 | 1.362 | A04 | MICL0.01907026/SDB
Build-In Floor | Mini Canal | MICL.01907026/SNA | 19 | 70 | 26 | 26 | 196 | 196 | 196 | 0.0046667 | 76 | 0.0018095 | 223 | 0.0053095 | 1.362 | A04 | MICL0.01907026/SNA
Build-In Floor | Mini Canal | MICL.01907026/SNC | 19 | 70 | 26 | 26 | 196 | 196 | 196 | 0.0046667 | 76 | 0.0018095 | 223 | 0.0053095 | 1.362 | A04 | MICL0.01907026/SNC
Build-In Floor | Mini Canal | MICL.01907034/ANA | 19 | 70 | 34 | 34 | 199 | 199 | 199 | 0.0047381 | 77 | 0.0018333 | 227 | 0.0054048 | 1.362 | A04 | MICL0.01907034/ANA
Build-In Floor | Mini Canal | MICL.01907034/DBL | 19 | 70 | 34 | 34 | 257 | 257 | 257 | 0.006119 | 100 | 0.002381 | 293 | 0.0069762 | 1.362 | A04 | MICL0.01907034/DBL
Build-In Floor | Mini Canal | MICL.01907034/DBN | 19 | 70 | 34 | 34 | 246 | 246 | 246 | 0.0058571 | 96 | 0.0022857 | 280 | 0.0066667 | 1.362 | A04 | MICL0.01907034/DBN
Build-In Floor | Mini Canal | MICL.01907034/DBR | 19 | 70 | 34 | 34 | 257 | 257 | 257 | 0.006119 | 100 | 0.002381 | 293 | 0.0069762 | 1.362 | A04 | MICL0.01907034/DBR
Build-In Floor | Mini Canal | MICL.01907034/DBV | 19 | 70 | 34 | 34 | 246 | 246 | 246 | 0.0058571 | 96 | 0.0022857 | 280 | 0.0066667 | 1.362 | A04 | MICL0.01907034/DBV
Build-In Floor | Mini Canal | MICL.01907034/DDB | 19 | 70 | 34 | 34 | 257 | 257 | 257 | 0.006119 | 100 | 0.002381 | 293 | 0.0069762 | 1.362 | A04 | MICL0.01907034/DDB
Build-In Floor | Mini Canal | MICL.01907034/DMN | 19 | 70 | 34 | 34 | 246 | 246 | 246 | 0.0058571 | 96 | 0.0022857 | 280 | 0.0066667 | 1.362 | A04 | MICL0.01907034/DMN
Build-In Floor | Mini Canal | MICL.01907034/DMV | 19 | 70 | 34 | 34 | 246 | 246 | 246 | 0.0058571 | 96 | 0.0022857 | 280 | 0.0066667 | 1.362 | A04 | MICL0.01907034/DMV
Build-In Floor | Mini Canal | MICL.01907034/DNA | 19 | 70 | 34 | 34 | 257 | 257 | 257 | 0.006119 | 100 | 0.002381 | 293 | 0.0069762 | 1.362 | A04 | MICL0.01907034/DNA
Build-In Floor | Mini Canal | MICL.01907034/DNC | 19 | 70 | 34 | 34 | 257 | 257 | 257 | 0.006119 | 100 | 0.002381 | 293 | 0.0069762 | 1.362 | A04 | MICL0.01907034/DNC
Build-In Floor | Mini Canal | MICL.01907034/DON | 19 | 70 | 34 | 34 | 246 | 246 | 246 | 0.0058571 | 96 | 0.0022857 | 280 | 0.0066667 | 1.362 | A04 | MICL0.01907034/DON
Build-In Floor | Mini Canal | MICL.01907034/DOV | 19 | 70 | 34 | 34 | 246 | 246 | 246 | 0.0058571 | 96 | 0.0022857 | 280 | 0.0066667 | 1.362 | A04 | MICL0.01907034/DOV
Build-In Floor | Mini Canal | MICL.01907034/PNC | 19 | 70 | 34 | 34 | 225 | 225 | 225 | 0.0053571 | 88 | 0.0020952 | 256 | 0.0060952 | 1.362 | A04 | MICL0.01907034/PNC
Build-In Floor | Mini Canal | MICL.01907034/RBL | 19 | 70 | 34 | 34 | 265 | 265 | 265 | 0.0063095 | 103 | 0.0024524 | 302 | 0.0071905 | 1.362 | A04 | MICL0.01907034/RBL
Build-In Floor | Mini Canal | MICL.01907034/RBN | 19 | 70 | 34 | 34 | 257 | 257 | 257 | 0.006119 | 100 | 0.002381 | 293 | 0.0069762 | 1.362 | A04 | MICL0.01907034/RBN
Build-In Floor | Mini Canal | MICL.01907034/RBR | 19 | 70 | 34 | 34 | 265 | 265 | 265 | 0.0063095 | 103 | 0.0024524 | 302 | 0.0071905 | 1.362 | A04 | MICL0.01907034/RBR
Build-In Floor | Mini Canal | MICL.01907034/RBV | 19 | 70 | 34 | 34 | 257 | 257 | 257 | 0.006119 | 100 | 0.002381 | 293 | 0.0069762 | 1.362 | A04 | MICL0.01907034/RBV
Build-In Floor | Mini Canal | MICL.01907034/RDB | 19 | 70 | 34 | 34 | 265 | 265 | 265 | 0.0063095 | 103 | 0.0024524 | 302 | 0.0071905 | 1.362 | A04 | MICL0.01907034/RDB
Build-In Floor | Mini Canal | MICL.01907034/RMN | 19 | 70 | 34 | 34 | 257 | 257 | 257 | 0.006119 | 100 | 0.002381 | 293 | 0.0069762 | 1.362 | A04 | MICL0.01907034/RMN
Build-In Floor | Mini Canal | MICL.01907034/RMV | 19 | 70 | 34 | 34 | 257 | 257 | 257 | 0.006119 | 100 | 0.002381 | 293 | 0.0069762 | 1.362 | A04 | MICL0.01907034/RMV
Build-In Floor | Mini Canal | MICL.01907034/RNA | 19 | 70 | 34 | 34 | 265 | 265 | 265 | 0.0063095 | 103 | 0.0024524 | 302 | 0.0071905 | 1.362 | A04 | MICL0.01907034/RNA
Build-In Floor | Mini Canal | MICL.01907034/RON | 19 | 70 | 34 | 34 | 257 | 257 | 257 | 0.006119 | 100 | 0.002381 | 293 | 0.0069762 | 1.362 | A04 | MICL0.01907034/RON
Build-In Floor | Mini Canal | MICL.01907034/ROV | 19 | 70 | 34 | 34 | 257 | 257 | 257 | 0.006119 | 100 | 0.002381 | 293 | 0.0069762 | 1.362 | A04 | MICL0.01907034/ROV
Build-In Floor | Mini Canal | MICL.01907034/RSS | 19 | 70 | 34 | 34 | 254 | 254 | 254 | 0.0060476 | 99 | 0.0023571 | 289 | 0.006881 | 1.362 | A04 | MICL0.01907034/RSS
Build-In Floor | Mini Canal | MICL.01907034/SBL | 19 | 70 | 34 | 34 | 265 | 265 | 265 | 0.0063095 | 103 | 0.0024524 | 302 | 0.0071905 | 1.362 | A04 | MICL0.01907034/SBL
Build-In Floor | Mini Canal | MICL.01907034/SBR | 19 | 70 | 34 | 34 | 265 | 265 | 265 | 0.0063095 | 103 | 0.0024524 | 302 | 0.0071905 | 1.362 | A04 | MICL0.01907034/SBR
Build-In Floor | Mini Canal | MICL.01907034/SDB | 19 | 70 | 34 | 34 | 265 | 265 | 265 | 0.0063095 | 103 | 0.0024524 | 302 | 0.0071905 | 1.362 | A04 | MICL0.01907034/SDB
Build-In Floor | Mini Canal | MICL.01907034/SNA | 19 | 70 | 34 | 34 | 265 | 265 | 265 | 0.0063095 | 103 | 0.0024524 | 302 | 0.0071905 | 1.362 | A04 | MICL0.01907034/SNA
Build-In Floor | Mini Canal | MICL.01907034/SNC | 19 | 70 | 34 | 34 | 265 | 265 | 265 | 0.0063095 | 103 | 0.0024524 | 302 | 0.0071905 | 1.362 | A04 | MICL0.01907034/SNC
Build-In Floor | Mini Canal | MICL.01907042/ANA | 19 | 70 | 42 | 42 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01907042/ANA
Build-In Floor | Mini Canal | MICL.01907042/DBL | 19 | 70 | 42 | 42 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01907042/DBL
Build-In Floor | Mini Canal | MICL.01907042/DBN | 19 | 70 | 42 | 42 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01907042/DBN
Build-In Floor | Mini Canal | MICL.01907042/DBR | 19 | 70 | 42 | 42 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01907042/DBR
Build-In Floor | Mini Canal | MICL.01907042/DBV | 19 | 70 | 42 | 42 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01907042/DBV
Build-In Floor | Mini Canal | MICL.01907042/DDB | 19 | 70 | 42 | 42 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01907042/DDB
Build-In Floor | Mini Canal | MICL.01907042/DMN | 19 | 70 | 42 | 42 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01907042/DMN
Build-In Floor | Mini Canal | MICL.01907042/DMV | 19 | 70 | 42 | 42 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01907042/DMV
Build-In Floor | Mini Canal | MICL.01907042/DNA | 19 | 70 | 42 | 42 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01907042/DNA
Build-In Floor | Mini Canal | MICL.01907042/DNC | 19 | 70 | 42 | 42 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01907042/DNC
Build-In Floor | Mini Canal | MICL.01907042/DON | 19 | 70 | 42 | 42 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01907042/DON
Build-In Floor | Mini Canal | MICL.01907042/DOV | 19 | 70 | 42 | 42 | 338 | 338 | 338 | 0.0080476 | 131 | 0.003119 | 385 | 0.0091667 | 1.362 | A04 | MICL0.01907042/DOV
Build-In Floor | Mini Canal | MICL.01907042/PNC | 19 | 70 | 42 | 42 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01907042/PNC
Build-In Floor | Mini Canal | MICL.01907042/RBL | 19 | 70 | 42 | 42 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01907042/RBL
Build-In Floor | Mini Canal | MICL.01907042/RBN | 19 | 70 | 42 | 42 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01907042/RBN
Build-In Floor | Mini Canal | MICL.01907042/RBR | 19 | 70 | 42 | 42 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01907042/RBR
Build-In Floor | Mini Canal | MICL.01907042/RBV | 19 | 70 | 42 | 42 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01907042/RBV
Build-In Floor | Mini Canal | MICL.01907042/RDB | 19 | 70 | 42 | 42 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01907042/RDB
Build-In Floor | Mini Canal | MICL.01907042/RMN | 19 | 70 | 42 | 42 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01907042/RMN
Build-In Floor | Mini Canal | MICL.01907042/RMV | 19 | 70 | 42 | 42 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01907042/RMV
Build-In Floor | Mini Canal | MICL.01907042/RNA | 19 | 70 | 42 | 42 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01907042/RNA
Build-In Floor | Mini Canal | MICL.01907042/RON | 19 | 70 | 42 | 42 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01907042/RON
Build-In Floor | Mini Canal | MICL.01907042/ROV | 19 | 70 | 42 | 42 | 352 | 352 | 352 | 0.008381 | 137 | 0.0032619 | 401 | 0.0095476 | 1.362 | A04 | MICL0.01907042/ROV
Build-In Floor | Mini Canal | MICL.01907042/RSS | 19 | 70 | 42 | 42 | 348 | 348 | 348 | 0.0082857 | 135 | 0.0032143 | 396 | 0.0094286 | 1.362 | A04 | MICL0.01907042/RSS
Build-In Floor | Mini Canal | MICL.01907042/SBL | 19 | 70 | 42 | 42 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01907042/SBL
Build-In Floor | Mini Canal | MICL.01907042/SBR | 19 | 70 | 42 | 42 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01907042/SBR
Build-In Floor | Mini Canal | MICL.01907042/SDB | 19 | 70 | 42 | 42 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01907042/SDB
Build-In Floor | Mini Canal | MICL.01907042/SNA | 19 | 70 | 42 | 42 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01907042/SNA
Build-In Floor | Mini Canal | MICL.01907042/SNC | 19 | 70 | 42 | 42 | 363 | 363 | 363 | 0.0086429 | 141 | 0.0033571 | 413 | 0.0098333 | 1.362 | A04 | MICL0.01907042/SNC
Build-In Floor | Mini Canal | MICL.01908026/ANA | 19 | 80 | 26 | 26 | 184 | 184 | 184 | 0.004381 | 72 | 0.0017143 | 210 | 0.005 | 1.362 | A04 | MICL0.01908026/ANA
Build-In Floor | Mini Canal | MICL.01908026/DBL | 19 | 80 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01908026/DBL
Build-In Floor | Mini Canal | MICL.01908026/DBN | 19 | 80 | 26 | 26 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01908026/DBN
Build-In Floor | Mini Canal | MICL.01908026/DBR | 19 | 80 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01908026/DBR
Build-In Floor | Mini Canal | MICL.01908026/DBV | 19 | 80 | 26 | 26 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01908026/DBV
Build-In Floor | Mini Canal | MICL.01908026/DDB | 19 | 80 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01908026/DDB
Build-In Floor | Mini Canal | MICL.01908026/DMN | 19 | 80 | 26 | 26 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01908026/DMN
Build-In Floor | Mini Canal | MICL.01908026/DMV | 19 | 80 | 26 | 26 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01908026/DMV
Build-In Floor | Mini Canal | MICL.01908026/DNA | 19 | 80 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01908026/DNA
Build-In Floor | Mini Canal | MICL.01908026/DNC | 19 | 80 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01908026/DNC
Build-In Floor | Mini Canal | MICL.01908026/DON | 19 | 80 | 26 | 26 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01908026/DON
Build-In Floor | Mini Canal | MICL.01908026/DOV | 19 | 80 | 26 | 26 | 228 | 228 | 228 | 0.0054286 | 89 | 0.002119 | 260 | 0.0061905 | 1.362 | A04 | MICL0.01908026/DOV
Build-In Floor | Mini Canal | MICL.01908026/PNC | 19 | 80 | 26 | 26 | 208 | 208 | 208 | 0.0049524 | 81 | 0.0019286 | 237 | 0.0056429 | 1.362 | A04 | MICL0.01908026/PNC
Build-In Floor | Mini Canal | MICL.01908026/RBL | 19 | 80 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01908026/RBL
Build-In Floor | Mini Canal | MICL.01908026/RBN | 19 | 80 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01908026/RBN
Build-In Floor | Mini Canal | MICL.01908026/RBR | 19 | 80 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01908026/RBR
Build-In Floor | Mini Canal | MICL.01908026/RBV | 19 | 80 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01908026/RBV
Build-In Floor | Mini Canal | MICL.01908026/RDB | 19 | 80 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01908026/RDB
Build-In Floor | Mini Canal | MICL.01908026/RMN | 19 | 80 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01908026/RMN
Build-In Floor | Mini Canal | MICL.01908026/RMV | 19 | 80 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01908026/RMV
Build-In Floor | Mini Canal | MICL.01908026/RNA | 19 | 80 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01908026/RNA
Build-In Floor | Mini Canal | MICL.01908026/RON | 19 | 80 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01908026/RON
Build-In Floor | Mini Canal | MICL.01908026/ROV | 19 | 80 | 26 | 26 | 238 | 238 | 238 | 0.0056667 | 93 | 0.0022143 | 271 | 0.0064524 | 1.362 | A04 | MICL0.01908026/ROV
Build-In Floor | Mini Canal | MICL.01908026/RSS | 19 | 80 | 26 | 26 | 235 | 235 | 235 | 0.0055952 | 91 | 0.0021667 | 268 | 0.006381 | 1.362 | A04 | MICL0.01908026/RSS
Build-In Floor | Mini Canal | MICL.01908026/SBL | 19 | 80 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01908026/SBL
Build-In Floor | Mini Canal | MICL.01908026/SBR | 19 | 80 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01908026/SBR
Build-In Floor | Mini Canal | MICL.01908026/SDB | 19 | 80 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01908026/SDB
Build-In Floor | Mini Canal | MICL.01908026/SNA | 19 | 80 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01908026/SNA
Build-In Floor | Mini Canal | MICL.01908026/SNC | 19 | 80 | 26 | 26 | 245 | 245 | 245 | 0.0058333 | 95 | 0.0022619 | 279 | 0.0066429 | 1.362 | A04 | MICL0.01908026/SNC
Build-In Floor | Mini Canal | MICL.01908034/ANA | 19 | 80 | 34 | 34 | 249 | 249 | 249 | 0.0059286 | 97 | 0.0023095 | 284 | 0.0067619 | 1.362 | A04 | MICL0.01908034/ANA
Build-In Floor | Mini Canal | MICL.01908034/DBL | 19 | 80 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.01908034/DBL
Build-In Floor | Mini Canal | MICL.01908034/DBN | 19 | 80 | 34 | 34 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01908034/DBN
Build-In Floor | Mini Canal | MICL.01908034/DBR | 19 | 80 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.01908034/DBR
Build-In Floor | Mini Canal | MICL.01908034/DBV | 19 | 80 | 34 | 34 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01908034/DBV
Build-In Floor | Mini Canal | MICL.01908034/DDB | 19 | 80 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.01908034/DDB
Build-In Floor | Mini Canal | MICL.01908034/DMN | 19 | 80 | 34 | 34 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01908034/DMN
Build-In Floor | Mini Canal | MICL.01908034/DMV | 19 | 80 | 34 | 34 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01908034/DMV
Build-In Floor | Mini Canal | MICL.01908034/DNA | 19 | 80 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.01908034/DNA
Build-In Floor | Mini Canal | MICL.01908034/DNC | 19 | 80 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.01908034/DNC
Build-In Floor | Mini Canal | MICL.01908034/DON | 19 | 80 | 34 | 34 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01908034/DON
Build-In Floor | Mini Canal | MICL.01908034/DOV | 19 | 80 | 34 | 34 | 309 | 309 | 309 | 0.0073571 | 120 | 0.0028571 | 352 | 0.008381 | 1.362 | A04 | MICL0.01908034/DOV
Build-In Floor | Mini Canal | MICL.01908034/PNC | 19 | 80 | 34 | 34 | 282 | 282 | 282 | 0.0067143 | 110 | 0.002619 | 321 | 0.0076429 | 1.362 | A04 | MICL0.01908034/PNC
Build-In Floor | Mini Canal | MICL.01908034/RBL | 19 | 80 | 34 | 34 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01908034/RBL
Build-In Floor | Mini Canal | MICL.01908034/RBN | 19 | 80 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.01908034/RBN
Build-In Floor | Mini Canal | MICL.01908034/RBR | 19 | 80 | 34 | 34 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01908034/RBR
Build-In Floor | Mini Canal | MICL.01908034/RBV | 19 | 80 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.01908034/RBV
Build-In Floor | Mini Canal | MICL.01908034/RDB | 19 | 80 | 34 | 34 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01908034/RDB
Build-In Floor | Mini Canal | MICL.01908034/RMN | 19 | 80 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.01908034/RMN
Build-In Floor | Mini Canal | MICL.01908034/RMV | 19 | 80 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.01908034/RMV
Build-In Floor | Mini Canal | MICL.01908034/RNA | 19 | 80 | 34 | 34 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01908034/RNA
Build-In Floor | Mini Canal | MICL.01908034/RON | 19 | 80 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.01908034/RON
Build-In Floor | Mini Canal | MICL.01908034/ROV | 19 | 80 | 34 | 34 | 322 | 322 | 322 | 0.0076667 | 125 | 0.0029762 | 367 | 0.0087381 | 1.362 | A04 | MICL0.01908034/ROV
Build-In Floor | Mini Canal | MICL.01908034/RSS | 19 | 80 | 34 | 34 | 319 | 319 | 319 | 0.0075952 | 124 | 0.0029524 | 363 | 0.0086429 | 1.362 | A04 | MICL0.01908034/RSS
Build-In Floor | Mini Canal | MICL.01908034/SBL | 19 | 80 | 34 | 34 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01908034/SBL
Build-In Floor | Mini Canal | MICL.01908034/SBR | 19 | 80 | 34 | 34 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01908034/SBR
Build-In Floor | Mini Canal | MICL.01908034/SDB | 19 | 80 | 34 | 34 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01908034/SDB
Build-In Floor | Mini Canal | MICL.01908034/SNA | 19 | 80 | 34 | 34 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01908034/SNA
Build-In Floor | Mini Canal | MICL.01908034/SNC | 19 | 80 | 34 | 34 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01908034/SNC
Build-In Floor | Mini Canal | MICL.01908042/ANA | 19 | 80 | 42 | 42 | 341 | 341 | 341 | 0.008119 | 133 | 0.0031667 | 388 | 0.0092381 | 1.362 | A04 | MICL0.01908042/ANA
Build-In Floor | Mini Canal | MICL.01908042/DBL | 19 | 80 | 42 | 42 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.01908042/DBL
Build-In Floor | Mini Canal | MICL.01908042/DBN | 19 | 80 | 42 | 42 | 423 | 423 | 423 | 0.010071 | 165 | 0.0039286 | 482 | 0.011476 | 1.362 | A04 | MICL0.01908042/DBN
Build-In Floor | Mini Canal | MICL.01908042/DBR | 19 | 80 | 42 | 42 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.01908042/DBR
Build-In Floor | Mini Canal | MICL.01908042/DBV | 19 | 80 | 42 | 42 | 423 | 423 | 423 | 0.010071 | 165 | 0.0039286 | 482 | 0.011476 | 1.362 | A04 | MICL0.01908042/DBV
Build-In Floor | Mini Canal | MICL.01908042/DDB | 19 | 80 | 42 | 42 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.01908042/DDB
Build-In Floor | Mini Canal | MICL.01908042/DMN | 19 | 80 | 42 | 42 | 423 | 423 | 423 | 0.010071 | 165 | 0.0039286 | 482 | 0.011476 | 1.362 | A04 | MICL0.01908042/DMN
Build-In Floor | Mini Canal | MICL.01908042/DMV | 19 | 80 | 42 | 42 | 423 | 423 | 423 | 0.010071 | 165 | 0.0039286 | 482 | 0.011476 | 1.362 | A04 | MICL0.01908042/DMV
Build-In Floor | Mini Canal | MICL.01908042/DNA | 19 | 80 | 42 | 42 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.01908042/DNA
Build-In Floor | Mini Canal | MICL.01908042/DNC | 19 | 80 | 42 | 42 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.01908042/DNC
Build-In Floor | Mini Canal | MICL.01908042/DON | 19 | 80 | 42 | 42 | 423 | 423 | 423 | 0.010071 | 165 | 0.0039286 | 482 | 0.011476 | 1.362 | A04 | MICL0.01908042/DON
Build-In Floor | Mini Canal | MICL.01908042/DOV | 19 | 80 | 42 | 42 | 423 | 423 | 423 | 0.010071 | 165 | 0.0039286 | 482 | 0.011476 | 1.362 | A04 | MICL0.01908042/DOV
Build-In Floor | Mini Canal | MICL.01908042/PNC | 19 | 80 | 42 | 42 | 387 | 387 | 387 | 0.0092143 | 151 | 0.0035952 | 441 | 0.0105 | 1.362 | A04 | MICL0.01908042/PNC
Build-In Floor | Mini Canal | MICL.01908042/RBL | 19 | 80 | 42 | 42 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01908042/RBL
Build-In Floor | Mini Canal | MICL.01908042/RBN | 19 | 80 | 42 | 42 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.01908042/RBN
Build-In Floor | Mini Canal | MICL.01908042/RBR | 19 | 80 | 42 | 42 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01908042/RBR
Build-In Floor | Mini Canal | MICL.01908042/RBV | 19 | 80 | 42 | 42 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.01908042/RBV
Build-In Floor | Mini Canal | MICL.01908042/RDB | 19 | 80 | 42 | 42 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01908042/RDB
Build-In Floor | Mini Canal | MICL.01908042/RMN | 19 | 80 | 42 | 42 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.01908042/RMN
Build-In Floor | Mini Canal | MICL.01908042/RMV | 19 | 80 | 42 | 42 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.01908042/RMV
Build-In Floor | Mini Canal | MICL.01908042/RNA | 19 | 80 | 42 | 42 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01908042/RNA
Build-In Floor | Mini Canal | MICL.01908042/RON | 19 | 80 | 42 | 42 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.01908042/RON
Build-In Floor | Mini Canal | MICL.01908042/ROV | 19 | 80 | 42 | 42 | 441 | 441 | 441 | 0.0105 | 172 | 0.0040952 | 502 | 0.011952 | 1.362 | A04 | MICL0.01908042/ROV
Build-In Floor | Mini Canal | MICL.01908042/RSS | 19 | 80 | 42 | 42 | 437 | 437 | 437 | 0.010405 | 170 | 0.0040476 | 498 | 0.011857 | 1.362 | A04 | MICL0.01908042/RSS
Build-In Floor | Mini Canal | MICL.01908042/SBL | 19 | 80 | 42 | 42 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01908042/SBL
Build-In Floor | Mini Canal | MICL.01908042/SBR | 19 | 80 | 42 | 42 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01908042/SBR
Build-In Floor | Mini Canal | MICL.01908042/SDB | 19 | 80 | 42 | 42 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01908042/SDB
Build-In Floor | Mini Canal | MICL.01908042/SNA | 19 | 80 | 42 | 42 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01908042/SNA
Build-In Floor | Mini Canal | MICL.01908042/SNC | 19 | 80 | 42 | 42 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01908042/SNC
Build-In Floor | Mini Canal | MICL.01909026/ANA | 19 | 90 | 26 | 26 | 220 | 220 | 220 | 0.0052381 | 86 | 0.0020476 | 251 | 0.0059762 | 1.362 | A04 | MICL0.01909026/ANA
Build-In Floor | Mini Canal | MICL.01909026/DBL | 19 | 90 | 26 | 26 | 284 | 284 | 284 | 0.0067619 | 110 | 0.002619 | 323 | 0.0076905 | 1.362 | A04 | MICL0.01909026/DBL
Build-In Floor | Mini Canal | MICL.01909026/DBN | 19 | 90 | 26 | 26 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01909026/DBN
Build-In Floor | Mini Canal | MICL.01909026/DBR | 19 | 90 | 26 | 26 | 284 | 284 | 284 | 0.0067619 | 110 | 0.002619 | 323 | 0.0076905 | 1.362 | A04 | MICL0.01909026/DBR
Build-In Floor | Mini Canal | MICL.01909026/DBV | 19 | 90 | 26 | 26 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01909026/DBV
Build-In Floor | Mini Canal | MICL.01909026/DDB | 19 | 90 | 26 | 26 | 284 | 284 | 284 | 0.0067619 | 110 | 0.002619 | 323 | 0.0076905 | 1.362 | A04 | MICL0.01909026/DDB
Build-In Floor | Mini Canal | MICL.01909026/DMN | 19 | 90 | 26 | 26 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01909026/DMN
Build-In Floor | Mini Canal | MICL.01909026/DMV | 19 | 90 | 26 | 26 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01909026/DMV
Build-In Floor | Mini Canal | MICL.01909026/DNA | 19 | 90 | 26 | 26 | 284 | 284 | 284 | 0.0067619 | 110 | 0.002619 | 323 | 0.0076905 | 1.362 | A04 | MICL0.01909026/DNA
Build-In Floor | Mini Canal | MICL.01909026/DNC | 19 | 90 | 26 | 26 | 284 | 284 | 284 | 0.0067619 | 110 | 0.002619 | 323 | 0.0076905 | 1.362 | A04 | MICL0.01909026/DNC
Build-In Floor | Mini Canal | MICL.01909026/DON | 19 | 90 | 26 | 26 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01909026/DON
Build-In Floor | Mini Canal | MICL.01909026/DOV | 19 | 90 | 26 | 26 | 272 | 272 | 272 | 0.0064762 | 106 | 0.0025238 | 310 | 0.007381 | 1.362 | A04 | MICL0.01909026/DOV
Build-In Floor | Mini Canal | MICL.01909026/PNC | 19 | 90 | 26 | 26 | 249 | 249 | 249 | 0.0059286 | 97 | 0.0023095 | 284 | 0.0067619 | 1.362 | A04 | MICL0.01909026/PNC
Build-In Floor | Mini Canal | MICL.01909026/RBL | 19 | 90 | 26 | 26 | 293 | 293 | 293 | 0.0069762 | 114 | 0.0027143 | 334 | 0.0079524 | 1.362 | A04 | MICL0.01909026/RBL
Build-In Floor | Mini Canal | MICL.01909026/RBN | 19 | 90 | 26 | 26 | 284 | 284 | 284 | 0.0067619 | 110 | 0.002619 | 323 | 0.0076905 | 1.362 | A04 | MICL0.01909026/RBN
Build-In Floor | Mini Canal | MICL.01909026/RBR | 19 | 90 | 26 | 26 | 293 | 293 | 293 | 0.0069762 | 114 | 0.0027143 | 334 | 0.0079524 | 1.362 | A04 | MICL0.01909026/RBR
Build-In Floor | Mini Canal | MICL.01909026/RBV | 19 | 90 | 26 | 26 | 284 | 284 | 284 | 0.0067619 | 110 | 0.002619 | 323 | 0.0076905 | 1.362 | A04 | MICL0.01909026/RBV
Build-In Floor | Mini Canal | MICL.01909026/RDB | 19 | 90 | 26 | 26 | 293 | 293 | 293 | 0.0069762 | 114 | 0.0027143 | 334 | 0.0079524 | 1.362 | A04 | MICL0.01909026/RDB
Build-In Floor | Mini Canal | MICL.01909026/RMN | 19 | 90 | 26 | 26 | 284 | 284 | 284 | 0.0067619 | 110 | 0.002619 | 323 | 0.0076905 | 1.362 | A04 | MICL0.01909026/RMN
Build-In Floor | Mini Canal | MICL.01909026/RMV | 19 | 90 | 26 | 26 | 284 | 284 | 284 | 0.0067619 | 110 | 0.002619 | 323 | 0.0076905 | 1.362 | A04 | MICL0.01909026/RMV
Build-In Floor | Mini Canal | MICL.01909026/RNA | 19 | 90 | 26 | 26 | 293 | 293 | 293 | 0.0069762 | 114 | 0.0027143 | 334 | 0.0079524 | 1.362 | A04 | MICL0.01909026/RNA
Build-In Floor | Mini Canal | MICL.01909026/RON | 19 | 90 | 26 | 26 | 284 | 284 | 284 | 0.0067619 | 110 | 0.002619 | 323 | 0.0076905 | 1.362 | A04 | MICL0.01909026/RON
Build-In Floor | Mini Canal | MICL.01909026/ROV | 19 | 90 | 26 | 26 | 284 | 284 | 284 | 0.0067619 | 110 | 0.002619 | 323 | 0.0076905 | 1.362 | A04 | MICL0.01909026/ROV
Build-In Floor | Mini Canal | MICL.01909026/RSS | 19 | 90 | 26 | 26 | 281 | 281 | 281 | 0.0066905 | 109 | 0.0025952 | 320 | 0.007619 | 1.362 | A04 | MICL0.01909026/RSS
Build-In Floor | Mini Canal | MICL.01909026/SBL | 19 | 90 | 26 | 26 | 293 | 293 | 293 | 0.0069762 | 114 | 0.0027143 | 334 | 0.0079524 | 1.362 | A04 | MICL0.01909026/SBL
Build-In Floor | Mini Canal | MICL.01909026/SBR | 19 | 90 | 26 | 26 | 293 | 293 | 293 | 0.0069762 | 114 | 0.0027143 | 334 | 0.0079524 | 1.362 | A04 | MICL0.01909026/SBR
Build-In Floor | Mini Canal | MICL.01909026/SDB | 19 | 90 | 26 | 26 | 293 | 293 | 293 | 0.0069762 | 114 | 0.0027143 | 334 | 0.0079524 | 1.362 | A04 | MICL0.01909026/SDB
Build-In Floor | Mini Canal | MICL.01909026/SNA | 19 | 90 | 26 | 26 | 293 | 293 | 293 | 0.0069762 | 114 | 0.0027143 | 334 | 0.0079524 | 1.362 | A04 | MICL0.01909026/SNA
Build-In Floor | Mini Canal | MICL.01909026/SNC | 19 | 90 | 26 | 26 | 293 | 293 | 293 | 0.0069762 | 114 | 0.0027143 | 334 | 0.0079524 | 1.362 | A04 | MICL0.01909026/SNC
Build-In Floor | Mini Canal | MICL.01909034/ANA | 19 | 90 | 34 | 34 | 298 | 298 | 298 | 0.0070952 | 116 | 0.0027619 | 339 | 0.0080714 | 1.362 | A04 | MICL0.01909034/ANA
Build-In Floor | Mini Canal | MICL.01909034/DBL | 19 | 90 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01909034/DBL
Build-In Floor | Mini Canal | MICL.01909034/DBN | 19 | 90 | 34 | 34 | 369 | 369 | 369 | 0.0087857 | 144 | 0.0034286 | 420 | 0.01 | 1.362 | A04 | MICL0.01909034/DBN
Build-In Floor | Mini Canal | MICL.01909034/DBR | 19 | 90 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01909034/DBR
Build-In Floor | Mini Canal | MICL.01909034/DBV | 19 | 90 | 34 | 34 | 369 | 369 | 369 | 0.0087857 | 144 | 0.0034286 | 420 | 0.01 | 1.362 | A04 | MICL0.01909034/DBV
Build-In Floor | Mini Canal | MICL.01909034/DDB | 19 | 90 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01909034/DDB
Build-In Floor | Mini Canal | MICL.01909034/DMN | 19 | 90 | 34 | 34 | 369 | 369 | 369 | 0.0087857 | 144 | 0.0034286 | 420 | 0.01 | 1.362 | A04 | MICL0.01909034/DMN
Build-In Floor | Mini Canal | MICL.01909034/DMV | 19 | 90 | 34 | 34 | 369 | 369 | 369 | 0.0087857 | 144 | 0.0034286 | 420 | 0.01 | 1.362 | A04 | MICL0.01909034/DMV
Build-In Floor | Mini Canal | MICL.01909034/DNA | 19 | 90 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01909034/DNA
Build-In Floor | Mini Canal | MICL.01909034/DNC | 19 | 90 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01909034/DNC
Build-In Floor | Mini Canal | MICL.01909034/DON | 19 | 90 | 34 | 34 | 369 | 369 | 369 | 0.0087857 | 144 | 0.0034286 | 420 | 0.01 | 1.362 | A04 | MICL0.01909034/DON
Build-In Floor | Mini Canal | MICL.01909034/DOV | 19 | 90 | 34 | 34 | 369 | 369 | 369 | 0.0087857 | 144 | 0.0034286 | 420 | 0.01 | 1.362 | A04 | MICL0.01909034/DOV
Build-In Floor | Mini Canal | MICL.01909034/PNC | 19 | 90 | 34 | 34 | 337 | 337 | 337 | 0.0080238 | 131 | 0.003119 | 384 | 0.0091429 | 1.362 | A04 | MICL0.01909034/PNC
Build-In Floor | Mini Canal | MICL.01909034/RBL | 19 | 90 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01909034/RBL
Build-In Floor | Mini Canal | MICL.01909034/RBN | 19 | 90 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01909034/RBN
Build-In Floor | Mini Canal | MICL.01909034/RBR | 19 | 90 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01909034/RBR
Build-In Floor | Mini Canal | MICL.01909034/RBV | 19 | 90 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01909034/RBV
Build-In Floor | Mini Canal | MICL.01909034/RDB | 19 | 90 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01909034/RDB
Build-In Floor | Mini Canal | MICL.01909034/RMN | 19 | 90 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01909034/RMN
Build-In Floor | Mini Canal | MICL.01909034/RMV | 19 | 90 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01909034/RMV
Build-In Floor | Mini Canal | MICL.01909034/RNA | 19 | 90 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01909034/RNA
Build-In Floor | Mini Canal | MICL.01909034/RON | 19 | 90 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01909034/RON
Build-In Floor | Mini Canal | MICL.01909034/ROV | 19 | 90 | 34 | 34 | 385 | 385 | 385 | 0.0091667 | 150 | 0.0035714 | 439 | 0.010452 | 1.362 | A04 | MICL0.01909034/ROV
Build-In Floor | Mini Canal | MICL.01909034/RSS | 19 | 90 | 34 | 34 | 381 | 381 | 381 | 0.0090714 | 148 | 0.0035238 | 434 | 0.010333 | 1.362 | A04 | MICL0.01909034/RSS
Build-In Floor | Mini Canal | MICL.01909034/SBL | 19 | 90 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01909034/SBL
Build-In Floor | Mini Canal | MICL.01909034/SBR | 19 | 90 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01909034/SBR
Build-In Floor | Mini Canal | MICL.01909034/SDB | 19 | 90 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01909034/SDB
Build-In Floor | Mini Canal | MICL.01909034/SNA | 19 | 90 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01909034/SNA
Build-In Floor | Mini Canal | MICL.01909034/SNC | 19 | 90 | 34 | 34 | 397 | 397 | 397 | 0.0094524 | 154 | 0.0036667 | 452 | 0.010762 | 1.362 | A04 | MICL0.01909034/SNC
Build-In Floor | Mini Canal | MICL.01909042/ANA | 19 | 90 | 42 | 42 | 410 | 410 | 410 | 0.0097619 | 159 | 0.0037857 | 467 | 0.011119 | 1.362 | A04 | MICL0.01909042/ANA
Build-In Floor | Mini Canal | MICL.01909042/DBL | 19 | 90 | 42 | 42 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01909042/DBL
Build-In Floor | Mini Canal | MICL.01909042/DBN | 19 | 90 | 42 | 42 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01909042/DBN
Build-In Floor | Mini Canal | MICL.01909042/DBR | 19 | 90 | 42 | 42 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01909042/DBR
Build-In Floor | Mini Canal | MICL.01909042/DBV | 19 | 90 | 42 | 42 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01909042/DBV
Build-In Floor | Mini Canal | MICL.01909042/DDB | 19 | 90 | 42 | 42 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01909042/DDB
Build-In Floor | Mini Canal | MICL.01909042/DMN | 19 | 90 | 42 | 42 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01909042/DMN
Build-In Floor | Mini Canal | MICL.01909042/DMV | 19 | 90 | 42 | 42 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01909042/DMV
Build-In Floor | Mini Canal | MICL.01909042/DNA | 19 | 90 | 42 | 42 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01909042/DNA
Build-In Floor | Mini Canal | MICL.01909042/DNC | 19 | 90 | 42 | 42 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01909042/DNC
Build-In Floor | Mini Canal | MICL.01909042/DON | 19 | 90 | 42 | 42 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01909042/DON
Build-In Floor | Mini Canal | MICL.01909042/DOV | 19 | 90 | 42 | 42 | 508 | 508 | 508 | 0.012095 | 198 | 0.0047143 | 579 | 0.013786 | 1.362 | A04 | MICL0.01909042/DOV
Build-In Floor | Mini Canal | MICL.01909042/PNC | 19 | 90 | 42 | 42 | 464 | 464 | 464 | 0.011048 | 180 | 0.0042857 | 528 | 0.012571 | 1.362 | A04 | MICL0.01909042/PNC
Build-In Floor | Mini Canal | MICL.01909042/RBL | 19 | 90 | 42 | 42 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01909042/RBL
Build-In Floor | Mini Canal | MICL.01909042/RBN | 19 | 90 | 42 | 42 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01909042/RBN
Build-In Floor | Mini Canal | MICL.01909042/RBR | 19 | 90 | 42 | 42 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01909042/RBR
Build-In Floor | Mini Canal | MICL.01909042/RBV | 19 | 90 | 42 | 42 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01909042/RBV
Build-In Floor | Mini Canal | MICL.01909042/RDB | 19 | 90 | 42 | 42 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01909042/RDB
Build-In Floor | Mini Canal | MICL.01909042/RMN | 19 | 90 | 42 | 42 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01909042/RMN
Build-In Floor | Mini Canal | MICL.01909042/RMV | 19 | 90 | 42 | 42 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01909042/RMV
Build-In Floor | Mini Canal | MICL.01909042/RNA | 19 | 90 | 42 | 42 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01909042/RNA
Build-In Floor | Mini Canal | MICL.01909042/RON | 19 | 90 | 42 | 42 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01909042/RON
Build-In Floor | Mini Canal | MICL.01909042/ROV | 19 | 90 | 42 | 42 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01909042/ROV
Build-In Floor | Mini Canal | MICL.01909042/RSS | 19 | 90 | 42 | 42 | 524 | 524 | 524 | 0.012476 | 204 | 0.0048571 | 597 | 0.014214 | 1.362 | A04 | MICL0.01909042/RSS
Build-In Floor | Mini Canal | MICL.01909042/SBL | 19 | 90 | 42 | 42 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01909042/SBL
Build-In Floor | Mini Canal | MICL.01909042/SBR | 19 | 90 | 42 | 42 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01909042/SBR
Build-In Floor | Mini Canal | MICL.01909042/SDB | 19 | 90 | 42 | 42 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01909042/SDB
Build-In Floor | Mini Canal | MICL.01909042/SNA | 19 | 90 | 42 | 42 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01909042/SNA
Build-In Floor | Mini Canal | MICL.01909042/SNC | 19 | 90 | 42 | 42 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01909042/SNC
Build-In Floor | Mini Canal | MICL.01910026/ANA | 19 | 100 | 26 | 26 | 257 | 257 | 257 | 0.006119 | 100 | 0.002381 | 293 | 0.0069762 | 1.362 | A04 | MICL0.01910026/ANA
Build-In Floor | Mini Canal | MICL.01910026/DBL | 19 | 100 | 26 | 26 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01910026/DBL
Build-In Floor | Mini Canal | MICL.01910026/DBN | 19 | 100 | 26 | 26 | 318 | 318 | 318 | 0.0075714 | 124 | 0.0029524 | 362 | 0.008619 | 1.362 | A04 | MICL0.01910026/DBN
Build-In Floor | Mini Canal | MICL.01910026/DBR | 19 | 100 | 26 | 26 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01910026/DBR
Build-In Floor | Mini Canal | MICL.01910026/DBV | 19 | 100 | 26 | 26 | 318 | 318 | 318 | 0.0075714 | 124 | 0.0029524 | 362 | 0.008619 | 1.362 | A04 | MICL0.01910026/DBV
Build-In Floor | Mini Canal | MICL.01910026/DDB | 19 | 100 | 26 | 26 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01910026/DDB
Build-In Floor | Mini Canal | MICL.01910026/DMN | 19 | 100 | 26 | 26 | 318 | 318 | 318 | 0.0075714 | 124 | 0.0029524 | 362 | 0.008619 | 1.362 | A04 | MICL0.01910026/DMN
Build-In Floor | Mini Canal | MICL.01910026/DMV | 19 | 100 | 26 | 26 | 318 | 318 | 318 | 0.0075714 | 124 | 0.0029524 | 362 | 0.008619 | 1.362 | A04 | MICL0.01910026/DMV
Build-In Floor | Mini Canal | MICL.01910026/DNA | 19 | 100 | 26 | 26 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01910026/DNA
Build-In Floor | Mini Canal | MICL.01910026/DNC | 19 | 100 | 26 | 26 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01910026/DNC
Build-In Floor | Mini Canal | MICL.01910026/DON | 19 | 100 | 26 | 26 | 318 | 318 | 318 | 0.0075714 | 124 | 0.0029524 | 362 | 0.008619 | 1.362 | A04 | MICL0.01910026/DON
Build-In Floor | Mini Canal | MICL.01910026/DOV | 19 | 100 | 26 | 26 | 318 | 318 | 318 | 0.0075714 | 124 | 0.0029524 | 362 | 0.008619 | 1.362 | A04 | MICL0.01910026/DOV
Build-In Floor | Mini Canal | MICL.01910026/PNC | 19 | 100 | 26 | 26 | 291 | 291 | 291 | 0.0069286 | 113 | 0.0026905 | 331 | 0.007881 | 1.362 | A04 | MICL0.01910026/PNC
Build-In Floor | Mini Canal | MICL.01910026/RBL | 19 | 100 | 26 | 26 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01910026/RBL
Build-In Floor | Mini Canal | MICL.01910026/RBN | 19 | 100 | 26 | 26 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01910026/RBN
Build-In Floor | Mini Canal | MICL.01910026/RBR | 19 | 100 | 26 | 26 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01910026/RBR
Build-In Floor | Mini Canal | MICL.01910026/RBV | 19 | 100 | 26 | 26 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01910026/RBV
Build-In Floor | Mini Canal | MICL.01910026/RDB | 19 | 100 | 26 | 26 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01910026/RDB
Build-In Floor | Mini Canal | MICL.01910026/RMN | 19 | 100 | 26 | 26 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01910026/RMN
Build-In Floor | Mini Canal | MICL.01910026/RMV | 19 | 100 | 26 | 26 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01910026/RMV
Build-In Floor | Mini Canal | MICL.01910026/RNA | 19 | 100 | 26 | 26 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01910026/RNA
Build-In Floor | Mini Canal | MICL.01910026/RON | 19 | 100 | 26 | 26 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01910026/RON
Build-In Floor | Mini Canal | MICL.01910026/ROV | 19 | 100 | 26 | 26 | 332 | 332 | 332 | 0.0079048 | 129 | 0.0030714 | 378 | 0.009 | 1.362 | A04 | MICL0.01910026/ROV
Build-In Floor | Mini Canal | MICL.01910026/RSS | 19 | 100 | 26 | 26 | 328 | 328 | 328 | 0.0078095 | 128 | 0.0030476 | 374 | 0.0089048 | 1.362 | A04 | MICL0.01910026/RSS
Build-In Floor | Mini Canal | MICL.01910026/SBL | 19 | 100 | 26 | 26 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01910026/SBL
Build-In Floor | Mini Canal | MICL.01910026/SBR | 19 | 100 | 26 | 26 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01910026/SBR
Build-In Floor | Mini Canal | MICL.01910026/SDB | 19 | 100 | 26 | 26 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01910026/SDB
Build-In Floor | Mini Canal | MICL.01910026/SNA | 19 | 100 | 26 | 26 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01910026/SNA
Build-In Floor | Mini Canal | MICL.01910026/SNC | 19 | 100 | 26 | 26 | 342 | 342 | 342 | 0.0081429 | 133 | 0.0031667 | 390 | 0.0092857 | 1.362 | A04 | MICL0.01910026/SNC
Build-In Floor | Mini Canal | MICL.01910034/ANA | 19 | 100 | 34 | 34 | 347 | 347 | 347 | 0.0082619 | 135 | 0.0032143 | 395 | 0.0094048 | 1.362 | A04 | MICL0.01910034/ANA
Build-In Floor | Mini Canal | MICL.01910034/DBL | 19 | 100 | 34 | 34 | 449 | 449 | 449 | 0.01069 | 175 | 0.0041667 | 511 | 0.012167 | 1.362 | A04 | MICL0.01910034/DBL
Build-In Floor | Mini Canal | MICL.01910034/DBN | 19 | 100 | 34 | 34 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01910034/DBN
Build-In Floor | Mini Canal | MICL.01910034/DBR | 19 | 100 | 34 | 34 | 449 | 449 | 449 | 0.01069 | 175 | 0.0041667 | 511 | 0.012167 | 1.362 | A04 | MICL0.01910034/DBR
Build-In Floor | Mini Canal | MICL.01910034/DBV | 19 | 100 | 34 | 34 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01910034/DBV
Build-In Floor | Mini Canal | MICL.01910034/DDB | 19 | 100 | 34 | 34 | 449 | 449 | 449 | 0.01069 | 175 | 0.0041667 | 511 | 0.012167 | 1.362 | A04 | MICL0.01910034/DDB
Build-In Floor | Mini Canal | MICL.01910034/DMN | 19 | 100 | 34 | 34 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01910034/DMN
Build-In Floor | Mini Canal | MICL.01910034/DMV | 19 | 100 | 34 | 34 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01910034/DMV
Build-In Floor | Mini Canal | MICL.01910034/DNA | 19 | 100 | 34 | 34 | 449 | 449 | 449 | 0.01069 | 175 | 0.0041667 | 511 | 0.012167 | 1.362 | A04 | MICL0.01910034/DNA
Build-In Floor | Mini Canal | MICL.01910034/DNC | 19 | 100 | 34 | 34 | 449 | 449 | 449 | 0.01069 | 175 | 0.0041667 | 511 | 0.012167 | 1.362 | A04 | MICL0.01910034/DNC
Build-In Floor | Mini Canal | MICL.01910034/DON | 19 | 100 | 34 | 34 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01910034/DON
Build-In Floor | Mini Canal | MICL.01910034/DOV | 19 | 100 | 34 | 34 | 431 | 431 | 431 | 0.010262 | 168 | 0.004 | 491 | 0.01169 | 1.362 | A04 | MICL0.01910034/DOV
Build-In Floor | Mini Canal | MICL.01910034/PNC | 19 | 100 | 34 | 34 | 394 | 394 | 394 | 0.009381 | 153 | 0.0036429 | 449 | 0.01069 | 1.362 | A04 | MICL0.01910034/PNC
Build-In Floor | Mini Canal | MICL.01910034/RBL | 19 | 100 | 34 | 34 | 463 | 463 | 463 | 0.011024 | 180 | 0.0042857 | 527 | 0.012548 | 1.362 | A04 | MICL0.01910034/RBL
Build-In Floor | Mini Canal | MICL.01910034/RBN | 19 | 100 | 34 | 34 | 449 | 449 | 449 | 0.01069 | 175 | 0.0041667 | 511 | 0.012167 | 1.362 | A04 | MICL0.01910034/RBN
Build-In Floor | Mini Canal | MICL.01910034/RBR | 19 | 100 | 34 | 34 | 463 | 463 | 463 | 0.011024 | 180 | 0.0042857 | 527 | 0.012548 | 1.362 | A04 | MICL0.01910034/RBR
Build-In Floor | Mini Canal | MICL.01910034/RBV | 19 | 100 | 34 | 34 | 449 | 449 | 449 | 0.01069 | 175 | 0.0041667 | 511 | 0.012167 | 1.362 | A04 | MICL0.01910034/RBV
Build-In Floor | Mini Canal | MICL.01910034/RDB | 19 | 100 | 34 | 34 | 463 | 463 | 463 | 0.011024 | 180 | 0.0042857 | 527 | 0.012548 | 1.362 | A04 | MICL0.01910034/RDB
Build-In Floor | Mini Canal | MICL.01910034/RMN | 19 | 100 | 34 | 34 | 449 | 449 | 449 | 0.01069 | 175 | 0.0041667 | 511 | 0.012167 | 1.362 | A04 | MICL0.01910034/RMN
Build-In Floor | Mini Canal | MICL.01910034/RMV | 19 | 100 | 34 | 34 | 449 | 449 | 449 | 0.01069 | 175 | 0.0041667 | 511 | 0.012167 | 1.362 | A04 | MICL0.01910034/RMV
Build-In Floor | Mini Canal | MICL.01910034/RNA | 19 | 100 | 34 | 34 | 463 | 463 | 463 | 0.011024 | 180 | 0.0042857 | 527 | 0.012548 | 1.362 | A04 | MICL0.01910034/RNA
Build-In Floor | Mini Canal | MICL.01910034/RON | 19 | 100 | 34 | 34 | 449 | 449 | 449 | 0.01069 | 175 | 0.0041667 | 511 | 0.012167 | 1.362 | A04 | MICL0.01910034/RON
Build-In Floor | Mini Canal | MICL.01910034/ROV | 19 | 100 | 34 | 34 | 449 | 449 | 449 | 0.01069 | 175 | 0.0041667 | 511 | 0.012167 | 1.362 | A04 | MICL0.01910034/ROV
Build-In Floor | Mini Canal | MICL.01910034/RSS | 19 | 100 | 34 | 34 | 444 | 444 | 444 | 0.010571 | 173 | 0.004119 | 506 | 0.012048 | 1.362 | A04 | MICL0.01910034/RSS
Build-In Floor | Mini Canal | MICL.01910034/SBL | 19 | 100 | 34 | 34 | 463 | 463 | 463 | 0.011024 | 180 | 0.0042857 | 527 | 0.012548 | 1.362 | A04 | MICL0.01910034/SBL
Build-In Floor | Mini Canal | MICL.01910034/SBR | 19 | 100 | 34 | 34 | 463 | 463 | 463 | 0.011024 | 180 | 0.0042857 | 527 | 0.012548 | 1.362 | A04 | MICL0.01910034/SBR
Build-In Floor | Mini Canal | MICL.01910034/SDB | 19 | 100 | 34 | 34 | 463 | 463 | 463 | 0.011024 | 180 | 0.0042857 | 527 | 0.012548 | 1.362 | A04 | MICL0.01910034/SDB
Build-In Floor | Mini Canal | MICL.01910034/SNA | 19 | 100 | 34 | 34 | 463 | 463 | 463 | 0.011024 | 180 | 0.0042857 | 527 | 0.012548 | 1.362 | A04 | MICL0.01910034/SNA
Build-In Floor | Mini Canal | MICL.01910034/SNC | 19 | 100 | 34 | 34 | 463 | 463 | 463 | 0.011024 | 180 | 0.0042857 | 527 | 0.012548 | 1.362 | A04 | MICL0.01910034/SNC
Build-In Floor | Mini Canal | MICL.01910042/ANA | 19 | 100 | 42 | 42 | 477 | 477 | 477 | 0.011357 | 186 | 0.0044286 | 543 | 0.012929 | 1.362 | A04 | MICL0.01910042/ANA
Build-In Floor | Mini Canal | MICL.01910042/DBL | 19 | 100 | 42 | 42 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01910042/DBL
Build-In Floor | Mini Canal | MICL.01910042/DBN | 19 | 100 | 42 | 42 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.01910042/DBN
Build-In Floor | Mini Canal | MICL.01910042/DBR | 19 | 100 | 42 | 42 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01910042/DBR
Build-In Floor | Mini Canal | MICL.01910042/DBV | 19 | 100 | 42 | 42 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.01910042/DBV
Build-In Floor | Mini Canal | MICL.01910042/DDB | 19 | 100 | 42 | 42 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01910042/DDB
Build-In Floor | Mini Canal | MICL.01910042/DMN | 19 | 100 | 42 | 42 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.01910042/DMN
Build-In Floor | Mini Canal | MICL.01910042/DMV | 19 | 100 | 42 | 42 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.01910042/DMV
Build-In Floor | Mini Canal | MICL.01910042/DNA | 19 | 100 | 42 | 42 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01910042/DNA
Build-In Floor | Mini Canal | MICL.01910042/DNC | 19 | 100 | 42 | 42 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01910042/DNC
Build-In Floor | Mini Canal | MICL.01910042/DON | 19 | 100 | 42 | 42 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.01910042/DON
Build-In Floor | Mini Canal | MICL.01910042/DOV | 19 | 100 | 42 | 42 | 591 | 591 | 591 | 0.014071 | 230 | 0.0054762 | 673 | 0.016024 | 1.362 | A04 | MICL0.01910042/DOV
Build-In Floor | Mini Canal | MICL.01910042/PNC | 19 | 100 | 42 | 42 | 541 | 541 | 541 | 0.012881 | 210 | 0.005 | 616 | 0.014667 | 1.362 | A04 | MICL0.01910042/PNC
Build-In Floor | Mini Canal | MICL.01910042/RBL | 19 | 100 | 42 | 42 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01910042/RBL
Build-In Floor | Mini Canal | MICL.01910042/RBN | 19 | 100 | 42 | 42 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01910042/RBN
Build-In Floor | Mini Canal | MICL.01910042/RBR | 19 | 100 | 42 | 42 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01910042/RBR
Build-In Floor | Mini Canal | MICL.01910042/RBV | 19 | 100 | 42 | 42 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01910042/RBV
Build-In Floor | Mini Canal | MICL.01910042/RDB | 19 | 100 | 42 | 42 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01910042/RDB
Build-In Floor | Mini Canal | MICL.01910042/RMN | 19 | 100 | 42 | 42 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01910042/RMN
Build-In Floor | Mini Canal | MICL.01910042/RMV | 19 | 100 | 42 | 42 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01910042/RMV
Build-In Floor | Mini Canal | MICL.01910042/RNA | 19 | 100 | 42 | 42 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01910042/RNA
Build-In Floor | Mini Canal | MICL.01910042/RON | 19 | 100 | 42 | 42 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01910042/RON
Build-In Floor | Mini Canal | MICL.01910042/ROV | 19 | 100 | 42 | 42 | 617 | 617 | 617 | 0.01469 | 240 | 0.0057143 | 703 | 0.016738 | 1.362 | A04 | MICL0.01910042/ROV
Build-In Floor | Mini Canal | MICL.01910042/RSS | 19 | 100 | 42 | 42 | 611 | 611 | 611 | 0.014548 | 238 | 0.0056667 | 696 | 0.016571 | 1.362 | A04 | MICL0.01910042/RSS
Build-In Floor | Mini Canal | MICL.01910042/SBL | 19 | 100 | 42 | 42 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01910042/SBL
Build-In Floor | Mini Canal | MICL.01910042/SBR | 19 | 100 | 42 | 42 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01910042/SBR
Build-In Floor | Mini Canal | MICL.01910042/SDB | 19 | 100 | 42 | 42 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01910042/SDB
Build-In Floor | Mini Canal | MICL.01910042/SNA | 19 | 100 | 42 | 42 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01910042/SNA
Build-In Floor | Mini Canal | MICL.01910042/SNC | 19 | 100 | 42 | 42 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01910042/SNC
Build-In Floor | Mini Canal | MICL.01911026/ANA | 19 | 110 | 26 | 26 | 294 | 294 | 294 | 0.007 | 114 | 0.0027143 | 335 | 0.0079762 | 1.362 | A04 | MICL0.01911026/ANA
Build-In Floor | Mini Canal | MICL.01911026/DBL | 19 | 110 | 26 | 26 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01911026/DBL
Build-In Floor | Mini Canal | MICL.01911026/DBN | 19 | 110 | 26 | 26 | 365 | 365 | 365 | 0.0086905 | 142 | 0.003381 | 416 | 0.0099048 | 1.362 | A04 | MICL0.01911026/DBN
Build-In Floor | Mini Canal | MICL.01911026/DBR | 19 | 110 | 26 | 26 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01911026/DBR
Build-In Floor | Mini Canal | MICL.01911026/DBV | 19 | 110 | 26 | 26 | 365 | 365 | 365 | 0.0086905 | 142 | 0.003381 | 416 | 0.0099048 | 1.362 | A04 | MICL0.01911026/DBV
Build-In Floor | Mini Canal | MICL.01911026/DDB | 19 | 110 | 26 | 26 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01911026/DDB
Build-In Floor | Mini Canal | MICL.01911026/DMN | 19 | 110 | 26 | 26 | 365 | 365 | 365 | 0.0086905 | 142 | 0.003381 | 416 | 0.0099048 | 1.362 | A04 | MICL0.01911026/DMN
Build-In Floor | Mini Canal | MICL.01911026/DMV | 19 | 110 | 26 | 26 | 365 | 365 | 365 | 0.0086905 | 142 | 0.003381 | 416 | 0.0099048 | 1.362 | A04 | MICL0.01911026/DMV
Build-In Floor | Mini Canal | MICL.01911026/DNA | 19 | 110 | 26 | 26 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01911026/DNA
Build-In Floor | Mini Canal | MICL.01911026/DNC | 19 | 110 | 26 | 26 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01911026/DNC
Build-In Floor | Mini Canal | MICL.01911026/DON | 19 | 110 | 26 | 26 | 365 | 365 | 365 | 0.0086905 | 142 | 0.003381 | 416 | 0.0099048 | 1.362 | A04 | MICL0.01911026/DON
Build-In Floor | Mini Canal | MICL.01911026/DOV | 19 | 110 | 26 | 26 | 365 | 365 | 365 | 0.0086905 | 142 | 0.003381 | 416 | 0.0099048 | 1.362 | A04 | MICL0.01911026/DOV
Build-In Floor | Mini Canal | MICL.01911026/PNC | 19 | 110 | 26 | 26 | 333 | 333 | 333 | 0.0079286 | 130 | 0.0030952 | 379 | 0.0090238 | 1.362 | A04 | MICL0.01911026/PNC
Build-In Floor | Mini Canal | MICL.01911026/RBL | 19 | 110 | 26 | 26 | 392 | 392 | 392 | 0.0093333 | 152 | 0.003619 | 446 | 0.010619 | 1.362 | A04 | MICL0.01911026/RBL
Build-In Floor | Mini Canal | MICL.01911026/RBN | 19 | 110 | 26 | 26 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01911026/RBN
Build-In Floor | Mini Canal | MICL.01911026/RBR | 19 | 110 | 26 | 26 | 392 | 392 | 392 | 0.0093333 | 152 | 0.003619 | 446 | 0.010619 | 1.362 | A04 | MICL0.01911026/RBR
Build-In Floor | Mini Canal | MICL.01911026/RBV | 19 | 110 | 26 | 26 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01911026/RBV
Build-In Floor | Mini Canal | MICL.01911026/RDB | 19 | 110 | 26 | 26 | 392 | 392 | 392 | 0.0093333 | 152 | 0.003619 | 446 | 0.010619 | 1.362 | A04 | MICL0.01911026/RDB
Build-In Floor | Mini Canal | MICL.01911026/RMN | 19 | 110 | 26 | 26 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01911026/RMN
Build-In Floor | Mini Canal | MICL.01911026/RMV | 19 | 110 | 26 | 26 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01911026/RMV
Build-In Floor | Mini Canal | MICL.01911026/RNA | 19 | 110 | 26 | 26 | 392 | 392 | 392 | 0.0093333 | 152 | 0.003619 | 446 | 0.010619 | 1.362 | A04 | MICL0.01911026/RNA
Build-In Floor | Mini Canal | MICL.01911026/RON | 19 | 110 | 26 | 26 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01911026/RON
Build-In Floor | Mini Canal | MICL.01911026/ROV | 19 | 110 | 26 | 26 | 380 | 380 | 380 | 0.0090476 | 148 | 0.0035238 | 433 | 0.01031 | 1.362 | A04 | MICL0.01911026/ROV
Build-In Floor | Mini Canal | MICL.01911026/RSS | 19 | 110 | 26 | 26 | 376 | 376 | 376 | 0.0089524 | 146 | 0.0034762 | 428 | 0.01019 | 1.362 | A04 | MICL0.01911026/RSS
Build-In Floor | Mini Canal | MICL.01911026/SBL | 19 | 110 | 26 | 26 | 392 | 392 | 392 | 0.0093333 | 152 | 0.003619 | 446 | 0.010619 | 1.362 | A04 | MICL0.01911026/SBL
Build-In Floor | Mini Canal | MICL.01911026/SBR | 19 | 110 | 26 | 26 | 392 | 392 | 392 | 0.0093333 | 152 | 0.003619 | 446 | 0.010619 | 1.362 | A04 | MICL0.01911026/SBR
Build-In Floor | Mini Canal | MICL.01911026/SDB | 19 | 110 | 26 | 26 | 392 | 392 | 392 | 0.0093333 | 152 | 0.003619 | 446 | 0.010619 | 1.362 | A04 | MICL0.01911026/SDB
Build-In Floor | Mini Canal | MICL.01911026/SNA | 19 | 110 | 26 | 26 | 392 | 392 | 392 | 0.0093333 | 152 | 0.003619 | 446 | 0.010619 | 1.362 | A04 | MICL0.01911026/SNA
Build-In Floor | Mini Canal | MICL.01911026/SNC | 19 | 110 | 26 | 26 | 392 | 392 | 392 | 0.0093333 | 152 | 0.003619 | 446 | 0.010619 | 1.362 | A04 | MICL0.01911026/SNC
Build-In Floor | Mini Canal | MICL.01911034/ANA | 19 | 110 | 34 | 34 | 398 | 398 | 398 | 0.0094762 | 155 | 0.0036905 | 453 | 0.010786 | 1.362 | A04 | MICL0.01911034/ANA
Build-In Floor | Mini Canal | MICL.01911034/DBL | 19 | 110 | 34 | 34 | 514 | 514 | 514 | 0.012238 | 200 | 0.0047619 | 585 | 0.013929 | 1.362 | A04 | MICL0.01911034/DBL
Build-In Floor | Mini Canal | MICL.01911034/DBN | 19 | 110 | 34 | 34 | 493 | 493 | 493 | 0.011738 | 192 | 0.0045714 | 562 | 0.013381 | 1.362 | A04 | MICL0.01911034/DBN
Build-In Floor | Mini Canal | MICL.01911034/DBR | 19 | 110 | 34 | 34 | 514 | 514 | 514 | 0.012238 | 200 | 0.0047619 | 585 | 0.013929 | 1.362 | A04 | MICL0.01911034/DBR
Build-In Floor | Mini Canal | MICL.01911034/DBV | 19 | 110 | 34 | 34 | 493 | 493 | 493 | 0.011738 | 192 | 0.0045714 | 562 | 0.013381 | 1.362 | A04 | MICL0.01911034/DBV
Build-In Floor | Mini Canal | MICL.01911034/DDB | 19 | 110 | 34 | 34 | 514 | 514 | 514 | 0.012238 | 200 | 0.0047619 | 585 | 0.013929 | 1.362 | A04 | MICL0.01911034/DDB
Build-In Floor | Mini Canal | MICL.01911034/DMN | 19 | 110 | 34 | 34 | 493 | 493 | 493 | 0.011738 | 192 | 0.0045714 | 562 | 0.013381 | 1.362 | A04 | MICL0.01911034/DMN
Build-In Floor | Mini Canal | MICL.01911034/DMV | 19 | 110 | 34 | 34 | 493 | 493 | 493 | 0.011738 | 192 | 0.0045714 | 562 | 0.013381 | 1.362 | A04 | MICL0.01911034/DMV
Build-In Floor | Mini Canal | MICL.01911034/DNA | 19 | 110 | 34 | 34 | 514 | 514 | 514 | 0.012238 | 200 | 0.0047619 | 585 | 0.013929 | 1.362 | A04 | MICL0.01911034/DNA
Build-In Floor | Mini Canal | MICL.01911034/DNC | 19 | 110 | 34 | 34 | 514 | 514 | 514 | 0.012238 | 200 | 0.0047619 | 585 | 0.013929 | 1.362 | A04 | MICL0.01911034/DNC
Build-In Floor | Mini Canal | MICL.01911034/DON | 19 | 110 | 34 | 34 | 493 | 493 | 493 | 0.011738 | 192 | 0.0045714 | 562 | 0.013381 | 1.362 | A04 | MICL0.01911034/DON
Build-In Floor | Mini Canal | MICL.01911034/DOV | 19 | 110 | 34 | 34 | 493 | 493 | 493 | 0.011738 | 192 | 0.0045714 | 562 | 0.013381 | 1.362 | A04 | MICL0.01911034/DOV
Build-In Floor | Mini Canal | MICL.01911034/PNC | 19 | 110 | 34 | 34 | 451 | 451 | 451 | 0.010738 | 175 | 0.0041667 | 514 | 0.012238 | 1.362 | A04 | MICL0.01911034/PNC
Build-In Floor | Mini Canal | MICL.01911034/RBL | 19 | 110 | 34 | 34 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01911034/RBL
Build-In Floor | Mini Canal | MICL.01911034/RBN | 19 | 110 | 34 | 34 | 514 | 514 | 514 | 0.012238 | 200 | 0.0047619 | 585 | 0.013929 | 1.362 | A04 | MICL0.01911034/RBN
Build-In Floor | Mini Canal | MICL.01911034/RBR | 19 | 110 | 34 | 34 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01911034/RBR
Build-In Floor | Mini Canal | MICL.01911034/RBV | 19 | 110 | 34 | 34 | 514 | 514 | 514 | 0.012238 | 200 | 0.0047619 | 585 | 0.013929 | 1.362 | A04 | MICL0.01911034/RBV
Build-In Floor | Mini Canal | MICL.01911034/RDB | 19 | 110 | 34 | 34 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01911034/RDB
Build-In Floor | Mini Canal | MICL.01911034/RMN | 19 | 110 | 34 | 34 | 514 | 514 | 514 | 0.012238 | 200 | 0.0047619 | 585 | 0.013929 | 1.362 | A04 | MICL0.01911034/RMN
Build-In Floor | Mini Canal | MICL.01911034/RMV | 19 | 110 | 34 | 34 | 514 | 514 | 514 | 0.012238 | 200 | 0.0047619 | 585 | 0.013929 | 1.362 | A04 | MICL0.01911034/RMV
Build-In Floor | Mini Canal | MICL.01911034/RNA | 19 | 110 | 34 | 34 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01911034/RNA
Build-In Floor | Mini Canal | MICL.01911034/RON | 19 | 110 | 34 | 34 | 514 | 514 | 514 | 0.012238 | 200 | 0.0047619 | 585 | 0.013929 | 1.362 | A04 | MICL0.01911034/RON
Build-In Floor | Mini Canal | MICL.01911034/ROV | 19 | 110 | 34 | 34 | 514 | 514 | 514 | 0.012238 | 200 | 0.0047619 | 585 | 0.013929 | 1.362 | A04 | MICL0.01911034/ROV
Build-In Floor | Mini Canal | MICL.01911034/RSS | 19 | 110 | 34 | 34 | 509 | 509 | 509 | 0.012119 | 198 | 0.0047143 | 580 | 0.01381 | 1.362 | A04 | MICL0.01911034/RSS
Build-In Floor | Mini Canal | MICL.01911034/SBL | 19 | 110 | 34 | 34 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01911034/SBL
Build-In Floor | Mini Canal | MICL.01911034/SBR | 19 | 110 | 34 | 34 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01911034/SBR
Build-In Floor | Mini Canal | MICL.01911034/SDB | 19 | 110 | 34 | 34 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01911034/SDB
Build-In Floor | Mini Canal | MICL.01911034/SNA | 19 | 110 | 34 | 34 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01911034/SNA
Build-In Floor | Mini Canal | MICL.01911034/SNC | 19 | 110 | 34 | 34 | 530 | 530 | 530 | 0.012619 | 206 | 0.0049048 | 604 | 0.014381 | 1.362 | A04 | MICL0.01911034/SNC
Build-In Floor | Mini Canal | MICL.01911042/ANA | 19 | 110 | 42 | 42 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01911042/ANA
Build-In Floor | Mini Canal | MICL.01911042/DBL | 19 | 110 | 42 | 42 | 706 | 706 | 706 | 0.01681 | 275 | 0.0065476 | 804 | 0.019143 | 1.362 | A04 | MICL0.01911042/DBL
Build-In Floor | Mini Canal | MICL.01911042/DBN | 19 | 110 | 42 | 42 | 677 | 677 | 677 | 0.016119 | 263 | 0.0062619 | 771 | 0.018357 | 1.362 | A04 | MICL0.01911042/DBN
Build-In Floor | Mini Canal | MICL.01911042/DBR | 19 | 110 | 42 | 42 | 706 | 706 | 706 | 0.01681 | 275 | 0.0065476 | 804 | 0.019143 | 1.362 | A04 | MICL0.01911042/DBR
Build-In Floor | Mini Canal | MICL.01911042/DBV | 19 | 110 | 42 | 42 | 677 | 677 | 677 | 0.016119 | 263 | 0.0062619 | 771 | 0.018357 | 1.362 | A04 | MICL0.01911042/DBV
Build-In Floor | Mini Canal | MICL.01911042/DDB | 19 | 110 | 42 | 42 | 706 | 706 | 706 | 0.01681 | 275 | 0.0065476 | 804 | 0.019143 | 1.362 | A04 | MICL0.01911042/DDB
Build-In Floor | Mini Canal | MICL.01911042/DMN | 19 | 110 | 42 | 42 | 677 | 677 | 677 | 0.016119 | 263 | 0.0062619 | 771 | 0.018357 | 1.362 | A04 | MICL0.01911042/DMN
Build-In Floor | Mini Canal | MICL.01911042/DMV | 19 | 110 | 42 | 42 | 677 | 677 | 677 | 0.016119 | 263 | 0.0062619 | 771 | 0.018357 | 1.362 | A04 | MICL0.01911042/DMV
Build-In Floor | Mini Canal | MICL.01911042/DNA | 19 | 110 | 42 | 42 | 706 | 706 | 706 | 0.01681 | 275 | 0.0065476 | 804 | 0.019143 | 1.362 | A04 | MICL0.01911042/DNA
Build-In Floor | Mini Canal | MICL.01911042/DNC | 19 | 110 | 42 | 42 | 706 | 706 | 706 | 0.01681 | 275 | 0.0065476 | 804 | 0.019143 | 1.362 | A04 | MICL0.01911042/DNC
Build-In Floor | Mini Canal | MICL.01911042/DON | 19 | 110 | 42 | 42 | 677 | 677 | 677 | 0.016119 | 263 | 0.0062619 | 771 | 0.018357 | 1.362 | A04 | MICL0.01911042/DON
Build-In Floor | Mini Canal | MICL.01911042/DOV | 19 | 110 | 42 | 42 | 677 | 677 | 677 | 0.016119 | 263 | 0.0062619 | 771 | 0.018357 | 1.362 | A04 | MICL0.01911042/DOV
Build-In Floor | Mini Canal | MICL.01911042/PNC | 19 | 110 | 42 | 42 | 619 | 619 | 619 | 0.014738 | 241 | 0.0057381 | 705 | 0.016786 | 1.362 | A04 | MICL0.01911042/PNC
Build-In Floor | Mini Canal | MICL.01911042/RBL | 19 | 110 | 42 | 42 | 728 | 728 | 728 | 0.017333 | 283 | 0.0067381 | 829 | 0.019738 | 1.362 | A04 | MICL0.01911042/RBL
Build-In Floor | Mini Canal | MICL.01911042/RBN | 19 | 110 | 42 | 42 | 706 | 706 | 706 | 0.01681 | 275 | 0.0065476 | 804 | 0.019143 | 1.362 | A04 | MICL0.01911042/RBN
Build-In Floor | Mini Canal | MICL.01911042/RBR | 19 | 110 | 42 | 42 | 728 | 728 | 728 | 0.017333 | 283 | 0.0067381 | 829 | 0.019738 | 1.362 | A04 | MICL0.01911042/RBR
Build-In Floor | Mini Canal | MICL.01911042/RBV | 19 | 110 | 42 | 42 | 706 | 706 | 706 | 0.01681 | 275 | 0.0065476 | 804 | 0.019143 | 1.362 | A04 | MICL0.01911042/RBV
Build-In Floor | Mini Canal | MICL.01911042/RDB | 19 | 110 | 42 | 42 | 728 | 728 | 728 | 0.017333 | 283 | 0.0067381 | 829 | 0.019738 | 1.362 | A04 | MICL0.01911042/RDB
Build-In Floor | Mini Canal | MICL.01911042/RMN | 19 | 110 | 42 | 42 | 706 | 706 | 706 | 0.01681 | 275 | 0.0065476 | 804 | 0.019143 | 1.362 | A04 | MICL0.01911042/RMN
Build-In Floor | Mini Canal | MICL.01911042/RMV | 19 | 110 | 42 | 42 | 706 | 706 | 706 | 0.01681 | 275 | 0.0065476 | 804 | 0.019143 | 1.362 | A04 | MICL0.01911042/RMV
Build-In Floor | Mini Canal | MICL.01911042/RNA | 19 | 110 | 42 | 42 | 728 | 728 | 728 | 0.017333 | 283 | 0.0067381 | 829 | 0.019738 | 1.362 | A04 | MICL0.01911042/RNA
Build-In Floor | Mini Canal | MICL.01911042/RON | 19 | 110 | 42 | 42 | 706 | 706 | 706 | 0.01681 | 275 | 0.0065476 | 804 | 0.019143 | 1.362 | A04 | MICL0.01911042/RON
Build-In Floor | Mini Canal | MICL.01911042/ROV | 19 | 110 | 42 | 42 | 706 | 706 | 706 | 0.01681 | 275 | 0.0065476 | 804 | 0.019143 | 1.362 | A04 | MICL0.01911042/ROV
Build-In Floor | Mini Canal | MICL.01911042/RSS | 19 | 110 | 42 | 42 | 699 | 699 | 699 | 0.016643 | 272 | 0.0064762 | 796 | 0.018952 | 1.362 | A04 | MICL0.01911042/RSS
Build-In Floor | Mini Canal | MICL.01911042/SBL | 19 | 110 | 42 | 42 | 728 | 728 | 728 | 0.017333 | 283 | 0.0067381 | 829 | 0.019738 | 1.362 | A04 | MICL0.01911042/SBL
Build-In Floor | Mini Canal | MICL.01911042/SBR | 19 | 110 | 42 | 42 | 728 | 728 | 728 | 0.017333 | 283 | 0.0067381 | 829 | 0.019738 | 1.362 | A04 | MICL0.01911042/SBR
Build-In Floor | Mini Canal | MICL.01911042/SDB | 19 | 110 | 42 | 42 | 728 | 728 | 728 | 0.017333 | 283 | 0.0067381 | 829 | 0.019738 | 1.362 | A04 | MICL0.01911042/SDB
Build-In Floor | Mini Canal | MICL.01911042/SNA | 19 | 110 | 42 | 42 | 728 | 728 | 728 | 0.017333 | 283 | 0.0067381 | 829 | 0.019738 | 1.362 | A04 | MICL0.01911042/SNA
Build-In Floor | Mini Canal | MICL.01911042/SNC | 19 | 110 | 42 | 42 | 728 | 728 | 728 | 0.017333 | 283 | 0.0067381 | 829 | 0.019738 | 1.362 | A04 | MICL0.01911042/SNC
Build-In Floor | Mini Canal | MICL.01912026/ANA | 19 | 120 | 26 | 26 | 330 | 330 | 330 | 0.0078571 | 128 | 0.0030476 | 376 | 0.0089524 | 1.362 | A04 | MICL0.01912026/ANA
Build-In Floor | Mini Canal | MICL.01912026/DBL | 19 | 120 | 26 | 26 | 427 | 427 | 427 | 0.010167 | 166 | 0.0039524 | 486 | 0.011571 | 1.362 | A04 | MICL0.01912026/DBL
Build-In Floor | Mini Canal | MICL.01912026/DBN | 19 | 120 | 26 | 26 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01912026/DBN
Build-In Floor | Mini Canal | MICL.01912026/DBR | 19 | 120 | 26 | 26 | 427 | 427 | 427 | 0.010167 | 166 | 0.0039524 | 486 | 0.011571 | 1.362 | A04 | MICL0.01912026/DBR
Build-In Floor | Mini Canal | MICL.01912026/DBV | 19 | 120 | 26 | 26 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01912026/DBV
Build-In Floor | Mini Canal | MICL.01912026/DDB | 19 | 120 | 26 | 26 | 427 | 427 | 427 | 0.010167 | 166 | 0.0039524 | 486 | 0.011571 | 1.362 | A04 | MICL0.01912026/DDB
Build-In Floor | Mini Canal | MICL.01912026/DMN | 19 | 120 | 26 | 26 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01912026/DMN
Build-In Floor | Mini Canal | MICL.01912026/DMV | 19 | 120 | 26 | 26 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01912026/DMV
Build-In Floor | Mini Canal | MICL.01912026/DNA | 19 | 120 | 26 | 26 | 427 | 427 | 427 | 0.010167 | 166 | 0.0039524 | 486 | 0.011571 | 1.362 | A04 | MICL0.01912026/DNA
Build-In Floor | Mini Canal | MICL.01912026/DNC | 19 | 120 | 26 | 26 | 427 | 427 | 427 | 0.010167 | 166 | 0.0039524 | 486 | 0.011571 | 1.362 | A04 | MICL0.01912026/DNC
Build-In Floor | Mini Canal | MICL.01912026/DON | 19 | 120 | 26 | 26 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01912026/DON
Build-In Floor | Mini Canal | MICL.01912026/DOV | 19 | 120 | 26 | 26 | 409 | 409 | 409 | 0.0097381 | 159 | 0.0037857 | 466 | 0.011095 | 1.362 | A04 | MICL0.01912026/DOV
Build-In Floor | Mini Canal | MICL.01912026/PNC | 19 | 120 | 26 | 26 | 374 | 374 | 374 | 0.0089048 | 145 | 0.0034524 | 426 | 0.010143 | 1.362 | A04 | MICL0.01912026/PNC
Build-In Floor | Mini Canal | MICL.01912026/RBL | 19 | 120 | 26 | 26 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01912026/RBL
Build-In Floor | Mini Canal | MICL.01912026/RBN | 19 | 120 | 26 | 26 | 427 | 427 | 427 | 0.010167 | 166 | 0.0039524 | 486 | 0.011571 | 1.362 | A04 | MICL0.01912026/RBN
Build-In Floor | Mini Canal | MICL.01912026/RBR | 19 | 120 | 26 | 26 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01912026/RBR
Build-In Floor | Mini Canal | MICL.01912026/RBV | 19 | 120 | 26 | 26 | 427 | 427 | 427 | 0.010167 | 166 | 0.0039524 | 486 | 0.011571 | 1.362 | A04 | MICL0.01912026/RBV
Build-In Floor | Mini Canal | MICL.01912026/RDB | 19 | 120 | 26 | 26 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01912026/RDB
Build-In Floor | Mini Canal | MICL.01912026/RMN | 19 | 120 | 26 | 26 | 427 | 427 | 427 | 0.010167 | 166 | 0.0039524 | 486 | 0.011571 | 1.362 | A04 | MICL0.01912026/RMN
Build-In Floor | Mini Canal | MICL.01912026/RMV | 19 | 120 | 26 | 26 | 427 | 427 | 427 | 0.010167 | 166 | 0.0039524 | 486 | 0.011571 | 1.362 | A04 | MICL0.01912026/RMV
Build-In Floor | Mini Canal | MICL.01912026/RNA | 19 | 120 | 26 | 26 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01912026/RNA
Build-In Floor | Mini Canal | MICL.01912026/RON | 19 | 120 | 26 | 26 | 427 | 427 | 427 | 0.010167 | 166 | 0.0039524 | 486 | 0.011571 | 1.362 | A04 | MICL0.01912026/RON
Build-In Floor | Mini Canal | MICL.01912026/ROV | 19 | 120 | 26 | 26 | 427 | 427 | 427 | 0.010167 | 166 | 0.0039524 | 486 | 0.011571 | 1.362 | A04 | MICL0.01912026/ROV
Build-In Floor | Mini Canal | MICL.01912026/RSS | 19 | 120 | 26 | 26 | 422 | 422 | 422 | 0.010048 | 164 | 0.0039048 | 481 | 0.011452 | 1.362 | A04 | MICL0.01912026/RSS
Build-In Floor | Mini Canal | MICL.01912026/SBL | 19 | 120 | 26 | 26 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01912026/SBL
Build-In Floor | Mini Canal | MICL.01912026/SBR | 19 | 120 | 26 | 26 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01912026/SBR
Build-In Floor | Mini Canal | MICL.01912026/SDB | 19 | 120 | 26 | 26 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01912026/SDB
Build-In Floor | Mini Canal | MICL.01912026/SNA | 19 | 120 | 26 | 26 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01912026/SNA
Build-In Floor | Mini Canal | MICL.01912026/SNC | 19 | 120 | 26 | 26 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01912026/SNC
Build-In Floor | Mini Canal | MICL.01912034/ANA | 19 | 120 | 34 | 34 | 447 | 447 | 447 | 0.010643 | 174 | 0.0041429 | 509 | 0.012119 | 1.362 | A04 | MICL0.01912034/ANA
Build-In Floor | Mini Canal | MICL.01912034/DBL | 19 | 120 | 34 | 34 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01912034/DBL
Build-In Floor | Mini Canal | MICL.01912034/DBN | 19 | 120 | 34 | 34 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.01912034/DBN
Build-In Floor | Mini Canal | MICL.01912034/DBR | 19 | 120 | 34 | 34 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01912034/DBR
Build-In Floor | Mini Canal | MICL.01912034/DBV | 19 | 120 | 34 | 34 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.01912034/DBV
Build-In Floor | Mini Canal | MICL.01912034/DDB | 19 | 120 | 34 | 34 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01912034/DDB
Build-In Floor | Mini Canal | MICL.01912034/DMN | 19 | 120 | 34 | 34 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.01912034/DMN
Build-In Floor | Mini Canal | MICL.01912034/DMV | 19 | 120 | 34 | 34 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.01912034/DMV
Build-In Floor | Mini Canal | MICL.01912034/DNA | 19 | 120 | 34 | 34 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01912034/DNA
Build-In Floor | Mini Canal | MICL.01912034/DNC | 19 | 120 | 34 | 34 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01912034/DNC
Build-In Floor | Mini Canal | MICL.01912034/DON | 19 | 120 | 34 | 34 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.01912034/DON
Build-In Floor | Mini Canal | MICL.01912034/DOV | 19 | 120 | 34 | 34 | 554 | 554 | 554 | 0.01319 | 216 | 0.0051429 | 631 | 0.015024 | 1.362 | A04 | MICL0.01912034/DOV
Build-In Floor | Mini Canal | MICL.01912034/PNC | 19 | 120 | 34 | 34 | 507 | 507 | 507 | 0.012071 | 197 | 0.0046905 | 577 | 0.013738 | 1.362 | A04 | MICL0.01912034/PNC
Build-In Floor | Mini Canal | MICL.01912034/RBL | 19 | 120 | 34 | 34 | 596 | 596 | 596 | 0.01419 | 232 | 0.0055238 | 679 | 0.016167 | 1.362 | A04 | MICL0.01912034/RBL
Build-In Floor | Mini Canal | MICL.01912034/RBN | 19 | 120 | 34 | 34 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01912034/RBN
Build-In Floor | Mini Canal | MICL.01912034/RBR | 19 | 120 | 34 | 34 | 596 | 596 | 596 | 0.01419 | 232 | 0.0055238 | 679 | 0.016167 | 1.362 | A04 | MICL0.01912034/RBR
Build-In Floor | Mini Canal | MICL.01912034/RBV | 19 | 120 | 34 | 34 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01912034/RBV
Build-In Floor | Mini Canal | MICL.01912034/RDB | 19 | 120 | 34 | 34 | 596 | 596 | 596 | 0.01419 | 232 | 0.0055238 | 679 | 0.016167 | 1.362 | A04 | MICL0.01912034/RDB
Build-In Floor | Mini Canal | MICL.01912034/RMN | 19 | 120 | 34 | 34 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01912034/RMN
Build-In Floor | Mini Canal | MICL.01912034/RMV | 19 | 120 | 34 | 34 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01912034/RMV
Build-In Floor | Mini Canal | MICL.01912034/RNA | 19 | 120 | 34 | 34 | 596 | 596 | 596 | 0.01419 | 232 | 0.0055238 | 679 | 0.016167 | 1.362 | A04 | MICL0.01912034/RNA
Build-In Floor | Mini Canal | MICL.01912034/RON | 19 | 120 | 34 | 34 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01912034/RON
Build-In Floor | Mini Canal | MICL.01912034/ROV | 19 | 120 | 34 | 34 | 578 | 578 | 578 | 0.013762 | 225 | 0.0053571 | 658 | 0.015667 | 1.362 | A04 | MICL0.01912034/ROV
Build-In Floor | Mini Canal | MICL.01912034/RSS | 19 | 120 | 34 | 34 | 572 | 572 | 572 | 0.013619 | 223 | 0.0053095 | 652 | 0.015524 | 1.362 | A04 | MICL0.01912034/RSS
Build-In Floor | Mini Canal | MICL.01912034/SBL | 19 | 120 | 34 | 34 | 596 | 596 | 596 | 0.01419 | 232 | 0.0055238 | 679 | 0.016167 | 1.362 | A04 | MICL0.01912034/SBL
Build-In Floor | Mini Canal | MICL.01912034/SBR | 19 | 120 | 34 | 34 | 596 | 596 | 596 | 0.01419 | 232 | 0.0055238 | 679 | 0.016167 | 1.362 | A04 | MICL0.01912034/SBR
Build-In Floor | Mini Canal | MICL.01912034/SDB | 19 | 120 | 34 | 34 | 596 | 596 | 596 | 0.01419 | 232 | 0.0055238 | 679 | 0.016167 | 1.362 | A04 | MICL0.01912034/SDB
Build-In Floor | Mini Canal | MICL.01912034/SNA | 19 | 120 | 34 | 34 | 596 | 596 | 596 | 0.01419 | 232 | 0.0055238 | 679 | 0.016167 | 1.362 | A04 | MICL0.01912034/SNA
Build-In Floor | Mini Canal | MICL.01912034/SNC | 19 | 120 | 34 | 34 | 596 | 596 | 596 | 0.01419 | 232 | 0.0055238 | 679 | 0.016167 | 1.362 | A04 | MICL0.01912034/SNC
Build-In Floor | Mini Canal | MICL.01912042/ANA | 19 | 120 | 42 | 42 | 614 | 614 | 614 | 0.014619 | 239 | 0.0056905 | 699 | 0.016643 | 1.362 | A04 | MICL0.01912042/ANA
Build-In Floor | Mini Canal | MICL.01912042/DBL | 19 | 120 | 42 | 42 | 793 | 793 | 793 | 0.018881 | 308 | 0.0073333 | 903 | 0.0215 | 1.362 | A04 | MICL0.01912042/DBL
Build-In Floor | Mini Canal | MICL.01912042/DBN | 19 | 120 | 42 | 42 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.01912042/DBN
Build-In Floor | Mini Canal | MICL.01912042/DBR | 19 | 120 | 42 | 42 | 793 | 793 | 793 | 0.018881 | 308 | 0.0073333 | 903 | 0.0215 | 1.362 | A04 | MICL0.01912042/DBR
Build-In Floor | Mini Canal | MICL.01912042/DBV | 19 | 120 | 42 | 42 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.01912042/DBV
Build-In Floor | Mini Canal | MICL.01912042/DDB | 19 | 120 | 42 | 42 | 793 | 793 | 793 | 0.018881 | 308 | 0.0073333 | 903 | 0.0215 | 1.362 | A04 | MICL0.01912042/DDB
Build-In Floor | Mini Canal | MICL.01912042/DMN | 19 | 120 | 42 | 42 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.01912042/DMN
Build-In Floor | Mini Canal | MICL.01912042/DMV | 19 | 120 | 42 | 42 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.01912042/DMV
Build-In Floor | Mini Canal | MICL.01912042/DNA | 19 | 120 | 42 | 42 | 793 | 793 | 793 | 0.018881 | 308 | 0.0073333 | 903 | 0.0215 | 1.362 | A04 | MICL0.01912042/DNA
Build-In Floor | Mini Canal | MICL.01912042/DNC | 19 | 120 | 42 | 42 | 793 | 793 | 793 | 0.018881 | 308 | 0.0073333 | 903 | 0.0215 | 1.362 | A04 | MICL0.01912042/DNC
Build-In Floor | Mini Canal | MICL.01912042/DON | 19 | 120 | 42 | 42 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.01912042/DON
Build-In Floor | Mini Canal | MICL.01912042/DOV | 19 | 120 | 42 | 42 | 761 | 761 | 761 | 0.018119 | 296 | 0.0070476 | 867 | 0.020643 | 1.362 | A04 | MICL0.01912042/DOV
Build-In Floor | Mini Canal | MICL.01912042/PNC | 19 | 120 | 42 | 42 | 695 | 695 | 695 | 0.016548 | 270 | 0.0064286 | 792 | 0.018857 | 1.362 | A04 | MICL0.01912042/PNC
Build-In Floor | Mini Canal | MICL.01912042/RBL | 19 | 120 | 42 | 42 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01912042/RBL
Build-In Floor | Mini Canal | MICL.01912042/RBN | 19 | 120 | 42 | 42 | 793 | 793 | 793 | 0.018881 | 308 | 0.0073333 | 903 | 0.0215 | 1.362 | A04 | MICL0.01912042/RBN
Build-In Floor | Mini Canal | MICL.01912042/RBR | 19 | 120 | 42 | 42 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01912042/RBR
Build-In Floor | Mini Canal | MICL.01912042/RBV | 19 | 120 | 42 | 42 | 793 | 793 | 793 | 0.018881 | 308 | 0.0073333 | 903 | 0.0215 | 1.362 | A04 | MICL0.01912042/RBV
Build-In Floor | Mini Canal | MICL.01912042/RDB | 19 | 120 | 42 | 42 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01912042/RDB
Build-In Floor | Mini Canal | MICL.01912042/RMN | 19 | 120 | 42 | 42 | 793 | 793 | 793 | 0.018881 | 308 | 0.0073333 | 903 | 0.0215 | 1.362 | A04 | MICL0.01912042/RMN
Build-In Floor | Mini Canal | MICL.01912042/RMV | 19 | 120 | 42 | 42 | 793 | 793 | 793 | 0.018881 | 308 | 0.0073333 | 903 | 0.0215 | 1.362 | A04 | MICL0.01912042/RMV
Build-In Floor | Mini Canal | MICL.01912042/RNA | 19 | 120 | 42 | 42 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01912042/RNA
Build-In Floor | Mini Canal | MICL.01912042/RON | 19 | 120 | 42 | 42 | 793 | 793 | 793 | 0.018881 | 308 | 0.0073333 | 903 | 0.0215 | 1.362 | A04 | MICL0.01912042/RON
Build-In Floor | Mini Canal | MICL.01912042/ROV | 19 | 120 | 42 | 42 | 793 | 793 | 793 | 0.018881 | 308 | 0.0073333 | 903 | 0.0215 | 1.362 | A04 | MICL0.01912042/ROV
Build-In Floor | Mini Canal | MICL.01912042/RSS | 19 | 120 | 42 | 42 | 785 | 785 | 785 | 0.01869 | 305 | 0.0072619 | 894 | 0.021286 | 1.362 | A04 | MICL0.01912042/RSS
Build-In Floor | Mini Canal | MICL.01912042/SBL | 19 | 120 | 42 | 42 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01912042/SBL
Build-In Floor | Mini Canal | MICL.01912042/SBR | 19 | 120 | 42 | 42 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01912042/SBR
Build-In Floor | Mini Canal | MICL.01912042/SDB | 19 | 120 | 42 | 42 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01912042/SDB
Build-In Floor | Mini Canal | MICL.01912042/SNA | 19 | 120 | 42 | 42 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01912042/SNA
Build-In Floor | Mini Canal | MICL.01912042/SNC | 19 | 120 | 42 | 42 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01912042/SNC
Build-In Floor | Mini Canal | MICL.01913026/ANA | 19 | 130 | 26 | 26 | 367 | 367 | 367 | 0.0087381 | 143 | 0.0034048 | 418 | 0.0099524 | 1.362 | A04 | MICL0.01913026/ANA
Build-In Floor | Mini Canal | MICL.01913026/DBL | 19 | 130 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01913026/DBL
Build-In Floor | Mini Canal | MICL.01913026/DBN | 19 | 130 | 26 | 26 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01913026/DBN
Build-In Floor | Mini Canal | MICL.01913026/DBR | 19 | 130 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01913026/DBR
Build-In Floor | Mini Canal | MICL.01913026/DBV | 19 | 130 | 26 | 26 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01913026/DBV
Build-In Floor | Mini Canal | MICL.01913026/DDB | 19 | 130 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01913026/DDB
Build-In Floor | Mini Canal | MICL.01913026/DMN | 19 | 130 | 26 | 26 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01913026/DMN
Build-In Floor | Mini Canal | MICL.01913026/DMV | 19 | 130 | 26 | 26 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01913026/DMV
Build-In Floor | Mini Canal | MICL.01913026/DNA | 19 | 130 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01913026/DNA
Build-In Floor | Mini Canal | MICL.01913026/DNC | 19 | 130 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01913026/DNC
Build-In Floor | Mini Canal | MICL.01913026/DON | 19 | 130 | 26 | 26 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01913026/DON
Build-In Floor | Mini Canal | MICL.01913026/DOV | 19 | 130 | 26 | 26 | 455 | 455 | 455 | 0.010833 | 177 | 0.0042143 | 518 | 0.012333 | 1.362 | A04 | MICL0.01913026/DOV
Build-In Floor | Mini Canal | MICL.01913026/PNC | 19 | 130 | 26 | 26 | 416 | 416 | 416 | 0.0099048 | 162 | 0.0038571 | 474 | 0.011286 | 1.362 | A04 | MICL0.01913026/PNC
Build-In Floor | Mini Canal | MICL.01913026/RBL | 19 | 130 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01913026/RBL
Build-In Floor | Mini Canal | MICL.01913026/RBN | 19 | 130 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01913026/RBN
Build-In Floor | Mini Canal | MICL.01913026/RBR | 19 | 130 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01913026/RBR
Build-In Floor | Mini Canal | MICL.01913026/RBV | 19 | 130 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01913026/RBV
Build-In Floor | Mini Canal | MICL.01913026/RDB | 19 | 130 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01913026/RDB
Build-In Floor | Mini Canal | MICL.01913026/RMN | 19 | 130 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01913026/RMN
Build-In Floor | Mini Canal | MICL.01913026/RMV | 19 | 130 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01913026/RMV
Build-In Floor | Mini Canal | MICL.01913026/RNA | 19 | 130 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01913026/RNA
Build-In Floor | Mini Canal | MICL.01913026/RON | 19 | 130 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01913026/RON
Build-In Floor | Mini Canal | MICL.01913026/ROV | 19 | 130 | 26 | 26 | 474 | 474 | 474 | 0.011286 | 184 | 0.004381 | 540 | 0.012857 | 1.362 | A04 | MICL0.01913026/ROV
Build-In Floor | Mini Canal | MICL.01913026/RSS | 19 | 130 | 26 | 26 | 469 | 469 | 469 | 0.011167 | 182 | 0.0043333 | 534 | 0.012714 | 1.362 | A04 | MICL0.01913026/RSS
Build-In Floor | Mini Canal | MICL.01913026/SBL | 19 | 130 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01913026/SBL
Build-In Floor | Mini Canal | MICL.01913026/SBR | 19 | 130 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01913026/SBR
Build-In Floor | Mini Canal | MICL.01913026/SDB | 19 | 130 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01913026/SDB
Build-In Floor | Mini Canal | MICL.01913026/SNA | 19 | 130 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01913026/SNA
Build-In Floor | Mini Canal | MICL.01913026/SNC | 19 | 130 | 26 | 26 | 489 | 489 | 489 | 0.011643 | 190 | 0.0045238 | 557 | 0.013262 | 1.362 | A04 | MICL0.01913026/SNC
Build-In Floor | Mini Canal | MICL.01913034/ANA | 19 | 130 | 34 | 34 | 497 | 497 | 497 | 0.011833 | 193 | 0.0045952 | 566 | 0.013476 | 1.362 | A04 | MICL0.01913034/ANA
Build-In Floor | Mini Canal | MICL.01913034/DBL | 19 | 130 | 34 | 34 | 642 | 642 | 642 | 0.015286 | 250 | 0.0059524 | 731 | 0.017405 | 1.362 | A04 | MICL0.01913034/DBL
Build-In Floor | Mini Canal | MICL.01913034/DBN | 19 | 130 | 34 | 34 | 616 | 616 | 616 | 0.014667 | 240 | 0.0057143 | 702 | 0.016714 | 1.362 | A04 | MICL0.01913034/DBN
Build-In Floor | Mini Canal | MICL.01913034/DBR | 19 | 130 | 34 | 34 | 642 | 642 | 642 | 0.015286 | 250 | 0.0059524 | 731 | 0.017405 | 1.362 | A04 | MICL0.01913034/DBR
Build-In Floor | Mini Canal | MICL.01913034/DBV | 19 | 130 | 34 | 34 | 616 | 616 | 616 | 0.014667 | 240 | 0.0057143 | 702 | 0.016714 | 1.362 | A04 | MICL0.01913034/DBV
Build-In Floor | Mini Canal | MICL.01913034/DDB | 19 | 130 | 34 | 34 | 642 | 642 | 642 | 0.015286 | 250 | 0.0059524 | 731 | 0.017405 | 1.362 | A04 | MICL0.01913034/DDB
Build-In Floor | Mini Canal | MICL.01913034/DMN | 19 | 130 | 34 | 34 | 616 | 616 | 616 | 0.014667 | 240 | 0.0057143 | 702 | 0.016714 | 1.362 | A04 | MICL0.01913034/DMN
Build-In Floor | Mini Canal | MICL.01913034/DMV | 19 | 130 | 34 | 34 | 616 | 616 | 616 | 0.014667 | 240 | 0.0057143 | 702 | 0.016714 | 1.362 | A04 | MICL0.01913034/DMV
Build-In Floor | Mini Canal | MICL.01913034/DNA | 19 | 130 | 34 | 34 | 642 | 642 | 642 | 0.015286 | 250 | 0.0059524 | 731 | 0.017405 | 1.362 | A04 | MICL0.01913034/DNA
Build-In Floor | Mini Canal | MICL.01913034/DNC | 19 | 130 | 34 | 34 | 642 | 642 | 642 | 0.015286 | 250 | 0.0059524 | 731 | 0.017405 | 1.362 | A04 | MICL0.01913034/DNC
Build-In Floor | Mini Canal | MICL.01913034/DON | 19 | 130 | 34 | 34 | 616 | 616 | 616 | 0.014667 | 240 | 0.0057143 | 702 | 0.016714 | 1.362 | A04 | MICL0.01913034/DON
Build-In Floor | Mini Canal | MICL.01913034/DOV | 19 | 130 | 34 | 34 | 616 | 616 | 616 | 0.014667 | 240 | 0.0057143 | 702 | 0.016714 | 1.362 | A04 | MICL0.01913034/DOV
Build-In Floor | Mini Canal | MICL.01913034/PNC | 19 | 130 | 34 | 34 | 563 | 563 | 563 | 0.013405 | 219 | 0.0052143 | 641 | 0.015262 | 1.362 | A04 | MICL0.01913034/PNC
Build-In Floor | Mini Canal | MICL.01913034/RBL | 19 | 130 | 34 | 34 | 662 | 662 | 662 | 0.015762 | 258 | 0.0061429 | 754 | 0.017952 | 1.362 | A04 | MICL0.01913034/RBL
Build-In Floor | Mini Canal | MICL.01913034/RBN | 19 | 130 | 34 | 34 | 642 | 642 | 642 | 0.015286 | 250 | 0.0059524 | 731 | 0.017405 | 1.362 | A04 | MICL0.01913034/RBN
Build-In Floor | Mini Canal | MICL.01913034/RBR | 19 | 130 | 34 | 34 | 662 | 662 | 662 | 0.015762 | 258 | 0.0061429 | 754 | 0.017952 | 1.362 | A04 | MICL0.01913034/RBR
Build-In Floor | Mini Canal | MICL.01913034/RBV | 19 | 130 | 34 | 34 | 642 | 642 | 642 | 0.015286 | 250 | 0.0059524 | 731 | 0.017405 | 1.362 | A04 | MICL0.01913034/RBV
Build-In Floor | Mini Canal | MICL.01913034/RDB | 19 | 130 | 34 | 34 | 662 | 662 | 662 | 0.015762 | 258 | 0.0061429 | 754 | 0.017952 | 1.362 | A04 | MICL0.01913034/RDB
Build-In Floor | Mini Canal | MICL.01913034/RMN | 19 | 130 | 34 | 34 | 642 | 642 | 642 | 0.015286 | 250 | 0.0059524 | 731 | 0.017405 | 1.362 | A04 | MICL0.01913034/RMN
Build-In Floor | Mini Canal | MICL.01913034/RMV | 19 | 130 | 34 | 34 | 642 | 642 | 642 | 0.015286 | 250 | 0.0059524 | 731 | 0.017405 | 1.362 | A04 | MICL0.01913034/RMV
Build-In Floor | Mini Canal | MICL.01913034/RNA | 19 | 130 | 34 | 34 | 662 | 662 | 662 | 0.015762 | 258 | 0.0061429 | 754 | 0.017952 | 1.362 | A04 | MICL0.01913034/RNA
Build-In Floor | Mini Canal | MICL.01913034/RON | 19 | 130 | 34 | 34 | 642 | 642 | 642 | 0.015286 | 250 | 0.0059524 | 731 | 0.017405 | 1.362 | A04 | MICL0.01913034/RON
Build-In Floor | Mini Canal | MICL.01913034/ROV | 19 | 130 | 34 | 34 | 642 | 642 | 642 | 0.015286 | 250 | 0.0059524 | 731 | 0.017405 | 1.362 | A04 | MICL0.01913034/ROV
Build-In Floor | Mini Canal | MICL.01913034/RSS | 19 | 130 | 34 | 34 | 636 | 636 | 636 | 0.015143 | 247 | 0.005881 | 724 | 0.017238 | 1.362 | A04 | MICL0.01913034/RSS
Build-In Floor | Mini Canal | MICL.01913034/SBL | 19 | 130 | 34 | 34 | 662 | 662 | 662 | 0.015762 | 258 | 0.0061429 | 754 | 0.017952 | 1.362 | A04 | MICL0.01913034/SBL
Build-In Floor | Mini Canal | MICL.01913034/SBR | 19 | 130 | 34 | 34 | 662 | 662 | 662 | 0.015762 | 258 | 0.0061429 | 754 | 0.017952 | 1.362 | A04 | MICL0.01913034/SBR
Build-In Floor | Mini Canal | MICL.01913034/SDB | 19 | 130 | 34 | 34 | 662 | 662 | 662 | 0.015762 | 258 | 0.0061429 | 754 | 0.017952 | 1.362 | A04 | MICL0.01913034/SDB
Build-In Floor | Mini Canal | MICL.01913034/SNA | 19 | 130 | 34 | 34 | 662 | 662 | 662 | 0.015762 | 258 | 0.0061429 | 754 | 0.017952 | 1.362 | A04 | MICL0.01913034/SNA
Build-In Floor | Mini Canal | MICL.01913034/SNC | 19 | 130 | 34 | 34 | 662 | 662 | 662 | 0.015762 | 258 | 0.0061429 | 754 | 0.017952 | 1.362 | A04 | MICL0.01913034/SNC
Build-In Floor | Mini Canal | MICL.01913042/ANA | 19 | 130 | 42 | 42 | 682 | 682 | 682 | 0.016238 | 265 | 0.0063095 | 777 | 0.0185 | 1.362 | A04 | MICL0.01913042/ANA
Build-In Floor | Mini Canal | MICL.01913042/DBL | 19 | 130 | 42 | 42 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01913042/DBL
Build-In Floor | Mini Canal | MICL.01913042/DBN | 19 | 130 | 42 | 42 | 845 | 845 | 845 | 0.020119 | 329 | 0.0078333 | 962 | 0.022905 | 1.362 | A04 | MICL0.01913042/DBN
Build-In Floor | Mini Canal | MICL.01913042/DBR | 19 | 130 | 42 | 42 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01913042/DBR
Build-In Floor | Mini Canal | MICL.01913042/DBV | 19 | 130 | 42 | 42 | 845 | 845 | 845 | 0.020119 | 329 | 0.0078333 | 962 | 0.022905 | 1.362 | A04 | MICL0.01913042/DBV
Build-In Floor | Mini Canal | MICL.01913042/DDB | 19 | 130 | 42 | 42 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01913042/DDB
Build-In Floor | Mini Canal | MICL.01913042/DMN | 19 | 130 | 42 | 42 | 845 | 845 | 845 | 0.020119 | 329 | 0.0078333 | 962 | 0.022905 | 1.362 | A04 | MICL0.01913042/DMN
Build-In Floor | Mini Canal | MICL.01913042/DMV | 19 | 130 | 42 | 42 | 845 | 845 | 845 | 0.020119 | 329 | 0.0078333 | 962 | 0.022905 | 1.362 | A04 | MICL0.01913042/DMV
Build-In Floor | Mini Canal | MICL.01913042/DNA | 19 | 130 | 42 | 42 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01913042/DNA
Build-In Floor | Mini Canal | MICL.01913042/DNC | 19 | 130 | 42 | 42 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01913042/DNC
Build-In Floor | Mini Canal | MICL.01913042/DON | 19 | 130 | 42 | 42 | 845 | 845 | 845 | 0.020119 | 329 | 0.0078333 | 962 | 0.022905 | 1.362 | A04 | MICL0.01913042/DON
Build-In Floor | Mini Canal | MICL.01913042/DOV | 19 | 130 | 42 | 42 | 845 | 845 | 845 | 0.020119 | 329 | 0.0078333 | 962 | 0.022905 | 1.362 | A04 | MICL0.01913042/DOV
Build-In Floor | Mini Canal | MICL.01913042/PNC | 19 | 130 | 42 | 42 | 773 | 773 | 773 | 0.018405 | 301 | 0.0071667 | 880 | 0.020952 | 1.362 | A04 | MICL0.01913042/PNC
Build-In Floor | Mini Canal | MICL.01913042/RBL | 19 | 130 | 42 | 42 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01913042/RBL
Build-In Floor | Mini Canal | MICL.01913042/RBN | 19 | 130 | 42 | 42 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01913042/RBN
Build-In Floor | Mini Canal | MICL.01913042/RBR | 19 | 130 | 42 | 42 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01913042/RBR
Build-In Floor | Mini Canal | MICL.01913042/RBV | 19 | 130 | 42 | 42 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01913042/RBV
Build-In Floor | Mini Canal | MICL.01913042/RDB | 19 | 130 | 42 | 42 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01913042/RDB
Build-In Floor | Mini Canal | MICL.01913042/RMN | 19 | 130 | 42 | 42 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01913042/RMN
Build-In Floor | Mini Canal | MICL.01913042/RMV | 19 | 130 | 42 | 42 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01913042/RMV
Build-In Floor | Mini Canal | MICL.01913042/RNA | 19 | 130 | 42 | 42 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01913042/RNA
Build-In Floor | Mini Canal | MICL.01913042/RON | 19 | 130 | 42 | 42 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01913042/RON
Build-In Floor | Mini Canal | MICL.01913042/ROV | 19 | 130 | 42 | 42 | 882 | 882 | 882 | 0.021 | 343 | 0.0081667 | 1005 | 0.023929 | 1.362 | A04 | MICL0.01913042/ROV
Build-In Floor | Mini Canal | MICL.01913042/RSS | 19 | 130 | 42 | 42 | 873 | 873 | 873 | 0.020786 | 340 | 0.0080952 | 994 | 0.023667 | 1.362 | A04 | MICL0.01913042/RSS
Build-In Floor | Mini Canal | MICL.01913042/SBL | 19 | 130 | 42 | 42 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01913042/SBL
Build-In Floor | Mini Canal | MICL.01913042/SBR | 19 | 130 | 42 | 42 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01913042/SBR
Build-In Floor | Mini Canal | MICL.01913042/SDB | 19 | 130 | 42 | 42 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01913042/SDB
Build-In Floor | Mini Canal | MICL.01913042/SNA | 19 | 130 | 42 | 42 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01913042/SNA
Build-In Floor | Mini Canal | MICL.01913042/SNC | 19 | 130 | 42 | 42 | 909 | 909 | 909 | 0.021643 | 354 | 0.0084286 | 1035 | 0.024643 | 1.362 | A04 | MICL0.01913042/SNC
Build-In Floor | Mini Canal | MICL.01915026/ANA | 19 | 150 | 26 | 26 | 440 | 440 | 440 | 0.010476 | 171 | 0.0040714 | 501 | 0.011929 | 1.362 | A04 | MICL0.01915026/ANA
Build-In Floor | Mini Canal | MICL.01915026/DBL | 19 | 150 | 26 | 26 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01915026/DBL
Build-In Floor | Mini Canal | MICL.01915026/DBN | 19 | 150 | 26 | 26 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01915026/DBN
Build-In Floor | Mini Canal | MICL.01915026/DBR | 19 | 150 | 26 | 26 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01915026/DBR
Build-In Floor | Mini Canal | MICL.01915026/DBV | 19 | 150 | 26 | 26 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01915026/DBV
Build-In Floor | Mini Canal | MICL.01915026/DDB | 19 | 150 | 26 | 26 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01915026/DDB
Build-In Floor | Mini Canal | MICL.01915026/DMN | 19 | 150 | 26 | 26 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01915026/DMN
Build-In Floor | Mini Canal | MICL.01915026/DMV | 19 | 150 | 26 | 26 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01915026/DMV
Build-In Floor | Mini Canal | MICL.01915026/DNA | 19 | 150 | 26 | 26 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01915026/DNA
Build-In Floor | Mini Canal | MICL.01915026/DNC | 19 | 150 | 26 | 26 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01915026/DNC
Build-In Floor | Mini Canal | MICL.01915026/DON | 19 | 150 | 26 | 26 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01915026/DON
Build-In Floor | Mini Canal | MICL.01915026/DOV | 19 | 150 | 26 | 26 | 546 | 546 | 546 | 0.013 | 212 | 0.0050476 | 622 | 0.01481 | 1.362 | A04 | MICL0.01915026/DOV
Build-In Floor | Mini Canal | MICL.01915026/PNC | 19 | 150 | 26 | 26 | 499 | 499 | 499 | 0.011881 | 194 | 0.004619 | 568 | 0.013524 | 1.362 | A04 | MICL0.01915026/PNC
Build-In Floor | Mini Canal | MICL.01915026/RBL | 19 | 150 | 26 | 26 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01915026/RBL
Build-In Floor | Mini Canal | MICL.01915026/RBN | 19 | 150 | 26 | 26 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01915026/RBN
Build-In Floor | Mini Canal | MICL.01915026/RBR | 19 | 150 | 26 | 26 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01915026/RBR
Build-In Floor | Mini Canal | MICL.01915026/RBV | 19 | 150 | 26 | 26 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01915026/RBV
Build-In Floor | Mini Canal | MICL.01915026/RDB | 19 | 150 | 26 | 26 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01915026/RDB
Build-In Floor | Mini Canal | MICL.01915026/RMN | 19 | 150 | 26 | 26 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01915026/RMN
Build-In Floor | Mini Canal | MICL.01915026/RMV | 19 | 150 | 26 | 26 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01915026/RMV
Build-In Floor | Mini Canal | MICL.01915026/RNA | 19 | 150 | 26 | 26 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01915026/RNA
Build-In Floor | Mini Canal | MICL.01915026/RON | 19 | 150 | 26 | 26 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01915026/RON
Build-In Floor | Mini Canal | MICL.01915026/ROV | 19 | 150 | 26 | 26 | 569 | 569 | 569 | 0.013548 | 221 | 0.0052619 | 648 | 0.015429 | 1.362 | A04 | MICL0.01915026/ROV
Build-In Floor | Mini Canal | MICL.01915026/RSS | 19 | 150 | 26 | 26 | 564 | 564 | 564 | 0.013429 | 219 | 0.0052143 | 642 | 0.015286 | 1.362 | A04 | MICL0.01915026/RSS
Build-In Floor | Mini Canal | MICL.01915026/SBL | 19 | 150 | 26 | 26 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01915026/SBL
Build-In Floor | Mini Canal | MICL.01915026/SBR | 19 | 150 | 26 | 26 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01915026/SBR
Build-In Floor | Mini Canal | MICL.01915026/SDB | 19 | 150 | 26 | 26 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01915026/SDB
Build-In Floor | Mini Canal | MICL.01915026/SNA | 19 | 150 | 26 | 26 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01915026/SNA
Build-In Floor | Mini Canal | MICL.01915026/SNC | 19 | 150 | 26 | 26 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01915026/SNC
Build-In Floor | Mini Canal | MICL.01915034/ANA | 19 | 150 | 34 | 34 | 596 | 596 | 596 | 0.01419 | 232 | 0.0055238 | 679 | 0.016167 | 1.362 | A04 | MICL0.01915034/ANA
Build-In Floor | Mini Canal | MICL.01915034/DBL | 19 | 150 | 34 | 34 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.01915034/DBL
Build-In Floor | Mini Canal | MICL.01915034/DBN | 19 | 150 | 34 | 34 | 739 | 739 | 739 | 0.017595 | 287 | 0.0068333 | 842 | 0.020048 | 1.362 | A04 | MICL0.01915034/DBN
Build-In Floor | Mini Canal | MICL.01915034/DBR | 19 | 150 | 34 | 34 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.01915034/DBR
Build-In Floor | Mini Canal | MICL.01915034/DBV | 19 | 150 | 34 | 34 | 739 | 739 | 739 | 0.017595 | 287 | 0.0068333 | 842 | 0.020048 | 1.362 | A04 | MICL0.01915034/DBV
Build-In Floor | Mini Canal | MICL.01915034/DDB | 19 | 150 | 34 | 34 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.01915034/DDB
Build-In Floor | Mini Canal | MICL.01915034/DMN | 19 | 150 | 34 | 34 | 739 | 739 | 739 | 0.017595 | 287 | 0.0068333 | 842 | 0.020048 | 1.362 | A04 | MICL0.01915034/DMN
Build-In Floor | Mini Canal | MICL.01915034/DMV | 19 | 150 | 34 | 34 | 739 | 739 | 739 | 0.017595 | 287 | 0.0068333 | 842 | 0.020048 | 1.362 | A04 | MICL0.01915034/DMV
Build-In Floor | Mini Canal | MICL.01915034/DNA | 19 | 150 | 34 | 34 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.01915034/DNA
Build-In Floor | Mini Canal | MICL.01915034/DNC | 19 | 150 | 34 | 34 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.01915034/DNC
Build-In Floor | Mini Canal | MICL.01915034/DON | 19 | 150 | 34 | 34 | 739 | 739 | 739 | 0.017595 | 287 | 0.0068333 | 842 | 0.020048 | 1.362 | A04 | MICL0.01915034/DON
Build-In Floor | Mini Canal | MICL.01915034/DOV | 19 | 150 | 34 | 34 | 739 | 739 | 739 | 0.017595 | 287 | 0.0068333 | 842 | 0.020048 | 1.362 | A04 | MICL0.01915034/DOV
Build-In Floor | Mini Canal | MICL.01915034/PNC | 19 | 150 | 34 | 34 | 676 | 676 | 676 | 0.016095 | 263 | 0.0062619 | 770 | 0.018333 | 1.362 | A04 | MICL0.01915034/PNC
Build-In Floor | Mini Canal | MICL.01915034/RBL | 19 | 150 | 34 | 34 | 795 | 795 | 795 | 0.018929 | 309 | 0.0073571 | 906 | 0.021571 | 1.362 | A04 | MICL0.01915034/RBL
Build-In Floor | Mini Canal | MICL.01915034/RBN | 19 | 150 | 34 | 34 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.01915034/RBN
Build-In Floor | Mini Canal | MICL.01915034/RBR | 19 | 150 | 34 | 34 | 795 | 795 | 795 | 0.018929 | 309 | 0.0073571 | 906 | 0.021571 | 1.362 | A04 | MICL0.01915034/RBR
Build-In Floor | Mini Canal | MICL.01915034/RBV | 19 | 150 | 34 | 34 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.01915034/RBV
Build-In Floor | Mini Canal | MICL.01915034/RDB | 19 | 150 | 34 | 34 | 795 | 795 | 795 | 0.018929 | 309 | 0.0073571 | 906 | 0.021571 | 1.362 | A04 | MICL0.01915034/RDB
Build-In Floor | Mini Canal | MICL.01915034/RMN | 19 | 150 | 34 | 34 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.01915034/RMN
Build-In Floor | Mini Canal | MICL.01915034/RMV | 19 | 150 | 34 | 34 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.01915034/RMV
Build-In Floor | Mini Canal | MICL.01915034/RNA | 19 | 150 | 34 | 34 | 795 | 795 | 795 | 0.018929 | 309 | 0.0073571 | 906 | 0.021571 | 1.362 | A04 | MICL0.01915034/RNA
Build-In Floor | Mini Canal | MICL.01915034/RON | 19 | 150 | 34 | 34 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.01915034/RON
Build-In Floor | Mini Canal | MICL.01915034/ROV | 19 | 150 | 34 | 34 | 771 | 771 | 771 | 0.018357 | 300 | 0.0071429 | 878 | 0.020905 | 1.362 | A04 | MICL0.01915034/ROV
Build-In Floor | Mini Canal | MICL.01915034/RSS | 19 | 150 | 34 | 34 | 763 | 763 | 763 | 0.018167 | 297 | 0.0070714 | 869 | 0.02069 | 1.362 | A04 | MICL0.01915034/RSS
Build-In Floor | Mini Canal | MICL.01915034/SBL | 19 | 150 | 34 | 34 | 795 | 795 | 795 | 0.018929 | 309 | 0.0073571 | 906 | 0.021571 | 1.362 | A04 | MICL0.01915034/SBL
Build-In Floor | Mini Canal | MICL.01915034/SBR | 19 | 150 | 34 | 34 | 795 | 795 | 795 | 0.018929 | 309 | 0.0073571 | 906 | 0.021571 | 1.362 | A04 | MICL0.01915034/SBR
Build-In Floor | Mini Canal | MICL.01915034/SDB | 19 | 150 | 34 | 34 | 795 | 795 | 795 | 0.018929 | 309 | 0.0073571 | 906 | 0.021571 | 1.362 | A04 | MICL0.01915034/SDB
Build-In Floor | Mini Canal | MICL.01915034/SNA | 19 | 150 | 34 | 34 | 795 | 795 | 795 | 0.018929 | 309 | 0.0073571 | 906 | 0.021571 | 1.362 | A04 | MICL0.01915034/SNA
Build-In Floor | Mini Canal | MICL.01915034/SNC | 19 | 150 | 34 | 34 | 795 | 795 | 795 | 0.018929 | 309 | 0.0073571 | 906 | 0.021571 | 1.362 | A04 | MICL0.01915034/SNC
Build-In Floor | Mini Canal | MICL.01915042/ANA | 19 | 150 | 42 | 42 | 818 | 818 | 818 | 0.019476 | 318 | 0.0075714 | 932 | 0.02219 | 1.362 | A04 | MICL0.01915042/ANA
Build-In Floor | Mini Canal | MICL.01915042/DBL | 19 | 150 | 42 | 42 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01915042/DBL
Build-In Floor | Mini Canal | MICL.01915042/DBN | 19 | 150 | 42 | 42 | 1015 | 1015 | 1015 | 0.024167 | 395 | 0.0094048 | 1156 | 0.027524 | 1.362 | A04 | MICL0.01915042/DBN
Build-In Floor | Mini Canal | MICL.01915042/DBR | 19 | 150 | 42 | 42 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01915042/DBR
Build-In Floor | Mini Canal | MICL.01915042/DBV | 19 | 150 | 42 | 42 | 1015 | 1015 | 1015 | 0.024167 | 395 | 0.0094048 | 1156 | 0.027524 | 1.362 | A04 | MICL0.01915042/DBV
Build-In Floor | Mini Canal | MICL.01915042/DDB | 19 | 150 | 42 | 42 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01915042/DDB
Build-In Floor | Mini Canal | MICL.01915042/DMN | 19 | 150 | 42 | 42 | 1015 | 1015 | 1015 | 0.024167 | 395 | 0.0094048 | 1156 | 0.027524 | 1.362 | A04 | MICL0.01915042/DMN
Build-In Floor | Mini Canal | MICL.01915042/DMV | 19 | 150 | 42 | 42 | 1015 | 1015 | 1015 | 0.024167 | 395 | 0.0094048 | 1156 | 0.027524 | 1.362 | A04 | MICL0.01915042/DMV
Build-In Floor | Mini Canal | MICL.01915042/DNA | 19 | 150 | 42 | 42 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01915042/DNA
Build-In Floor | Mini Canal | MICL.01915042/DNC | 19 | 150 | 42 | 42 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01915042/DNC
Build-In Floor | Mini Canal | MICL.01915042/DON | 19 | 150 | 42 | 42 | 1015 | 1015 | 1015 | 0.024167 | 395 | 0.0094048 | 1156 | 0.027524 | 1.362 | A04 | MICL0.01915042/DON
Build-In Floor | Mini Canal | MICL.01915042/DOV | 19 | 150 | 42 | 42 | 1015 | 1015 | 1015 | 0.024167 | 395 | 0.0094048 | 1156 | 0.027524 | 1.362 | A04 | MICL0.01915042/DOV
Build-In Floor | Mini Canal | MICL.01915042/PNC | 19 | 150 | 42 | 42 | 927 | 927 | 927 | 0.022071 | 361 | 0.0085952 | 1056 | 0.025143 | 1.362 | A04 | MICL0.01915042/PNC
Build-In Floor | Mini Canal | MICL.01915042/RBL | 19 | 150 | 42 | 42 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01915042/RBL
Build-In Floor | Mini Canal | MICL.01915042/RBN | 19 | 150 | 42 | 42 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01915042/RBN
Build-In Floor | Mini Canal | MICL.01915042/RBR | 19 | 150 | 42 | 42 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01915042/RBR
Build-In Floor | Mini Canal | MICL.01915042/RBV | 19 | 150 | 42 | 42 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01915042/RBV
Build-In Floor | Mini Canal | MICL.01915042/RDB | 19 | 150 | 42 | 42 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01915042/RDB
Build-In Floor | Mini Canal | MICL.01915042/RMN | 19 | 150 | 42 | 42 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01915042/RMN
Build-In Floor | Mini Canal | MICL.01915042/RMV | 19 | 150 | 42 | 42 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01915042/RMV
Build-In Floor | Mini Canal | MICL.01915042/RNA | 19 | 150 | 42 | 42 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01915042/RNA
Build-In Floor | Mini Canal | MICL.01915042/RON | 19 | 150 | 42 | 42 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01915042/RON
Build-In Floor | Mini Canal | MICL.01915042/ROV | 19 | 150 | 42 | 42 | 1058 | 1058 | 1058 | 0.02519 | 412 | 0.0098095 | 1205 | 0.02869 | 1.362 | A04 | MICL0.01915042/ROV
Build-In Floor | Mini Canal | MICL.01915042/RSS | 19 | 150 | 42 | 42 | 1047 | 1047 | 1047 | 0.024929 | 407 | 0.0096905 | 1193 | 0.028405 | 1.362 | A04 | MICL0.01915042/RSS
Build-In Floor | Mini Canal | MICL.01915042/SBL | 19 | 150 | 42 | 42 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01915042/SBL
Build-In Floor | Mini Canal | MICL.01915042/SBR | 19 | 150 | 42 | 42 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01915042/SBR
Build-In Floor | Mini Canal | MICL.01915042/SDB | 19 | 150 | 42 | 42 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01915042/SDB
Build-In Floor | Mini Canal | MICL.01915042/SNA | 19 | 150 | 42 | 42 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01915042/SNA
Build-In Floor | Mini Canal | MICL.01915042/SNC | 19 | 150 | 42 | 42 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01915042/SNC
Build-In Floor | Mini Canal | MICL.01917026/ANA | 19 | 170 | 26 | 26 | 514 | 514 | 514 | 0.012238 | 200 | 0.0047619 | 585 | 0.013929 | 1.362 | A04 | MICL0.01917026/ANA
Build-In Floor | Mini Canal | MICL.01917026/DBL | 19 | 170 | 26 | 26 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.01917026/DBL
Build-In Floor | Mini Canal | MICL.01917026/DBN | 19 | 170 | 26 | 26 | 637 | 637 | 637 | 0.015167 | 248 | 0.0059048 | 726 | 0.017286 | 1.362 | A04 | MICL0.01917026/DBN
Build-In Floor | Mini Canal | MICL.01917026/DBR | 19 | 170 | 26 | 26 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.01917026/DBR
Build-In Floor | Mini Canal | MICL.01917026/DBV | 19 | 170 | 26 | 26 | 637 | 637 | 637 | 0.015167 | 248 | 0.0059048 | 726 | 0.017286 | 1.362 | A04 | MICL0.01917026/DBV
Build-In Floor | Mini Canal | MICL.01917026/DDB | 19 | 170 | 26 | 26 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.01917026/DDB
Build-In Floor | Mini Canal | MICL.01917026/DMN | 19 | 170 | 26 | 26 | 637 | 637 | 637 | 0.015167 | 248 | 0.0059048 | 726 | 0.017286 | 1.362 | A04 | MICL0.01917026/DMN
Build-In Floor | Mini Canal | MICL.01917026/DMV | 19 | 170 | 26 | 26 | 637 | 637 | 637 | 0.015167 | 248 | 0.0059048 | 726 | 0.017286 | 1.362 | A04 | MICL0.01917026/DMV
Build-In Floor | Mini Canal | MICL.01917026/DNA | 19 | 170 | 26 | 26 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.01917026/DNA
Build-In Floor | Mini Canal | MICL.01917026/DNC | 19 | 170 | 26 | 26 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.01917026/DNC
Build-In Floor | Mini Canal | MICL.01917026/DON | 19 | 170 | 26 | 26 | 637 | 637 | 637 | 0.015167 | 248 | 0.0059048 | 726 | 0.017286 | 1.362 | A04 | MICL0.01917026/DON
Build-In Floor | Mini Canal | MICL.01917026/DOV | 19 | 170 | 26 | 26 | 637 | 637 | 637 | 0.015167 | 248 | 0.0059048 | 726 | 0.017286 | 1.362 | A04 | MICL0.01917026/DOV
Build-In Floor | Mini Canal | MICL.01917026/PNC | 19 | 170 | 26 | 26 | 582 | 582 | 582 | 0.013857 | 226 | 0.005381 | 663 | 0.015786 | 1.362 | A04 | MICL0.01917026/PNC
Build-In Floor | Mini Canal | MICL.01917026/RBL | 19 | 170 | 26 | 26 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.01917026/RBL
Build-In Floor | Mini Canal | MICL.01917026/RBN | 19 | 170 | 26 | 26 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.01917026/RBN
Build-In Floor | Mini Canal | MICL.01917026/RBR | 19 | 170 | 26 | 26 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.01917026/RBR
Build-In Floor | Mini Canal | MICL.01917026/RBV | 19 | 170 | 26 | 26 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.01917026/RBV
Build-In Floor | Mini Canal | MICL.01917026/RDB | 19 | 170 | 26 | 26 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.01917026/RDB
Build-In Floor | Mini Canal | MICL.01917026/RMN | 19 | 170 | 26 | 26 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.01917026/RMN
Build-In Floor | Mini Canal | MICL.01917026/RMV | 19 | 170 | 26 | 26 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.01917026/RMV
Build-In Floor | Mini Canal | MICL.01917026/RNA | 19 | 170 | 26 | 26 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.01917026/RNA
Build-In Floor | Mini Canal | MICL.01917026/RON | 19 | 170 | 26 | 26 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.01917026/RON
Build-In Floor | Mini Canal | MICL.01917026/ROV | 19 | 170 | 26 | 26 | 664 | 664 | 664 | 0.01581 | 258 | 0.0061429 | 756 | 0.018 | 1.362 | A04 | MICL0.01917026/ROV
Build-In Floor | Mini Canal | MICL.01917026/RSS | 19 | 170 | 26 | 26 | 658 | 658 | 658 | 0.015667 | 256 | 0.0060952 | 749 | 0.017833 | 1.362 | A04 | MICL0.01917026/RSS
Build-In Floor | Mini Canal | MICL.01917026/SBL | 19 | 170 | 26 | 26 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.01917026/SBL
Build-In Floor | Mini Canal | MICL.01917026/SBR | 19 | 170 | 26 | 26 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.01917026/SBR
Build-In Floor | Mini Canal | MICL.01917026/SDB | 19 | 170 | 26 | 26 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.01917026/SDB
Build-In Floor | Mini Canal | MICL.01917026/SNA | 19 | 170 | 26 | 26 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.01917026/SNA
Build-In Floor | Mini Canal | MICL.01917026/SNC | 19 | 170 | 26 | 26 | 685 | 685 | 685 | 0.01631 | 266 | 0.0063333 | 780 | 0.018571 | 1.362 | A04 | MICL0.01917026/SNC
Build-In Floor | Mini Canal | MICL.01917034/ANA | 19 | 170 | 34 | 34 | 695 | 695 | 695 | 0.016548 | 270 | 0.0064286 | 792 | 0.018857 | 1.362 | A04 | MICL0.01917034/ANA
Build-In Floor | Mini Canal | MICL.01917034/DBL | 19 | 170 | 34 | 34 | 899 | 899 | 899 | 0.021405 | 350 | 0.0083333 | 1024 | 0.024381 | 1.362 | A04 | MICL0.01917034/DBL
Build-In Floor | Mini Canal | MICL.01917034/DBN | 19 | 170 | 34 | 34 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.01917034/DBN
Build-In Floor | Mini Canal | MICL.01917034/DBR | 19 | 170 | 34 | 34 | 899 | 899 | 899 | 0.021405 | 350 | 0.0083333 | 1024 | 0.024381 | 1.362 | A04 | MICL0.01917034/DBR
Build-In Floor | Mini Canal | MICL.01917034/DBV | 19 | 170 | 34 | 34 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.01917034/DBV
Build-In Floor | Mini Canal | MICL.01917034/DDB | 19 | 170 | 34 | 34 | 899 | 899 | 899 | 0.021405 | 350 | 0.0083333 | 1024 | 0.024381 | 1.362 | A04 | MICL0.01917034/DDB
Build-In Floor | Mini Canal | MICL.01917034/DMN | 19 | 170 | 34 | 34 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.01917034/DMN
Build-In Floor | Mini Canal | MICL.01917034/DMV | 19 | 170 | 34 | 34 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.01917034/DMV
Build-In Floor | Mini Canal | MICL.01917034/DNA | 19 | 170 | 34 | 34 | 899 | 899 | 899 | 0.021405 | 350 | 0.0083333 | 1024 | 0.024381 | 1.362 | A04 | MICL0.01917034/DNA
Build-In Floor | Mini Canal | MICL.01917034/DNC | 19 | 170 | 34 | 34 | 899 | 899 | 899 | 0.021405 | 350 | 0.0083333 | 1024 | 0.024381 | 1.362 | A04 | MICL0.01917034/DNC
Build-In Floor | Mini Canal | MICL.01917034/DON | 19 | 170 | 34 | 34 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.01917034/DON
Build-In Floor | Mini Canal | MICL.01917034/DOV | 19 | 170 | 34 | 34 | 862 | 862 | 862 | 0.020524 | 335 | 0.0079762 | 982 | 0.023381 | 1.362 | A04 | MICL0.01917034/DOV
Build-In Floor | Mini Canal | MICL.01917034/PNC | 19 | 170 | 34 | 34 | 788 | 788 | 788 | 0.018762 | 307 | 0.0073095 | 898 | 0.021381 | 1.362 | A04 | MICL0.01917034/PNC
Build-In Floor | Mini Canal | MICL.01917034/RBL | 19 | 170 | 34 | 34 | 927 | 927 | 927 | 0.022071 | 361 | 0.0085952 | 1056 | 0.025143 | 1.362 | A04 | MICL0.01917034/RBL
Build-In Floor | Mini Canal | MICL.01917034/RBN | 19 | 170 | 34 | 34 | 899 | 899 | 899 | 0.021405 | 350 | 0.0083333 | 1024 | 0.024381 | 1.362 | A04 | MICL0.01917034/RBN
Build-In Floor | Mini Canal | MICL.01917034/RBR | 19 | 170 | 34 | 34 | 927 | 927 | 927 | 0.022071 | 361 | 0.0085952 | 1056 | 0.025143 | 1.362 | A04 | MICL0.01917034/RBR
Build-In Floor | Mini Canal | MICL.01917034/RBV | 19 | 170 | 34 | 34 | 899 | 899 | 899 | 0.021405 | 350 | 0.0083333 | 1024 | 0.024381 | 1.362 | A04 | MICL0.01917034/RBV
Build-In Floor | Mini Canal | MICL.01917034/RDB | 19 | 170 | 34 | 34 | 927 | 927 | 927 | 0.022071 | 361 | 0.0085952 | 1056 | 0.025143 | 1.362 | A04 | MICL0.01917034/RDB
Build-In Floor | Mini Canal | MICL.01917034/RMN | 19 | 170 | 34 | 34 | 899 | 899 | 899 | 0.021405 | 350 | 0.0083333 | 1024 | 0.024381 | 1.362 | A04 | MICL0.01917034/RMN
Build-In Floor | Mini Canal | MICL.01917034/RMV | 19 | 170 | 34 | 34 | 899 | 899 | 899 | 0.021405 | 350 | 0.0083333 | 1024 | 0.024381 | 1.362 | A04 | MICL0.01917034/RMV
Build-In Floor | Mini Canal | MICL.01917034/RNA | 19 | 170 | 34 | 34 | 927 | 927 | 927 | 0.022071 | 361 | 0.0085952 | 1056 | 0.025143 | 1.362 | A04 | MICL0.01917034/RNA
Build-In Floor | Mini Canal | MICL.01917034/RON | 19 | 170 | 34 | 34 | 899 | 899 | 899 | 0.021405 | 350 | 0.0083333 | 1024 | 0.024381 | 1.362 | A04 | MICL0.01917034/RON
Build-In Floor | Mini Canal | MICL.01917034/ROV | 19 | 170 | 34 | 34 | 899 | 899 | 899 | 0.021405 | 350 | 0.0083333 | 1024 | 0.024381 | 1.362 | A04 | MICL0.01917034/ROV
Build-In Floor | Mini Canal | MICL.01917034/RSS | 19 | 170 | 34 | 34 | 890 | 890 | 890 | 0.02119 | 346 | 0.0082381 | 1014 | 0.024143 | 1.362 | A04 | MICL0.01917034/RSS
Build-In Floor | Mini Canal | MICL.01917034/SBL | 19 | 170 | 34 | 34 | 927 | 927 | 927 | 0.022071 | 361 | 0.0085952 | 1056 | 0.025143 | 1.362 | A04 | MICL0.01917034/SBL
Build-In Floor | Mini Canal | MICL.01917034/SBR | 19 | 170 | 34 | 34 | 927 | 927 | 927 | 0.022071 | 361 | 0.0085952 | 1056 | 0.025143 | 1.362 | A04 | MICL0.01917034/SBR
Build-In Floor | Mini Canal | MICL.01917034/SDB | 19 | 170 | 34 | 34 | 927 | 927 | 927 | 0.022071 | 361 | 0.0085952 | 1056 | 0.025143 | 1.362 | A04 | MICL0.01917034/SDB
Build-In Floor | Mini Canal | MICL.01917034/SNA | 19 | 170 | 34 | 34 | 927 | 927 | 927 | 0.022071 | 361 | 0.0085952 | 1056 | 0.025143 | 1.362 | A04 | MICL0.01917034/SNA
Build-In Floor | Mini Canal | MICL.01917034/SNC | 19 | 170 | 34 | 34 | 927 | 927 | 927 | 0.022071 | 361 | 0.0085952 | 1056 | 0.025143 | 1.362 | A04 | MICL0.01917034/SNC
Build-In Floor | Mini Canal | MICL.01917042/ANA | 19 | 170 | 42 | 42 | 955 | 955 | 955 | 0.022738 | 371 | 0.0088333 | 1088 | 0.025905 | 1.362 | A04 | MICL0.01917042/ANA
Build-In Floor | Mini Canal | MICL.01917042/DBL | 19 | 170 | 42 | 42 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01917042/DBL
Build-In Floor | Mini Canal | MICL.01917042/DBN | 19 | 170 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.01917042/DBN
Build-In Floor | Mini Canal | MICL.01917042/DBR | 19 | 170 | 42 | 42 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01917042/DBR
Build-In Floor | Mini Canal | MICL.01917042/DBV | 19 | 170 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.01917042/DBV
Build-In Floor | Mini Canal | MICL.01917042/DDB | 19 | 170 | 42 | 42 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01917042/DDB
Build-In Floor | Mini Canal | MICL.01917042/DMN | 19 | 170 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.01917042/DMN
Build-In Floor | Mini Canal | MICL.01917042/DMV | 19 | 170 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.01917042/DMV
Build-In Floor | Mini Canal | MICL.01917042/DNA | 19 | 170 | 42 | 42 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01917042/DNA
Build-In Floor | Mini Canal | MICL.01917042/DNC | 19 | 170 | 42 | 42 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01917042/DNC
Build-In Floor | Mini Canal | MICL.01917042/DON | 19 | 170 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.01917042/DON
Build-In Floor | Mini Canal | MICL.01917042/DOV | 19 | 170 | 42 | 42 | 1184 | 1184 | 1184 | 0.02819 | 461 | 0.010976 | 1349 | 0.032119 | 1.362 | A04 | MICL0.01917042/DOV
Build-In Floor | Mini Canal | MICL.01917042/PNC | 19 | 170 | 42 | 42 | 1082 | 1082 | 1082 | 0.025762 | 421 | 0.010024 | 1232 | 0.029333 | 1.362 | A04 | MICL0.01917042/PNC
Build-In Floor | Mini Canal | MICL.01917042/RBL | 19 | 170 | 42 | 42 | 1273 | 1273 | 1273 | 0.03031 | 495 | 0.011786 | 1450 | 0.034524 | 1.362 | A04 | MICL0.01917042/RBL
Build-In Floor | Mini Canal | MICL.01917042/RBN | 19 | 170 | 42 | 42 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01917042/RBN
Build-In Floor | Mini Canal | MICL.01917042/RBR | 19 | 170 | 42 | 42 | 1273 | 1273 | 1273 | 0.03031 | 495 | 0.011786 | 1450 | 0.034524 | 1.362 | A04 | MICL0.01917042/RBR
Build-In Floor | Mini Canal | MICL.01917042/RBV | 19 | 170 | 42 | 42 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01917042/RBV
Build-In Floor | Mini Canal | MICL.01917042/RDB | 19 | 170 | 42 | 42 | 1273 | 1273 | 1273 | 0.03031 | 495 | 0.011786 | 1450 | 0.034524 | 1.362 | A04 | MICL0.01917042/RDB
Build-In Floor | Mini Canal | MICL.01917042/RMN | 19 | 170 | 42 | 42 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01917042/RMN
Build-In Floor | Mini Canal | MICL.01917042/RMV | 19 | 170 | 42 | 42 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01917042/RMV
Build-In Floor | Mini Canal | MICL.01917042/RNA | 19 | 170 | 42 | 42 | 1273 | 1273 | 1273 | 0.03031 | 495 | 0.011786 | 1450 | 0.034524 | 1.362 | A04 | MICL0.01917042/RNA
Build-In Floor | Mini Canal | MICL.01917042/RON | 19 | 170 | 42 | 42 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01917042/RON
Build-In Floor | Mini Canal | MICL.01917042/ROV | 19 | 170 | 42 | 42 | 1235 | 1235 | 1235 | 0.029405 | 480 | 0.011429 | 1407 | 0.0335 | 1.362 | A04 | MICL0.01917042/ROV
Build-In Floor | Mini Canal | MICL.01917042/RSS | 19 | 170 | 42 | 42 | 1222 | 1222 | 1222 | 0.029095 | 475 | 0.01131 | 1392 | 0.033143 | 1.362 | A04 | MICL0.01917042/RSS
Build-In Floor | Mini Canal | MICL.01917042/SBL | 19 | 170 | 42 | 42 | 1273 | 1273 | 1273 | 0.03031 | 495 | 0.011786 | 1450 | 0.034524 | 1.362 | A04 | MICL0.01917042/SBL
Build-In Floor | Mini Canal | MICL.01917042/SBR | 19 | 170 | 42 | 42 | 1273 | 1273 | 1273 | 0.03031 | 495 | 0.011786 | 1450 | 0.034524 | 1.362 | A04 | MICL0.01917042/SBR
Build-In Floor | Mini Canal | MICL.01917042/SDB | 19 | 170 | 42 | 42 | 1273 | 1273 | 1273 | 0.03031 | 495 | 0.011786 | 1450 | 0.034524 | 1.362 | A04 | MICL0.01917042/SDB
Build-In Floor | Mini Canal | MICL.01917042/SNA | 19 | 170 | 42 | 42 | 1273 | 1273 | 1273 | 0.03031 | 495 | 0.011786 | 1450 | 0.034524 | 1.362 | A04 | MICL0.01917042/SNA
Build-In Floor | Mini Canal | MICL.01917042/SNC | 19 | 170 | 42 | 42 | 1273 | 1273 | 1273 | 0.03031 | 495 | 0.011786 | 1450 | 0.034524 | 1.362 | A04 | MICL0.01917042/SNC
Build-In Floor | Mini Canal | MICL.01919026/ANA | 19 | 190 | 26 | 26 | 587 | 587 | 587 | 0.013976 | 228 | 0.0054286 | 669 | 0.015929 | 1.362 | A04 | MICL0.01919026/ANA
Build-In Floor | Mini Canal | MICL.01919026/DBL | 19 | 190 | 26 | 26 | 759 | 759 | 759 | 0.018071 | 295 | 0.0070238 | 865 | 0.020595 | 1.362 | A04 | MICL0.01919026/DBL
Build-In Floor | Mini Canal | MICL.01919026/DBN | 19 | 190 | 26 | 26 | 727 | 727 | 727 | 0.01731 | 283 | 0.0067381 | 828 | 0.019714 | 1.362 | A04 | MICL0.01919026/DBN
Build-In Floor | Mini Canal | MICL.01919026/DBR | 19 | 190 | 26 | 26 | 759 | 759 | 759 | 0.018071 | 295 | 0.0070238 | 865 | 0.020595 | 1.362 | A04 | MICL0.01919026/DBR
Build-In Floor | Mini Canal | MICL.01919026/DBV | 19 | 190 | 26 | 26 | 727 | 727 | 727 | 0.01731 | 283 | 0.0067381 | 828 | 0.019714 | 1.362 | A04 | MICL0.01919026/DBV
Build-In Floor | Mini Canal | MICL.01919026/DDB | 19 | 190 | 26 | 26 | 759 | 759 | 759 | 0.018071 | 295 | 0.0070238 | 865 | 0.020595 | 1.362 | A04 | MICL0.01919026/DDB
Build-In Floor | Mini Canal | MICL.01919026/DMN | 19 | 190 | 26 | 26 | 727 | 727 | 727 | 0.01731 | 283 | 0.0067381 | 828 | 0.019714 | 1.362 | A04 | MICL0.01919026/DMN
Build-In Floor | Mini Canal | MICL.01919026/DMV | 19 | 190 | 26 | 26 | 727 | 727 | 727 | 0.01731 | 283 | 0.0067381 | 828 | 0.019714 | 1.362 | A04 | MICL0.01919026/DMV
Build-In Floor | Mini Canal | MICL.01919026/DNA | 19 | 190 | 26 | 26 | 759 | 759 | 759 | 0.018071 | 295 | 0.0070238 | 865 | 0.020595 | 1.362 | A04 | MICL0.01919026/DNA
Build-In Floor | Mini Canal | MICL.01919026/DNC | 19 | 190 | 26 | 26 | 759 | 759 | 759 | 0.018071 | 295 | 0.0070238 | 865 | 0.020595 | 1.362 | A04 | MICL0.01919026/DNC
Build-In Floor | Mini Canal | MICL.01919026/DON | 19 | 190 | 26 | 26 | 727 | 727 | 727 | 0.01731 | 283 | 0.0067381 | 828 | 0.019714 | 1.362 | A04 | MICL0.01919026/DON
Build-In Floor | Mini Canal | MICL.01919026/DOV | 19 | 190 | 26 | 26 | 727 | 727 | 727 | 0.01731 | 283 | 0.0067381 | 828 | 0.019714 | 1.362 | A04 | MICL0.01919026/DOV
Build-In Floor | Mini Canal | MICL.01919026/PNC | 19 | 190 | 26 | 26 | 665 | 665 | 665 | 0.015833 | 259 | 0.0061667 | 757 | 0.018024 | 1.362 | A04 | MICL0.01919026/PNC
Build-In Floor | Mini Canal | MICL.01919026/RBL | 19 | 190 | 26 | 26 | 782 | 782 | 782 | 0.018619 | 304 | 0.0072381 | 891 | 0.021214 | 1.362 | A04 | MICL0.01919026/RBL
Build-In Floor | Mini Canal | MICL.01919026/RBN | 19 | 190 | 26 | 26 | 759 | 759 | 759 | 0.018071 | 295 | 0.0070238 | 865 | 0.020595 | 1.362 | A04 | MICL0.01919026/RBN
Build-In Floor | Mini Canal | MICL.01919026/RBR | 19 | 190 | 26 | 26 | 782 | 782 | 782 | 0.018619 | 304 | 0.0072381 | 891 | 0.021214 | 1.362 | A04 | MICL0.01919026/RBR
Build-In Floor | Mini Canal | MICL.01919026/RBV | 19 | 190 | 26 | 26 | 759 | 759 | 759 | 0.018071 | 295 | 0.0070238 | 865 | 0.020595 | 1.362 | A04 | MICL0.01919026/RBV
Build-In Floor | Mini Canal | MICL.01919026/RDB | 19 | 190 | 26 | 26 | 782 | 782 | 782 | 0.018619 | 304 | 0.0072381 | 891 | 0.021214 | 1.362 | A04 | MICL0.01919026/RDB
Build-In Floor | Mini Canal | MICL.01919026/RMN | 19 | 190 | 26 | 26 | 759 | 759 | 759 | 0.018071 | 295 | 0.0070238 | 865 | 0.020595 | 1.362 | A04 | MICL0.01919026/RMN
Build-In Floor | Mini Canal | MICL.01919026/RMV | 19 | 190 | 26 | 26 | 759 | 759 | 759 | 0.018071 | 295 | 0.0070238 | 865 | 0.020595 | 1.362 | A04 | MICL0.01919026/RMV
Build-In Floor | Mini Canal | MICL.01919026/RNA | 19 | 190 | 26 | 26 | 782 | 782 | 782 | 0.018619 | 304 | 0.0072381 | 891 | 0.021214 | 1.362 | A04 | MICL0.01919026/RNA
Build-In Floor | Mini Canal | MICL.01919026/RON | 19 | 190 | 26 | 26 | 759 | 759 | 759 | 0.018071 | 295 | 0.0070238 | 865 | 0.020595 | 1.362 | A04 | MICL0.01919026/RON
Build-In Floor | Mini Canal | MICL.01919026/ROV | 19 | 190 | 26 | 26 | 759 | 759 | 759 | 0.018071 | 295 | 0.0070238 | 865 | 0.020595 | 1.362 | A04 | MICL0.01919026/ROV
Build-In Floor | Mini Canal | MICL.01919026/RSS | 19 | 190 | 26 | 26 | 751 | 751 | 751 | 0.017881 | 292 | 0.0069524 | 855 | 0.020357 | 1.362 | A04 | MICL0.01919026/RSS
Build-In Floor | Mini Canal | MICL.01919026/SBL | 19 | 190 | 26 | 26 | 782 | 782 | 782 | 0.018619 | 304 | 0.0072381 | 891 | 0.021214 | 1.362 | A04 | MICL0.01919026/SBL
Build-In Floor | Mini Canal | MICL.01919026/SBR | 19 | 190 | 26 | 26 | 782 | 782 | 782 | 0.018619 | 304 | 0.0072381 | 891 | 0.021214 | 1.362 | A04 | MICL0.01919026/SBR
Build-In Floor | Mini Canal | MICL.01919026/SDB | 19 | 190 | 26 | 26 | 782 | 782 | 782 | 0.018619 | 304 | 0.0072381 | 891 | 0.021214 | 1.362 | A04 | MICL0.01919026/SDB
Build-In Floor | Mini Canal | MICL.01919026/SNA | 19 | 190 | 26 | 26 | 782 | 782 | 782 | 0.018619 | 304 | 0.0072381 | 891 | 0.021214 | 1.362 | A04 | MICL0.01919026/SNA
Build-In Floor | Mini Canal | MICL.01919026/SNC | 19 | 190 | 26 | 26 | 782 | 782 | 782 | 0.018619 | 304 | 0.0072381 | 891 | 0.021214 | 1.362 | A04 | MICL0.01919026/SNC
Build-In Floor | Mini Canal | MICL.01919034/ANA | 19 | 190 | 34 | 34 | 794 | 794 | 794 | 0.018905 | 309 | 0.0073571 | 904 | 0.021524 | 1.362 | A04 | MICL0.01919034/ANA
Build-In Floor | Mini Canal | MICL.01919034/DBL | 19 | 190 | 34 | 34 | 1027 | 1027 | 1027 | 0.024452 | 400 | 0.0095238 | 1170 | 0.027857 | 1.362 | A04 | MICL0.01919034/DBL
Build-In Floor | Mini Canal | MICL.01919034/DBN | 19 | 190 | 34 | 34 | 985 | 985 | 985 | 0.023452 | 383 | 0.009119 | 1122 | 0.026714 | 1.362 | A04 | MICL0.01919034/DBN
Build-In Floor | Mini Canal | MICL.01919034/DBR | 19 | 190 | 34 | 34 | 1027 | 1027 | 1027 | 0.024452 | 400 | 0.0095238 | 1170 | 0.027857 | 1.362 | A04 | MICL0.01919034/DBR
Build-In Floor | Mini Canal | MICL.01919034/DBV | 19 | 190 | 34 | 34 | 985 | 985 | 985 | 0.023452 | 383 | 0.009119 | 1122 | 0.026714 | 1.362 | A04 | MICL0.01919034/DBV
Build-In Floor | Mini Canal | MICL.01919034/DDB | 19 | 190 | 34 | 34 | 1027 | 1027 | 1027 | 0.024452 | 400 | 0.0095238 | 1170 | 0.027857 | 1.362 | A04 | MICL0.01919034/DDB
Build-In Floor | Mini Canal | MICL.01919034/DMN | 19 | 190 | 34 | 34 | 985 | 985 | 985 | 0.023452 | 383 | 0.009119 | 1122 | 0.026714 | 1.362 | A04 | MICL0.01919034/DMN
Build-In Floor | Mini Canal | MICL.01919034/DMV | 19 | 190 | 34 | 34 | 985 | 985 | 985 | 0.023452 | 383 | 0.009119 | 1122 | 0.026714 | 1.362 | A04 | MICL0.01919034/DMV
Build-In Floor | Mini Canal | MICL.01919034/DNA | 19 | 190 | 34 | 34 | 1027 | 1027 | 1027 | 0.024452 | 400 | 0.0095238 | 1170 | 0.027857 | 1.362 | A04 | MICL0.01919034/DNA
Build-In Floor | Mini Canal | MICL.01919034/DNC | 19 | 190 | 34 | 34 | 1027 | 1027 | 1027 | 0.024452 | 400 | 0.0095238 | 1170 | 0.027857 | 1.362 | A04 | MICL0.01919034/DNC
Build-In Floor | Mini Canal | MICL.01919034/DON | 19 | 190 | 34 | 34 | 985 | 985 | 985 | 0.023452 | 383 | 0.009119 | 1122 | 0.026714 | 1.362 | A04 | MICL0.01919034/DON
Build-In Floor | Mini Canal | MICL.01919034/DOV | 19 | 190 | 34 | 34 | 985 | 985 | 985 | 0.023452 | 383 | 0.009119 | 1122 | 0.026714 | 1.362 | A04 | MICL0.01919034/DOV
Build-In Floor | Mini Canal | MICL.01919034/PNC | 19 | 190 | 34 | 34 | 900 | 900 | 900 | 0.021429 | 350 | 0.0083333 | 1025 | 0.024405 | 1.362 | A04 | MICL0.01919034/PNC
Build-In Floor | Mini Canal | MICL.01919034/RBL | 19 | 190 | 34 | 34 | 1059 | 1059 | 1059 | 0.025214 | 412 | 0.0098095 | 1206 | 0.028714 | 1.362 | A04 | MICL0.01919034/RBL
Build-In Floor | Mini Canal | MICL.01919034/RBN | 19 | 190 | 34 | 34 | 1027 | 1027 | 1027 | 0.024452 | 400 | 0.0095238 | 1170 | 0.027857 | 1.362 | A04 | MICL0.01919034/RBN
Build-In Floor | Mini Canal | MICL.01919034/RBR | 19 | 190 | 34 | 34 | 1059 | 1059 | 1059 | 0.025214 | 412 | 0.0098095 | 1206 | 0.028714 | 1.362 | A04 | MICL0.01919034/RBR
Build-In Floor | Mini Canal | MICL.01919034/RBV | 19 | 190 | 34 | 34 | 1027 | 1027 | 1027 | 0.024452 | 400 | 0.0095238 | 1170 | 0.027857 | 1.362 | A04 | MICL0.01919034/RBV
Build-In Floor | Mini Canal | MICL.01919034/RDB | 19 | 190 | 34 | 34 | 1059 | 1059 | 1059 | 0.025214 | 412 | 0.0098095 | 1206 | 0.028714 | 1.362 | A04 | MICL0.01919034/RDB
Build-In Floor | Mini Canal | MICL.01919034/RMN | 19 | 190 | 34 | 34 | 1027 | 1027 | 1027 | 0.024452 | 400 | 0.0095238 | 1170 | 0.027857 | 1.362 | A04 | MICL0.01919034/RMN
Build-In Floor | Mini Canal | MICL.01919034/RMV | 19 | 190 | 34 | 34 | 1027 | 1027 | 1027 | 0.024452 | 400 | 0.0095238 | 1170 | 0.027857 | 1.362 | A04 | MICL0.01919034/RMV
Build-In Floor | Mini Canal | MICL.01919034/RNA | 19 | 190 | 34 | 34 | 1059 | 1059 | 1059 | 0.025214 | 412 | 0.0098095 | 1206 | 0.028714 | 1.362 | A04 | MICL0.01919034/RNA
Build-In Floor | Mini Canal | MICL.01919034/RON | 19 | 190 | 34 | 34 | 1027 | 1027 | 1027 | 0.024452 | 400 | 0.0095238 | 1170 | 0.027857 | 1.362 | A04 | MICL0.01919034/RON
Build-In Floor | Mini Canal | MICL.01919034/ROV | 19 | 190 | 34 | 34 | 1027 | 1027 | 1027 | 0.024452 | 400 | 0.0095238 | 1170 | 0.027857 | 1.362 | A04 | MICL0.01919034/ROV
Build-In Floor | Mini Canal | MICL.01919034/RSS | 19 | 190 | 34 | 34 | 1017 | 1017 | 1017 | 0.024214 | 396 | 0.0094286 | 1158 | 0.027571 | 1.362 | A04 | MICL0.01919034/RSS
Build-In Floor | Mini Canal | MICL.01919034/SBL | 19 | 190 | 34 | 34 | 1059 | 1059 | 1059 | 0.025214 | 412 | 0.0098095 | 1206 | 0.028714 | 1.362 | A04 | MICL0.01919034/SBL
Build-In Floor | Mini Canal | MICL.01919034/SBR | 19 | 190 | 34 | 34 | 1059 | 1059 | 1059 | 0.025214 | 412 | 0.0098095 | 1206 | 0.028714 | 1.362 | A04 | MICL0.01919034/SBR
Build-In Floor | Mini Canal | MICL.01919034/SDB | 19 | 190 | 34 | 34 | 1059 | 1059 | 1059 | 0.025214 | 412 | 0.0098095 | 1206 | 0.028714 | 1.362 | A04 | MICL0.01919034/SDB
Build-In Floor | Mini Canal | MICL.01919034/SNA | 19 | 190 | 34 | 34 | 1059 | 1059 | 1059 | 0.025214 | 412 | 0.0098095 | 1206 | 0.028714 | 1.362 | A04 | MICL0.01919034/SNA
Build-In Floor | Mini Canal | MICL.01919034/SNC | 19 | 190 | 34 | 34 | 1059 | 1059 | 1059 | 0.025214 | 412 | 0.0098095 | 1206 | 0.028714 | 1.362 | A04 | MICL0.01919034/SNC
Build-In Floor | Mini Canal | MICL.01919042/ANA | 19 | 190 | 42 | 42 | 1091 | 1091 | 1091 | 0.025976 | 424 | 0.010095 | 1243 | 0.029595 | 1.362 | A04 | MICL0.01919042/ANA
Build-In Floor | Mini Canal | MICL.01919042/DBL | 19 | 190 | 42 | 42 | 1411 | 1411 | 1411 | 0.033595 | 549 | 0.013071 | 1607 | 0.038262 | 1.362 | A04 | MICL0.01919042/DBL
Build-In Floor | Mini Canal | MICL.01919042/DBN | 19 | 190 | 42 | 42 | 1353 | 1353 | 1353 | 0.032214 | 526 | 0.012524 | 1541 | 0.03669 | 1.362 | A04 | MICL0.01919042/DBN
Build-In Floor | Mini Canal | MICL.01919042/DBR | 19 | 190 | 42 | 42 | 1411 | 1411 | 1411 | 0.033595 | 549 | 0.013071 | 1607 | 0.038262 | 1.362 | A04 | MICL0.01919042/DBR
Build-In Floor | Mini Canal | MICL.01919042/DBV | 19 | 190 | 42 | 42 | 1353 | 1353 | 1353 | 0.032214 | 526 | 0.012524 | 1541 | 0.03669 | 1.362 | A04 | MICL0.01919042/DBV
Build-In Floor | Mini Canal | MICL.01919042/DDB | 19 | 190 | 42 | 42 | 1411 | 1411 | 1411 | 0.033595 | 549 | 0.013071 | 1607 | 0.038262 | 1.362 | A04 | MICL0.01919042/DDB
Build-In Floor | Mini Canal | MICL.01919042/DMN | 19 | 190 | 42 | 42 | 1353 | 1353 | 1353 | 0.032214 | 526 | 0.012524 | 1541 | 0.03669 | 1.362 | A04 | MICL0.01919042/DMN
Build-In Floor | Mini Canal | MICL.01919042/DMV | 19 | 190 | 42 | 42 | 1353 | 1353 | 1353 | 0.032214 | 526 | 0.012524 | 1541 | 0.03669 | 1.362 | A04 | MICL0.01919042/DMV
Build-In Floor | Mini Canal | MICL.01919042/DNA | 19 | 190 | 42 | 42 | 1411 | 1411 | 1411 | 0.033595 | 549 | 0.013071 | 1607 | 0.038262 | 1.362 | A04 | MICL0.01919042/DNA
Build-In Floor | Mini Canal | MICL.01919042/DNC | 19 | 190 | 42 | 42 | 1411 | 1411 | 1411 | 0.033595 | 549 | 0.013071 | 1607 | 0.038262 | 1.362 | A04 | MICL0.01919042/DNC
Build-In Floor | Mini Canal | MICL.01919042/DON | 19 | 190 | 42 | 42 | 1353 | 1353 | 1353 | 0.032214 | 526 | 0.012524 | 1541 | 0.03669 | 1.362 | A04 | MICL0.01919042/DON
Build-In Floor | Mini Canal | MICL.01919042/DOV | 19 | 190 | 42 | 42 | 1353 | 1353 | 1353 | 0.032214 | 526 | 0.012524 | 1541 | 0.03669 | 1.362 | A04 | MICL0.01919042/DOV
Build-In Floor | Mini Canal | MICL.01919042/PNC | 19 | 190 | 42 | 42 | 1237 | 1237 | 1237 | 0.029452 | 481 | 0.011452 | 1409 | 0.033548 | 1.362 | A04 | MICL0.01919042/PNC
Build-In Floor | Mini Canal | MICL.01919042/RBL | 19 | 190 | 42 | 42 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01919042/RBL
Build-In Floor | Mini Canal | MICL.01919042/RBN | 19 | 190 | 42 | 42 | 1411 | 1411 | 1411 | 0.033595 | 549 | 0.013071 | 1607 | 0.038262 | 1.362 | A04 | MICL0.01919042/RBN
Build-In Floor | Mini Canal | MICL.01919042/RBR | 19 | 190 | 42 | 42 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01919042/RBR
Build-In Floor | Mini Canal | MICL.01919042/RBV | 19 | 190 | 42 | 42 | 1411 | 1411 | 1411 | 0.033595 | 549 | 0.013071 | 1607 | 0.038262 | 1.362 | A04 | MICL0.01919042/RBV
Build-In Floor | Mini Canal | MICL.01919042/RDB | 19 | 190 | 42 | 42 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01919042/RDB
Build-In Floor | Mini Canal | MICL.01919042/RMN | 19 | 190 | 42 | 42 | 1411 | 1411 | 1411 | 0.033595 | 549 | 0.013071 | 1607 | 0.038262 | 1.362 | A04 | MICL0.01919042/RMN
Build-In Floor | Mini Canal | MICL.01919042/RMV | 19 | 190 | 42 | 42 | 1411 | 1411 | 1411 | 0.033595 | 549 | 0.013071 | 1607 | 0.038262 | 1.362 | A04 | MICL0.01919042/RMV
Build-In Floor | Mini Canal | MICL.01919042/RNA | 19 | 190 | 42 | 42 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01919042/RNA
Build-In Floor | Mini Canal | MICL.01919042/RON | 19 | 190 | 42 | 42 | 1411 | 1411 | 1411 | 0.033595 | 549 | 0.013071 | 1607 | 0.038262 | 1.362 | A04 | MICL0.01919042/RON
Build-In Floor | Mini Canal | MICL.01919042/ROV | 19 | 190 | 42 | 42 | 1411 | 1411 | 1411 | 0.033595 | 549 | 0.013071 | 1607 | 0.038262 | 1.362 | A04 | MICL0.01919042/ROV
Build-In Floor | Mini Canal | MICL.01919042/RSS | 19 | 190 | 42 | 42 | 1397 | 1397 | 1397 | 0.033262 | 543 | 0.012929 | 1591 | 0.037881 | 1.362 | A04 | MICL0.01919042/RSS
Build-In Floor | Mini Canal | MICL.01919042/SBL | 19 | 190 | 42 | 42 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01919042/SBL
Build-In Floor | Mini Canal | MICL.01919042/SBR | 19 | 190 | 42 | 42 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01919042/SBR
Build-In Floor | Mini Canal | MICL.01919042/SDB | 19 | 190 | 42 | 42 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01919042/SDB
Build-In Floor | Mini Canal | MICL.01919042/SNA | 19 | 190 | 42 | 42 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01919042/SNA
Build-In Floor | Mini Canal | MICL.01919042/SNC | 19 | 190 | 42 | 42 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01919042/SNC
Build-In Floor | Mini Canal | MICL.01921026/ANA | 19 | 210 | 26 | 26 | 661 | 661 | 661 | 0.015738 | 257 | 0.006119 | 753 | 0.017929 | 1.362 | A04 | MICL0.01921026/ANA
Build-In Floor | Mini Canal | MICL.01921026/DBL | 19 | 210 | 26 | 26 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01921026/DBL
Build-In Floor | Mini Canal | MICL.01921026/DBN | 19 | 210 | 26 | 26 | 819 | 819 | 819 | 0.0195 | 319 | 0.0075952 | 933 | 0.022214 | 1.362 | A04 | MICL0.01921026/DBN
Build-In Floor | Mini Canal | MICL.01921026/DBR | 19 | 210 | 26 | 26 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01921026/DBR
Build-In Floor | Mini Canal | MICL.01921026/DBV | 19 | 210 | 26 | 26 | 819 | 819 | 819 | 0.0195 | 319 | 0.0075952 | 933 | 0.022214 | 1.362 | A04 | MICL0.01921026/DBV
Build-In Floor | Mini Canal | MICL.01921026/DDB | 19 | 210 | 26 | 26 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01921026/DDB
Build-In Floor | Mini Canal | MICL.01921026/DMN | 19 | 210 | 26 | 26 | 819 | 819 | 819 | 0.0195 | 319 | 0.0075952 | 933 | 0.022214 | 1.362 | A04 | MICL0.01921026/DMN
Build-In Floor | Mini Canal | MICL.01921026/DMV | 19 | 210 | 26 | 26 | 819 | 819 | 819 | 0.0195 | 319 | 0.0075952 | 933 | 0.022214 | 1.362 | A04 | MICL0.01921026/DMV
Build-In Floor | Mini Canal | MICL.01921026/DNA | 19 | 210 | 26 | 26 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01921026/DNA
Build-In Floor | Mini Canal | MICL.01921026/DNC | 19 | 210 | 26 | 26 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01921026/DNC
Build-In Floor | Mini Canal | MICL.01921026/DON | 19 | 210 | 26 | 26 | 819 | 819 | 819 | 0.0195 | 319 | 0.0075952 | 933 | 0.022214 | 1.362 | A04 | MICL0.01921026/DON
Build-In Floor | Mini Canal | MICL.01921026/DOV | 19 | 210 | 26 | 26 | 819 | 819 | 819 | 0.0195 | 319 | 0.0075952 | 933 | 0.022214 | 1.362 | A04 | MICL0.01921026/DOV
Build-In Floor | Mini Canal | MICL.01921026/PNC | 19 | 210 | 26 | 26 | 749 | 749 | 749 | 0.017833 | 291 | 0.0069286 | 853 | 0.02031 | 1.362 | A04 | MICL0.01921026/PNC
Build-In Floor | Mini Canal | MICL.01921026/RBL | 19 | 210 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01921026/RBL
Build-In Floor | Mini Canal | MICL.01921026/RBN | 19 | 210 | 26 | 26 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01921026/RBN
Build-In Floor | Mini Canal | MICL.01921026/RBR | 19 | 210 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01921026/RBR
Build-In Floor | Mini Canal | MICL.01921026/RBV | 19 | 210 | 26 | 26 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01921026/RBV
Build-In Floor | Mini Canal | MICL.01921026/RDB | 19 | 210 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01921026/RDB
Build-In Floor | Mini Canal | MICL.01921026/RMN | 19 | 210 | 26 | 26 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01921026/RMN
Build-In Floor | Mini Canal | MICL.01921026/RMV | 19 | 210 | 26 | 26 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01921026/RMV
Build-In Floor | Mini Canal | MICL.01921026/RNA | 19 | 210 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01921026/RNA
Build-In Floor | Mini Canal | MICL.01921026/RON | 19 | 210 | 26 | 26 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01921026/RON
Build-In Floor | Mini Canal | MICL.01921026/ROV | 19 | 210 | 26 | 26 | 855 | 855 | 855 | 0.020357 | 333 | 0.0079286 | 974 | 0.02319 | 1.362 | A04 | MICL0.01921026/ROV
Build-In Floor | Mini Canal | MICL.01921026/RSS | 19 | 210 | 26 | 26 | 846 | 846 | 846 | 0.020143 | 329 | 0.0078333 | 964 | 0.022952 | 1.362 | A04 | MICL0.01921026/RSS
Build-In Floor | Mini Canal | MICL.01921026/SBL | 19 | 210 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01921026/SBL
Build-In Floor | Mini Canal | MICL.01921026/SBR | 19 | 210 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01921026/SBR
Build-In Floor | Mini Canal | MICL.01921026/SDB | 19 | 210 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01921026/SDB
Build-In Floor | Mini Canal | MICL.01921026/SNA | 19 | 210 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01921026/SNA
Build-In Floor | Mini Canal | MICL.01921026/SNC | 19 | 210 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01921026/SNC
Build-In Floor | Mini Canal | MICL.01921034/ANA | 19 | 210 | 34 | 34 | 894 | 894 | 894 | 0.021286 | 348 | 0.0082857 | 1018 | 0.024238 | 1.362 | A04 | MICL0.01921034/ANA
Build-In Floor | Mini Canal | MICL.01921034/DBL | 19 | 210 | 34 | 34 | 1156 | 1156 | 1156 | 0.027524 | 450 | 0.010714 | 1317 | 0.031357 | 1.362 | A04 | MICL0.01921034/DBL
Build-In Floor | Mini Canal | MICL.01921034/DBN | 19 | 210 | 34 | 34 | 1109 | 1109 | 1109 | 0.026405 | 431 | 0.010262 | 1263 | 0.030071 | 1.362 | A04 | MICL0.01921034/DBN
Build-In Floor | Mini Canal | MICL.01921034/DBR | 19 | 210 | 34 | 34 | 1156 | 1156 | 1156 | 0.027524 | 450 | 0.010714 | 1317 | 0.031357 | 1.362 | A04 | MICL0.01921034/DBR
Build-In Floor | Mini Canal | MICL.01921034/DBV | 19 | 210 | 34 | 34 | 1109 | 1109 | 1109 | 0.026405 | 431 | 0.010262 | 1263 | 0.030071 | 1.362 | A04 | MICL0.01921034/DBV
Build-In Floor | Mini Canal | MICL.01921034/DDB | 19 | 210 | 34 | 34 | 1156 | 1156 | 1156 | 0.027524 | 450 | 0.010714 | 1317 | 0.031357 | 1.362 | A04 | MICL0.01921034/DDB
Build-In Floor | Mini Canal | MICL.01921034/DMN | 19 | 210 | 34 | 34 | 1109 | 1109 | 1109 | 0.026405 | 431 | 0.010262 | 1263 | 0.030071 | 1.362 | A04 | MICL0.01921034/DMN
Build-In Floor | Mini Canal | MICL.01921034/DMV | 19 | 210 | 34 | 34 | 1109 | 1109 | 1109 | 0.026405 | 431 | 0.010262 | 1263 | 0.030071 | 1.362 | A04 | MICL0.01921034/DMV
Build-In Floor | Mini Canal | MICL.01921034/DNA | 19 | 210 | 34 | 34 | 1156 | 1156 | 1156 | 0.027524 | 450 | 0.010714 | 1317 | 0.031357 | 1.362 | A04 | MICL0.01921034/DNA
Build-In Floor | Mini Canal | MICL.01921034/DNC | 19 | 210 | 34 | 34 | 1156 | 1156 | 1156 | 0.027524 | 450 | 0.010714 | 1317 | 0.031357 | 1.362 | A04 | MICL0.01921034/DNC
Build-In Floor | Mini Canal | MICL.01921034/DON | 19 | 210 | 34 | 34 | 1109 | 1109 | 1109 | 0.026405 | 431 | 0.010262 | 1263 | 0.030071 | 1.362 | A04 | MICL0.01921034/DON
Build-In Floor | Mini Canal | MICL.01921034/DOV | 19 | 210 | 34 | 34 | 1109 | 1109 | 1109 | 0.026405 | 431 | 0.010262 | 1263 | 0.030071 | 1.362 | A04 | MICL0.01921034/DOV
Build-In Floor | Mini Canal | MICL.01921034/PNC | 19 | 210 | 34 | 34 | 1013 | 1013 | 1013 | 0.024119 | 394 | 0.009381 | 1154 | 0.027476 | 1.362 | A04 | MICL0.01921034/PNC
Build-In Floor | Mini Canal | MICL.01921034/RBL | 19 | 210 | 34 | 34 | 1192 | 1192 | 1192 | 0.028381 | 464 | 0.011048 | 1358 | 0.032333 | 1.362 | A04 | MICL0.01921034/RBL
Build-In Floor | Mini Canal | MICL.01921034/RBN | 19 | 210 | 34 | 34 | 1156 | 1156 | 1156 | 0.027524 | 450 | 0.010714 | 1317 | 0.031357 | 1.362 | A04 | MICL0.01921034/RBN
Build-In Floor | Mini Canal | MICL.01921034/RBR | 19 | 210 | 34 | 34 | 1192 | 1192 | 1192 | 0.028381 | 464 | 0.011048 | 1358 | 0.032333 | 1.362 | A04 | MICL0.01921034/RBR
Build-In Floor | Mini Canal | MICL.01921034/RBV | 19 | 210 | 34 | 34 | 1156 | 1156 | 1156 | 0.027524 | 450 | 0.010714 | 1317 | 0.031357 | 1.362 | A04 | MICL0.01921034/RBV
Build-In Floor | Mini Canal | MICL.01921034/RDB | 19 | 210 | 34 | 34 | 1192 | 1192 | 1192 | 0.028381 | 464 | 0.011048 | 1358 | 0.032333 | 1.362 | A04 | MICL0.01921034/RDB
Build-In Floor | Mini Canal | MICL.01921034/RMN | 19 | 210 | 34 | 34 | 1156 | 1156 | 1156 | 0.027524 | 450 | 0.010714 | 1317 | 0.031357 | 1.362 | A04 | MICL0.01921034/RMN
Build-In Floor | Mini Canal | MICL.01921034/RMV | 19 | 210 | 34 | 34 | 1156 | 1156 | 1156 | 0.027524 | 450 | 0.010714 | 1317 | 0.031357 | 1.362 | A04 | MICL0.01921034/RMV
Build-In Floor | Mini Canal | MICL.01921034/RNA | 19 | 210 | 34 | 34 | 1192 | 1192 | 1192 | 0.028381 | 464 | 0.011048 | 1358 | 0.032333 | 1.362 | A04 | MICL0.01921034/RNA
Build-In Floor | Mini Canal | MICL.01921034/RON | 19 | 210 | 34 | 34 | 1156 | 1156 | 1156 | 0.027524 | 450 | 0.010714 | 1317 | 0.031357 | 1.362 | A04 | MICL0.01921034/RON
Build-In Floor | Mini Canal | MICL.01921034/ROV | 19 | 210 | 34 | 34 | 1156 | 1156 | 1156 | 0.027524 | 450 | 0.010714 | 1317 | 0.031357 | 1.362 | A04 | MICL0.01921034/ROV
Build-In Floor | Mini Canal | MICL.01921034/RSS | 19 | 210 | 34 | 34 | 1144 | 1144 | 1144 | 0.027238 | 445 | 0.010595 | 1303 | 0.031024 | 1.362 | A04 | MICL0.01921034/RSS
Build-In Floor | Mini Canal | MICL.01921034/SBL | 19 | 210 | 34 | 34 | 1192 | 1192 | 1192 | 0.028381 | 464 | 0.011048 | 1358 | 0.032333 | 1.362 | A04 | MICL0.01921034/SBL
Build-In Floor | Mini Canal | MICL.01921034/SBR | 19 | 210 | 34 | 34 | 1192 | 1192 | 1192 | 0.028381 | 464 | 0.011048 | 1358 | 0.032333 | 1.362 | A04 | MICL0.01921034/SBR
Build-In Floor | Mini Canal | MICL.01921034/SDB | 19 | 210 | 34 | 34 | 1192 | 1192 | 1192 | 0.028381 | 464 | 0.011048 | 1358 | 0.032333 | 1.362 | A04 | MICL0.01921034/SDB
Build-In Floor | Mini Canal | MICL.01921034/SNA | 19 | 210 | 34 | 34 | 1192 | 1192 | 1192 | 0.028381 | 464 | 0.011048 | 1358 | 0.032333 | 1.362 | A04 | MICL0.01921034/SNA
Build-In Floor | Mini Canal | MICL.01921034/SNC | 19 | 210 | 34 | 34 | 1192 | 1192 | 1192 | 0.028381 | 464 | 0.011048 | 1358 | 0.032333 | 1.362 | A04 | MICL0.01921034/SNC
Build-In Floor | Mini Canal | MICL.01921042/ANA | 19 | 210 | 42 | 42 | 1228 | 1228 | 1228 | 0.029238 | 478 | 0.011381 | 1399 | 0.03331 | 1.362 | A04 | MICL0.01921042/ANA
Build-In Floor | Mini Canal | MICL.01921042/DBL | 19 | 210 | 42 | 42 | 1588 | 1588 | 1588 | 0.03781 | 618 | 0.014714 | 1809 | 0.043071 | 1.362 | A04 | MICL0.01921042/DBL
Build-In Floor | Mini Canal | MICL.01921042/DBN | 19 | 210 | 42 | 42 | 1522 | 1522 | 1522 | 0.036238 | 592 | 0.014095 | 1734 | 0.041286 | 1.362 | A04 | MICL0.01921042/DBN
Build-In Floor | Mini Canal | MICL.01921042/DBR | 19 | 210 | 42 | 42 | 1588 | 1588 | 1588 | 0.03781 | 618 | 0.014714 | 1809 | 0.043071 | 1.362 | A04 | MICL0.01921042/DBR
Build-In Floor | Mini Canal | MICL.01921042/DBV | 19 | 210 | 42 | 42 | 1522 | 1522 | 1522 | 0.036238 | 592 | 0.014095 | 1734 | 0.041286 | 1.362 | A04 | MICL0.01921042/DBV
Build-In Floor | Mini Canal | MICL.01921042/DDB | 19 | 210 | 42 | 42 | 1588 | 1588 | 1588 | 0.03781 | 618 | 0.014714 | 1809 | 0.043071 | 1.362 | A04 | MICL0.01921042/DDB
Build-In Floor | Mini Canal | MICL.01921042/DMN | 19 | 210 | 42 | 42 | 1522 | 1522 | 1522 | 0.036238 | 592 | 0.014095 | 1734 | 0.041286 | 1.362 | A04 | MICL0.01921042/DMN
Build-In Floor | Mini Canal | MICL.01921042/DMV | 19 | 210 | 42 | 42 | 1522 | 1522 | 1522 | 0.036238 | 592 | 0.014095 | 1734 | 0.041286 | 1.362 | A04 | MICL0.01921042/DMV
Build-In Floor | Mini Canal | MICL.01921042/DNA | 19 | 210 | 42 | 42 | 1588 | 1588 | 1588 | 0.03781 | 618 | 0.014714 | 1809 | 0.043071 | 1.362 | A04 | MICL0.01921042/DNA
Build-In Floor | Mini Canal | MICL.01921042/DNC | 19 | 210 | 42 | 42 | 1588 | 1588 | 1588 | 0.03781 | 618 | 0.014714 | 1809 | 0.043071 | 1.362 | A04 | MICL0.01921042/DNC
Build-In Floor | Mini Canal | MICL.01921042/DON | 19 | 210 | 42 | 42 | 1522 | 1522 | 1522 | 0.036238 | 592 | 0.014095 | 1734 | 0.041286 | 1.362 | A04 | MICL0.01921042/DON
Build-In Floor | Mini Canal | MICL.01921042/DOV | 19 | 210 | 42 | 42 | 1522 | 1522 | 1522 | 0.036238 | 592 | 0.014095 | 1734 | 0.041286 | 1.362 | A04 | MICL0.01921042/DOV
Build-In Floor | Mini Canal | MICL.01921042/PNC | 19 | 210 | 42 | 42 | 1391 | 1391 | 1391 | 0.033119 | 541 | 0.012881 | 1584 | 0.037714 | 1.362 | A04 | MICL0.01921042/PNC
Build-In Floor | Mini Canal | MICL.01921042/RBL | 19 | 210 | 42 | 42 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01921042/RBL
Build-In Floor | Mini Canal | MICL.01921042/RBN | 19 | 210 | 42 | 42 | 1588 | 1588 | 1588 | 0.03781 | 618 | 0.014714 | 1809 | 0.043071 | 1.362 | A04 | MICL0.01921042/RBN
Build-In Floor | Mini Canal | MICL.01921042/RBR | 19 | 210 | 42 | 42 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01921042/RBR
Build-In Floor | Mini Canal | MICL.01921042/RBV | 19 | 210 | 42 | 42 | 1588 | 1588 | 1588 | 0.03781 | 618 | 0.014714 | 1809 | 0.043071 | 1.362 | A04 | MICL0.01921042/RBV
Build-In Floor | Mini Canal | MICL.01921042/RDB | 19 | 210 | 42 | 42 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01921042/RDB
Build-In Floor | Mini Canal | MICL.01921042/RMN | 19 | 210 | 42 | 42 | 1588 | 1588 | 1588 | 0.03781 | 618 | 0.014714 | 1809 | 0.043071 | 1.362 | A04 | MICL0.01921042/RMN
Build-In Floor | Mini Canal | MICL.01921042/RMV | 19 | 210 | 42 | 42 | 1588 | 1588 | 1588 | 0.03781 | 618 | 0.014714 | 1809 | 0.043071 | 1.362 | A04 | MICL0.01921042/RMV
Build-In Floor | Mini Canal | MICL.01921042/RNA | 19 | 210 | 42 | 42 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01921042/RNA
Build-In Floor | Mini Canal | MICL.01921042/RON | 19 | 210 | 42 | 42 | 1588 | 1588 | 1588 | 0.03781 | 618 | 0.014714 | 1809 | 0.043071 | 1.362 | A04 | MICL0.01921042/RON
Build-In Floor | Mini Canal | MICL.01921042/ROV | 19 | 210 | 42 | 42 | 1588 | 1588 | 1588 | 0.03781 | 618 | 0.014714 | 1809 | 0.043071 | 1.362 | A04 | MICL0.01921042/ROV
Build-In Floor | Mini Canal | MICL.01921042/RSS | 19 | 210 | 42 | 42 | 1572 | 1572 | 1572 | 0.037429 | 612 | 0.014571 | 1791 | 0.042643 | 1.362 | A04 | MICL0.01921042/RSS
Build-In Floor | Mini Canal | MICL.01921042/SBL | 19 | 210 | 42 | 42 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01921042/SBL
Build-In Floor | Mini Canal | MICL.01921042/SBR | 19 | 210 | 42 | 42 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01921042/SBR
Build-In Floor | Mini Canal | MICL.01921042/SDB | 19 | 210 | 42 | 42 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01921042/SDB
Build-In Floor | Mini Canal | MICL.01921042/SNA | 19 | 210 | 42 | 42 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01921042/SNA
Build-In Floor | Mini Canal | MICL.01921042/SNC | 19 | 210 | 42 | 42 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01921042/SNC
Build-In Floor | Mini Canal | MICL.01923026/ANA | 19 | 230 | 26 | 26 | 734 | 734 | 734 | 0.017476 | 286 | 0.0068095 | 836 | 0.019905 | 1.362 | A04 | MICL0.01923026/ANA
Build-In Floor | Mini Canal | MICL.01923026/DBL | 19 | 230 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01923026/DBL
Build-In Floor | Mini Canal | MICL.01923026/DBN | 19 | 230 | 26 | 26 | 910 | 910 | 910 | 0.021667 | 354 | 0.0084286 | 1036 | 0.024667 | 1.362 | A04 | MICL0.01923026/DBN
Build-In Floor | Mini Canal | MICL.01923026/DBR | 19 | 230 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01923026/DBR
Build-In Floor | Mini Canal | MICL.01923026/DBV | 19 | 230 | 26 | 26 | 910 | 910 | 910 | 0.021667 | 354 | 0.0084286 | 1036 | 0.024667 | 1.362 | A04 | MICL0.01923026/DBV
Build-In Floor | Mini Canal | MICL.01923026/DDB | 19 | 230 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01923026/DDB
Build-In Floor | Mini Canal | MICL.01923026/DMN | 19 | 230 | 26 | 26 | 910 | 910 | 910 | 0.021667 | 354 | 0.0084286 | 1036 | 0.024667 | 1.362 | A04 | MICL0.01923026/DMN
Build-In Floor | Mini Canal | MICL.01923026/DMV | 19 | 230 | 26 | 26 | 910 | 910 | 910 | 0.021667 | 354 | 0.0084286 | 1036 | 0.024667 | 1.362 | A04 | MICL0.01923026/DMV
Build-In Floor | Mini Canal | MICL.01923026/DNA | 19 | 230 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01923026/DNA
Build-In Floor | Mini Canal | MICL.01923026/DNC | 19 | 230 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01923026/DNC
Build-In Floor | Mini Canal | MICL.01923026/DON | 19 | 230 | 26 | 26 | 910 | 910 | 910 | 0.021667 | 354 | 0.0084286 | 1036 | 0.024667 | 1.362 | A04 | MICL0.01923026/DON
Build-In Floor | Mini Canal | MICL.01923026/DOV | 19 | 230 | 26 | 26 | 910 | 910 | 910 | 0.021667 | 354 | 0.0084286 | 1036 | 0.024667 | 1.362 | A04 | MICL0.01923026/DOV
Build-In Floor | Mini Canal | MICL.01923026/PNC | 19 | 230 | 26 | 26 | 831 | 831 | 831 | 0.019786 | 323 | 0.0076905 | 947 | 0.022548 | 1.362 | A04 | MICL0.01923026/PNC
Build-In Floor | Mini Canal | MICL.01923026/RBL | 19 | 230 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01923026/RBL
Build-In Floor | Mini Canal | MICL.01923026/RBN | 19 | 230 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01923026/RBN
Build-In Floor | Mini Canal | MICL.01923026/RBR | 19 | 230 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01923026/RBR
Build-In Floor | Mini Canal | MICL.01923026/RBV | 19 | 230 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01923026/RBV
Build-In Floor | Mini Canal | MICL.01923026/RDB | 19 | 230 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01923026/RDB
Build-In Floor | Mini Canal | MICL.01923026/RMN | 19 | 230 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01923026/RMN
Build-In Floor | Mini Canal | MICL.01923026/RMV | 19 | 230 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01923026/RMV
Build-In Floor | Mini Canal | MICL.01923026/RNA | 19 | 230 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01923026/RNA
Build-In Floor | Mini Canal | MICL.01923026/RON | 19 | 230 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01923026/RON
Build-In Floor | Mini Canal | MICL.01923026/ROV | 19 | 230 | 26 | 26 | 949 | 949 | 949 | 0.022595 | 369 | 0.0087857 | 1081 | 0.025738 | 1.362 | A04 | MICL0.01923026/ROV
Build-In Floor | Mini Canal | MICL.01923026/RSS | 19 | 230 | 26 | 26 | 939 | 939 | 939 | 0.022357 | 365 | 0.0086905 | 1070 | 0.025476 | 1.362 | A04 | MICL0.01923026/RSS
Build-In Floor | Mini Canal | MICL.01923026/SBL | 19 | 230 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01923026/SBL
Build-In Floor | Mini Canal | MICL.01923026/SBR | 19 | 230 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01923026/SBR
Build-In Floor | Mini Canal | MICL.01923026/SDB | 19 | 230 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01923026/SDB
Build-In Floor | Mini Canal | MICL.01923026/SNA | 19 | 230 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01923026/SNA
Build-In Floor | Mini Canal | MICL.01923026/SNC | 19 | 230 | 26 | 26 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | A04 | MICL0.01923026/SNC
Build-In Floor | Mini Canal | MICL.01923034/ANA | 19 | 230 | 34 | 34 | 993 | 993 | 993 | 0.023643 | 386 | 0.0091905 | 1131 | 0.026929 | 1.362 | A04 | MICL0.01923034/ANA
Build-In Floor | Mini Canal | MICL.01923034/DBL | 19 | 230 | 34 | 34 | 1284 | 1284 | 1284 | 0.030571 | 499 | 0.011881 | 1462 | 0.03481 | 1.362 | A04 | MICL0.01923034/DBL
Build-In Floor | Mini Canal | MICL.01923034/DBN | 19 | 230 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.01923034/DBN
Build-In Floor | Mini Canal | MICL.01923034/DBR | 19 | 230 | 34 | 34 | 1284 | 1284 | 1284 | 0.030571 | 499 | 0.011881 | 1462 | 0.03481 | 1.362 | A04 | MICL0.01923034/DBR
Build-In Floor | Mini Canal | MICL.01923034/DBV | 19 | 230 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.01923034/DBV
Build-In Floor | Mini Canal | MICL.01923034/DDB | 19 | 230 | 34 | 34 | 1284 | 1284 | 1284 | 0.030571 | 499 | 0.011881 | 1462 | 0.03481 | 1.362 | A04 | MICL0.01923034/DDB
Build-In Floor | Mini Canal | MICL.01923034/DMN | 19 | 230 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.01923034/DMN
Build-In Floor | Mini Canal | MICL.01923034/DMV | 19 | 230 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.01923034/DMV
Build-In Floor | Mini Canal | MICL.01923034/DNA | 19 | 230 | 34 | 34 | 1284 | 1284 | 1284 | 0.030571 | 499 | 0.011881 | 1462 | 0.03481 | 1.362 | A04 | MICL0.01923034/DNA
Build-In Floor | Mini Canal | MICL.01923034/DNC | 19 | 230 | 34 | 34 | 1284 | 1284 | 1284 | 0.030571 | 499 | 0.011881 | 1462 | 0.03481 | 1.362 | A04 | MICL0.01923034/DNC
Build-In Floor | Mini Canal | MICL.01923034/DON | 19 | 230 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.01923034/DON
Build-In Floor | Mini Canal | MICL.01923034/DOV | 19 | 230 | 34 | 34 | 1231 | 1231 | 1231 | 0.02931 | 479 | 0.011405 | 1402 | 0.033381 | 1.362 | A04 | MICL0.01923034/DOV
Build-In Floor | Mini Canal | MICL.01923034/PNC | 19 | 230 | 34 | 34 | 1125 | 1125 | 1125 | 0.026786 | 438 | 0.010429 | 1281 | 0.0305 | 1.362 | A04 | MICL0.01923034/PNC
Build-In Floor | Mini Canal | MICL.01923034/RBL | 19 | 230 | 34 | 34 | 1324 | 1324 | 1324 | 0.031524 | 515 | 0.012262 | 1508 | 0.035905 | 1.362 | A04 | MICL0.01923034/RBL
Build-In Floor | Mini Canal | MICL.01923034/RBN | 19 | 230 | 34 | 34 | 1284 | 1284 | 1284 | 0.030571 | 499 | 0.011881 | 1462 | 0.03481 | 1.362 | A04 | MICL0.01923034/RBN
Build-In Floor | Mini Canal | MICL.01923034/RBR | 19 | 230 | 34 | 34 | 1324 | 1324 | 1324 | 0.031524 | 515 | 0.012262 | 1508 | 0.035905 | 1.362 | A04 | MICL0.01923034/RBR
Build-In Floor | Mini Canal | MICL.01923034/RBV | 19 | 230 | 34 | 34 | 1284 | 1284 | 1284 | 0.030571 | 499 | 0.011881 | 1462 | 0.03481 | 1.362 | A04 | MICL0.01923034/RBV
Build-In Floor | Mini Canal | MICL.01923034/RDB | 19 | 230 | 34 | 34 | 1324 | 1324 | 1324 | 0.031524 | 515 | 0.012262 | 1508 | 0.035905 | 1.362 | A04 | MICL0.01923034/RDB
Build-In Floor | Mini Canal | MICL.01923034/RMN | 19 | 230 | 34 | 34 | 1284 | 1284 | 1284 | 0.030571 | 499 | 0.011881 | 1462 | 0.03481 | 1.362 | A04 | MICL0.01923034/RMN
Build-In Floor | Mini Canal | MICL.01923034/RMV | 19 | 230 | 34 | 34 | 1284 | 1284 | 1284 | 0.030571 | 499 | 0.011881 | 1462 | 0.03481 | 1.362 | A04 | MICL0.01923034/RMV
Build-In Floor | Mini Canal | MICL.01923034/RNA | 19 | 230 | 34 | 34 | 1324 | 1324 | 1324 | 0.031524 | 515 | 0.012262 | 1508 | 0.035905 | 1.362 | A04 | MICL0.01923034/RNA
Build-In Floor | Mini Canal | MICL.01923034/RON | 19 | 230 | 34 | 34 | 1284 | 1284 | 1284 | 0.030571 | 499 | 0.011881 | 1462 | 0.03481 | 1.362 | A04 | MICL0.01923034/RON
Build-In Floor | Mini Canal | MICL.01923034/ROV | 19 | 230 | 34 | 34 | 1284 | 1284 | 1284 | 0.030571 | 499 | 0.011881 | 1462 | 0.03481 | 1.362 | A04 | MICL0.01923034/ROV
Build-In Floor | Mini Canal | MICL.01923034/RSS | 19 | 230 | 34 | 34 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01923034/RSS
Build-In Floor | Mini Canal | MICL.01923034/SBL | 19 | 230 | 34 | 34 | 1324 | 1324 | 1324 | 0.031524 | 515 | 0.012262 | 1508 | 0.035905 | 1.362 | A04 | MICL0.01923034/SBL
Build-In Floor | Mini Canal | MICL.01923034/SBR | 19 | 230 | 34 | 34 | 1324 | 1324 | 1324 | 0.031524 | 515 | 0.012262 | 1508 | 0.035905 | 1.362 | A04 | MICL0.01923034/SBR
Build-In Floor | Mini Canal | MICL.01923034/SDB | 19 | 230 | 34 | 34 | 1324 | 1324 | 1324 | 0.031524 | 515 | 0.012262 | 1508 | 0.035905 | 1.362 | A04 | MICL0.01923034/SDB
Build-In Floor | Mini Canal | MICL.01923034/SNA | 19 | 230 | 34 | 34 | 1324 | 1324 | 1324 | 0.031524 | 515 | 0.012262 | 1508 | 0.035905 | 1.362 | A04 | MICL0.01923034/SNA
Build-In Floor | Mini Canal | MICL.01923034/SNC | 19 | 230 | 34 | 34 | 1324 | 1324 | 1324 | 0.031524 | 515 | 0.012262 | 1508 | 0.035905 | 1.362 | A04 | MICL0.01923034/SNC
Build-In Floor | Mini Canal | MICL.01923042/ANA | 19 | 230 | 42 | 42 | 1364 | 1364 | 1364 | 0.032476 | 531 | 0.012643 | 1554 | 0.037 | 1.362 | A04 | MICL0.01923042/ANA
Build-In Floor | Mini Canal | MICL.01923042/DBL | 19 | 230 | 42 | 42 | 1764 | 1764 | 1764 | 0.042 | 686 | 0.016333 | 2009 | 0.047833 | 1.362 | A04 | MICL0.01923042/DBL
Build-In Floor | Mini Canal | MICL.01923042/DBN | 19 | 230 | 42 | 42 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.01923042/DBN
Build-In Floor | Mini Canal | MICL.01923042/DBR | 19 | 230 | 42 | 42 | 1764 | 1764 | 1764 | 0.042 | 686 | 0.016333 | 2009 | 0.047833 | 1.362 | A04 | MICL0.01923042/DBR
Build-In Floor | Mini Canal | MICL.01923042/DBV | 19 | 230 | 42 | 42 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.01923042/DBV
Build-In Floor | Mini Canal | MICL.01923042/DDB | 19 | 230 | 42 | 42 | 1764 | 1764 | 1764 | 0.042 | 686 | 0.016333 | 2009 | 0.047833 | 1.362 | A04 | MICL0.01923042/DDB
Build-In Floor | Mini Canal | MICL.01923042/DMN | 19 | 230 | 42 | 42 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.01923042/DMN
Build-In Floor | Mini Canal | MICL.01923042/DMV | 19 | 230 | 42 | 42 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.01923042/DMV
Build-In Floor | Mini Canal | MICL.01923042/DNA | 19 | 230 | 42 | 42 | 1764 | 1764 | 1764 | 0.042 | 686 | 0.016333 | 2009 | 0.047833 | 1.362 | A04 | MICL0.01923042/DNA
Build-In Floor | Mini Canal | MICL.01923042/DNC | 19 | 230 | 42 | 42 | 1764 | 1764 | 1764 | 0.042 | 686 | 0.016333 | 2009 | 0.047833 | 1.362 | A04 | MICL0.01923042/DNC
Build-In Floor | Mini Canal | MICL.01923042/DON | 19 | 230 | 42 | 42 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.01923042/DON
Build-In Floor | Mini Canal | MICL.01923042/DOV | 19 | 230 | 42 | 42 | 1692 | 1692 | 1692 | 0.040286 | 658 | 0.015667 | 1927 | 0.045881 | 1.362 | A04 | MICL0.01923042/DOV
Build-In Floor | Mini Canal | MICL.01923042/PNC | 19 | 230 | 42 | 42 | 1546 | 1546 | 1546 | 0.03681 | 601 | 0.01431 | 1761 | 0.041929 | 1.362 | A04 | MICL0.01923042/PNC
Build-In Floor | Mini Canal | MICL.01923042/RBL | 19 | 230 | 42 | 42 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01923042/RBL
Build-In Floor | Mini Canal | MICL.01923042/RBN | 19 | 230 | 42 | 42 | 1764 | 1764 | 1764 | 0.042 | 686 | 0.016333 | 2009 | 0.047833 | 1.362 | A04 | MICL0.01923042/RBN
Build-In Floor | Mini Canal | MICL.01923042/RBR | 19 | 230 | 42 | 42 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01923042/RBR
Build-In Floor | Mini Canal | MICL.01923042/RBV | 19 | 230 | 42 | 42 | 1764 | 1764 | 1764 | 0.042 | 686 | 0.016333 | 2009 | 0.047833 | 1.362 | A04 | MICL0.01923042/RBV
Build-In Floor | Mini Canal | MICL.01923042/RDB | 19 | 230 | 42 | 42 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01923042/RDB
Build-In Floor | Mini Canal | MICL.01923042/RMN | 19 | 230 | 42 | 42 | 1764 | 1764 | 1764 | 0.042 | 686 | 0.016333 | 2009 | 0.047833 | 1.362 | A04 | MICL0.01923042/RMN
Build-In Floor | Mini Canal | MICL.01923042/RMV | 19 | 230 | 42 | 42 | 1764 | 1764 | 1764 | 0.042 | 686 | 0.016333 | 2009 | 0.047833 | 1.362 | A04 | MICL0.01923042/RMV
Build-In Floor | Mini Canal | MICL.01923042/RNA | 19 | 230 | 42 | 42 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01923042/RNA
Build-In Floor | Mini Canal | MICL.01923042/RON | 19 | 230 | 42 | 42 | 1764 | 1764 | 1764 | 0.042 | 686 | 0.016333 | 2009 | 0.047833 | 1.362 | A04 | MICL0.01923042/RON
Build-In Floor | Mini Canal | MICL.01923042/ROV | 19 | 230 | 42 | 42 | 1764 | 1764 | 1764 | 0.042 | 686 | 0.016333 | 2009 | 0.047833 | 1.362 | A04 | MICL0.01923042/ROV
Build-In Floor | Mini Canal | MICL.01923042/RSS | 19 | 230 | 42 | 42 | 1746 | 1746 | 1746 | 0.041571 | 679 | 0.016167 | 1989 | 0.047357 | 1.362 | A04 | MICL0.01923042/RSS
Build-In Floor | Mini Canal | MICL.01923042/SBL | 19 | 230 | 42 | 42 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01923042/SBL
Build-In Floor | Mini Canal | MICL.01923042/SBR | 19 | 230 | 42 | 42 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01923042/SBR
Build-In Floor | Mini Canal | MICL.01923042/SDB | 19 | 230 | 42 | 42 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01923042/SDB
Build-In Floor | Mini Canal | MICL.01923042/SNA | 19 | 230 | 42 | 42 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01923042/SNA
Build-In Floor | Mini Canal | MICL.01923042/SNC | 19 | 230 | 42 | 42 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01923042/SNC
Build-In Floor | Mini Canal | MICL.01925026/ANA | 19 | 250 | 26 | 26 | 807 | 807 | 807 | 0.019214 | 314 | 0.0074762 | 919 | 0.021881 | 1.362 | A04 | MICL0.01925026/ANA
Build-In Floor | Mini Canal | MICL.01925026/DBL | 19 | 250 | 26 | 26 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.01925026/DBL
Build-In Floor | Mini Canal | MICL.01925026/DBN | 19 | 250 | 26 | 26 | 1001 | 1001 | 1001 | 0.023833 | 389 | 0.0092619 | 1140 | 0.027143 | 1.362 | A04 | MICL0.01925026/DBN
Build-In Floor | Mini Canal | MICL.01925026/DBR | 19 | 250 | 26 | 26 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.01925026/DBR
Build-In Floor | Mini Canal | MICL.01925026/DBV | 19 | 250 | 26 | 26 | 1001 | 1001 | 1001 | 0.023833 | 389 | 0.0092619 | 1140 | 0.027143 | 1.362 | A04 | MICL0.01925026/DBV
Build-In Floor | Mini Canal | MICL.01925026/DDB | 19 | 250 | 26 | 26 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.01925026/DDB
Build-In Floor | Mini Canal | MICL.01925026/DMN | 19 | 250 | 26 | 26 | 1001 | 1001 | 1001 | 0.023833 | 389 | 0.0092619 | 1140 | 0.027143 | 1.362 | A04 | MICL0.01925026/DMN
Build-In Floor | Mini Canal | MICL.01925026/DMV | 19 | 250 | 26 | 26 | 1001 | 1001 | 1001 | 0.023833 | 389 | 0.0092619 | 1140 | 0.027143 | 1.362 | A04 | MICL0.01925026/DMV
Build-In Floor | Mini Canal | MICL.01925026/DNA | 19 | 250 | 26 | 26 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.01925026/DNA
Build-In Floor | Mini Canal | MICL.01925026/DNC | 19 | 250 | 26 | 26 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.01925026/DNC
Build-In Floor | Mini Canal | MICL.01925026/DON | 19 | 250 | 26 | 26 | 1001 | 1001 | 1001 | 0.023833 | 389 | 0.0092619 | 1140 | 0.027143 | 1.362 | A04 | MICL0.01925026/DON
Build-In Floor | Mini Canal | MICL.01925026/DOV | 19 | 250 | 26 | 26 | 1001 | 1001 | 1001 | 0.023833 | 389 | 0.0092619 | 1140 | 0.027143 | 1.362 | A04 | MICL0.01925026/DOV
Build-In Floor | Mini Canal | MICL.01925026/PNC | 19 | 250 | 26 | 26 | 915 | 915 | 915 | 0.021786 | 356 | 0.0084762 | 1042 | 0.02481 | 1.362 | A04 | MICL0.01925026/PNC
Build-In Floor | Mini Canal | MICL.01925026/RBL | 19 | 250 | 26 | 26 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.01925026/RBL
Build-In Floor | Mini Canal | MICL.01925026/RBN | 19 | 250 | 26 | 26 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.01925026/RBN
Build-In Floor | Mini Canal | MICL.01925026/RBR | 19 | 250 | 26 | 26 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.01925026/RBR
Build-In Floor | Mini Canal | MICL.01925026/RBV | 19 | 250 | 26 | 26 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.01925026/RBV
Build-In Floor | Mini Canal | MICL.01925026/RDB | 19 | 250 | 26 | 26 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.01925026/RDB
Build-In Floor | Mini Canal | MICL.01925026/RMN | 19 | 250 | 26 | 26 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.01925026/RMN
Build-In Floor | Mini Canal | MICL.01925026/RMV | 19 | 250 | 26 | 26 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.01925026/RMV
Build-In Floor | Mini Canal | MICL.01925026/RNA | 19 | 250 | 26 | 26 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.01925026/RNA
Build-In Floor | Mini Canal | MICL.01925026/RON | 19 | 250 | 26 | 26 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.01925026/RON
Build-In Floor | Mini Canal | MICL.01925026/ROV | 19 | 250 | 26 | 26 | 1044 | 1044 | 1044 | 0.024857 | 406 | 0.0096667 | 1189 | 0.02831 | 1.362 | A04 | MICL0.01925026/ROV
Build-In Floor | Mini Canal | MICL.01925026/RSS | 19 | 250 | 26 | 26 | 1033 | 1033 | 1033 | 0.024595 | 402 | 0.0095714 | 1177 | 0.028024 | 1.362 | A04 | MICL0.01925026/RSS
Build-In Floor | Mini Canal | MICL.01925026/SBL | 19 | 250 | 26 | 26 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.01925026/SBL
Build-In Floor | Mini Canal | MICL.01925026/SBR | 19 | 250 | 26 | 26 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.01925026/SBR
Build-In Floor | Mini Canal | MICL.01925026/SDB | 19 | 250 | 26 | 26 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.01925026/SDB
Build-In Floor | Mini Canal | MICL.01925026/SNA | 19 | 250 | 26 | 26 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.01925026/SNA
Build-In Floor | Mini Canal | MICL.01925026/SNC | 19 | 250 | 26 | 26 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | A04 | MICL0.01925026/SNC
Build-In Floor | Mini Canal | MICL.01925034/ANA | 19 | 250 | 34 | 34 | 1093 | 1093 | 1093 | 0.026024 | 425 | 0.010119 | 1245 | 0.029643 | 1.362 | A04 | MICL0.01925034/ANA
Build-In Floor | Mini Canal | MICL.01925034/DBL | 19 | 250 | 34 | 34 | 1413 | 1413 | 1413 | 0.033643 | 550 | 0.013095 | 1609 | 0.03831 | 1.362 | A04 | MICL0.01925034/DBL
Build-In Floor | Mini Canal | MICL.01925034/DBN | 19 | 250 | 34 | 34 | 1355 | 1355 | 1355 | 0.032262 | 527 | 0.012548 | 1543 | 0.036738 | 1.362 | A04 | MICL0.01925034/DBN
Build-In Floor | Mini Canal | MICL.01925034/DBR | 19 | 250 | 34 | 34 | 1413 | 1413 | 1413 | 0.033643 | 550 | 0.013095 | 1609 | 0.03831 | 1.362 | A04 | MICL0.01925034/DBR
Build-In Floor | Mini Canal | MICL.01925034/DBV | 19 | 250 | 34 | 34 | 1355 | 1355 | 1355 | 0.032262 | 527 | 0.012548 | 1543 | 0.036738 | 1.362 | A04 | MICL0.01925034/DBV
Build-In Floor | Mini Canal | MICL.01925034/DDB | 19 | 250 | 34 | 34 | 1413 | 1413 | 1413 | 0.033643 | 550 | 0.013095 | 1609 | 0.03831 | 1.362 | A04 | MICL0.01925034/DDB
Build-In Floor | Mini Canal | MICL.01925034/DMN | 19 | 250 | 34 | 34 | 1355 | 1355 | 1355 | 0.032262 | 527 | 0.012548 | 1543 | 0.036738 | 1.362 | A04 | MICL0.01925034/DMN
Build-In Floor | Mini Canal | MICL.01925034/DMV | 19 | 250 | 34 | 34 | 1355 | 1355 | 1355 | 0.032262 | 527 | 0.012548 | 1543 | 0.036738 | 1.362 | A04 | MICL0.01925034/DMV
Build-In Floor | Mini Canal | MICL.01925034/DNA | 19 | 250 | 34 | 34 | 1413 | 1413 | 1413 | 0.033643 | 550 | 0.013095 | 1609 | 0.03831 | 1.362 | A04 | MICL0.01925034/DNA
Build-In Floor | Mini Canal | MICL.01925034/DNC | 19 | 250 | 34 | 34 | 1413 | 1413 | 1413 | 0.033643 | 550 | 0.013095 | 1609 | 0.03831 | 1.362 | A04 | MICL0.01925034/DNC
Build-In Floor | Mini Canal | MICL.01925034/DON | 19 | 250 | 34 | 34 | 1355 | 1355 | 1355 | 0.032262 | 527 | 0.012548 | 1543 | 0.036738 | 1.362 | A04 | MICL0.01925034/DON
Build-In Floor | Mini Canal | MICL.01925034/DOV | 19 | 250 | 34 | 34 | 1355 | 1355 | 1355 | 0.032262 | 527 | 0.012548 | 1543 | 0.036738 | 1.362 | A04 | MICL0.01925034/DOV
Build-In Floor | Mini Canal | MICL.01925034/PNC | 19 | 250 | 34 | 34 | 1238 | 1238 | 1238 | 0.029476 | 482 | 0.011476 | 1410 | 0.033571 | 1.362 | A04 | MICL0.01925034/PNC
Build-In Floor | Mini Canal | MICL.01925034/RBL | 19 | 250 | 34 | 34 | 1457 | 1457 | 1457 | 0.03469 | 567 | 0.0135 | 1660 | 0.039524 | 1.362 | A04 | MICL0.01925034/RBL
Build-In Floor | Mini Canal | MICL.01925034/RBN | 19 | 250 | 34 | 34 | 1413 | 1413 | 1413 | 0.033643 | 550 | 0.013095 | 1609 | 0.03831 | 1.362 | A04 | MICL0.01925034/RBN
Build-In Floor | Mini Canal | MICL.01925034/RBR | 19 | 250 | 34 | 34 | 1457 | 1457 | 1457 | 0.03469 | 567 | 0.0135 | 1660 | 0.039524 | 1.362 | A04 | MICL0.01925034/RBR
Build-In Floor | Mini Canal | MICL.01925034/RBV | 19 | 250 | 34 | 34 | 1413 | 1413 | 1413 | 0.033643 | 550 | 0.013095 | 1609 | 0.03831 | 1.362 | A04 | MICL0.01925034/RBV
Build-In Floor | Mini Canal | MICL.01925034/RDB | 19 | 250 | 34 | 34 | 1457 | 1457 | 1457 | 0.03469 | 567 | 0.0135 | 1660 | 0.039524 | 1.362 | A04 | MICL0.01925034/RDB
Build-In Floor | Mini Canal | MICL.01925034/RMN | 19 | 250 | 34 | 34 | 1413 | 1413 | 1413 | 0.033643 | 550 | 0.013095 | 1609 | 0.03831 | 1.362 | A04 | MICL0.01925034/RMN
Build-In Floor | Mini Canal | MICL.01925034/RMV | 19 | 250 | 34 | 34 | 1413 | 1413 | 1413 | 0.033643 | 550 | 0.013095 | 1609 | 0.03831 | 1.362 | A04 | MICL0.01925034/RMV
Build-In Floor | Mini Canal | MICL.01925034/RNA | 19 | 250 | 34 | 34 | 1457 | 1457 | 1457 | 0.03469 | 567 | 0.0135 | 1660 | 0.039524 | 1.362 | A04 | MICL0.01925034/RNA
Build-In Floor | Mini Canal | MICL.01925034/RON | 19 | 250 | 34 | 34 | 1413 | 1413 | 1413 | 0.033643 | 550 | 0.013095 | 1609 | 0.03831 | 1.362 | A04 | MICL0.01925034/RON
Build-In Floor | Mini Canal | MICL.01925034/ROV | 19 | 250 | 34 | 34 | 1413 | 1413 | 1413 | 0.033643 | 550 | 0.013095 | 1609 | 0.03831 | 1.362 | A04 | MICL0.01925034/ROV
Build-In Floor | Mini Canal | MICL.01925034/RSS | 19 | 250 | 34 | 34 | 1399 | 1399 | 1399 | 0.03331 | 544 | 0.012952 | 1593 | 0.037929 | 1.362 | A04 | MICL0.01925034/RSS
Build-In Floor | Mini Canal | MICL.01925034/SBL | 19 | 250 | 34 | 34 | 1457 | 1457 | 1457 | 0.03469 | 567 | 0.0135 | 1660 | 0.039524 | 1.362 | A04 | MICL0.01925034/SBL
Build-In Floor | Mini Canal | MICL.01925034/SBR | 19 | 250 | 34 | 34 | 1457 | 1457 | 1457 | 0.03469 | 567 | 0.0135 | 1660 | 0.039524 | 1.362 | A04 | MICL0.01925034/SBR
Build-In Floor | Mini Canal | MICL.01925034/SDB | 19 | 250 | 34 | 34 | 1457 | 1457 | 1457 | 0.03469 | 567 | 0.0135 | 1660 | 0.039524 | 1.362 | A04 | MICL0.01925034/SDB
Build-In Floor | Mini Canal | MICL.01925034/SNA | 19 | 250 | 34 | 34 | 1457 | 1457 | 1457 | 0.03469 | 567 | 0.0135 | 1660 | 0.039524 | 1.362 | A04 | MICL0.01925034/SNA
Build-In Floor | Mini Canal | MICL.01925034/SNC | 19 | 250 | 34 | 34 | 1457 | 1457 | 1457 | 0.03469 | 567 | 0.0135 | 1660 | 0.039524 | 1.362 | A04 | MICL0.01925034/SNC
Build-In Floor | Mini Canal | MICL.01925042/ANA | 19 | 250 | 42 | 42 | 1501 | 1501 | 1501 | 0.035738 | 584 | 0.013905 | 1710 | 0.040714 | 1.362 | A04 | MICL0.01925042/ANA
Build-In Floor | Mini Canal | MICL.01925042/DBL | 19 | 250 | 42 | 42 | 1941 | 1941 | 1941 | 0.046214 | 755 | 0.017976 | 2211 | 0.052643 | 1.362 | A04 | MICL0.01925042/DBL
Build-In Floor | Mini Canal | MICL.01925042/DBN | 19 | 250 | 42 | 42 | 1861 | 1861 | 1861 | 0.04431 | 724 | 0.017238 | 2120 | 0.050476 | 1.362 | A04 | MICL0.01925042/DBN
Build-In Floor | Mini Canal | MICL.01925042/DBR | 19 | 250 | 42 | 42 | 1941 | 1941 | 1941 | 0.046214 | 755 | 0.017976 | 2211 | 0.052643 | 1.362 | A04 | MICL0.01925042/DBR
Build-In Floor | Mini Canal | MICL.01925042/DBV | 19 | 250 | 42 | 42 | 1861 | 1861 | 1861 | 0.04431 | 724 | 0.017238 | 2120 | 0.050476 | 1.362 | A04 | MICL0.01925042/DBV
Build-In Floor | Mini Canal | MICL.01925042/DDB | 19 | 250 | 42 | 42 | 1941 | 1941 | 1941 | 0.046214 | 755 | 0.017976 | 2211 | 0.052643 | 1.362 | A04 | MICL0.01925042/DDB
Build-In Floor | Mini Canal | MICL.01925042/DMN | 19 | 250 | 42 | 42 | 1861 | 1861 | 1861 | 0.04431 | 724 | 0.017238 | 2120 | 0.050476 | 1.362 | A04 | MICL0.01925042/DMN
Build-In Floor | Mini Canal | MICL.01925042/DMV | 19 | 250 | 42 | 42 | 1861 | 1861 | 1861 | 0.04431 | 724 | 0.017238 | 2120 | 0.050476 | 1.362 | A04 | MICL0.01925042/DMV
Build-In Floor | Mini Canal | MICL.01925042/DNA | 19 | 250 | 42 | 42 | 1941 | 1941 | 1941 | 0.046214 | 755 | 0.017976 | 2211 | 0.052643 | 1.362 | A04 | MICL0.01925042/DNA
Build-In Floor | Mini Canal | MICL.01925042/DNC | 19 | 250 | 42 | 42 | 1941 | 1941 | 1941 | 0.046214 | 755 | 0.017976 | 2211 | 0.052643 | 1.362 | A04 | MICL0.01925042/DNC
Build-In Floor | Mini Canal | MICL.01925042/DON | 19 | 250 | 42 | 42 | 1861 | 1861 | 1861 | 0.04431 | 724 | 0.017238 | 2120 | 0.050476 | 1.362 | A04 | MICL0.01925042/DON
Build-In Floor | Mini Canal | MICL.01925042/DOV | 19 | 250 | 42 | 42 | 1861 | 1861 | 1861 | 0.04431 | 724 | 0.017238 | 2120 | 0.050476 | 1.362 | A04 | MICL0.01925042/DOV
Build-In Floor | Mini Canal | MICL.01925042/PNC | 19 | 250 | 42 | 42 | 1701 | 1701 | 1701 | 0.0405 | 662 | 0.015762 | 1937 | 0.046119 | 1.362 | A04 | MICL0.01925042/PNC
Build-In Floor | Mini Canal | MICL.01925042/RBL | 19 | 250 | 42 | 42 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01925042/RBL
Build-In Floor | Mini Canal | MICL.01925042/RBN | 19 | 250 | 42 | 42 | 1941 | 1941 | 1941 | 0.046214 | 755 | 0.017976 | 2211 | 0.052643 | 1.362 | A04 | MICL0.01925042/RBN
Build-In Floor | Mini Canal | MICL.01925042/RBR | 19 | 250 | 42 | 42 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01925042/RBR
Build-In Floor | Mini Canal | MICL.01925042/RBV | 19 | 250 | 42 | 42 | 1941 | 1941 | 1941 | 0.046214 | 755 | 0.017976 | 2211 | 0.052643 | 1.362 | A04 | MICL0.01925042/RBV
Build-In Floor | Mini Canal | MICL.01925042/RDB | 19 | 250 | 42 | 42 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01925042/RDB
Build-In Floor | Mini Canal | MICL.01925042/RMN | 19 | 250 | 42 | 42 | 1941 | 1941 | 1941 | 0.046214 | 755 | 0.017976 | 2211 | 0.052643 | 1.362 | A04 | MICL0.01925042/RMN
Build-In Floor | Mini Canal | MICL.01925042/RMV | 19 | 250 | 42 | 42 | 1941 | 1941 | 1941 | 0.046214 | 755 | 0.017976 | 2211 | 0.052643 | 1.362 | A04 | MICL0.01925042/RMV
Build-In Floor | Mini Canal | MICL.01925042/RNA | 19 | 250 | 42 | 42 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01925042/RNA
Build-In Floor | Mini Canal | MICL.01925042/RON | 19 | 250 | 42 | 42 | 1941 | 1941 | 1941 | 0.046214 | 755 | 0.017976 | 2211 | 0.052643 | 1.362 | A04 | MICL0.01925042/RON
Build-In Floor | Mini Canal | MICL.01925042/ROV | 19 | 250 | 42 | 42 | 1941 | 1941 | 1941 | 0.046214 | 755 | 0.017976 | 2211 | 0.052643 | 1.362 | A04 | MICL0.01925042/ROV
Build-In Floor | Mini Canal | MICL.01925042/RSS | 19 | 250 | 42 | 42 | 1921 | 1921 | 1921 | 0.045738 | 747 | 0.017786 | 2188 | 0.052095 | 1.362 | A04 | MICL0.01925042/RSS
Build-In Floor | Mini Canal | MICL.01925042/SBL | 19 | 250 | 42 | 42 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01925042/SBL
Build-In Floor | Mini Canal | MICL.01925042/SBR | 19 | 250 | 42 | 42 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01925042/SBR
Build-In Floor | Mini Canal | MICL.01925042/SDB | 19 | 250 | 42 | 42 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01925042/SDB
Build-In Floor | Mini Canal | MICL.01925042/SNA | 19 | 250 | 42 | 42 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01925042/SNA
Build-In Floor | Mini Canal | MICL.01925042/SNC | 19 | 250 | 42 | 42 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01925042/SNC
Build-In Floor | Mini Canal | MICL.01927026/ANA | 19 | 270 | 26 | 26 | 881 | 881 | 881 | 0.020976 | 343 | 0.0081667 | 1003 | 0.023881 | 1.362 | A04 | MICL0.01927026/ANA
Build-In Floor | Mini Canal | MICL.01927026/DBL | 19 | 270 | 26 | 26 | 1139 | 1139 | 1139 | 0.027119 | 443 | 0.010548 | 1297 | 0.030881 | 1.362 | A04 | MICL0.01927026/DBL
Build-In Floor | Mini Canal | MICL.01927026/DBN | 19 | 270 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.01927026/DBN
Build-In Floor | Mini Canal | MICL.01927026/DBR | 19 | 270 | 26 | 26 | 1139 | 1139 | 1139 | 0.027119 | 443 | 0.010548 | 1297 | 0.030881 | 1.362 | A04 | MICL0.01927026/DBR
Build-In Floor | Mini Canal | MICL.01927026/DBV | 19 | 270 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.01927026/DBV
Build-In Floor | Mini Canal | MICL.01927026/DDB | 19 | 270 | 26 | 26 | 1139 | 1139 | 1139 | 0.027119 | 443 | 0.010548 | 1297 | 0.030881 | 1.362 | A04 | MICL0.01927026/DDB
Build-In Floor | Mini Canal | MICL.01927026/DMN | 19 | 270 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.01927026/DMN
Build-In Floor | Mini Canal | MICL.01927026/DMV | 19 | 270 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.01927026/DMV
Build-In Floor | Mini Canal | MICL.01927026/DNA | 19 | 270 | 26 | 26 | 1139 | 1139 | 1139 | 0.027119 | 443 | 0.010548 | 1297 | 0.030881 | 1.362 | A04 | MICL0.01927026/DNA
Build-In Floor | Mini Canal | MICL.01927026/DNC | 19 | 270 | 26 | 26 | 1139 | 1139 | 1139 | 0.027119 | 443 | 0.010548 | 1297 | 0.030881 | 1.362 | A04 | MICL0.01927026/DNC
Build-In Floor | Mini Canal | MICL.01927026/DON | 19 | 270 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.01927026/DON
Build-In Floor | Mini Canal | MICL.01927026/DOV | 19 | 270 | 26 | 26 | 1092 | 1092 | 1092 | 0.026 | 425 | 0.010119 | 1244 | 0.029619 | 1.362 | A04 | MICL0.01927026/DOV
Build-In Floor | Mini Canal | MICL.01927026/PNC | 19 | 270 | 26 | 26 | 998 | 998 | 998 | 0.023762 | 388 | 0.0092381 | 1137 | 0.027071 | 1.362 | A04 | MICL0.01927026/PNC
Build-In Floor | Mini Canal | MICL.01927026/RBL | 19 | 270 | 26 | 26 | 1174 | 1174 | 1174 | 0.027952 | 457 | 0.010881 | 1337 | 0.031833 | 1.362 | A04 | MICL0.01927026/RBL
Build-In Floor | Mini Canal | MICL.01927026/RBN | 19 | 270 | 26 | 26 | 1139 | 1139 | 1139 | 0.027119 | 443 | 0.010548 | 1297 | 0.030881 | 1.362 | A04 | MICL0.01927026/RBN
Build-In Floor | Mini Canal | MICL.01927026/RBR | 19 | 270 | 26 | 26 | 1174 | 1174 | 1174 | 0.027952 | 457 | 0.010881 | 1337 | 0.031833 | 1.362 | A04 | MICL0.01927026/RBR
Build-In Floor | Mini Canal | MICL.01927026/RBV | 19 | 270 | 26 | 26 | 1139 | 1139 | 1139 | 0.027119 | 443 | 0.010548 | 1297 | 0.030881 | 1.362 | A04 | MICL0.01927026/RBV
Build-In Floor | Mini Canal | MICL.01927026/RDB | 19 | 270 | 26 | 26 | 1174 | 1174 | 1174 | 0.027952 | 457 | 0.010881 | 1337 | 0.031833 | 1.362 | A04 | MICL0.01927026/RDB
Build-In Floor | Mini Canal | MICL.01927026/RMN | 19 | 270 | 26 | 26 | 1139 | 1139 | 1139 | 0.027119 | 443 | 0.010548 | 1297 | 0.030881 | 1.362 | A04 | MICL0.01927026/RMN
Build-In Floor | Mini Canal | MICL.01927026/RMV | 19 | 270 | 26 | 26 | 1139 | 1139 | 1139 | 0.027119 | 443 | 0.010548 | 1297 | 0.030881 | 1.362 | A04 | MICL0.01927026/RMV
Build-In Floor | Mini Canal | MICL.01927026/RNA | 19 | 270 | 26 | 26 | 1174 | 1174 | 1174 | 0.027952 | 457 | 0.010881 | 1337 | 0.031833 | 1.362 | A04 | MICL0.01927026/RNA
Build-In Floor | Mini Canal | MICL.01927026/RON | 19 | 270 | 26 | 26 | 1139 | 1139 | 1139 | 0.027119 | 443 | 0.010548 | 1297 | 0.030881 | 1.362 | A04 | MICL0.01927026/RON
Build-In Floor | Mini Canal | MICL.01927026/ROV | 19 | 270 | 26 | 26 | 1139 | 1139 | 1139 | 0.027119 | 443 | 0.010548 | 1297 | 0.030881 | 1.362 | A04 | MICL0.01927026/ROV
Build-In Floor | Mini Canal | MICL.01927026/RSS | 19 | 270 | 26 | 26 | 1127 | 1127 | 1127 | 0.026833 | 438 | 0.010429 | 1284 | 0.030571 | 1.362 | A04 | MICL0.01927026/RSS
Build-In Floor | Mini Canal | MICL.01927026/SBL | 19 | 270 | 26 | 26 | 1174 | 1174 | 1174 | 0.027952 | 457 | 0.010881 | 1337 | 0.031833 | 1.362 | A04 | MICL0.01927026/SBL
Build-In Floor | Mini Canal | MICL.01927026/SBR | 19 | 270 | 26 | 26 | 1174 | 1174 | 1174 | 0.027952 | 457 | 0.010881 | 1337 | 0.031833 | 1.362 | A04 | MICL0.01927026/SBR
Build-In Floor | Mini Canal | MICL.01927026/SDB | 19 | 270 | 26 | 26 | 1174 | 1174 | 1174 | 0.027952 | 457 | 0.010881 | 1337 | 0.031833 | 1.362 | A04 | MICL0.01927026/SDB
Build-In Floor | Mini Canal | MICL.01927026/SNA | 19 | 270 | 26 | 26 | 1174 | 1174 | 1174 | 0.027952 | 457 | 0.010881 | 1337 | 0.031833 | 1.362 | A04 | MICL0.01927026/SNA
Build-In Floor | Mini Canal | MICL.01927026/SNC | 19 | 270 | 26 | 26 | 1174 | 1174 | 1174 | 0.027952 | 457 | 0.010881 | 1337 | 0.031833 | 1.362 | A04 | MICL0.01927026/SNC
Build-In Floor | Mini Canal | MICL.01927034/ANA | 19 | 270 | 34 | 34 | 1193 | 1193 | 1193 | 0.028405 | 464 | 0.011048 | 1359 | 0.032357 | 1.362 | A04 | MICL0.01927034/ANA
Build-In Floor | Mini Canal | MICL.01927034/DBL | 19 | 270 | 34 | 34 | 1542 | 1542 | 1542 | 0.036714 | 600 | 0.014286 | 1756 | 0.04181 | 1.362 | A04 | MICL0.01927034/DBL
Build-In Floor | Mini Canal | MICL.01927034/DBN | 19 | 270 | 34 | 34 | 1479 | 1479 | 1479 | 0.035214 | 575 | 0.01369 | 1685 | 0.040119 | 1.362 | A04 | MICL0.01927034/DBN
Build-In Floor | Mini Canal | MICL.01927034/DBR | 19 | 270 | 34 | 34 | 1542 | 1542 | 1542 | 0.036714 | 600 | 0.014286 | 1756 | 0.04181 | 1.362 | A04 | MICL0.01927034/DBR
Build-In Floor | Mini Canal | MICL.01927034/DBV | 19 | 270 | 34 | 34 | 1479 | 1479 | 1479 | 0.035214 | 575 | 0.01369 | 1685 | 0.040119 | 1.362 | A04 | MICL0.01927034/DBV
Build-In Floor | Mini Canal | MICL.01927034/DDB | 19 | 270 | 34 | 34 | 1542 | 1542 | 1542 | 0.036714 | 600 | 0.014286 | 1756 | 0.04181 | 1.362 | A04 | MICL0.01927034/DDB
Build-In Floor | Mini Canal | MICL.01927034/DMN | 19 | 270 | 34 | 34 | 1479 | 1479 | 1479 | 0.035214 | 575 | 0.01369 | 1685 | 0.040119 | 1.362 | A04 | MICL0.01927034/DMN
Build-In Floor | Mini Canal | MICL.01927034/DMV | 19 | 270 | 34 | 34 | 1479 | 1479 | 1479 | 0.035214 | 575 | 0.01369 | 1685 | 0.040119 | 1.362 | A04 | MICL0.01927034/DMV
Build-In Floor | Mini Canal | MICL.01927034/DNA | 19 | 270 | 34 | 34 | 1542 | 1542 | 1542 | 0.036714 | 600 | 0.014286 | 1756 | 0.04181 | 1.362 | A04 | MICL0.01927034/DNA
Build-In Floor | Mini Canal | MICL.01927034/DNC | 19 | 270 | 34 | 34 | 1542 | 1542 | 1542 | 0.036714 | 600 | 0.014286 | 1756 | 0.04181 | 1.362 | A04 | MICL0.01927034/DNC
Build-In Floor | Mini Canal | MICL.01927034/DON | 19 | 270 | 34 | 34 | 1479 | 1479 | 1479 | 0.035214 | 575 | 0.01369 | 1685 | 0.040119 | 1.362 | A04 | MICL0.01927034/DON
Build-In Floor | Mini Canal | MICL.01927034/DOV | 19 | 270 | 34 | 34 | 1479 | 1479 | 1479 | 0.035214 | 575 | 0.01369 | 1685 | 0.040119 | 1.362 | A04 | MICL0.01927034/DOV
Build-In Floor | Mini Canal | MICL.01927034/PNC | 19 | 270 | 34 | 34 | 1352 | 1352 | 1352 | 0.03219 | 526 | 0.012524 | 1540 | 0.036667 | 1.362 | A04 | MICL0.01927034/PNC
Build-In Floor | Mini Canal | MICL.01927034/RBL | 19 | 270 | 34 | 34 | 1590 | 1590 | 1590 | 0.037857 | 619 | 0.014738 | 1811 | 0.043119 | 1.362 | A04 | MICL0.01927034/RBL
Build-In Floor | Mini Canal | MICL.01927034/RBN | 19 | 270 | 34 | 34 | 1542 | 1542 | 1542 | 0.036714 | 600 | 0.014286 | 1756 | 0.04181 | 1.362 | A04 | MICL0.01927034/RBN
Build-In Floor | Mini Canal | MICL.01927034/RBR | 19 | 270 | 34 | 34 | 1590 | 1590 | 1590 | 0.037857 | 619 | 0.014738 | 1811 | 0.043119 | 1.362 | A04 | MICL0.01927034/RBR
Build-In Floor | Mini Canal | MICL.01927034/RBV | 19 | 270 | 34 | 34 | 1542 | 1542 | 1542 | 0.036714 | 600 | 0.014286 | 1756 | 0.04181 | 1.362 | A04 | MICL0.01927034/RBV
Build-In Floor | Mini Canal | MICL.01927034/RDB | 19 | 270 | 34 | 34 | 1590 | 1590 | 1590 | 0.037857 | 619 | 0.014738 | 1811 | 0.043119 | 1.362 | A04 | MICL0.01927034/RDB
Build-In Floor | Mini Canal | MICL.01927034/RMN | 19 | 270 | 34 | 34 | 1542 | 1542 | 1542 | 0.036714 | 600 | 0.014286 | 1756 | 0.04181 | 1.362 | A04 | MICL0.01927034/RMN
Build-In Floor | Mini Canal | MICL.01927034/RMV | 19 | 270 | 34 | 34 | 1542 | 1542 | 1542 | 0.036714 | 600 | 0.014286 | 1756 | 0.04181 | 1.362 | A04 | MICL0.01927034/RMV
Build-In Floor | Mini Canal | MICL.01927034/RNA | 19 | 270 | 34 | 34 | 1590 | 1590 | 1590 | 0.037857 | 619 | 0.014738 | 1811 | 0.043119 | 1.362 | A04 | MICL0.01927034/RNA
Build-In Floor | Mini Canal | MICL.01927034/RON | 19 | 270 | 34 | 34 | 1542 | 1542 | 1542 | 0.036714 | 600 | 0.014286 | 1756 | 0.04181 | 1.362 | A04 | MICL0.01927034/RON
Build-In Floor | Mini Canal | MICL.01927034/ROV | 19 | 270 | 34 | 34 | 1542 | 1542 | 1542 | 0.036714 | 600 | 0.014286 | 1756 | 0.04181 | 1.362 | A04 | MICL0.01927034/ROV
Build-In Floor | Mini Canal | MICL.01927034/RSS | 19 | 270 | 34 | 34 | 1526 | 1526 | 1526 | 0.036333 | 594 | 0.014143 | 1738 | 0.041381 | 1.362 | A04 | MICL0.01927034/RSS
Build-In Floor | Mini Canal | MICL.01927034/SBL | 19 | 270 | 34 | 34 | 1590 | 1590 | 1590 | 0.037857 | 619 | 0.014738 | 1811 | 0.043119 | 1.362 | A04 | MICL0.01927034/SBL
Build-In Floor | Mini Canal | MICL.01927034/SBR | 19 | 270 | 34 | 34 | 1590 | 1590 | 1590 | 0.037857 | 619 | 0.014738 | 1811 | 0.043119 | 1.362 | A04 | MICL0.01927034/SBR
Build-In Floor | Mini Canal | MICL.01927034/SDB | 19 | 270 | 34 | 34 | 1590 | 1590 | 1590 | 0.037857 | 619 | 0.014738 | 1811 | 0.043119 | 1.362 | A04 | MICL0.01927034/SDB
Build-In Floor | Mini Canal | MICL.01927034/SNA | 19 | 270 | 34 | 34 | 1590 | 1590 | 1590 | 0.037857 | 619 | 0.014738 | 1811 | 0.043119 | 1.362 | A04 | MICL0.01927034/SNA
Build-In Floor | Mini Canal | MICL.01927034/SNC | 19 | 270 | 34 | 34 | 1590 | 1590 | 1590 | 0.037857 | 619 | 0.014738 | 1811 | 0.043119 | 1.362 | A04 | MICL0.01927034/SNC
Build-In Floor | Mini Canal | MICL.01927042/ANA | 19 | 270 | 42 | 42 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01927042/ANA
Build-In Floor | Mini Canal | MICL.01927042/DBL | 19 | 270 | 42 | 42 | 2117 | 2117 | 2117 | 0.050405 | 824 | 0.019619 | 2411 | 0.057405 | 1.362 | A04 | MICL0.01927042/DBL
Build-In Floor | Mini Canal | MICL.01927042/DBN | 19 | 270 | 42 | 42 | 2029 | 2029 | 2029 | 0.04831 | 789 | 0.018786 | 2311 | 0.055024 | 1.362 | A04 | MICL0.01927042/DBN
Build-In Floor | Mini Canal | MICL.01927042/DBR | 19 | 270 | 42 | 42 | 2117 | 2117 | 2117 | 0.050405 | 824 | 0.019619 | 2411 | 0.057405 | 1.362 | A04 | MICL0.01927042/DBR
Build-In Floor | Mini Canal | MICL.01927042/DBV | 19 | 270 | 42 | 42 | 2029 | 2029 | 2029 | 0.04831 | 789 | 0.018786 | 2311 | 0.055024 | 1.362 | A04 | MICL0.01927042/DBV
Build-In Floor | Mini Canal | MICL.01927042/DDB | 19 | 270 | 42 | 42 | 2117 | 2117 | 2117 | 0.050405 | 824 | 0.019619 | 2411 | 0.057405 | 1.362 | A04 | MICL0.01927042/DDB
Build-In Floor | Mini Canal | MICL.01927042/DMN | 19 | 270 | 42 | 42 | 2029 | 2029 | 2029 | 0.04831 | 789 | 0.018786 | 2311 | 0.055024 | 1.362 | A04 | MICL0.01927042/DMN
Build-In Floor | Mini Canal | MICL.01927042/DMV | 19 | 270 | 42 | 42 | 2029 | 2029 | 2029 | 0.04831 | 789 | 0.018786 | 2311 | 0.055024 | 1.362 | A04 | MICL0.01927042/DMV
Build-In Floor | Mini Canal | MICL.01927042/DNA | 19 | 270 | 42 | 42 | 2117 | 2117 | 2117 | 0.050405 | 824 | 0.019619 | 2411 | 0.057405 | 1.362 | A04 | MICL0.01927042/DNA
Build-In Floor | Mini Canal | MICL.01927042/DNC | 19 | 270 | 42 | 42 | 2117 | 2117 | 2117 | 0.050405 | 824 | 0.019619 | 2411 | 0.057405 | 1.362 | A04 | MICL0.01927042/DNC
Build-In Floor | Mini Canal | MICL.01927042/DON | 19 | 270 | 42 | 42 | 2029 | 2029 | 2029 | 0.04831 | 789 | 0.018786 | 2311 | 0.055024 | 1.362 | A04 | MICL0.01927042/DON
Build-In Floor | Mini Canal | MICL.01927042/DOV | 19 | 270 | 42 | 42 | 2029 | 2029 | 2029 | 0.04831 | 789 | 0.018786 | 2311 | 0.055024 | 1.362 | A04 | MICL0.01927042/DOV
Build-In Floor | Mini Canal | MICL.01927042/PNC | 19 | 270 | 42 | 42 | 1855 | 1855 | 1855 | 0.044167 | 722 | 0.01719 | 2113 | 0.05031 | 1.362 | A04 | MICL0.01927042/PNC
Build-In Floor | Mini Canal | MICL.01927042/RBL | 19 | 270 | 42 | 42 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01927042/RBL
Build-In Floor | Mini Canal | MICL.01927042/RBN | 19 | 270 | 42 | 42 | 2117 | 2117 | 2117 | 0.050405 | 824 | 0.019619 | 2411 | 0.057405 | 1.362 | A04 | MICL0.01927042/RBN
Build-In Floor | Mini Canal | MICL.01927042/RBR | 19 | 270 | 42 | 42 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01927042/RBR
Build-In Floor | Mini Canal | MICL.01927042/RBV | 19 | 270 | 42 | 42 | 2117 | 2117 | 2117 | 0.050405 | 824 | 0.019619 | 2411 | 0.057405 | 1.362 | A04 | MICL0.01927042/RBV
Build-In Floor | Mini Canal | MICL.01927042/RDB | 19 | 270 | 42 | 42 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01927042/RDB
Build-In Floor | Mini Canal | MICL.01927042/RMN | 19 | 270 | 42 | 42 | 2117 | 2117 | 2117 | 0.050405 | 824 | 0.019619 | 2411 | 0.057405 | 1.362 | A04 | MICL0.01927042/RMN
Build-In Floor | Mini Canal | MICL.01927042/RMV | 19 | 270 | 42 | 42 | 2117 | 2117 | 2117 | 0.050405 | 824 | 0.019619 | 2411 | 0.057405 | 1.362 | A04 | MICL0.01927042/RMV
Build-In Floor | Mini Canal | MICL.01927042/RNA | 19 | 270 | 42 | 42 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01927042/RNA
Build-In Floor | Mini Canal | MICL.01927042/RON | 19 | 270 | 42 | 42 | 2117 | 2117 | 2117 | 0.050405 | 824 | 0.019619 | 2411 | 0.057405 | 1.362 | A04 | MICL0.01927042/RON
Build-In Floor | Mini Canal | MICL.01927042/ROV | 19 | 270 | 42 | 42 | 2117 | 2117 | 2117 | 0.050405 | 824 | 0.019619 | 2411 | 0.057405 | 1.362 | A04 | MICL0.01927042/ROV
Build-In Floor | Mini Canal | MICL.01927042/RSS | 19 | 270 | 42 | 42 | 2095 | 2095 | 2095 | 0.049881 | 815 | 0.019405 | 2386 | 0.05681 | 1.362 | A04 | MICL0.01927042/RSS
Build-In Floor | Mini Canal | MICL.01927042/SBL | 19 | 270 | 42 | 42 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01927042/SBL
Build-In Floor | Mini Canal | MICL.01927042/SBR | 19 | 270 | 42 | 42 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01927042/SBR
Build-In Floor | Mini Canal | MICL.01927042/SDB | 19 | 270 | 42 | 42 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01927042/SDB
Build-In Floor | Mini Canal | MICL.01927042/SNA | 19 | 270 | 42 | 42 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01927042/SNA
Build-In Floor | Mini Canal | MICL.01927042/SNC | 19 | 270 | 42 | 42 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01927042/SNC
Build-In Floor | Mini Canal | MICL.01929026/ANA | 19 | 290 | 26 | 26 | 953 | 953 | 953 | 0.02269 | 371 | 0.0088333 | 1085 | 0.025833 | 1.362 | A04 | MICL0.01929026/ANA
Build-In Floor | Mini Canal | MICL.01929026/DBL | 19 | 290 | 26 | 26 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01929026/DBL
Build-In Floor | Mini Canal | MICL.01929026/DBN | 19 | 290 | 26 | 26 | 1182 | 1182 | 1182 | 0.028143 | 460 | 0.010952 | 1346 | 0.032048 | 1.362 | A04 | MICL0.01929026/DBN
Build-In Floor | Mini Canal | MICL.01929026/DBR | 19 | 290 | 26 | 26 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01929026/DBR
Build-In Floor | Mini Canal | MICL.01929026/DBV | 19 | 290 | 26 | 26 | 1182 | 1182 | 1182 | 0.028143 | 460 | 0.010952 | 1346 | 0.032048 | 1.362 | A04 | MICL0.01929026/DBV
Build-In Floor | Mini Canal | MICL.01929026/DDB | 19 | 290 | 26 | 26 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01929026/DDB
Build-In Floor | Mini Canal | MICL.01929026/DMN | 19 | 290 | 26 | 26 | 1182 | 1182 | 1182 | 0.028143 | 460 | 0.010952 | 1346 | 0.032048 | 1.362 | A04 | MICL0.01929026/DMN
Build-In Floor | Mini Canal | MICL.01929026/DMV | 19 | 290 | 26 | 26 | 1182 | 1182 | 1182 | 0.028143 | 460 | 0.010952 | 1346 | 0.032048 | 1.362 | A04 | MICL0.01929026/DMV
Build-In Floor | Mini Canal | MICL.01929026/DNA | 19 | 290 | 26 | 26 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01929026/DNA
Build-In Floor | Mini Canal | MICL.01929026/DNC | 19 | 290 | 26 | 26 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01929026/DNC
Build-In Floor | Mini Canal | MICL.01929026/DON | 19 | 290 | 26 | 26 | 1182 | 1182 | 1182 | 0.028143 | 460 | 0.010952 | 1346 | 0.032048 | 1.362 | A04 | MICL0.01929026/DON
Build-In Floor | Mini Canal | MICL.01929026/DOV | 19 | 290 | 26 | 26 | 1182 | 1182 | 1182 | 0.028143 | 460 | 0.010952 | 1346 | 0.032048 | 1.362 | A04 | MICL0.01929026/DOV
Build-In Floor | Mini Canal | MICL.01929026/PNC | 19 | 290 | 26 | 26 | 1080 | 1080 | 1080 | 0.025714 | 420 | 0.01 | 1230 | 0.029286 | 1.362 | A04 | MICL0.01929026/PNC
Build-In Floor | Mini Canal | MICL.01929026/RBL | 19 | 290 | 26 | 26 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01929026/RBL
Build-In Floor | Mini Canal | MICL.01929026/RBN | 19 | 290 | 26 | 26 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01929026/RBN
Build-In Floor | Mini Canal | MICL.01929026/RBR | 19 | 290 | 26 | 26 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01929026/RBR
Build-In Floor | Mini Canal | MICL.01929026/RBV | 19 | 290 | 26 | 26 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01929026/RBV
Build-In Floor | Mini Canal | MICL.01929026/RDB | 19 | 290 | 26 | 26 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01929026/RDB
Build-In Floor | Mini Canal | MICL.01929026/RMN | 19 | 290 | 26 | 26 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01929026/RMN
Build-In Floor | Mini Canal | MICL.01929026/RMV | 19 | 290 | 26 | 26 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01929026/RMV
Build-In Floor | Mini Canal | MICL.01929026/RNA | 19 | 290 | 26 | 26 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01929026/RNA
Build-In Floor | Mini Canal | MICL.01929026/RON | 19 | 290 | 26 | 26 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01929026/RON
Build-In Floor | Mini Canal | MICL.01929026/ROV | 19 | 290 | 26 | 26 | 1233 | 1233 | 1233 | 0.029357 | 480 | 0.011429 | 1404 | 0.033429 | 1.362 | A04 | MICL0.01929026/ROV
Build-In Floor | Mini Canal | MICL.01929026/RSS | 19 | 290 | 26 | 26 | 1220 | 1220 | 1220 | 0.029048 | 475 | 0.01131 | 1390 | 0.033095 | 1.362 | A04 | MICL0.01929026/RSS
Build-In Floor | Mini Canal | MICL.01929026/SBL | 19 | 290 | 26 | 26 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01929026/SBL
Build-In Floor | Mini Canal | MICL.01929026/SBR | 19 | 290 | 26 | 26 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01929026/SBR
Build-In Floor | Mini Canal | MICL.01929026/SDB | 19 | 290 | 26 | 26 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01929026/SDB
Build-In Floor | Mini Canal | MICL.01929026/SNA | 19 | 290 | 26 | 26 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01929026/SNA
Build-In Floor | Mini Canal | MICL.01929026/SNC | 19 | 290 | 26 | 26 | 1271 | 1271 | 1271 | 0.030262 | 494 | 0.011762 | 1448 | 0.034476 | 1.362 | A04 | MICL0.01929026/SNC
Build-In Floor | Mini Canal | MICL.01929034/ANA | 19 | 290 | 34 | 34 | 1291 | 1291 | 1291 | 0.030738 | 502 | 0.011952 | 1470 | 0.035 | 1.362 | A04 | MICL0.01929034/ANA
Build-In Floor | Mini Canal | MICL.01929034/DBL | 19 | 290 | 34 | 34 | 1669 | 1669 | 1669 | 0.039738 | 649 | 0.015452 | 1901 | 0.045262 | 1.362 | A04 | MICL0.01929034/DBL
Build-In Floor | Mini Canal | MICL.01929034/DBN | 19 | 290 | 34 | 34 | 1601 | 1601 | 1601 | 0.038119 | 623 | 0.014833 | 1824 | 0.043429 | 1.362 | A04 | MICL0.01929034/DBN
Build-In Floor | Mini Canal | MICL.01929034/DBR | 19 | 290 | 34 | 34 | 1669 | 1669 | 1669 | 0.039738 | 649 | 0.015452 | 1901 | 0.045262 | 1.362 | A04 | MICL0.01929034/DBR
Build-In Floor | Mini Canal | MICL.01929034/DBV | 19 | 290 | 34 | 34 | 1601 | 1601 | 1601 | 0.038119 | 623 | 0.014833 | 1824 | 0.043429 | 1.362 | A04 | MICL0.01929034/DBV
Build-In Floor | Mini Canal | MICL.01929034/DDB | 19 | 290 | 34 | 34 | 1669 | 1669 | 1669 | 0.039738 | 649 | 0.015452 | 1901 | 0.045262 | 1.362 | A04 | MICL0.01929034/DDB
Build-In Floor | Mini Canal | MICL.01929034/DMN | 19 | 290 | 34 | 34 | 1601 | 1601 | 1601 | 0.038119 | 623 | 0.014833 | 1824 | 0.043429 | 1.362 | A04 | MICL0.01929034/DMN
Build-In Floor | Mini Canal | MICL.01929034/DMV | 19 | 290 | 34 | 34 | 1601 | 1601 | 1601 | 0.038119 | 623 | 0.014833 | 1824 | 0.043429 | 1.362 | A04 | MICL0.01929034/DMV
Build-In Floor | Mini Canal | MICL.01929034/DNA | 19 | 290 | 34 | 34 | 1669 | 1669 | 1669 | 0.039738 | 649 | 0.015452 | 1901 | 0.045262 | 1.362 | A04 | MICL0.01929034/DNA
Build-In Floor | Mini Canal | MICL.01929034/DNC | 19 | 290 | 34 | 34 | 1669 | 1669 | 1669 | 0.039738 | 649 | 0.015452 | 1901 | 0.045262 | 1.362 | A04 | MICL0.01929034/DNC
Build-In Floor | Mini Canal | MICL.01929034/DON | 19 | 290 | 34 | 34 | 1601 | 1601 | 1601 | 0.038119 | 623 | 0.014833 | 1824 | 0.043429 | 1.362 | A04 | MICL0.01929034/DON
Build-In Floor | Mini Canal | MICL.01929034/DOV | 19 | 290 | 34 | 34 | 1601 | 1601 | 1601 | 0.038119 | 623 | 0.014833 | 1824 | 0.043429 | 1.362 | A04 | MICL0.01929034/DOV
Build-In Floor | Mini Canal | MICL.01929034/PNC | 19 | 290 | 34 | 34 | 1463 | 1463 | 1463 | 0.034833 | 569 | 0.013548 | 1666 | 0.039667 | 1.362 | A04 | MICL0.01929034/PNC
Build-In Floor | Mini Canal | MICL.01929034/RBL | 19 | 290 | 34 | 34 | 1721 | 1721 | 1721 | 0.040976 | 669 | 0.015929 | 1960 | 0.046667 | 1.362 | A04 | MICL0.01929034/RBL
Build-In Floor | Mini Canal | MICL.01929034/RBN | 19 | 290 | 34 | 34 | 1669 | 1669 | 1669 | 0.039738 | 649 | 0.015452 | 1901 | 0.045262 | 1.362 | A04 | MICL0.01929034/RBN
Build-In Floor | Mini Canal | MICL.01929034/RBR | 19 | 290 | 34 | 34 | 1721 | 1721 | 1721 | 0.040976 | 669 | 0.015929 | 1960 | 0.046667 | 1.362 | A04 | MICL0.01929034/RBR
Build-In Floor | Mini Canal | MICL.01929034/RBV | 19 | 290 | 34 | 34 | 1669 | 1669 | 1669 | 0.039738 | 649 | 0.015452 | 1901 | 0.045262 | 1.362 | A04 | MICL0.01929034/RBV
Build-In Floor | Mini Canal | MICL.01929034/RDB | 19 | 290 | 34 | 34 | 1721 | 1721 | 1721 | 0.040976 | 669 | 0.015929 | 1960 | 0.046667 | 1.362 | A04 | MICL0.01929034/RDB
Build-In Floor | Mini Canal | MICL.01929034/RMN | 19 | 290 | 34 | 34 | 1669 | 1669 | 1669 | 0.039738 | 649 | 0.015452 | 1901 | 0.045262 | 1.362 | A04 | MICL0.01929034/RMN
Build-In Floor | Mini Canal | MICL.01929034/RMV | 19 | 290 | 34 | 34 | 1669 | 1669 | 1669 | 0.039738 | 649 | 0.015452 | 1901 | 0.045262 | 1.362 | A04 | MICL0.01929034/RMV
Build-In Floor | Mini Canal | MICL.01929034/RNA | 19 | 290 | 34 | 34 | 1721 | 1721 | 1721 | 0.040976 | 669 | 0.015929 | 1960 | 0.046667 | 1.362 | A04 | MICL0.01929034/RNA
Build-In Floor | Mini Canal | MICL.01929034/RON | 19 | 290 | 34 | 34 | 1669 | 1669 | 1669 | 0.039738 | 649 | 0.015452 | 1901 | 0.045262 | 1.362 | A04 | MICL0.01929034/RON
Build-In Floor | Mini Canal | MICL.01929034/ROV | 19 | 290 | 34 | 34 | 1669 | 1669 | 1669 | 0.039738 | 649 | 0.015452 | 1901 | 0.045262 | 1.362 | A04 | MICL0.01929034/ROV
Build-In Floor | Mini Canal | MICL.01929034/RSS | 19 | 290 | 34 | 34 | 1652 | 1652 | 1652 | 0.039333 | 643 | 0.01531 | 1882 | 0.04481 | 1.362 | A04 | MICL0.01929034/RSS
Build-In Floor | Mini Canal | MICL.01929034/SBL | 19 | 290 | 34 | 34 | 1721 | 1721 | 1721 | 0.040976 | 669 | 0.015929 | 1960 | 0.046667 | 1.362 | A04 | MICL0.01929034/SBL
Build-In Floor | Mini Canal | MICL.01929034/SBR | 19 | 290 | 34 | 34 | 1721 | 1721 | 1721 | 0.040976 | 669 | 0.015929 | 1960 | 0.046667 | 1.362 | A04 | MICL0.01929034/SBR
Build-In Floor | Mini Canal | MICL.01929034/SDB | 19 | 290 | 34 | 34 | 1721 | 1721 | 1721 | 0.040976 | 669 | 0.015929 | 1960 | 0.046667 | 1.362 | A04 | MICL0.01929034/SDB
Build-In Floor | Mini Canal | MICL.01929034/SNA | 19 | 290 | 34 | 34 | 1721 | 1721 | 1721 | 0.040976 | 669 | 0.015929 | 1960 | 0.046667 | 1.362 | A04 | MICL0.01929034/SNA
Build-In Floor | Mini Canal | MICL.01929034/SNC | 19 | 290 | 34 | 34 | 1721 | 1721 | 1721 | 0.040976 | 669 | 0.015929 | 1960 | 0.046667 | 1.362 | A04 | MICL0.01929034/SNC
Build-In Floor | Mini Canal | MICL.01929042/ANA | 19 | 290 | 42 | 42 | 1774 | 1774 | 1774 | 0.042238 | 690 | 0.016429 | 2021 | 0.048119 | 1.362 | A04 | MICL0.01929042/ANA
Build-In Floor | Mini Canal | MICL.01929042/DBL | 19 | 290 | 42 | 42 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01929042/DBL
Build-In Floor | Mini Canal | MICL.01929042/DBN | 19 | 290 | 42 | 42 | 2199 | 2199 | 2199 | 0.052357 | 855 | 0.020357 | 2505 | 0.059643 | 1.362 | A04 | MICL0.01929042/DBN
Build-In Floor | Mini Canal | MICL.01929042/DBR | 19 | 290 | 42 | 42 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01929042/DBR
Build-In Floor | Mini Canal | MICL.01929042/DBV | 19 | 290 | 42 | 42 | 2199 | 2199 | 2199 | 0.052357 | 855 | 0.020357 | 2505 | 0.059643 | 1.362 | A04 | MICL0.01929042/DBV
Build-In Floor | Mini Canal | MICL.01929042/DDB | 19 | 290 | 42 | 42 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01929042/DDB
Build-In Floor | Mini Canal | MICL.01929042/DMN | 19 | 290 | 42 | 42 | 2199 | 2199 | 2199 | 0.052357 | 855 | 0.020357 | 2505 | 0.059643 | 1.362 | A04 | MICL0.01929042/DMN
Build-In Floor | Mini Canal | MICL.01929042/DMV | 19 | 290 | 42 | 42 | 2199 | 2199 | 2199 | 0.052357 | 855 | 0.020357 | 2505 | 0.059643 | 1.362 | A04 | MICL0.01929042/DMV
Build-In Floor | Mini Canal | MICL.01929042/DNA | 19 | 290 | 42 | 42 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01929042/DNA
Build-In Floor | Mini Canal | MICL.01929042/DNC | 19 | 290 | 42 | 42 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01929042/DNC
Build-In Floor | Mini Canal | MICL.01929042/DON | 19 | 290 | 42 | 42 | 2199 | 2199 | 2199 | 0.052357 | 855 | 0.020357 | 2505 | 0.059643 | 1.362 | A04 | MICL0.01929042/DON
Build-In Floor | Mini Canal | MICL.01929042/DOV | 19 | 290 | 42 | 42 | 2199 | 2199 | 2199 | 0.052357 | 855 | 0.020357 | 2505 | 0.059643 | 1.362 | A04 | MICL0.01929042/DOV
Build-In Floor | Mini Canal | MICL.01929042/PNC | 19 | 290 | 42 | 42 | 2010 | 2010 | 2010 | 0.047857 | 782 | 0.018619 | 2289 | 0.0545 | 1.362 | A04 | MICL0.01929042/PNC
Build-In Floor | Mini Canal | MICL.01929042/RBL | 19 | 290 | 42 | 42 | 2365 | 2365 | 2365 | 0.05631 | 920 | 0.021905 | 2694 | 0.064143 | 1.362 | A04 | MICL0.01929042/RBL
Build-In Floor | Mini Canal | MICL.01929042/RBN | 19 | 290 | 42 | 42 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01929042/RBN
Build-In Floor | Mini Canal | MICL.01929042/RBR | 19 | 290 | 42 | 42 | 2365 | 2365 | 2365 | 0.05631 | 920 | 0.021905 | 2694 | 0.064143 | 1.362 | A04 | MICL0.01929042/RBR
Build-In Floor | Mini Canal | MICL.01929042/RBV | 19 | 290 | 42 | 42 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01929042/RBV
Build-In Floor | Mini Canal | MICL.01929042/RDB | 19 | 290 | 42 | 42 | 2365 | 2365 | 2365 | 0.05631 | 920 | 0.021905 | 2694 | 0.064143 | 1.362 | A04 | MICL0.01929042/RDB
Build-In Floor | Mini Canal | MICL.01929042/RMN | 19 | 290 | 42 | 42 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01929042/RMN
Build-In Floor | Mini Canal | MICL.01929042/RMV | 19 | 290 | 42 | 42 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01929042/RMV
Build-In Floor | Mini Canal | MICL.01929042/RNA | 19 | 290 | 42 | 42 | 2365 | 2365 | 2365 | 0.05631 | 920 | 0.021905 | 2694 | 0.064143 | 1.362 | A04 | MICL0.01929042/RNA
Build-In Floor | Mini Canal | MICL.01929042/RON | 19 | 290 | 42 | 42 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01929042/RON
Build-In Floor | Mini Canal | MICL.01929042/ROV | 19 | 290 | 42 | 42 | 2294 | 2294 | 2294 | 0.054619 | 892 | 0.021238 | 2613 | 0.062214 | 1.362 | A04 | MICL0.01929042/ROV
Build-In Floor | Mini Canal | MICL.01929042/RSS | 19 | 290 | 42 | 42 | 2270 | 2270 | 2270 | 0.054048 | 883 | 0.021024 | 2586 | 0.061571 | 1.362 | A04 | MICL0.01929042/RSS
Build-In Floor | Mini Canal | MICL.01929042/SBL | 19 | 290 | 42 | 42 | 2365 | 2365 | 2365 | 0.05631 | 920 | 0.021905 | 2694 | 0.064143 | 1.362 | A04 | MICL0.01929042/SBL
Build-In Floor | Mini Canal | MICL.01929042/SBR | 19 | 290 | 42 | 42 | 2365 | 2365 | 2365 | 0.05631 | 920 | 0.021905 | 2694 | 0.064143 | 1.362 | A04 | MICL0.01929042/SBR
Build-In Floor | Mini Canal | MICL.01929042/SDB | 19 | 290 | 42 | 42 | 2365 | 2365 | 2365 | 0.05631 | 920 | 0.021905 | 2694 | 0.064143 | 1.362 | A04 | MICL0.01929042/SDB
Build-In Floor | Mini Canal | MICL.01929042/SNA | 19 | 290 | 42 | 42 | 2365 | 2365 | 2365 | 0.05631 | 920 | 0.021905 | 2694 | 0.064143 | 1.362 | A04 | MICL0.01929042/SNA
Build-In Floor | Mini Canal | MICL.01929042/SNC | 19 | 290 | 42 | 42 | 2365 | 2365 | 2365 | 0.05631 | 920 | 0.021905 | 2694 | 0.064143 | 1.362 | A04 | MICL0.01929042/SNC
Build-In Floor | Mini Canal | MICL.01931026/ANA | 19 | 310 | 26 | 26 | 1028 | 1028 | 1028 | 0.024476 | 400 | 0.0095238 | 1171 | 0.027881 | 1.362 | A04 | MICL0.01931026/ANA
Build-In Floor | Mini Canal | MICL.01931026/DBL | 19 | 310 | 26 | 26 | 1329 | 1329 | 1329 | 0.031643 | 517 | 0.01231 | 1514 | 0.036048 | 1.362 | A04 | MICL0.01931026/DBL
Build-In Floor | Mini Canal | MICL.01931026/DBN | 19 | 310 | 26 | 26 | 1274 | 1274 | 1274 | 0.030333 | 496 | 0.01181 | 1451 | 0.034548 | 1.362 | A04 | MICL0.01931026/DBN
Build-In Floor | Mini Canal | MICL.01931026/DBR | 19 | 310 | 26 | 26 | 1329 | 1329 | 1329 | 0.031643 | 517 | 0.01231 | 1514 | 0.036048 | 1.362 | A04 | MICL0.01931026/DBR
Build-In Floor | Mini Canal | MICL.01931026/DBV | 19 | 310 | 26 | 26 | 1274 | 1274 | 1274 | 0.030333 | 496 | 0.01181 | 1451 | 0.034548 | 1.362 | A04 | MICL0.01931026/DBV
Build-In Floor | Mini Canal | MICL.01931026/DDB | 19 | 310 | 26 | 26 | 1329 | 1329 | 1329 | 0.031643 | 517 | 0.01231 | 1514 | 0.036048 | 1.362 | A04 | MICL0.01931026/DDB
Build-In Floor | Mini Canal | MICL.01931026/DMN | 19 | 310 | 26 | 26 | 1274 | 1274 | 1274 | 0.030333 | 496 | 0.01181 | 1451 | 0.034548 | 1.362 | A04 | MICL0.01931026/DMN
Build-In Floor | Mini Canal | MICL.01931026/DMV | 19 | 310 | 26 | 26 | 1274 | 1274 | 1274 | 0.030333 | 496 | 0.01181 | 1451 | 0.034548 | 1.362 | A04 | MICL0.01931026/DMV
Build-In Floor | Mini Canal | MICL.01931026/DNA | 19 | 310 | 26 | 26 | 1329 | 1329 | 1329 | 0.031643 | 517 | 0.01231 | 1514 | 0.036048 | 1.362 | A04 | MICL0.01931026/DNA
Build-In Floor | Mini Canal | MICL.01931026/DNC | 19 | 310 | 26 | 26 | 1329 | 1329 | 1329 | 0.031643 | 517 | 0.01231 | 1514 | 0.036048 | 1.362 | A04 | MICL0.01931026/DNC
Build-In Floor | Mini Canal | MICL.01931026/DON | 19 | 310 | 26 | 26 | 1274 | 1274 | 1274 | 0.030333 | 496 | 0.01181 | 1451 | 0.034548 | 1.362 | A04 | MICL0.01931026/DON
Build-In Floor | Mini Canal | MICL.01931026/DOV | 19 | 310 | 26 | 26 | 1274 | 1274 | 1274 | 0.030333 | 496 | 0.01181 | 1451 | 0.034548 | 1.362 | A04 | MICL0.01931026/DOV
Build-In Floor | Mini Canal | MICL.01931026/PNC | 19 | 310 | 26 | 26 | 1165 | 1165 | 1165 | 0.027738 | 453 | 0.010786 | 1327 | 0.031595 | 1.362 | A04 | MICL0.01931026/PNC
Build-In Floor | Mini Canal | MICL.01931026/RBL | 19 | 310 | 26 | 26 | 1370 | 1370 | 1370 | 0.032619 | 533 | 0.01269 | 1560 | 0.037143 | 1.362 | A04 | MICL0.01931026/RBL
Build-In Floor | Mini Canal | MICL.01931026/RBN | 19 | 310 | 26 | 26 | 1329 | 1329 | 1329 | 0.031643 | 517 | 0.01231 | 1514 | 0.036048 | 1.362 | A04 | MICL0.01931026/RBN
Build-In Floor | Mini Canal | MICL.01931026/RBR | 19 | 310 | 26 | 26 | 1370 | 1370 | 1370 | 0.032619 | 533 | 0.01269 | 1560 | 0.037143 | 1.362 | A04 | MICL0.01931026/RBR
Build-In Floor | Mini Canal | MICL.01931026/RBV | 19 | 310 | 26 | 26 | 1329 | 1329 | 1329 | 0.031643 | 517 | 0.01231 | 1514 | 0.036048 | 1.362 | A04 | MICL0.01931026/RBV
Build-In Floor | Mini Canal | MICL.01931026/RDB | 19 | 310 | 26 | 26 | 1370 | 1370 | 1370 | 0.032619 | 533 | 0.01269 | 1560 | 0.037143 | 1.362 | A04 | MICL0.01931026/RDB
Build-In Floor | Mini Canal | MICL.01931026/RMN | 19 | 310 | 26 | 26 | 1329 | 1329 | 1329 | 0.031643 | 517 | 0.01231 | 1514 | 0.036048 | 1.362 | A04 | MICL0.01931026/RMN
Build-In Floor | Mini Canal | MICL.01931026/RMV | 19 | 310 | 26 | 26 | 1329 | 1329 | 1329 | 0.031643 | 517 | 0.01231 | 1514 | 0.036048 | 1.362 | A04 | MICL0.01931026/RMV
Build-In Floor | Mini Canal | MICL.01931026/RNA | 19 | 310 | 26 | 26 | 1370 | 1370 | 1370 | 0.032619 | 533 | 0.01269 | 1560 | 0.037143 | 1.362 | A04 | MICL0.01931026/RNA
Build-In Floor | Mini Canal | MICL.01931026/RON | 19 | 310 | 26 | 26 | 1329 | 1329 | 1329 | 0.031643 | 517 | 0.01231 | 1514 | 0.036048 | 1.362 | A04 | MICL0.01931026/RON
Build-In Floor | Mini Canal | MICL.01931026/ROV | 19 | 310 | 26 | 26 | 1329 | 1329 | 1329 | 0.031643 | 517 | 0.01231 | 1514 | 0.036048 | 1.362 | A04 | MICL0.01931026/ROV
Build-In Floor | Mini Canal | MICL.01931026/RSS | 19 | 310 | 26 | 26 | 1315 | 1315 | 1315 | 0.03131 | 512 | 0.01219 | 1498 | 0.035667 | 1.362 | A04 | MICL0.01931026/RSS
Build-In Floor | Mini Canal | MICL.01931026/SBL | 19 | 310 | 26 | 26 | 1370 | 1370 | 1370 | 0.032619 | 533 | 0.01269 | 1560 | 0.037143 | 1.362 | A04 | MICL0.01931026/SBL
Build-In Floor | Mini Canal | MICL.01931026/SBR | 19 | 310 | 26 | 26 | 1370 | 1370 | 1370 | 0.032619 | 533 | 0.01269 | 1560 | 0.037143 | 1.362 | A04 | MICL0.01931026/SBR
Build-In Floor | Mini Canal | MICL.01931026/SDB | 19 | 310 | 26 | 26 | 1370 | 1370 | 1370 | 0.032619 | 533 | 0.01269 | 1560 | 0.037143 | 1.362 | A04 | MICL0.01931026/SDB
Build-In Floor | Mini Canal | MICL.01931026/SNA | 19 | 310 | 26 | 26 | 1370 | 1370 | 1370 | 0.032619 | 533 | 0.01269 | 1560 | 0.037143 | 1.362 | A04 | MICL0.01931026/SNA
Build-In Floor | Mini Canal | MICL.01931026/SNC | 19 | 310 | 26 | 26 | 1370 | 1370 | 1370 | 0.032619 | 533 | 0.01269 | 1560 | 0.037143 | 1.362 | A04 | MICL0.01931026/SNC
Build-In Floor | Mini Canal | MICL.01931034/ANA | 19 | 310 | 34 | 34 | 1391 | 1391 | 1391 | 0.033119 | 541 | 0.012881 | 1584 | 0.037714 | 1.362 | A04 | MICL0.01931034/ANA
Build-In Floor | Mini Canal | MICL.01931034/DBL | 19 | 310 | 34 | 34 | 1798 | 1798 | 1798 | 0.04281 | 699 | 0.016643 | 2048 | 0.048762 | 1.362 | A04 | MICL0.01931034/DBL
Build-In Floor | Mini Canal | MICL.01931034/DBN | 19 | 310 | 34 | 34 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.01931034/DBN
Build-In Floor | Mini Canal | MICL.01931034/DBR | 19 | 310 | 34 | 34 | 1798 | 1798 | 1798 | 0.04281 | 699 | 0.016643 | 2048 | 0.048762 | 1.362 | A04 | MICL0.01931034/DBR
Build-In Floor | Mini Canal | MICL.01931034/DBV | 19 | 310 | 34 | 34 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.01931034/DBV
Build-In Floor | Mini Canal | MICL.01931034/DDB | 19 | 310 | 34 | 34 | 1798 | 1798 | 1798 | 0.04281 | 699 | 0.016643 | 2048 | 0.048762 | 1.362 | A04 | MICL0.01931034/DDB
Build-In Floor | Mini Canal | MICL.01931034/DMN | 19 | 310 | 34 | 34 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.01931034/DMN
Build-In Floor | Mini Canal | MICL.01931034/DMV | 19 | 310 | 34 | 34 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.01931034/DMV
Build-In Floor | Mini Canal | MICL.01931034/DNA | 19 | 310 | 34 | 34 | 1798 | 1798 | 1798 | 0.04281 | 699 | 0.016643 | 2048 | 0.048762 | 1.362 | A04 | MICL0.01931034/DNA
Build-In Floor | Mini Canal | MICL.01931034/DNC | 19 | 310 | 34 | 34 | 1798 | 1798 | 1798 | 0.04281 | 699 | 0.016643 | 2048 | 0.048762 | 1.362 | A04 | MICL0.01931034/DNC
Build-In Floor | Mini Canal | MICL.01931034/DON | 19 | 310 | 34 | 34 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.01931034/DON
Build-In Floor | Mini Canal | MICL.01931034/DOV | 19 | 310 | 34 | 34 | 1724 | 1724 | 1724 | 0.041048 | 671 | 0.015976 | 1964 | 0.046762 | 1.362 | A04 | MICL0.01931034/DOV
Build-In Floor | Mini Canal | MICL.01931034/PNC | 19 | 310 | 34 | 34 | 1576 | 1576 | 1576 | 0.037524 | 613 | 0.014595 | 1795 | 0.042738 | 1.362 | A04 | MICL0.01931034/PNC
Build-In Floor | Mini Canal | MICL.01931034/RBL | 19 | 310 | 34 | 34 | 1854 | 1854 | 1854 | 0.044143 | 721 | 0.017167 | 2112 | 0.050286 | 1.362 | A04 | MICL0.01931034/RBL
Build-In Floor | Mini Canal | MICL.01931034/RBN | 19 | 310 | 34 | 34 | 1798 | 1798 | 1798 | 0.04281 | 699 | 0.016643 | 2048 | 0.048762 | 1.362 | A04 | MICL0.01931034/RBN
Build-In Floor | Mini Canal | MICL.01931034/RBR | 19 | 310 | 34 | 34 | 1854 | 1854 | 1854 | 0.044143 | 721 | 0.017167 | 2112 | 0.050286 | 1.362 | A04 | MICL0.01931034/RBR
Build-In Floor | Mini Canal | MICL.01931034/RBV | 19 | 310 | 34 | 34 | 1798 | 1798 | 1798 | 0.04281 | 699 | 0.016643 | 2048 | 0.048762 | 1.362 | A04 | MICL0.01931034/RBV
Build-In Floor | Mini Canal | MICL.01931034/RDB | 19 | 310 | 34 | 34 | 1854 | 1854 | 1854 | 0.044143 | 721 | 0.017167 | 2112 | 0.050286 | 1.362 | A04 | MICL0.01931034/RDB
Build-In Floor | Mini Canal | MICL.01931034/RMN | 19 | 310 | 34 | 34 | 1798 | 1798 | 1798 | 0.04281 | 699 | 0.016643 | 2048 | 0.048762 | 1.362 | A04 | MICL0.01931034/RMN
Build-In Floor | Mini Canal | MICL.01931034/RMV | 19 | 310 | 34 | 34 | 1798 | 1798 | 1798 | 0.04281 | 699 | 0.016643 | 2048 | 0.048762 | 1.362 | A04 | MICL0.01931034/RMV
Build-In Floor | Mini Canal | MICL.01931034/RNA | 19 | 310 | 34 | 34 | 1854 | 1854 | 1854 | 0.044143 | 721 | 0.017167 | 2112 | 0.050286 | 1.362 | A04 | MICL0.01931034/RNA
Build-In Floor | Mini Canal | MICL.01931034/RON | 19 | 310 | 34 | 34 | 1798 | 1798 | 1798 | 0.04281 | 699 | 0.016643 | 2048 | 0.048762 | 1.362 | A04 | MICL0.01931034/RON
Build-In Floor | Mini Canal | MICL.01931034/ROV | 19 | 310 | 34 | 34 | 1798 | 1798 | 1798 | 0.04281 | 699 | 0.016643 | 2048 | 0.048762 | 1.362 | A04 | MICL0.01931034/ROV
Build-In Floor | Mini Canal | MICL.01931034/RSS | 19 | 310 | 34 | 34 | 1780 | 1780 | 1780 | 0.042381 | 692 | 0.016476 | 2027 | 0.048262 | 1.362 | A04 | MICL0.01931034/RSS
Build-In Floor | Mini Canal | MICL.01931034/SBL | 19 | 310 | 34 | 34 | 1854 | 1854 | 1854 | 0.044143 | 721 | 0.017167 | 2112 | 0.050286 | 1.362 | A04 | MICL0.01931034/SBL
Build-In Floor | Mini Canal | MICL.01931034/SBR | 19 | 310 | 34 | 34 | 1854 | 1854 | 1854 | 0.044143 | 721 | 0.017167 | 2112 | 0.050286 | 1.362 | A04 | MICL0.01931034/SBR
Build-In Floor | Mini Canal | MICL.01931034/SDB | 19 | 310 | 34 | 34 | 1854 | 1854 | 1854 | 0.044143 | 721 | 0.017167 | 2112 | 0.050286 | 1.362 | A04 | MICL0.01931034/SDB
Build-In Floor | Mini Canal | MICL.01931034/SNA | 19 | 310 | 34 | 34 | 1854 | 1854 | 1854 | 0.044143 | 721 | 0.017167 | 2112 | 0.050286 | 1.362 | A04 | MICL0.01931034/SNA
Build-In Floor | Mini Canal | MICL.01931034/SNC | 19 | 310 | 34 | 34 | 1854 | 1854 | 1854 | 0.044143 | 721 | 0.017167 | 2112 | 0.050286 | 1.362 | A04 | MICL0.01931034/SNC
Build-In Floor | Mini Canal | MICL.01931042/ANA | 19 | 310 | 42 | 42 | 1910 | 1910 | 1910 | 0.045476 | 743 | 0.01769 | 2175 | 0.051786 | 1.362 | A04 | MICL0.01931042/ANA
Build-In Floor | Mini Canal | MICL.01931042/DBL | 19 | 310 | 42 | 42 | 2471 | 2471 | 2471 | 0.058833 | 961 | 0.022881 | 2814 | 0.067 | 1.362 | A04 | MICL0.01931042/DBL
Build-In Floor | Mini Canal | MICL.01931042/DBN | 19 | 310 | 42 | 42 | 2369 | 2369 | 2369 | 0.056405 | 922 | 0.021952 | 2698 | 0.064238 | 1.362 | A04 | MICL0.01931042/DBN
Build-In Floor | Mini Canal | MICL.01931042/DBR | 19 | 310 | 42 | 42 | 2471 | 2471 | 2471 | 0.058833 | 961 | 0.022881 | 2814 | 0.067 | 1.362 | A04 | MICL0.01931042/DBR
Build-In Floor | Mini Canal | MICL.01931042/DBV | 19 | 310 | 42 | 42 | 2369 | 2369 | 2369 | 0.056405 | 922 | 0.021952 | 2698 | 0.064238 | 1.362 | A04 | MICL0.01931042/DBV
Build-In Floor | Mini Canal | MICL.01931042/DDB | 19 | 310 | 42 | 42 | 2471 | 2471 | 2471 | 0.058833 | 961 | 0.022881 | 2814 | 0.067 | 1.362 | A04 | MICL0.01931042/DDB
Build-In Floor | Mini Canal | MICL.01931042/DMN | 19 | 310 | 42 | 42 | 2369 | 2369 | 2369 | 0.056405 | 922 | 0.021952 | 2698 | 0.064238 | 1.362 | A04 | MICL0.01931042/DMN
Build-In Floor | Mini Canal | MICL.01931042/DMV | 19 | 310 | 42 | 42 | 2369 | 2369 | 2369 | 0.056405 | 922 | 0.021952 | 2698 | 0.064238 | 1.362 | A04 | MICL0.01931042/DMV
Build-In Floor | Mini Canal | MICL.01931042/DNA | 19 | 310 | 42 | 42 | 2471 | 2471 | 2471 | 0.058833 | 961 | 0.022881 | 2814 | 0.067 | 1.362 | A04 | MICL0.01931042/DNA
Build-In Floor | Mini Canal | MICL.01931042/DNC | 19 | 310 | 42 | 42 | 2471 | 2471 | 2471 | 0.058833 | 961 | 0.022881 | 2814 | 0.067 | 1.362 | A04 | MICL0.01931042/DNC
Build-In Floor | Mini Canal | MICL.01931042/DON | 19 | 310 | 42 | 42 | 2369 | 2369 | 2369 | 0.056405 | 922 | 0.021952 | 2698 | 0.064238 | 1.362 | A04 | MICL0.01931042/DON
Build-In Floor | Mini Canal | MICL.01931042/DOV | 19 | 310 | 42 | 42 | 2369 | 2369 | 2369 | 0.056405 | 922 | 0.021952 | 2698 | 0.064238 | 1.362 | A04 | MICL0.01931042/DOV
Build-In Floor | Mini Canal | MICL.01931042/PNC | 19 | 310 | 42 | 42 | 2165 | 2165 | 2165 | 0.051548 | 842 | 0.020048 | 2466 | 0.058714 | 1.362 | A04 | MICL0.01931042/PNC
Build-In Floor | Mini Canal | MICL.01931042/RBL | 19 | 310 | 42 | 42 | 2547 | 2547 | 2547 | 0.060643 | 991 | 0.023595 | 2901 | 0.069071 | 1.362 | A04 | MICL0.01931042/RBL
Build-In Floor | Mini Canal | MICL.01931042/RBN | 19 | 310 | 42 | 42 | 2471 | 2471 | 2471 | 0.058833 | 961 | 0.022881 | 2814 | 0.067 | 1.362 | A04 | MICL0.01931042/RBN
Build-In Floor | Mini Canal | MICL.01931042/RBR | 19 | 310 | 42 | 42 | 2547 | 2547 | 2547 | 0.060643 | 991 | 0.023595 | 2901 | 0.069071 | 1.362 | A04 | MICL0.01931042/RBR
Build-In Floor | Mini Canal | MICL.01931042/RBV | 19 | 310 | 42 | 42 | 2471 | 2471 | 2471 | 0.058833 | 961 | 0.022881 | 2814 | 0.067 | 1.362 | A04 | MICL0.01931042/RBV
Build-In Floor | Mini Canal | MICL.01931042/RDB | 19 | 310 | 42 | 42 | 2547 | 2547 | 2547 | 0.060643 | 991 | 0.023595 | 2901 | 0.069071 | 1.362 | A04 | MICL0.01931042/RDB
Build-In Floor | Mini Canal | MICL.01931042/RMN | 19 | 310 | 42 | 42 | 2471 | 2471 | 2471 | 0.058833 | 961 | 0.022881 | 2814 | 0.067 | 1.362 | A04 | MICL0.01931042/RMN
Build-In Floor | Mini Canal | MICL.01931042/RMV | 19 | 310 | 42 | 42 | 2471 | 2471 | 2471 | 0.058833 | 961 | 0.022881 | 2814 | 0.067 | 1.362 | A04 | MICL0.01931042/RMV
Build-In Floor | Mini Canal | MICL.01931042/RNA | 19 | 310 | 42 | 42 | 2547 | 2547 | 2547 | 0.060643 | 991 | 0.023595 | 2901 | 0.069071 | 1.362 | A04 | MICL0.01931042/RNA
Build-In Floor | Mini Canal | MICL.01931042/RON | 19 | 310 | 42 | 42 | 2471 | 2471 | 2471 | 0.058833 | 961 | 0.022881 | 2814 | 0.067 | 1.362 | A04 | MICL0.01931042/RON
Build-In Floor | Mini Canal | MICL.01931042/ROV | 19 | 310 | 42 | 42 | 2471 | 2471 | 2471 | 0.058833 | 961 | 0.022881 | 2814 | 0.067 | 1.362 | A04 | MICL0.01931042/ROV
Build-In Floor | Mini Canal | MICL.01931042/RSS | 19 | 310 | 42 | 42 | 2445 | 2445 | 2445 | 0.058214 | 951 | 0.022643 | 2785 | 0.06631 | 1.362 | A04 | MICL0.01931042/RSS
Build-In Floor | Mini Canal | MICL.01931042/SBL | 19 | 310 | 42 | 42 | 2547 | 2547 | 2547 | 0.060643 | 991 | 0.023595 | 2901 | 0.069071 | 1.362 | A04 | MICL0.01931042/SBL
Build-In Floor | Mini Canal | MICL.01931042/SBR | 19 | 310 | 42 | 42 | 2547 | 2547 | 2547 | 0.060643 | 991 | 0.023595 | 2901 | 0.069071 | 1.362 | A04 | MICL0.01931042/SBR
Build-In Floor | Mini Canal | MICL.01931042/SDB | 19 | 310 | 42 | 42 | 2547 | 2547 | 2547 | 0.060643 | 991 | 0.023595 | 2901 | 0.069071 | 1.362 | A04 | MICL0.01931042/SDB
Build-In Floor | Mini Canal | MICL.01931042/SNA | 19 | 310 | 42 | 42 | 2547 | 2547 | 2547 | 0.060643 | 991 | 0.023595 | 2901 | 0.069071 | 1.362 | A04 | MICL0.01931042/SNA
Build-In Floor | Mini Canal | MICL.01931042/SNC | 19 | 310 | 42 | 42 | 2547 | 2547 | 2547 | 0.060643 | 991 | 0.023595 | 2901 | 0.069071 | 1.362 | A04 | MICL0.01931042/SNC
Build-In Floor | Mini Canal | MICL.01933026/ANA | 19 | 330 | 26 | 26 | 1100 | 1100 | 1100 | 0.02619 | 428 | 0.01019 | 1253 | 0.029833 | 1.362 | A04 | MICL0.01933026/ANA
Build-In Floor | Mini Canal | MICL.01933026/DBL | 19 | 330 | 26 | 26 | 1423 | 1423 | 1423 | 0.033881 | 554 | 0.01319 | 1621 | 0.038595 | 1.362 | A04 | MICL0.01933026/DBL
Build-In Floor | Mini Canal | MICL.01933026/DBN | 19 | 330 | 26 | 26 | 1364 | 1364 | 1364 | 0.032476 | 531 | 0.012643 | 1554 | 0.037 | 1.362 | A04 | MICL0.01933026/DBN
Build-In Floor | Mini Canal | MICL.01933026/DBR | 19 | 330 | 26 | 26 | 1423 | 1423 | 1423 | 0.033881 | 554 | 0.01319 | 1621 | 0.038595 | 1.362 | A04 | MICL0.01933026/DBR
Build-In Floor | Mini Canal | MICL.01933026/DBV | 19 | 330 | 26 | 26 | 1364 | 1364 | 1364 | 0.032476 | 531 | 0.012643 | 1554 | 0.037 | 1.362 | A04 | MICL0.01933026/DBV
Build-In Floor | Mini Canal | MICL.01933026/DDB | 19 | 330 | 26 | 26 | 1423 | 1423 | 1423 | 0.033881 | 554 | 0.01319 | 1621 | 0.038595 | 1.362 | A04 | MICL0.01933026/DDB
Build-In Floor | Mini Canal | MICL.01933026/DMN | 19 | 330 | 26 | 26 | 1364 | 1364 | 1364 | 0.032476 | 531 | 0.012643 | 1554 | 0.037 | 1.362 | A04 | MICL0.01933026/DMN
Build-In Floor | Mini Canal | MICL.01933026/DMV | 19 | 330 | 26 | 26 | 1364 | 1364 | 1364 | 0.032476 | 531 | 0.012643 | 1554 | 0.037 | 1.362 | A04 | MICL0.01933026/DMV
Build-In Floor | Mini Canal | MICL.01933026/DNA | 19 | 330 | 26 | 26 | 1423 | 1423 | 1423 | 0.033881 | 554 | 0.01319 | 1621 | 0.038595 | 1.362 | A04 | MICL0.01933026/DNA
Build-In Floor | Mini Canal | MICL.01933026/DNC | 19 | 330 | 26 | 26 | 1423 | 1423 | 1423 | 0.033881 | 554 | 0.01319 | 1621 | 0.038595 | 1.362 | A04 | MICL0.01933026/DNC
Build-In Floor | Mini Canal | MICL.01933026/DON | 19 | 330 | 26 | 26 | 1364 | 1364 | 1364 | 0.032476 | 531 | 0.012643 | 1554 | 0.037 | 1.362 | A04 | MICL0.01933026/DON
Build-In Floor | Mini Canal | MICL.01933026/DOV | 19 | 330 | 26 | 26 | 1364 | 1364 | 1364 | 0.032476 | 531 | 0.012643 | 1554 | 0.037 | 1.362 | A04 | MICL0.01933026/DOV
Build-In Floor | Mini Canal | MICL.01933026/PNC | 19 | 330 | 26 | 26 | 1247 | 1247 | 1247 | 0.02969 | 485 | 0.011548 | 1420 | 0.03381 | 1.362 | A04 | MICL0.01933026/PNC
Build-In Floor | Mini Canal | MICL.01933026/RBL | 19 | 330 | 26 | 26 | 1467 | 1467 | 1467 | 0.034929 | 571 | 0.013595 | 1671 | 0.039786 | 1.362 | A04 | MICL0.01933026/RBL
Build-In Floor | Mini Canal | MICL.01933026/RBN | 19 | 330 | 26 | 26 | 1423 | 1423 | 1423 | 0.033881 | 554 | 0.01319 | 1621 | 0.038595 | 1.362 | A04 | MICL0.01933026/RBN
Build-In Floor | Mini Canal | MICL.01933026/RBR | 19 | 330 | 26 | 26 | 1467 | 1467 | 1467 | 0.034929 | 571 | 0.013595 | 1671 | 0.039786 | 1.362 | A04 | MICL0.01933026/RBR
Build-In Floor | Mini Canal | MICL.01933026/RBV | 19 | 330 | 26 | 26 | 1423 | 1423 | 1423 | 0.033881 | 554 | 0.01319 | 1621 | 0.038595 | 1.362 | A04 | MICL0.01933026/RBV
Build-In Floor | Mini Canal | MICL.01933026/RDB | 19 | 330 | 26 | 26 | 1467 | 1467 | 1467 | 0.034929 | 571 | 0.013595 | 1671 | 0.039786 | 1.362 | A04 | MICL0.01933026/RDB
Build-In Floor | Mini Canal | MICL.01933026/RMN | 19 | 330 | 26 | 26 | 1423 | 1423 | 1423 | 0.033881 | 554 | 0.01319 | 1621 | 0.038595 | 1.362 | A04 | MICL0.01933026/RMN
Build-In Floor | Mini Canal | MICL.01933026/RMV | 19 | 330 | 26 | 26 | 1423 | 1423 | 1423 | 0.033881 | 554 | 0.01319 | 1621 | 0.038595 | 1.362 | A04 | MICL0.01933026/RMV
Build-In Floor | Mini Canal | MICL.01933026/RNA | 19 | 330 | 26 | 26 | 1467 | 1467 | 1467 | 0.034929 | 571 | 0.013595 | 1671 | 0.039786 | 1.362 | A04 | MICL0.01933026/RNA
Build-In Floor | Mini Canal | MICL.01933026/RON | 19 | 330 | 26 | 26 | 1423 | 1423 | 1423 | 0.033881 | 554 | 0.01319 | 1621 | 0.038595 | 1.362 | A04 | MICL0.01933026/RON
Build-In Floor | Mini Canal | MICL.01933026/ROV | 19 | 330 | 26 | 26 | 1423 | 1423 | 1423 | 0.033881 | 554 | 0.01319 | 1621 | 0.038595 | 1.362 | A04 | MICL0.01933026/ROV
Build-In Floor | Mini Canal | MICL.01933026/RSS | 19 | 330 | 26 | 26 | 1408 | 1408 | 1408 | 0.033524 | 548 | 0.013048 | 1604 | 0.03819 | 1.362 | A04 | MICL0.01933026/RSS
Build-In Floor | Mini Canal | MICL.01933026/SBL | 19 | 330 | 26 | 26 | 1467 | 1467 | 1467 | 0.034929 | 571 | 0.013595 | 1671 | 0.039786 | 1.362 | A04 | MICL0.01933026/SBL
Build-In Floor | Mini Canal | MICL.01933026/SBR | 19 | 330 | 26 | 26 | 1467 | 1467 | 1467 | 0.034929 | 571 | 0.013595 | 1671 | 0.039786 | 1.362 | A04 | MICL0.01933026/SBR
Build-In Floor | Mini Canal | MICL.01933026/SDB | 19 | 330 | 26 | 26 | 1467 | 1467 | 1467 | 0.034929 | 571 | 0.013595 | 1671 | 0.039786 | 1.362 | A04 | MICL0.01933026/SDB
Build-In Floor | Mini Canal | MICL.01933026/SNA | 19 | 330 | 26 | 26 | 1467 | 1467 | 1467 | 0.034929 | 571 | 0.013595 | 1671 | 0.039786 | 1.362 | A04 | MICL0.01933026/SNA
Build-In Floor | Mini Canal | MICL.01933026/SNC | 19 | 330 | 26 | 26 | 1467 | 1467 | 1467 | 0.034929 | 571 | 0.013595 | 1671 | 0.039786 | 1.362 | A04 | MICL0.01933026/SNC
Build-In Floor | Mini Canal | MICL.01933034/ANA | 19 | 330 | 34 | 34 | 1490 | 1490 | 1490 | 0.035476 | 580 | 0.01381 | 1697 | 0.040405 | 1.362 | A04 | MICL0.01933034/ANA
Build-In Floor | Mini Canal | MICL.01933034/DBL | 19 | 330 | 34 | 34 | 1927 | 1927 | 1927 | 0.045881 | 750 | 0.017857 | 2195 | 0.052262 | 1.362 | A04 | MICL0.01933034/DBL
Build-In Floor | Mini Canal | MICL.01933034/DBN | 19 | 330 | 34 | 34 | 1848 | 1848 | 1848 | 0.044 | 719 | 0.017119 | 2105 | 0.050119 | 1.362 | A04 | MICL0.01933034/DBN
Build-In Floor | Mini Canal | MICL.01933034/DBR | 19 | 330 | 34 | 34 | 1927 | 1927 | 1927 | 0.045881 | 750 | 0.017857 | 2195 | 0.052262 | 1.362 | A04 | MICL0.01933034/DBR
Build-In Floor | Mini Canal | MICL.01933034/DBV | 19 | 330 | 34 | 34 | 1848 | 1848 | 1848 | 0.044 | 719 | 0.017119 | 2105 | 0.050119 | 1.362 | A04 | MICL0.01933034/DBV
Build-In Floor | Mini Canal | MICL.01933034/DDB | 19 | 330 | 34 | 34 | 1927 | 1927 | 1927 | 0.045881 | 750 | 0.017857 | 2195 | 0.052262 | 1.362 | A04 | MICL0.01933034/DDB
Build-In Floor | Mini Canal | MICL.01933034/DMN | 19 | 330 | 34 | 34 | 1848 | 1848 | 1848 | 0.044 | 719 | 0.017119 | 2105 | 0.050119 | 1.362 | A04 | MICL0.01933034/DMN
Build-In Floor | Mini Canal | MICL.01933034/DMV | 19 | 330 | 34 | 34 | 1848 | 1848 | 1848 | 0.044 | 719 | 0.017119 | 2105 | 0.050119 | 1.362 | A04 | MICL0.01933034/DMV
Build-In Floor | Mini Canal | MICL.01933034/DNA | 19 | 330 | 34 | 34 | 1927 | 1927 | 1927 | 0.045881 | 750 | 0.017857 | 2195 | 0.052262 | 1.362 | A04 | MICL0.01933034/DNA
Build-In Floor | Mini Canal | MICL.01933034/DNC | 19 | 330 | 34 | 34 | 1927 | 1927 | 1927 | 0.045881 | 750 | 0.017857 | 2195 | 0.052262 | 1.362 | A04 | MICL0.01933034/DNC
Build-In Floor | Mini Canal | MICL.01933034/DON | 19 | 330 | 34 | 34 | 1848 | 1848 | 1848 | 0.044 | 719 | 0.017119 | 2105 | 0.050119 | 1.362 | A04 | MICL0.01933034/DON
Build-In Floor | Mini Canal | MICL.01933034/DOV | 19 | 330 | 34 | 34 | 1848 | 1848 | 1848 | 0.044 | 719 | 0.017119 | 2105 | 0.050119 | 1.362 | A04 | MICL0.01933034/DOV
Build-In Floor | Mini Canal | MICL.01933034/PNC | 19 | 330 | 34 | 34 | 1689 | 1689 | 1689 | 0.040214 | 657 | 0.015643 | 1924 | 0.04581 | 1.362 | A04 | MICL0.01933034/PNC
Build-In Floor | Mini Canal | MICL.01933034/RBL | 19 | 330 | 34 | 34 | 1987 | 1987 | 1987 | 0.04731 | 773 | 0.018405 | 2263 | 0.053881 | 1.362 | A04 | MICL0.01933034/RBL
Build-In Floor | Mini Canal | MICL.01933034/RBN | 19 | 330 | 34 | 34 | 1927 | 1927 | 1927 | 0.045881 | 750 | 0.017857 | 2195 | 0.052262 | 1.362 | A04 | MICL0.01933034/RBN
Build-In Floor | Mini Canal | MICL.01933034/RBR | 19 | 330 | 34 | 34 | 1987 | 1987 | 1987 | 0.04731 | 773 | 0.018405 | 2263 | 0.053881 | 1.362 | A04 | MICL0.01933034/RBR
Build-In Floor | Mini Canal | MICL.01933034/RBV | 19 | 330 | 34 | 34 | 1927 | 1927 | 1927 | 0.045881 | 750 | 0.017857 | 2195 | 0.052262 | 1.362 | A04 | MICL0.01933034/RBV
Build-In Floor | Mini Canal | MICL.01933034/RDB | 19 | 330 | 34 | 34 | 1987 | 1987 | 1987 | 0.04731 | 773 | 0.018405 | 2263 | 0.053881 | 1.362 | A04 | MICL0.01933034/RDB
Build-In Floor | Mini Canal | MICL.01933034/RMN | 19 | 330 | 34 | 34 | 1927 | 1927 | 1927 | 0.045881 | 750 | 0.017857 | 2195 | 0.052262 | 1.362 | A04 | MICL0.01933034/RMN
Build-In Floor | Mini Canal | MICL.01933034/RMV | 19 | 330 | 34 | 34 | 1927 | 1927 | 1927 | 0.045881 | 750 | 0.017857 | 2195 | 0.052262 | 1.362 | A04 | MICL0.01933034/RMV
Build-In Floor | Mini Canal | MICL.01933034/RNA | 19 | 330 | 34 | 34 | 1987 | 1987 | 1987 | 0.04731 | 773 | 0.018405 | 2263 | 0.053881 | 1.362 | A04 | MICL0.01933034/RNA
Build-In Floor | Mini Canal | MICL.01933034/RON | 19 | 330 | 34 | 34 | 1927 | 1927 | 1927 | 0.045881 | 750 | 0.017857 | 2195 | 0.052262 | 1.362 | A04 | MICL0.01933034/RON
Build-In Floor | Mini Canal | MICL.01933034/ROV | 19 | 330 | 34 | 34 | 1927 | 1927 | 1927 | 0.045881 | 750 | 0.017857 | 2195 | 0.052262 | 1.362 | A04 | MICL0.01933034/ROV
Build-In Floor | Mini Canal | MICL.01933034/RSS | 19 | 330 | 34 | 34 | 1908 | 1908 | 1908 | 0.045429 | 742 | 0.017667 | 2173 | 0.051738 | 1.362 | A04 | MICL0.01933034/RSS
Build-In Floor | Mini Canal | MICL.01933034/SBL | 19 | 330 | 34 | 34 | 1987 | 1987 | 1987 | 0.04731 | 773 | 0.018405 | 2263 | 0.053881 | 1.362 | A04 | MICL0.01933034/SBL
Build-In Floor | Mini Canal | MICL.01933034/SBR | 19 | 330 | 34 | 34 | 1987 | 1987 | 1987 | 0.04731 | 773 | 0.018405 | 2263 | 0.053881 | 1.362 | A04 | MICL0.01933034/SBR
Build-In Floor | Mini Canal | MICL.01933034/SDB | 19 | 330 | 34 | 34 | 1987 | 1987 | 1987 | 0.04731 | 773 | 0.018405 | 2263 | 0.053881 | 1.362 | A04 | MICL0.01933034/SDB
Build-In Floor | Mini Canal | MICL.01933034/SNA | 19 | 330 | 34 | 34 | 1987 | 1987 | 1987 | 0.04731 | 773 | 0.018405 | 2263 | 0.053881 | 1.362 | A04 | MICL0.01933034/SNA
Build-In Floor | Mini Canal | MICL.01933034/SNC | 19 | 330 | 34 | 34 | 1987 | 1987 | 1987 | 0.04731 | 773 | 0.018405 | 2263 | 0.053881 | 1.362 | A04 | MICL0.01933034/SNC
Build-In Floor | Mini Canal | MICL.01933042/ANA | 19 | 330 | 42 | 42 | 2046 | 2046 | 2046 | 0.048714 | 796 | 0.018952 | 2330 | 0.055476 | 1.362 | A04 | MICL0.01933042/ANA
Build-In Floor | Mini Canal | MICL.01933042/DBL | 19 | 330 | 42 | 42 | 2646 | 2646 | 2646 | 0.063 | 1029 | 0.0245 | 3014 | 0.071762 | 1.362 | A04 | MICL0.01933042/DBL
Build-In Floor | Mini Canal | MICL.01933042/DBN | 19 | 330 | 42 | 42 | 2537 | 2537 | 2537 | 0.060405 | 987 | 0.0235 | 2890 | 0.06881 | 1.362 | A04 | MICL0.01933042/DBN
Build-In Floor | Mini Canal | MICL.01933042/DBR | 19 | 330 | 42 | 42 | 2646 | 2646 | 2646 | 0.063 | 1029 | 0.0245 | 3014 | 0.071762 | 1.362 | A04 | MICL0.01933042/DBR
Build-In Floor | Mini Canal | MICL.01933042/DBV | 19 | 330 | 42 | 42 | 2537 | 2537 | 2537 | 0.060405 | 987 | 0.0235 | 2890 | 0.06881 | 1.362 | A04 | MICL0.01933042/DBV
Build-In Floor | Mini Canal | MICL.01933042/DDB | 19 | 330 | 42 | 42 | 2646 | 2646 | 2646 | 0.063 | 1029 | 0.0245 | 3014 | 0.071762 | 1.362 | A04 | MICL0.01933042/DDB
Build-In Floor | Mini Canal | MICL.01933042/DMN | 19 | 330 | 42 | 42 | 2537 | 2537 | 2537 | 0.060405 | 987 | 0.0235 | 2890 | 0.06881 | 1.362 | A04 | MICL0.01933042/DMN
Build-In Floor | Mini Canal | MICL.01933042/DMV | 19 | 330 | 42 | 42 | 2537 | 2537 | 2537 | 0.060405 | 987 | 0.0235 | 2890 | 0.06881 | 1.362 | A04 | MICL0.01933042/DMV
Build-In Floor | Mini Canal | MICL.01933042/DNA | 19 | 330 | 42 | 42 | 2646 | 2646 | 2646 | 0.063 | 1029 | 0.0245 | 3014 | 0.071762 | 1.362 | A04 | MICL0.01933042/DNA
Build-In Floor | Mini Canal | MICL.01933042/DNC | 19 | 330 | 42 | 42 | 2646 | 2646 | 2646 | 0.063 | 1029 | 0.0245 | 3014 | 0.071762 | 1.362 | A04 | MICL0.01933042/DNC
Build-In Floor | Mini Canal | MICL.01933042/DON | 19 | 330 | 42 | 42 | 2537 | 2537 | 2537 | 0.060405 | 987 | 0.0235 | 2890 | 0.06881 | 1.362 | A04 | MICL0.01933042/DON
Build-In Floor | Mini Canal | MICL.01933042/DOV | 19 | 330 | 42 | 42 | 2537 | 2537 | 2537 | 0.060405 | 987 | 0.0235 | 2890 | 0.06881 | 1.362 | A04 | MICL0.01933042/DOV
Build-In Floor | Mini Canal | MICL.01933042/PNC | 19 | 330 | 42 | 42 | 2319 | 2319 | 2319 | 0.055214 | 902 | 0.021476 | 2641 | 0.062881 | 1.362 | A04 | MICL0.01933042/PNC
Build-In Floor | Mini Canal | MICL.01933042/RBL | 19 | 330 | 42 | 42 | 2728 | 2728 | 2728 | 0.064952 | 1061 | 0.025262 | 3107 | 0.073976 | 1.362 | A04 | MICL0.01933042/RBL
Build-In Floor | Mini Canal | MICL.01933042/RBN | 19 | 330 | 42 | 42 | 2646 | 2646 | 2646 | 0.063 | 1029 | 0.0245 | 3014 | 0.071762 | 1.362 | A04 | MICL0.01933042/RBN
Build-In Floor | Mini Canal | MICL.01933042/RBR | 19 | 330 | 42 | 42 | 2728 | 2728 | 2728 | 0.064952 | 1061 | 0.025262 | 3107 | 0.073976 | 1.362 | A04 | MICL0.01933042/RBR
Build-In Floor | Mini Canal | MICL.01933042/RBV | 19 | 330 | 42 | 42 | 2646 | 2646 | 2646 | 0.063 | 1029 | 0.0245 | 3014 | 0.071762 | 1.362 | A04 | MICL0.01933042/RBV
Build-In Floor | Mini Canal | MICL.01933042/RDB | 19 | 330 | 42 | 42 | 2728 | 2728 | 2728 | 0.064952 | 1061 | 0.025262 | 3107 | 0.073976 | 1.362 | A04 | MICL0.01933042/RDB
Build-In Floor | Mini Canal | MICL.01933042/RMN | 19 | 330 | 42 | 42 | 2646 | 2646 | 2646 | 0.063 | 1029 | 0.0245 | 3014 | 0.071762 | 1.362 | A04 | MICL0.01933042/RMN
Build-In Floor | Mini Canal | MICL.01933042/RMV | 19 | 330 | 42 | 42 | 2646 | 2646 | 2646 | 0.063 | 1029 | 0.0245 | 3014 | 0.071762 | 1.362 | A04 | MICL0.01933042/RMV
Build-In Floor | Mini Canal | MICL.01933042/RNA | 19 | 330 | 42 | 42 | 2728 | 2728 | 2728 | 0.064952 | 1061 | 0.025262 | 3107 | 0.073976 | 1.362 | A04 | MICL0.01933042/RNA
Build-In Floor | Mini Canal | MICL.01933042/RON | 19 | 330 | 42 | 42 | 2646 | 2646 | 2646 | 0.063 | 1029 | 0.0245 | 3014 | 0.071762 | 1.362 | A04 | MICL0.01933042/RON
Build-In Floor | Mini Canal | MICL.01933042/ROV | 19 | 330 | 42 | 42 | 2646 | 2646 | 2646 | 0.063 | 1029 | 0.0245 | 3014 | 0.071762 | 1.362 | A04 | MICL0.01933042/ROV
Build-In Floor | Mini Canal | MICL.01933042/RSS | 19 | 330 | 42 | 42 | 2619 | 2619 | 2619 | 0.062357 | 1019 | 0.024262 | 2983 | 0.071024 | 1.362 | A04 | MICL0.01933042/RSS
Build-In Floor | Mini Canal | MICL.01933042/SBL | 19 | 330 | 42 | 42 | 2728 | 2728 | 2728 | 0.064952 | 1061 | 0.025262 | 3107 | 0.073976 | 1.362 | A04 | MICL0.01933042/SBL
Build-In Floor | Mini Canal | MICL.01933042/SBR | 19 | 330 | 42 | 42 | 2728 | 2728 | 2728 | 0.064952 | 1061 | 0.025262 | 3107 | 0.073976 | 1.362 | A04 | MICL0.01933042/SBR
Build-In Floor | Mini Canal | MICL.01933042/SDB | 19 | 330 | 42 | 42 | 2728 | 2728 | 2728 | 0.064952 | 1061 | 0.025262 | 3107 | 0.073976 | 1.362 | A04 | MICL0.01933042/SDB
Build-In Floor | Mini Canal | MICL.01933042/SNA | 19 | 330 | 42 | 42 | 2728 | 2728 | 2728 | 0.064952 | 1061 | 0.025262 | 3107 | 0.073976 | 1.362 | A04 | MICL0.01933042/SNA
Build-In Floor | Mini Canal | MICL.01933042/SNC | 19 | 330 | 42 | 42 | 2728 | 2728 | 2728 | 0.064952 | 1061 | 0.025262 | 3107 | 0.073976 | 1.362 | A04 | MICL0.01933042/SNC
Build-In Floor | Mini Canal | MICL.01935026/ANA | 19 | 350 | 26 | 26 | 1174 | 1174 | 1174 | 0.027952 | 457 | 0.010881 | 1337 | 0.031833 | 1.362 | A04 | MICL0.01935026/ANA
Build-In Floor | Mini Canal | MICL.01935026/DBL | 19 | 350 | 26 | 26 | 1518 | 1518 | 1518 | 0.036143 | 591 | 0.014071 | 1729 | 0.041167 | 1.362 | A04 | MICL0.01935026/DBL
Build-In Floor | Mini Canal | MICL.01935026/DBN | 19 | 350 | 26 | 26 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01935026/DBN
Build-In Floor | Mini Canal | MICL.01935026/DBR | 19 | 350 | 26 | 26 | 1518 | 1518 | 1518 | 0.036143 | 591 | 0.014071 | 1729 | 0.041167 | 1.362 | A04 | MICL0.01935026/DBR
Build-In Floor | Mini Canal | MICL.01935026/DBV | 19 | 350 | 26 | 26 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01935026/DBV
Build-In Floor | Mini Canal | MICL.01935026/DDB | 19 | 350 | 26 | 26 | 1518 | 1518 | 1518 | 0.036143 | 591 | 0.014071 | 1729 | 0.041167 | 1.362 | A04 | MICL0.01935026/DDB
Build-In Floor | Mini Canal | MICL.01935026/DMN | 19 | 350 | 26 | 26 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01935026/DMN
Build-In Floor | Mini Canal | MICL.01935026/DMV | 19 | 350 | 26 | 26 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01935026/DMV
Build-In Floor | Mini Canal | MICL.01935026/DNA | 19 | 350 | 26 | 26 | 1518 | 1518 | 1518 | 0.036143 | 591 | 0.014071 | 1729 | 0.041167 | 1.362 | A04 | MICL0.01935026/DNA
Build-In Floor | Mini Canal | MICL.01935026/DNC | 19 | 350 | 26 | 26 | 1518 | 1518 | 1518 | 0.036143 | 591 | 0.014071 | 1729 | 0.041167 | 1.362 | A04 | MICL0.01935026/DNC
Build-In Floor | Mini Canal | MICL.01935026/DON | 19 | 350 | 26 | 26 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01935026/DON
Build-In Floor | Mini Canal | MICL.01935026/DOV | 19 | 350 | 26 | 26 | 1455 | 1455 | 1455 | 0.034643 | 566 | 0.013476 | 1657 | 0.039452 | 1.362 | A04 | MICL0.01935026/DOV
Build-In Floor | Mini Canal | MICL.01935026/PNC | 19 | 350 | 26 | 26 | 1330 | 1330 | 1330 | 0.031667 | 517 | 0.01231 | 1515 | 0.036071 | 1.362 | A04 | MICL0.01935026/PNC
Build-In Floor | Mini Canal | MICL.01935026/RBL | 19 | 350 | 26 | 26 | 1565 | 1565 | 1565 | 0.037262 | 609 | 0.0145 | 1783 | 0.042452 | 1.362 | A04 | MICL0.01935026/RBL
Build-In Floor | Mini Canal | MICL.01935026/RBN | 19 | 350 | 26 | 26 | 1518 | 1518 | 1518 | 0.036143 | 591 | 0.014071 | 1729 | 0.041167 | 1.362 | A04 | MICL0.01935026/RBN
Build-In Floor | Mini Canal | MICL.01935026/RBR | 19 | 350 | 26 | 26 | 1565 | 1565 | 1565 | 0.037262 | 609 | 0.0145 | 1783 | 0.042452 | 1.362 | A04 | MICL0.01935026/RBR
Build-In Floor | Mini Canal | MICL.01935026/RBV | 19 | 350 | 26 | 26 | 1518 | 1518 | 1518 | 0.036143 | 591 | 0.014071 | 1729 | 0.041167 | 1.362 | A04 | MICL0.01935026/RBV
Build-In Floor | Mini Canal | MICL.01935026/RDB | 19 | 350 | 26 | 26 | 1565 | 1565 | 1565 | 0.037262 | 609 | 0.0145 | 1783 | 0.042452 | 1.362 | A04 | MICL0.01935026/RDB
Build-In Floor | Mini Canal | MICL.01935026/RMN | 19 | 350 | 26 | 26 | 1518 | 1518 | 1518 | 0.036143 | 591 | 0.014071 | 1729 | 0.041167 | 1.362 | A04 | MICL0.01935026/RMN
Build-In Floor | Mini Canal | MICL.01935026/RMV | 19 | 350 | 26 | 26 | 1518 | 1518 | 1518 | 0.036143 | 591 | 0.014071 | 1729 | 0.041167 | 1.362 | A04 | MICL0.01935026/RMV
Build-In Floor | Mini Canal | MICL.01935026/RNA | 19 | 350 | 26 | 26 | 1565 | 1565 | 1565 | 0.037262 | 609 | 0.0145 | 1783 | 0.042452 | 1.362 | A04 | MICL0.01935026/RNA
Build-In Floor | Mini Canal | MICL.01935026/RON | 19 | 350 | 26 | 26 | 1518 | 1518 | 1518 | 0.036143 | 591 | 0.014071 | 1729 | 0.041167 | 1.362 | A04 | MICL0.01935026/RON
Build-In Floor | Mini Canal | MICL.01935026/ROV | 19 | 350 | 26 | 26 | 1518 | 1518 | 1518 | 0.036143 | 591 | 0.014071 | 1729 | 0.041167 | 1.362 | A04 | MICL0.01935026/ROV
Build-In Floor | Mini Canal | MICL.01935026/RSS | 19 | 350 | 26 | 26 | 1502 | 1502 | 1502 | 0.035762 | 584 | 0.013905 | 1711 | 0.040738 | 1.362 | A04 | MICL0.01935026/RSS
Build-In Floor | Mini Canal | MICL.01935026/SBL | 19 | 350 | 26 | 26 | 1565 | 1565 | 1565 | 0.037262 | 609 | 0.0145 | 1783 | 0.042452 | 1.362 | A04 | MICL0.01935026/SBL
Build-In Floor | Mini Canal | MICL.01935026/SBR | 19 | 350 | 26 | 26 | 1565 | 1565 | 1565 | 0.037262 | 609 | 0.0145 | 1783 | 0.042452 | 1.362 | A04 | MICL0.01935026/SBR
Build-In Floor | Mini Canal | MICL.01935026/SDB | 19 | 350 | 26 | 26 | 1565 | 1565 | 1565 | 0.037262 | 609 | 0.0145 | 1783 | 0.042452 | 1.362 | A04 | MICL0.01935026/SDB
Build-In Floor | Mini Canal | MICL.01935026/SNA | 19 | 350 | 26 | 26 | 1565 | 1565 | 1565 | 0.037262 | 609 | 0.0145 | 1783 | 0.042452 | 1.362 | A04 | MICL0.01935026/SNA
Build-In Floor | Mini Canal | MICL.01935026/SNC | 19 | 350 | 26 | 26 | 1565 | 1565 | 1565 | 0.037262 | 609 | 0.0145 | 1783 | 0.042452 | 1.362 | A04 | MICL0.01935026/SNC
Build-In Floor | Mini Canal | MICL.01935034/ANA | 19 | 350 | 34 | 34 | 1589 | 1589 | 1589 | 0.037833 | 618 | 0.014714 | 1810 | 0.043095 | 1.362 | A04 | MICL0.01935034/ANA
Build-In Floor | Mini Canal | MICL.01935034/DBL | 19 | 350 | 34 | 34 | 2055 | 2055 | 2055 | 0.048929 | 799 | 0.019024 | 2341 | 0.055738 | 1.362 | A04 | MICL0.01935034/DBL
Build-In Floor | Mini Canal | MICL.01935034/DBN | 19 | 350 | 34 | 34 | 1971 | 1971 | 1971 | 0.046929 | 767 | 0.018262 | 2245 | 0.053452 | 1.362 | A04 | MICL0.01935034/DBN
Build-In Floor | Mini Canal | MICL.01935034/DBR | 19 | 350 | 34 | 34 | 2055 | 2055 | 2055 | 0.048929 | 799 | 0.019024 | 2341 | 0.055738 | 1.362 | A04 | MICL0.01935034/DBR
Build-In Floor | Mini Canal | MICL.01935034/DBV | 19 | 350 | 34 | 34 | 1971 | 1971 | 1971 | 0.046929 | 767 | 0.018262 | 2245 | 0.053452 | 1.362 | A04 | MICL0.01935034/DBV
Build-In Floor | Mini Canal | MICL.01935034/DDB | 19 | 350 | 34 | 34 | 2055 | 2055 | 2055 | 0.048929 | 799 | 0.019024 | 2341 | 0.055738 | 1.362 | A04 | MICL0.01935034/DDB
Build-In Floor | Mini Canal | MICL.01935034/DMN | 19 | 350 | 34 | 34 | 1971 | 1971 | 1971 | 0.046929 | 767 | 0.018262 | 2245 | 0.053452 | 1.362 | A04 | MICL0.01935034/DMN
Build-In Floor | Mini Canal | MICL.01935034/DMV | 19 | 350 | 34 | 34 | 1971 | 1971 | 1971 | 0.046929 | 767 | 0.018262 | 2245 | 0.053452 | 1.362 | A04 | MICL0.01935034/DMV
Build-In Floor | Mini Canal | MICL.01935034/DNA | 19 | 350 | 34 | 34 | 2055 | 2055 | 2055 | 0.048929 | 799 | 0.019024 | 2341 | 0.055738 | 1.362 | A04 | MICL0.01935034/DNA
Build-In Floor | Mini Canal | MICL.01935034/DNC | 19 | 350 | 34 | 34 | 2055 | 2055 | 2055 | 0.048929 | 799 | 0.019024 | 2341 | 0.055738 | 1.362 | A04 | MICL0.01935034/DNC
Build-In Floor | Mini Canal | MICL.01935034/DON | 19 | 350 | 34 | 34 | 1971 | 1971 | 1971 | 0.046929 | 767 | 0.018262 | 2245 | 0.053452 | 1.362 | A04 | MICL0.01935034/DON
Build-In Floor | Mini Canal | MICL.01935034/DOV | 19 | 350 | 34 | 34 | 1971 | 1971 | 1971 | 0.046929 | 767 | 0.018262 | 2245 | 0.053452 | 1.362 | A04 | MICL0.01935034/DOV
Build-In Floor | Mini Canal | MICL.01935034/PNC | 19 | 350 | 34 | 34 | 1801 | 1801 | 1801 | 0.042881 | 701 | 0.01669 | 2051 | 0.048833 | 1.362 | A04 | MICL0.01935034/PNC
Build-In Floor | Mini Canal | MICL.01935034/RBL | 19 | 350 | 34 | 34 | 2119 | 2119 | 2119 | 0.050452 | 824 | 0.019619 | 2414 | 0.057476 | 1.362 | A04 | MICL0.01935034/RBL
Build-In Floor | Mini Canal | MICL.01935034/RBN | 19 | 350 | 34 | 34 | 2055 | 2055 | 2055 | 0.048929 | 799 | 0.019024 | 2341 | 0.055738 | 1.362 | A04 | MICL0.01935034/RBN
Build-In Floor | Mini Canal | MICL.01935034/RBR | 19 | 350 | 34 | 34 | 2119 | 2119 | 2119 | 0.050452 | 824 | 0.019619 | 2414 | 0.057476 | 1.362 | A04 | MICL0.01935034/RBR
Build-In Floor | Mini Canal | MICL.01935034/RBV | 19 | 350 | 34 | 34 | 2055 | 2055 | 2055 | 0.048929 | 799 | 0.019024 | 2341 | 0.055738 | 1.362 | A04 | MICL0.01935034/RBV
Build-In Floor | Mini Canal | MICL.01935034/RDB | 19 | 350 | 34 | 34 | 2119 | 2119 | 2119 | 0.050452 | 824 | 0.019619 | 2414 | 0.057476 | 1.362 | A04 | MICL0.01935034/RDB
Build-In Floor | Mini Canal | MICL.01935034/RMN | 19 | 350 | 34 | 34 | 2055 | 2055 | 2055 | 0.048929 | 799 | 0.019024 | 2341 | 0.055738 | 1.362 | A04 | MICL0.01935034/RMN
Build-In Floor | Mini Canal | MICL.01935034/RMV | 19 | 350 | 34 | 34 | 2055 | 2055 | 2055 | 0.048929 | 799 | 0.019024 | 2341 | 0.055738 | 1.362 | A04 | MICL0.01935034/RMV
Build-In Floor | Mini Canal | MICL.01935034/RNA | 19 | 350 | 34 | 34 | 2119 | 2119 | 2119 | 0.050452 | 824 | 0.019619 | 2414 | 0.057476 | 1.362 | A04 | MICL0.01935034/RNA
Build-In Floor | Mini Canal | MICL.01935034/RON | 19 | 350 | 34 | 34 | 2055 | 2055 | 2055 | 0.048929 | 799 | 0.019024 | 2341 | 0.055738 | 1.362 | A04 | MICL0.01935034/RON
Build-In Floor | Mini Canal | MICL.01935034/ROV | 19 | 350 | 34 | 34 | 2055 | 2055 | 2055 | 0.048929 | 799 | 0.019024 | 2341 | 0.055738 | 1.362 | A04 | MICL0.01935034/ROV
Build-In Floor | Mini Canal | MICL.01935034/RSS | 19 | 350 | 34 | 34 | 2034 | 2034 | 2034 | 0.048429 | 791 | 0.018833 | 2317 | 0.055167 | 1.362 | A04 | MICL0.01935034/RSS
Build-In Floor | Mini Canal | MICL.01935034/SBL | 19 | 350 | 34 | 34 | 2119 | 2119 | 2119 | 0.050452 | 824 | 0.019619 | 2414 | 0.057476 | 1.362 | A04 | MICL0.01935034/SBL
Build-In Floor | Mini Canal | MICL.01935034/SBR | 19 | 350 | 34 | 34 | 2119 | 2119 | 2119 | 0.050452 | 824 | 0.019619 | 2414 | 0.057476 | 1.362 | A04 | MICL0.01935034/SBR
Build-In Floor | Mini Canal | MICL.01935034/SDB | 19 | 350 | 34 | 34 | 2119 | 2119 | 2119 | 0.050452 | 824 | 0.019619 | 2414 | 0.057476 | 1.362 | A04 | MICL0.01935034/SDB
Build-In Floor | Mini Canal | MICL.01935034/SNA | 19 | 350 | 34 | 34 | 2119 | 2119 | 2119 | 0.050452 | 824 | 0.019619 | 2414 | 0.057476 | 1.362 | A04 | MICL0.01935034/SNA
Build-In Floor | Mini Canal | MICL.01935034/SNC | 19 | 350 | 34 | 34 | 2119 | 2119 | 2119 | 0.050452 | 824 | 0.019619 | 2414 | 0.057476 | 1.362 | A04 | MICL0.01935034/SNC
Build-In Floor | Mini Canal | MICL.01935042/ANA | 19 | 350 | 42 | 42 | 2183 | 2183 | 2183 | 0.051976 | 849 | 0.020214 | 2486 | 0.05919 | 1.362 | A04 | MICL0.01935042/ANA
Build-In Floor | Mini Canal | MICL.01935042/DBL | 19 | 350 | 42 | 42 | 2823 | 2823 | 2823 | 0.067214 | 1098 | 0.026143 | 3215 | 0.076548 | 1.362 | A04 | MICL0.01935042/DBL
Build-In Floor | Mini Canal | MICL.01935042/DBN | 19 | 350 | 42 | 42 | 2706 | 2706 | 2706 | 0.064429 | 1053 | 0.025071 | 3082 | 0.073381 | 1.362 | A04 | MICL0.01935042/DBN
Build-In Floor | Mini Canal | MICL.01935042/DBR | 19 | 350 | 42 | 42 | 2823 | 2823 | 2823 | 0.067214 | 1098 | 0.026143 | 3215 | 0.076548 | 1.362 | A04 | MICL0.01935042/DBR
Build-In Floor | Mini Canal | MICL.01935042/DBV | 19 | 350 | 42 | 42 | 2706 | 2706 | 2706 | 0.064429 | 1053 | 0.025071 | 3082 | 0.073381 | 1.362 | A04 | MICL0.01935042/DBV
Build-In Floor | Mini Canal | MICL.01935042/DDB | 19 | 350 | 42 | 42 | 2823 | 2823 | 2823 | 0.067214 | 1098 | 0.026143 | 3215 | 0.076548 | 1.362 | A04 | MICL0.01935042/DDB
Build-In Floor | Mini Canal | MICL.01935042/DMN | 19 | 350 | 42 | 42 | 2706 | 2706 | 2706 | 0.064429 | 1053 | 0.025071 | 3082 | 0.073381 | 1.362 | A04 | MICL0.01935042/DMN
Build-In Floor | Mini Canal | MICL.01935042/DMV | 19 | 350 | 42 | 42 | 2706 | 2706 | 2706 | 0.064429 | 1053 | 0.025071 | 3082 | 0.073381 | 1.362 | A04 | MICL0.01935042/DMV
Build-In Floor | Mini Canal | MICL.01935042/DNA | 19 | 350 | 42 | 42 | 2823 | 2823 | 2823 | 0.067214 | 1098 | 0.026143 | 3215 | 0.076548 | 1.362 | A04 | MICL0.01935042/DNA
Build-In Floor | Mini Canal | MICL.01935042/DNC | 19 | 350 | 42 | 42 | 2823 | 2823 | 2823 | 0.067214 | 1098 | 0.026143 | 3215 | 0.076548 | 1.362 | A04 | MICL0.01935042/DNC
Build-In Floor | Mini Canal | MICL.01935042/DON | 19 | 350 | 42 | 42 | 2706 | 2706 | 2706 | 0.064429 | 1053 | 0.025071 | 3082 | 0.073381 | 1.362 | A04 | MICL0.01935042/DON
Build-In Floor | Mini Canal | MICL.01935042/DOV | 19 | 350 | 42 | 42 | 2706 | 2706 | 2706 | 0.064429 | 1053 | 0.025071 | 3082 | 0.073381 | 1.362 | A04 | MICL0.01935042/DOV
Build-In Floor | Mini Canal | MICL.01935042/PNC | 19 | 350 | 42 | 42 | 2474 | 2474 | 2474 | 0.058905 | 962 | 0.022905 | 2818 | 0.067095 | 1.362 | A04 | MICL0.01935042/PNC
Build-In Floor | Mini Canal | MICL.01935042/RBL | 19 | 350 | 42 | 42 | 2910 | 2910 | 2910 | 0.069286 | 1132 | 0.026952 | 3314 | 0.078905 | 1.362 | A04 | MICL0.01935042/RBL
Build-In Floor | Mini Canal | MICL.01935042/RBN | 19 | 350 | 42 | 42 | 2823 | 2823 | 2823 | 0.067214 | 1098 | 0.026143 | 3215 | 0.076548 | 1.362 | A04 | MICL0.01935042/RBN
Build-In Floor | Mini Canal | MICL.01935042/RBR | 19 | 350 | 42 | 42 | 2910 | 2910 | 2910 | 0.069286 | 1132 | 0.026952 | 3314 | 0.078905 | 1.362 | A04 | MICL0.01935042/RBR
Build-In Floor | Mini Canal | MICL.01935042/RBV | 19 | 350 | 42 | 42 | 2823 | 2823 | 2823 | 0.067214 | 1098 | 0.026143 | 3215 | 0.076548 | 1.362 | A04 | MICL0.01935042/RBV
Build-In Floor | Mini Canal | MICL.01935042/RDB | 19 | 350 | 42 | 42 | 2910 | 2910 | 2910 | 0.069286 | 1132 | 0.026952 | 3314 | 0.078905 | 1.362 | A04 | MICL0.01935042/RDB
Build-In Floor | Mini Canal | MICL.01935042/RMN | 19 | 350 | 42 | 42 | 2823 | 2823 | 2823 | 0.067214 | 1098 | 0.026143 | 3215 | 0.076548 | 1.362 | A04 | MICL0.01935042/RMN
Build-In Floor | Mini Canal | MICL.01935042/RMV | 19 | 350 | 42 | 42 | 2823 | 2823 | 2823 | 0.067214 | 1098 | 0.026143 | 3215 | 0.076548 | 1.362 | A04 | MICL0.01935042/RMV
Build-In Floor | Mini Canal | MICL.01935042/RNA | 19 | 350 | 42 | 42 | 2910 | 2910 | 2910 | 0.069286 | 1132 | 0.026952 | 3314 | 0.078905 | 1.362 | A04 | MICL0.01935042/RNA
Build-In Floor | Mini Canal | MICL.01935042/RON | 19 | 350 | 42 | 42 | 2823 | 2823 | 2823 | 0.067214 | 1098 | 0.026143 | 3215 | 0.076548 | 1.362 | A04 | MICL0.01935042/RON
Build-In Floor | Mini Canal | MICL.01935042/ROV | 19 | 350 | 42 | 42 | 2823 | 2823 | 2823 | 0.067214 | 1098 | 0.026143 | 3215 | 0.076548 | 1.362 | A04 | MICL0.01935042/ROV
Build-In Floor | Mini Canal | MICL.01935042/RSS | 19 | 350 | 42 | 42 | 2794 | 2794 | 2794 | 0.066524 | 1087 | 0.025881 | 3182 | 0.075762 | 1.362 | A04 | MICL0.01935042/RSS
Build-In Floor | Mini Canal | MICL.01935042/SBL | 19 | 350 | 42 | 42 | 2910 | 2910 | 2910 | 0.069286 | 1132 | 0.026952 | 3314 | 0.078905 | 1.362 | A04 | MICL0.01935042/SBL
Build-In Floor | Mini Canal | MICL.01935042/SBR | 19 | 350 | 42 | 42 | 2910 | 2910 | 2910 | 0.069286 | 1132 | 0.026952 | 3314 | 0.078905 | 1.362 | A04 | MICL0.01935042/SBR
Build-In Floor | Mini Canal | MICL.01935042/SDB | 19 | 350 | 42 | 42 | 2910 | 2910 | 2910 | 0.069286 | 1132 | 0.026952 | 3314 | 0.078905 | 1.362 | A04 | MICL0.01935042/SDB
Build-In Floor | Mini Canal | MICL.01935042/SNA | 19 | 350 | 42 | 42 | 2910 | 2910 | 2910 | 0.069286 | 1132 | 0.026952 | 3314 | 0.078905 | 1.362 | A04 | MICL0.01935042/SNA
Build-In Floor | Mini Canal | MICL.01935042/SNC | 19 | 350 | 42 | 42 | 2910 | 2910 | 2910 | 0.069286 | 1132 | 0.026952 | 3314 | 0.078905 | 1.362 | A04 | MICL0.01935042/SNC
Build-In Floor | Mini Canal | MICL.01937026/ANA | 19 | 370 | 26 | 26 | 1247 | 1247 | 1247 | 0.02969 | 485 | 0.011548 | 1420 | 0.03381 | 1.362 | A04 | MICL0.01937026/ANA
Build-In Floor | Mini Canal | MICL.01937026/DBL | 19 | 370 | 26 | 26 | 1613 | 1613 | 1613 | 0.038405 | 627 | 0.014929 | 1837 | 0.043738 | 1.362 | A04 | MICL0.01937026/DBL
Build-In Floor | Mini Canal | MICL.01937026/DBN | 19 | 370 | 26 | 26 | 1547 | 1547 | 1547 | 0.036833 | 602 | 0.014333 | 1762 | 0.041952 | 1.362 | A04 | MICL0.01937026/DBN
Build-In Floor | Mini Canal | MICL.01937026/DBR | 19 | 370 | 26 | 26 | 1613 | 1613 | 1613 | 0.038405 | 627 | 0.014929 | 1837 | 0.043738 | 1.362 | A04 | MICL0.01937026/DBR
Build-In Floor | Mini Canal | MICL.01937026/DBV | 19 | 370 | 26 | 26 | 1547 | 1547 | 1547 | 0.036833 | 602 | 0.014333 | 1762 | 0.041952 | 1.362 | A04 | MICL0.01937026/DBV
Build-In Floor | Mini Canal | MICL.01937026/DDB | 19 | 370 | 26 | 26 | 1613 | 1613 | 1613 | 0.038405 | 627 | 0.014929 | 1837 | 0.043738 | 1.362 | A04 | MICL0.01937026/DDB
Build-In Floor | Mini Canal | MICL.01937026/DMN | 19 | 370 | 26 | 26 | 1547 | 1547 | 1547 | 0.036833 | 602 | 0.014333 | 1762 | 0.041952 | 1.362 | A04 | MICL0.01937026/DMN
Build-In Floor | Mini Canal | MICL.01937026/DMV | 19 | 370 | 26 | 26 | 1547 | 1547 | 1547 | 0.036833 | 602 | 0.014333 | 1762 | 0.041952 | 1.362 | A04 | MICL0.01937026/DMV
Build-In Floor | Mini Canal | MICL.01937026/DNA | 19 | 370 | 26 | 26 | 1613 | 1613 | 1613 | 0.038405 | 627 | 0.014929 | 1837 | 0.043738 | 1.362 | A04 | MICL0.01937026/DNA
Build-In Floor | Mini Canal | MICL.01937026/DNC | 19 | 370 | 26 | 26 | 1613 | 1613 | 1613 | 0.038405 | 627 | 0.014929 | 1837 | 0.043738 | 1.362 | A04 | MICL0.01937026/DNC
Build-In Floor | Mini Canal | MICL.01937026/DON | 19 | 370 | 26 | 26 | 1547 | 1547 | 1547 | 0.036833 | 602 | 0.014333 | 1762 | 0.041952 | 1.362 | A04 | MICL0.01937026/DON
Build-In Floor | Mini Canal | MICL.01937026/DOV | 19 | 370 | 26 | 26 | 1547 | 1547 | 1547 | 0.036833 | 602 | 0.014333 | 1762 | 0.041952 | 1.362 | A04 | MICL0.01937026/DOV
Build-In Floor | Mini Canal | MICL.01937026/PNC | 19 | 370 | 26 | 26 | 1414 | 1414 | 1414 | 0.033667 | 550 | 0.013095 | 1611 | 0.038357 | 1.362 | A04 | MICL0.01937026/PNC
Build-In Floor | Mini Canal | MICL.01937026/RBL | 19 | 370 | 26 | 26 | 1663 | 1663 | 1663 | 0.039595 | 647 | 0.015405 | 1894 | 0.045095 | 1.362 | A04 | MICL0.01937026/RBL
Build-In Floor | Mini Canal | MICL.01937026/RBN | 19 | 370 | 26 | 26 | 1613 | 1613 | 1613 | 0.038405 | 627 | 0.014929 | 1837 | 0.043738 | 1.362 | A04 | MICL0.01937026/RBN
Build-In Floor | Mini Canal | MICL.01937026/RBR | 19 | 370 | 26 | 26 | 1663 | 1663 | 1663 | 0.039595 | 647 | 0.015405 | 1894 | 0.045095 | 1.362 | A04 | MICL0.01937026/RBR
Build-In Floor | Mini Canal | MICL.01937026/RBV | 19 | 370 | 26 | 26 | 1613 | 1613 | 1613 | 0.038405 | 627 | 0.014929 | 1837 | 0.043738 | 1.362 | A04 | MICL0.01937026/RBV
Build-In Floor | Mini Canal | MICL.01937026/RDB | 19 | 370 | 26 | 26 | 1663 | 1663 | 1663 | 0.039595 | 647 | 0.015405 | 1894 | 0.045095 | 1.362 | A04 | MICL0.01937026/RDB
Build-In Floor | Mini Canal | MICL.01937026/RMN | 19 | 370 | 26 | 26 | 1613 | 1613 | 1613 | 0.038405 | 627 | 0.014929 | 1837 | 0.043738 | 1.362 | A04 | MICL0.01937026/RMN
Build-In Floor | Mini Canal | MICL.01937026/RMV | 19 | 370 | 26 | 26 | 1613 | 1613 | 1613 | 0.038405 | 627 | 0.014929 | 1837 | 0.043738 | 1.362 | A04 | MICL0.01937026/RMV
Build-In Floor | Mini Canal | MICL.01937026/RNA | 19 | 370 | 26 | 26 | 1663 | 1663 | 1663 | 0.039595 | 647 | 0.015405 | 1894 | 0.045095 | 1.362 | A04 | MICL0.01937026/RNA
Build-In Floor | Mini Canal | MICL.01937026/RON | 19 | 370 | 26 | 26 | 1613 | 1613 | 1613 | 0.038405 | 627 | 0.014929 | 1837 | 0.043738 | 1.362 | A04 | MICL0.01937026/RON
Build-In Floor | Mini Canal | MICL.01937026/ROV | 19 | 370 | 26 | 26 | 1613 | 1613 | 1613 | 0.038405 | 627 | 0.014929 | 1837 | 0.043738 | 1.362 | A04 | MICL0.01937026/ROV
Build-In Floor | Mini Canal | MICL.01937026/RSS | 19 | 370 | 26 | 26 | 1596 | 1596 | 1596 | 0.038 | 621 | 0.014786 | 1818 | 0.043286 | 1.362 | A04 | MICL0.01937026/RSS
Build-In Floor | Mini Canal | MICL.01937026/SBL | 19 | 370 | 26 | 26 | 1663 | 1663 | 1663 | 0.039595 | 647 | 0.015405 | 1894 | 0.045095 | 1.362 | A04 | MICL0.01937026/SBL
Build-In Floor | Mini Canal | MICL.01937026/SBR | 19 | 370 | 26 | 26 | 1663 | 1663 | 1663 | 0.039595 | 647 | 0.015405 | 1894 | 0.045095 | 1.362 | A04 | MICL0.01937026/SBR
Build-In Floor | Mini Canal | MICL.01937026/SDB | 19 | 370 | 26 | 26 | 1663 | 1663 | 1663 | 0.039595 | 647 | 0.015405 | 1894 | 0.045095 | 1.362 | A04 | MICL0.01937026/SDB
Build-In Floor | Mini Canal | MICL.01937026/SNA | 19 | 370 | 26 | 26 | 1663 | 1663 | 1663 | 0.039595 | 647 | 0.015405 | 1894 | 0.045095 | 1.362 | A04 | MICL0.01937026/SNA
Build-In Floor | Mini Canal | MICL.01937026/SNC | 19 | 370 | 26 | 26 | 1663 | 1663 | 1663 | 0.039595 | 647 | 0.015405 | 1894 | 0.045095 | 1.362 | A04 | MICL0.01937026/SNC
Build-In Floor | Mini Canal | MICL.01937034/ANA | 19 | 370 | 34 | 34 | 1689 | 1689 | 1689 | 0.040214 | 657 | 0.015643 | 1924 | 0.04581 | 1.362 | A04 | MICL0.01937034/ANA
Build-In Floor | Mini Canal | MICL.01937034/DBL | 19 | 370 | 34 | 34 | 2184 | 2184 | 2184 | 0.052 | 850 | 0.020238 | 2488 | 0.059238 | 1.362 | A04 | MICL0.01937034/DBL
Build-In Floor | Mini Canal | MICL.01937034/DBN | 19 | 370 | 34 | 34 | 2094 | 2094 | 2094 | 0.049857 | 815 | 0.019405 | 2385 | 0.056786 | 1.362 | A04 | MICL0.01937034/DBN
Build-In Floor | Mini Canal | MICL.01937034/DBR | 19 | 370 | 34 | 34 | 2184 | 2184 | 2184 | 0.052 | 850 | 0.020238 | 2488 | 0.059238 | 1.362 | A04 | MICL0.01937034/DBR
Build-In Floor | Mini Canal | MICL.01937034/DBV | 19 | 370 | 34 | 34 | 2094 | 2094 | 2094 | 0.049857 | 815 | 0.019405 | 2385 | 0.056786 | 1.362 | A04 | MICL0.01937034/DBV
Build-In Floor | Mini Canal | MICL.01937034/DDB | 19 | 370 | 34 | 34 | 2184 | 2184 | 2184 | 0.052 | 850 | 0.020238 | 2488 | 0.059238 | 1.362 | A04 | MICL0.01937034/DDB
Build-In Floor | Mini Canal | MICL.01937034/DMN | 19 | 370 | 34 | 34 | 2094 | 2094 | 2094 | 0.049857 | 815 | 0.019405 | 2385 | 0.056786 | 1.362 | A04 | MICL0.01937034/DMN
Build-In Floor | Mini Canal | MICL.01937034/DMV | 19 | 370 | 34 | 34 | 2094 | 2094 | 2094 | 0.049857 | 815 | 0.019405 | 2385 | 0.056786 | 1.362 | A04 | MICL0.01937034/DMV
Build-In Floor | Mini Canal | MICL.01937034/DNA | 19 | 370 | 34 | 34 | 2184 | 2184 | 2184 | 0.052 | 850 | 0.020238 | 2488 | 0.059238 | 1.362 | A04 | MICL0.01937034/DNA
Build-In Floor | Mini Canal | MICL.01937034/DNC | 19 | 370 | 34 | 34 | 2184 | 2184 | 2184 | 0.052 | 850 | 0.020238 | 2488 | 0.059238 | 1.362 | A04 | MICL0.01937034/DNC
Build-In Floor | Mini Canal | MICL.01937034/DON | 19 | 370 | 34 | 34 | 2094 | 2094 | 2094 | 0.049857 | 815 | 0.019405 | 2385 | 0.056786 | 1.362 | A04 | MICL0.01937034/DON
Build-In Floor | Mini Canal | MICL.01937034/DOV | 19 | 370 | 34 | 34 | 2094 | 2094 | 2094 | 0.049857 | 815 | 0.019405 | 2385 | 0.056786 | 1.362 | A04 | MICL0.01937034/DOV
Build-In Floor | Mini Canal | MICL.01937034/PNC | 19 | 370 | 34 | 34 | 1914 | 1914 | 1914 | 0.045571 | 745 | 0.017738 | 2180 | 0.051905 | 1.362 | A04 | MICL0.01937034/PNC
Build-In Floor | Mini Canal | MICL.01937034/RBL | 19 | 370 | 34 | 34 | 2252 | 2252 | 2252 | 0.053619 | 876 | 0.020857 | 2565 | 0.061071 | 1.362 | A04 | MICL0.01937034/RBL
Build-In Floor | Mini Canal | MICL.01937034/RBN | 19 | 370 | 34 | 34 | 2184 | 2184 | 2184 | 0.052 | 850 | 0.020238 | 2488 | 0.059238 | 1.362 | A04 | MICL0.01937034/RBN
Build-In Floor | Mini Canal | MICL.01937034/RBR | 19 | 370 | 34 | 34 | 2252 | 2252 | 2252 | 0.053619 | 876 | 0.020857 | 2565 | 0.061071 | 1.362 | A04 | MICL0.01937034/RBR
Build-In Floor | Mini Canal | MICL.01937034/RBV | 19 | 370 | 34 | 34 | 2184 | 2184 | 2184 | 0.052 | 850 | 0.020238 | 2488 | 0.059238 | 1.362 | A04 | MICL0.01937034/RBV
Build-In Floor | Mini Canal | MICL.01937034/RDB | 19 | 370 | 34 | 34 | 2252 | 2252 | 2252 | 0.053619 | 876 | 0.020857 | 2565 | 0.061071 | 1.362 | A04 | MICL0.01937034/RDB
Build-In Floor | Mini Canal | MICL.01937034/RMN | 19 | 370 | 34 | 34 | 2184 | 2184 | 2184 | 0.052 | 850 | 0.020238 | 2488 | 0.059238 | 1.362 | A04 | MICL0.01937034/RMN
Build-In Floor | Mini Canal | MICL.01937034/RMV | 19 | 370 | 34 | 34 | 2184 | 2184 | 2184 | 0.052 | 850 | 0.020238 | 2488 | 0.059238 | 1.362 | A04 | MICL0.01937034/RMV
Build-In Floor | Mini Canal | MICL.01937034/RNA | 19 | 370 | 34 | 34 | 2252 | 2252 | 2252 | 0.053619 | 876 | 0.020857 | 2565 | 0.061071 | 1.362 | A04 | MICL0.01937034/RNA
Build-In Floor | Mini Canal | MICL.01937034/RON | 19 | 370 | 34 | 34 | 2184 | 2184 | 2184 | 0.052 | 850 | 0.020238 | 2488 | 0.059238 | 1.362 | A04 | MICL0.01937034/RON
Build-In Floor | Mini Canal | MICL.01937034/ROV | 19 | 370 | 34 | 34 | 2184 | 2184 | 2184 | 0.052 | 850 | 0.020238 | 2488 | 0.059238 | 1.362 | A04 | MICL0.01937034/ROV
Build-In Floor | Mini Canal | MICL.01937034/RSS | 19 | 370 | 34 | 34 | 2162 | 2162 | 2162 | 0.051476 | 841 | 0.020024 | 2463 | 0.058643 | 1.362 | A04 | MICL0.01937034/RSS
Build-In Floor | Mini Canal | MICL.01937034/SBL | 19 | 370 | 34 | 34 | 2252 | 2252 | 2252 | 0.053619 | 876 | 0.020857 | 2565 | 0.061071 | 1.362 | A04 | MICL0.01937034/SBL
Build-In Floor | Mini Canal | MICL.01937034/SBR | 19 | 370 | 34 | 34 | 2252 | 2252 | 2252 | 0.053619 | 876 | 0.020857 | 2565 | 0.061071 | 1.362 | A04 | MICL0.01937034/SBR
Build-In Floor | Mini Canal | MICL.01937034/SDB | 19 | 370 | 34 | 34 | 2252 | 2252 | 2252 | 0.053619 | 876 | 0.020857 | 2565 | 0.061071 | 1.362 | A04 | MICL0.01937034/SDB
Build-In Floor | Mini Canal | MICL.01937034/SNA | 19 | 370 | 34 | 34 | 2252 | 2252 | 2252 | 0.053619 | 876 | 0.020857 | 2565 | 0.061071 | 1.362 | A04 | MICL0.01937034/SNA
Build-In Floor | Mini Canal | MICL.01937034/SNC | 19 | 370 | 34 | 34 | 2252 | 2252 | 2252 | 0.053619 | 876 | 0.020857 | 2565 | 0.061071 | 1.362 | A04 | MICL0.01937034/SNC
Build-In Floor | Mini Canal | MICL.01937042/ANA | 19 | 370 | 42 | 42 | 2319 | 2319 | 2319 | 0.055214 | 902 | 0.021476 | 2641 | 0.062881 | 1.362 | A04 | MICL0.01937042/ANA
Build-In Floor | Mini Canal | MICL.01937042/DBL | 19 | 370 | 42 | 42 | 2999 | 2999 | 2999 | 0.071405 | 1167 | 0.027786 | 3416 | 0.081333 | 1.362 | A04 | MICL0.01937042/DBL
Build-In Floor | Mini Canal | MICL.01937042/DBN | 19 | 370 | 42 | 42 | 2876 | 2876 | 2876 | 0.068476 | 1119 | 0.026643 | 3276 | 0.078 | 1.362 | A04 | MICL0.01937042/DBN
Build-In Floor | Mini Canal | MICL.01937042/DBR | 19 | 370 | 42 | 42 | 2999 | 2999 | 2999 | 0.071405 | 1167 | 0.027786 | 3416 | 0.081333 | 1.362 | A04 | MICL0.01937042/DBR
Build-In Floor | Mini Canal | MICL.01937042/DBV | 19 | 370 | 42 | 42 | 2876 | 2876 | 2876 | 0.068476 | 1119 | 0.026643 | 3276 | 0.078 | 1.362 | A04 | MICL0.01937042/DBV
Build-In Floor | Mini Canal | MICL.01937042/DDB | 19 | 370 | 42 | 42 | 2999 | 2999 | 2999 | 0.071405 | 1167 | 0.027786 | 3416 | 0.081333 | 1.362 | A04 | MICL0.01937042/DDB
Build-In Floor | Mini Canal | MICL.01937042/DMN | 19 | 370 | 42 | 42 | 2876 | 2876 | 2876 | 0.068476 | 1119 | 0.026643 | 3276 | 0.078 | 1.362 | A04 | MICL0.01937042/DMN
Build-In Floor | Mini Canal | MICL.01937042/DMV | 19 | 370 | 42 | 42 | 2876 | 2876 | 2876 | 0.068476 | 1119 | 0.026643 | 3276 | 0.078 | 1.362 | A04 | MICL0.01937042/DMV
Build-In Floor | Mini Canal | MICL.01937042/DNA | 19 | 370 | 42 | 42 | 2999 | 2999 | 2999 | 0.071405 | 1167 | 0.027786 | 3416 | 0.081333 | 1.362 | A04 | MICL0.01937042/DNA
Build-In Floor | Mini Canal | MICL.01937042/DNC | 19 | 370 | 42 | 42 | 2999 | 2999 | 2999 | 0.071405 | 1167 | 0.027786 | 3416 | 0.081333 | 1.362 | A04 | MICL0.01937042/DNC
Build-In Floor | Mini Canal | MICL.01937042/DON | 19 | 370 | 42 | 42 | 2876 | 2876 | 2876 | 0.068476 | 1119 | 0.026643 | 3276 | 0.078 | 1.362 | A04 | MICL0.01937042/DON
Build-In Floor | Mini Canal | MICL.01937042/DOV | 19 | 370 | 42 | 42 | 2876 | 2876 | 2876 | 0.068476 | 1119 | 0.026643 | 3276 | 0.078 | 1.362 | A04 | MICL0.01937042/DOV
Build-In Floor | Mini Canal | MICL.01937042/PNC | 19 | 370 | 42 | 42 | 2628 | 2628 | 2628 | 0.062571 | 1022 | 0.024333 | 2993 | 0.071262 | 1.362 | A04 | MICL0.01937042/PNC
Build-In Floor | Mini Canal | MICL.01937042/RBL | 19 | 370 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01937042/RBL
Build-In Floor | Mini Canal | MICL.01937042/RBN | 19 | 370 | 42 | 42 | 2999 | 2999 | 2999 | 0.071405 | 1167 | 0.027786 | 3416 | 0.081333 | 1.362 | A04 | MICL0.01937042/RBN
Build-In Floor | Mini Canal | MICL.01937042/RBR | 19 | 370 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01937042/RBR
Build-In Floor | Mini Canal | MICL.01937042/RBV | 19 | 370 | 42 | 42 | 2999 | 2999 | 2999 | 0.071405 | 1167 | 0.027786 | 3416 | 0.081333 | 1.362 | A04 | MICL0.01937042/RBV
Build-In Floor | Mini Canal | MICL.01937042/RDB | 19 | 370 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01937042/RDB
Build-In Floor | Mini Canal | MICL.01937042/RMN | 19 | 370 | 42 | 42 | 2999 | 2999 | 2999 | 0.071405 | 1167 | 0.027786 | 3416 | 0.081333 | 1.362 | A04 | MICL0.01937042/RMN
Build-In Floor | Mini Canal | MICL.01937042/RMV | 19 | 370 | 42 | 42 | 2999 | 2999 | 2999 | 0.071405 | 1167 | 0.027786 | 3416 | 0.081333 | 1.362 | A04 | MICL0.01937042/RMV
Build-In Floor | Mini Canal | MICL.01937042/RNA | 19 | 370 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01937042/RNA
Build-In Floor | Mini Canal | MICL.01937042/RON | 19 | 370 | 42 | 42 | 2999 | 2999 | 2999 | 0.071405 | 1167 | 0.027786 | 3416 | 0.081333 | 1.362 | A04 | MICL0.01937042/RON
Build-In Floor | Mini Canal | MICL.01937042/ROV | 19 | 370 | 42 | 42 | 2999 | 2999 | 2999 | 0.071405 | 1167 | 0.027786 | 3416 | 0.081333 | 1.362 | A04 | MICL0.01937042/ROV
Build-In Floor | Mini Canal | MICL.01937042/RSS | 19 | 370 | 42 | 42 | 2968 | 2968 | 2968 | 0.070667 | 1155 | 0.0275 | 3381 | 0.0805 | 1.362 | A04 | MICL0.01937042/RSS
Build-In Floor | Mini Canal | MICL.01937042/SBL | 19 | 370 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01937042/SBL
Build-In Floor | Mini Canal | MICL.01937042/SBR | 19 | 370 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01937042/SBR
Build-In Floor | Mini Canal | MICL.01937042/SDB | 19 | 370 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01937042/SDB
Build-In Floor | Mini Canal | MICL.01937042/SNA | 19 | 370 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01937042/SNA
Build-In Floor | Mini Canal | MICL.01937042/SNC | 19 | 370 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01937042/SNC
Build-In Floor | Mini Canal | MICL.01939026/ANA | 19 | 390 | 26 | 26 | 1320 | 1320 | 1320 | 0.031429 | 513 | 0.012214 | 1503 | 0.035786 | 1.362 | A04 | MICL0.01939026/ANA
Build-In Floor | Mini Canal | MICL.01939026/DBL | 19 | 390 | 26 | 26 | 1707 | 1707 | 1707 | 0.040643 | 664 | 0.01581 | 1944 | 0.046286 | 1.362 | A04 | MICL0.01939026/DBL
Build-In Floor | Mini Canal | MICL.01939026/DBN | 19 | 390 | 26 | 26 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01939026/DBN
Build-In Floor | Mini Canal | MICL.01939026/DBR | 19 | 390 | 26 | 26 | 1707 | 1707 | 1707 | 0.040643 | 664 | 0.01581 | 1944 | 0.046286 | 1.362 | A04 | MICL0.01939026/DBR
Build-In Floor | Mini Canal | MICL.01939026/DBV | 19 | 390 | 26 | 26 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01939026/DBV
Build-In Floor | Mini Canal | MICL.01939026/DDB | 19 | 390 | 26 | 26 | 1707 | 1707 | 1707 | 0.040643 | 664 | 0.01581 | 1944 | 0.046286 | 1.362 | A04 | MICL0.01939026/DDB
Build-In Floor | Mini Canal | MICL.01939026/DMN | 19 | 390 | 26 | 26 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01939026/DMN
Build-In Floor | Mini Canal | MICL.01939026/DMV | 19 | 390 | 26 | 26 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01939026/DMV
Build-In Floor | Mini Canal | MICL.01939026/DNA | 19 | 390 | 26 | 26 | 1707 | 1707 | 1707 | 0.040643 | 664 | 0.01581 | 1944 | 0.046286 | 1.362 | A04 | MICL0.01939026/DNA
Build-In Floor | Mini Canal | MICL.01939026/DNC | 19 | 390 | 26 | 26 | 1707 | 1707 | 1707 | 0.040643 | 664 | 0.01581 | 1944 | 0.046286 | 1.362 | A04 | MICL0.01939026/DNC
Build-In Floor | Mini Canal | MICL.01939026/DON | 19 | 390 | 26 | 26 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01939026/DON
Build-In Floor | Mini Canal | MICL.01939026/DOV | 19 | 390 | 26 | 26 | 1637 | 1637 | 1637 | 0.038976 | 637 | 0.015167 | 1865 | 0.044405 | 1.362 | A04 | MICL0.01939026/DOV
Build-In Floor | Mini Canal | MICL.01939026/PNC | 19 | 390 | 26 | 26 | 1496 | 1496 | 1496 | 0.035619 | 582 | 0.013857 | 1704 | 0.040571 | 1.362 | A04 | MICL0.01939026/PNC
Build-In Floor | Mini Canal | MICL.01939026/RBL | 19 | 390 | 26 | 26 | 1760 | 1760 | 1760 | 0.041905 | 685 | 0.01631 | 2005 | 0.047738 | 1.362 | A04 | MICL0.01939026/RBL
Build-In Floor | Mini Canal | MICL.01939026/RBN | 19 | 390 | 26 | 26 | 1707 | 1707 | 1707 | 0.040643 | 664 | 0.01581 | 1944 | 0.046286 | 1.362 | A04 | MICL0.01939026/RBN
Build-In Floor | Mini Canal | MICL.01939026/RBR | 19 | 390 | 26 | 26 | 1760 | 1760 | 1760 | 0.041905 | 685 | 0.01631 | 2005 | 0.047738 | 1.362 | A04 | MICL0.01939026/RBR
Build-In Floor | Mini Canal | MICL.01939026/RBV | 19 | 390 | 26 | 26 | 1707 | 1707 | 1707 | 0.040643 | 664 | 0.01581 | 1944 | 0.046286 | 1.362 | A04 | MICL0.01939026/RBV
Build-In Floor | Mini Canal | MICL.01939026/RDB | 19 | 390 | 26 | 26 | 1760 | 1760 | 1760 | 0.041905 | 685 | 0.01631 | 2005 | 0.047738 | 1.362 | A04 | MICL0.01939026/RDB
Build-In Floor | Mini Canal | MICL.01939026/RMN | 19 | 390 | 26 | 26 | 1707 | 1707 | 1707 | 0.040643 | 664 | 0.01581 | 1944 | 0.046286 | 1.362 | A04 | MICL0.01939026/RMN
Build-In Floor | Mini Canal | MICL.01939026/RMV | 19 | 390 | 26 | 26 | 1707 | 1707 | 1707 | 0.040643 | 664 | 0.01581 | 1944 | 0.046286 | 1.362 | A04 | MICL0.01939026/RMV
Build-In Floor | Mini Canal | MICL.01939026/RNA | 19 | 390 | 26 | 26 | 1760 | 1760 | 1760 | 0.041905 | 685 | 0.01631 | 2005 | 0.047738 | 1.362 | A04 | MICL0.01939026/RNA
Build-In Floor | Mini Canal | MICL.01939026/RON | 19 | 390 | 26 | 26 | 1707 | 1707 | 1707 | 0.040643 | 664 | 0.01581 | 1944 | 0.046286 | 1.362 | A04 | MICL0.01939026/RON
Build-In Floor | Mini Canal | MICL.01939026/ROV | 19 | 390 | 26 | 26 | 1707 | 1707 | 1707 | 0.040643 | 664 | 0.01581 | 1944 | 0.046286 | 1.362 | A04 | MICL0.01939026/ROV
Build-In Floor | Mini Canal | MICL.01939026/RSS | 19 | 390 | 26 | 26 | 1690 | 1690 | 1690 | 0.040238 | 657 | 0.015643 | 1925 | 0.045833 | 1.362 | A04 | MICL0.01939026/RSS
Build-In Floor | Mini Canal | MICL.01939026/SBL | 19 | 390 | 26 | 26 | 1760 | 1760 | 1760 | 0.041905 | 685 | 0.01631 | 2005 | 0.047738 | 1.362 | A04 | MICL0.01939026/SBL
Build-In Floor | Mini Canal | MICL.01939026/SBR | 19 | 390 | 26 | 26 | 1760 | 1760 | 1760 | 0.041905 | 685 | 0.01631 | 2005 | 0.047738 | 1.362 | A04 | MICL0.01939026/SBR
Build-In Floor | Mini Canal | MICL.01939026/SDB | 19 | 390 | 26 | 26 | 1760 | 1760 | 1760 | 0.041905 | 685 | 0.01631 | 2005 | 0.047738 | 1.362 | A04 | MICL0.01939026/SDB
Build-In Floor | Mini Canal | MICL.01939026/SNA | 19 | 390 | 26 | 26 | 1760 | 1760 | 1760 | 0.041905 | 685 | 0.01631 | 2005 | 0.047738 | 1.362 | A04 | MICL0.01939026/SNA
Build-In Floor | Mini Canal | MICL.01939026/SNC | 19 | 390 | 26 | 26 | 1760 | 1760 | 1760 | 0.041905 | 685 | 0.01631 | 2005 | 0.047738 | 1.362 | A04 | MICL0.01939026/SNC
Build-In Floor | Mini Canal | MICL.01939034/ANA | 19 | 390 | 34 | 34 | 1788 | 1788 | 1788 | 0.042571 | 696 | 0.016571 | 2037 | 0.0485 | 1.362 | A04 | MICL0.01939034/ANA
Build-In Floor | Mini Canal | MICL.01939034/DBL | 19 | 390 | 34 | 34 | 2312 | 2312 | 2312 | 0.055048 | 899 | 0.021405 | 2633 | 0.06269 | 1.362 | A04 | MICL0.01939034/DBL
Build-In Floor | Mini Canal | MICL.01939034/DBN | 19 | 390 | 34 | 34 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01939034/DBN
Build-In Floor | Mini Canal | MICL.01939034/DBR | 19 | 390 | 34 | 34 | 2312 | 2312 | 2312 | 0.055048 | 899 | 0.021405 | 2633 | 0.06269 | 1.362 | A04 | MICL0.01939034/DBR
Build-In Floor | Mini Canal | MICL.01939034/DBV | 19 | 390 | 34 | 34 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01939034/DBV
Build-In Floor | Mini Canal | MICL.01939034/DDB | 19 | 390 | 34 | 34 | 2312 | 2312 | 2312 | 0.055048 | 899 | 0.021405 | 2633 | 0.06269 | 1.362 | A04 | MICL0.01939034/DDB
Build-In Floor | Mini Canal | MICL.01939034/DMN | 19 | 390 | 34 | 34 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01939034/DMN
Build-In Floor | Mini Canal | MICL.01939034/DMV | 19 | 390 | 34 | 34 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01939034/DMV
Build-In Floor | Mini Canal | MICL.01939034/DNA | 19 | 390 | 34 | 34 | 2312 | 2312 | 2312 | 0.055048 | 899 | 0.021405 | 2633 | 0.06269 | 1.362 | A04 | MICL0.01939034/DNA
Build-In Floor | Mini Canal | MICL.01939034/DNC | 19 | 390 | 34 | 34 | 2312 | 2312 | 2312 | 0.055048 | 899 | 0.021405 | 2633 | 0.06269 | 1.362 | A04 | MICL0.01939034/DNC
Build-In Floor | Mini Canal | MICL.01939034/DON | 19 | 390 | 34 | 34 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01939034/DON
Build-In Floor | Mini Canal | MICL.01939034/DOV | 19 | 390 | 34 | 34 | 2217 | 2217 | 2217 | 0.052786 | 862 | 0.020524 | 2525 | 0.060119 | 1.362 | A04 | MICL0.01939034/DOV
Build-In Floor | Mini Canal | MICL.01939034/PNC | 19 | 390 | 34 | 34 | 2026 | 2026 | 2026 | 0.048238 | 788 | 0.018762 | 2308 | 0.054952 | 1.362 | A04 | MICL0.01939034/PNC
Build-In Floor | Mini Canal | MICL.01939034/RBL | 19 | 390 | 34 | 34 | 2384 | 2384 | 2384 | 0.056762 | 927 | 0.022071 | 2715 | 0.064643 | 1.362 | A04 | MICL0.01939034/RBL
Build-In Floor | Mini Canal | MICL.01939034/RBN | 19 | 390 | 34 | 34 | 2312 | 2312 | 2312 | 0.055048 | 899 | 0.021405 | 2633 | 0.06269 | 1.362 | A04 | MICL0.01939034/RBN
Build-In Floor | Mini Canal | MICL.01939034/RBR | 19 | 390 | 34 | 34 | 2384 | 2384 | 2384 | 0.056762 | 927 | 0.022071 | 2715 | 0.064643 | 1.362 | A04 | MICL0.01939034/RBR
Build-In Floor | Mini Canal | MICL.01939034/RBV | 19 | 390 | 34 | 34 | 2312 | 2312 | 2312 | 0.055048 | 899 | 0.021405 | 2633 | 0.06269 | 1.362 | A04 | MICL0.01939034/RBV
Build-In Floor | Mini Canal | MICL.01939034/RDB | 19 | 390 | 34 | 34 | 2384 | 2384 | 2384 | 0.056762 | 927 | 0.022071 | 2715 | 0.064643 | 1.362 | A04 | MICL0.01939034/RDB
Build-In Floor | Mini Canal | MICL.01939034/RMN | 19 | 390 | 34 | 34 | 2312 | 2312 | 2312 | 0.055048 | 899 | 0.021405 | 2633 | 0.06269 | 1.362 | A04 | MICL0.01939034/RMN
Build-In Floor | Mini Canal | MICL.01939034/RMV | 19 | 390 | 34 | 34 | 2312 | 2312 | 2312 | 0.055048 | 899 | 0.021405 | 2633 | 0.06269 | 1.362 | A04 | MICL0.01939034/RMV
Build-In Floor | Mini Canal | MICL.01939034/RNA | 19 | 390 | 34 | 34 | 2384 | 2384 | 2384 | 0.056762 | 927 | 0.022071 | 2715 | 0.064643 | 1.362 | A04 | MICL0.01939034/RNA
Build-In Floor | Mini Canal | MICL.01939034/RON | 19 | 390 | 34 | 34 | 2312 | 2312 | 2312 | 0.055048 | 899 | 0.021405 | 2633 | 0.06269 | 1.362 | A04 | MICL0.01939034/RON
Build-In Floor | Mini Canal | MICL.01939034/ROV | 19 | 390 | 34 | 34 | 2312 | 2312 | 2312 | 0.055048 | 899 | 0.021405 | 2633 | 0.06269 | 1.362 | A04 | MICL0.01939034/ROV
Build-In Floor | Mini Canal | MICL.01939034/RSS | 19 | 390 | 34 | 34 | 2289 | 2289 | 2289 | 0.0545 | 890 | 0.02119 | 2607 | 0.062071 | 1.362 | A04 | MICL0.01939034/RSS
Build-In Floor | Mini Canal | MICL.01939034/SBL | 19 | 390 | 34 | 34 | 2384 | 2384 | 2384 | 0.056762 | 927 | 0.022071 | 2715 | 0.064643 | 1.362 | A04 | MICL0.01939034/SBL
Build-In Floor | Mini Canal | MICL.01939034/SBR | 19 | 390 | 34 | 34 | 2384 | 2384 | 2384 | 0.056762 | 927 | 0.022071 | 2715 | 0.064643 | 1.362 | A04 | MICL0.01939034/SBR
Build-In Floor | Mini Canal | MICL.01939034/SDB | 19 | 390 | 34 | 34 | 2384 | 2384 | 2384 | 0.056762 | 927 | 0.022071 | 2715 | 0.064643 | 1.362 | A04 | MICL0.01939034/SDB
Build-In Floor | Mini Canal | MICL.01939034/SNA | 19 | 390 | 34 | 34 | 2384 | 2384 | 2384 | 0.056762 | 927 | 0.022071 | 2715 | 0.064643 | 1.362 | A04 | MICL0.01939034/SNA
Build-In Floor | Mini Canal | MICL.01939034/SNC | 19 | 390 | 34 | 34 | 2384 | 2384 | 2384 | 0.056762 | 927 | 0.022071 | 2715 | 0.064643 | 1.362 | A04 | MICL0.01939034/SNC
Build-In Floor | Mini Canal | MICL.01939042/ANA | 19 | 390 | 42 | 42 | 2456 | 2456 | 2456 | 0.058476 | 955 | 0.022738 | 2797 | 0.066595 | 1.362 | A04 | MICL0.01939042/ANA
Build-In Floor | Mini Canal | MICL.01939042/DBL | 19 | 390 | 42 | 42 | 3176 | 3176 | 3176 | 0.075619 | 1235 | 0.029405 | 3617 | 0.086119 | 1.362 | A04 | MICL0.01939042/DBL
Build-In Floor | Mini Canal | MICL.01939042/DBN | 19 | 390 | 42 | 42 | 3045 | 3045 | 3045 | 0.0725 | 1185 | 0.028214 | 3468 | 0.082571 | 1.362 | A04 | MICL0.01939042/DBN
Build-In Floor | Mini Canal | MICL.01939042/DBR | 19 | 390 | 42 | 42 | 3176 | 3176 | 3176 | 0.075619 | 1235 | 0.029405 | 3617 | 0.086119 | 1.362 | A04 | MICL0.01939042/DBR
Build-In Floor | Mini Canal | MICL.01939042/DBV | 19 | 390 | 42 | 42 | 3045 | 3045 | 3045 | 0.0725 | 1185 | 0.028214 | 3468 | 0.082571 | 1.362 | A04 | MICL0.01939042/DBV
Build-In Floor | Mini Canal | MICL.01939042/DDB | 19 | 390 | 42 | 42 | 3176 | 3176 | 3176 | 0.075619 | 1235 | 0.029405 | 3617 | 0.086119 | 1.362 | A04 | MICL0.01939042/DDB
Build-In Floor | Mini Canal | MICL.01939042/DMN | 19 | 390 | 42 | 42 | 3045 | 3045 | 3045 | 0.0725 | 1185 | 0.028214 | 3468 | 0.082571 | 1.362 | A04 | MICL0.01939042/DMN
Build-In Floor | Mini Canal | MICL.01939042/DMV | 19 | 390 | 42 | 42 | 3045 | 3045 | 3045 | 0.0725 | 1185 | 0.028214 | 3468 | 0.082571 | 1.362 | A04 | MICL0.01939042/DMV
Build-In Floor | Mini Canal | MICL.01939042/DNA | 19 | 390 | 42 | 42 | 3176 | 3176 | 3176 | 0.075619 | 1235 | 0.029405 | 3617 | 0.086119 | 1.362 | A04 | MICL0.01939042/DNA
Build-In Floor | Mini Canal | MICL.01939042/DNC | 19 | 390 | 42 | 42 | 3176 | 3176 | 3176 | 0.075619 | 1235 | 0.029405 | 3617 | 0.086119 | 1.362 | A04 | MICL0.01939042/DNC
Build-In Floor | Mini Canal | MICL.01939042/DON | 19 | 390 | 42 | 42 | 3045 | 3045 | 3045 | 0.0725 | 1185 | 0.028214 | 3468 | 0.082571 | 1.362 | A04 | MICL0.01939042/DON
Build-In Floor | Mini Canal | MICL.01939042/DOV | 19 | 390 | 42 | 42 | 3045 | 3045 | 3045 | 0.0725 | 1185 | 0.028214 | 3468 | 0.082571 | 1.362 | A04 | MICL0.01939042/DOV
Build-In Floor | Mini Canal | MICL.01939042/PNC | 19 | 390 | 42 | 42 | 2783 | 2783 | 2783 | 0.066262 | 1083 | 0.025786 | 3170 | 0.075476 | 1.362 | A04 | MICL0.01939042/PNC
Build-In Floor | Mini Canal | MICL.01939042/RBL | 19 | 390 | 42 | 42 | 3274 | 3274 | 3274 | 0.077952 | 1274 | 0.030333 | 3729 | 0.088786 | 1.362 | A04 | MICL0.01939042/RBL
Build-In Floor | Mini Canal | MICL.01939042/RBN | 19 | 390 | 42 | 42 | 3176 | 3176 | 3176 | 0.075619 | 1235 | 0.029405 | 3617 | 0.086119 | 1.362 | A04 | MICL0.01939042/RBN
Build-In Floor | Mini Canal | MICL.01939042/RBR | 19 | 390 | 42 | 42 | 3274 | 3274 | 3274 | 0.077952 | 1274 | 0.030333 | 3729 | 0.088786 | 1.362 | A04 | MICL0.01939042/RBR
Build-In Floor | Mini Canal | MICL.01939042/RBV | 19 | 390 | 42 | 42 | 3176 | 3176 | 3176 | 0.075619 | 1235 | 0.029405 | 3617 | 0.086119 | 1.362 | A04 | MICL0.01939042/RBV
Build-In Floor | Mini Canal | MICL.01939042/RDB | 19 | 390 | 42 | 42 | 3274 | 3274 | 3274 | 0.077952 | 1274 | 0.030333 | 3729 | 0.088786 | 1.362 | A04 | MICL0.01939042/RDB
Build-In Floor | Mini Canal | MICL.01939042/RMN | 19 | 390 | 42 | 42 | 3176 | 3176 | 3176 | 0.075619 | 1235 | 0.029405 | 3617 | 0.086119 | 1.362 | A04 | MICL0.01939042/RMN
Build-In Floor | Mini Canal | MICL.01939042/RMV | 19 | 390 | 42 | 42 | 3176 | 3176 | 3176 | 0.075619 | 1235 | 0.029405 | 3617 | 0.086119 | 1.362 | A04 | MICL0.01939042/RMV
Build-In Floor | Mini Canal | MICL.01939042/RNA | 19 | 390 | 42 | 42 | 3274 | 3274 | 3274 | 0.077952 | 1274 | 0.030333 | 3729 | 0.088786 | 1.362 | A04 | MICL0.01939042/RNA
Build-In Floor | Mini Canal | MICL.01939042/RON | 19 | 390 | 42 | 42 | 3176 | 3176 | 3176 | 0.075619 | 1235 | 0.029405 | 3617 | 0.086119 | 1.362 | A04 | MICL0.01939042/RON
Build-In Floor | Mini Canal | MICL.01939042/ROV | 19 | 390 | 42 | 42 | 3176 | 3176 | 3176 | 0.075619 | 1235 | 0.029405 | 3617 | 0.086119 | 1.362 | A04 | MICL0.01939042/ROV
Build-In Floor | Mini Canal | MICL.01939042/RSS | 19 | 390 | 42 | 42 | 3143 | 3143 | 3143 | 0.074833 | 1223 | 0.029119 | 3580 | 0.085238 | 1.362 | A04 | MICL0.01939042/RSS
Build-In Floor | Mini Canal | MICL.01939042/SBL | 19 | 390 | 42 | 42 | 3274 | 3274 | 3274 | 0.077952 | 1274 | 0.030333 | 3729 | 0.088786 | 1.362 | A04 | MICL0.01939042/SBL
Build-In Floor | Mini Canal | MICL.01939042/SBR | 19 | 390 | 42 | 42 | 3274 | 3274 | 3274 | 0.077952 | 1274 | 0.030333 | 3729 | 0.088786 | 1.362 | A04 | MICL0.01939042/SBR
Build-In Floor | Mini Canal | MICL.01939042/SDB | 19 | 390 | 42 | 42 | 3274 | 3274 | 3274 | 0.077952 | 1274 | 0.030333 | 3729 | 0.088786 | 1.362 | A04 | MICL0.01939042/SDB
Build-In Floor | Mini Canal | MICL.01939042/SNA | 19 | 390 | 42 | 42 | 3274 | 3274 | 3274 | 0.077952 | 1274 | 0.030333 | 3729 | 0.088786 | 1.362 | A04 | MICL0.01939042/SNA
Build-In Floor | Mini Canal | MICL.01939042/SNC | 19 | 390 | 42 | 42 | 3274 | 3274 | 3274 | 0.077952 | 1274 | 0.030333 | 3729 | 0.088786 | 1.362 | A04 | MICL0.01939042/SNC
Build-In Floor | Mini Canal | MICL.01941026/ANA | 19 | 410 | 26 | 26 | 1394 | 1394 | 1394 | 0.03319 | 542 | 0.012905 | 1588 | 0.03781 | 1.362 | A04 | MICL0.01941026/ANA
Build-In Floor | Mini Canal | MICL.01941026/DBL | 19 | 410 | 26 | 26 | 1803 | 1803 | 1803 | 0.042929 | 701 | 0.01669 | 2054 | 0.048905 | 1.362 | A04 | MICL0.01941026/DBL
Build-In Floor | Mini Canal | MICL.01941026/DBN | 19 | 410 | 26 | 26 | 1729 | 1729 | 1729 | 0.041167 | 673 | 0.016024 | 1969 | 0.046881 | 1.362 | A04 | MICL0.01941026/DBN
Build-In Floor | Mini Canal | MICL.01941026/DBR | 19 | 410 | 26 | 26 | 1803 | 1803 | 1803 | 0.042929 | 701 | 0.01669 | 2054 | 0.048905 | 1.362 | A04 | MICL0.01941026/DBR
Build-In Floor | Mini Canal | MICL.01941026/DBV | 19 | 410 | 26 | 26 | 1729 | 1729 | 1729 | 0.041167 | 673 | 0.016024 | 1969 | 0.046881 | 1.362 | A04 | MICL0.01941026/DBV
Build-In Floor | Mini Canal | MICL.01941026/DDB | 19 | 410 | 26 | 26 | 1803 | 1803 | 1803 | 0.042929 | 701 | 0.01669 | 2054 | 0.048905 | 1.362 | A04 | MICL0.01941026/DDB
Build-In Floor | Mini Canal | MICL.01941026/DMN | 19 | 410 | 26 | 26 | 1729 | 1729 | 1729 | 0.041167 | 673 | 0.016024 | 1969 | 0.046881 | 1.362 | A04 | MICL0.01941026/DMN
Build-In Floor | Mini Canal | MICL.01941026/DMV | 19 | 410 | 26 | 26 | 1729 | 1729 | 1729 | 0.041167 | 673 | 0.016024 | 1969 | 0.046881 | 1.362 | A04 | MICL0.01941026/DMV
Build-In Floor | Mini Canal | MICL.01941026/DNA | 19 | 410 | 26 | 26 | 1803 | 1803 | 1803 | 0.042929 | 701 | 0.01669 | 2054 | 0.048905 | 1.362 | A04 | MICL0.01941026/DNA
Build-In Floor | Mini Canal | MICL.01941026/DNC | 19 | 410 | 26 | 26 | 1803 | 1803 | 1803 | 0.042929 | 701 | 0.01669 | 2054 | 0.048905 | 1.362 | A04 | MICL0.01941026/DNC
Build-In Floor | Mini Canal | MICL.01941026/DON | 19 | 410 | 26 | 26 | 1729 | 1729 | 1729 | 0.041167 | 673 | 0.016024 | 1969 | 0.046881 | 1.362 | A04 | MICL0.01941026/DON
Build-In Floor | Mini Canal | MICL.01941026/DOV | 19 | 410 | 26 | 26 | 1729 | 1729 | 1729 | 0.041167 | 673 | 0.016024 | 1969 | 0.046881 | 1.362 | A04 | MICL0.01941026/DOV
Build-In Floor | Mini Canal | MICL.01941026/PNC | 19 | 410 | 26 | 26 | 1580 | 1580 | 1580 | 0.037619 | 615 | 0.014643 | 1800 | 0.042857 | 1.362 | A04 | MICL0.01941026/PNC
Build-In Floor | Mini Canal | MICL.01941026/RBL | 19 | 410 | 26 | 26 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.01941026/RBL
Build-In Floor | Mini Canal | MICL.01941026/RBN | 19 | 410 | 26 | 26 | 1803 | 1803 | 1803 | 0.042929 | 701 | 0.01669 | 2054 | 0.048905 | 1.362 | A04 | MICL0.01941026/RBN
Build-In Floor | Mini Canal | MICL.01941026/RBR | 19 | 410 | 26 | 26 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.01941026/RBR
Build-In Floor | Mini Canal | MICL.01941026/RBV | 19 | 410 | 26 | 26 | 1803 | 1803 | 1803 | 0.042929 | 701 | 0.01669 | 2054 | 0.048905 | 1.362 | A04 | MICL0.01941026/RBV
Build-In Floor | Mini Canal | MICL.01941026/RDB | 19 | 410 | 26 | 26 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.01941026/RDB
Build-In Floor | Mini Canal | MICL.01941026/RMN | 19 | 410 | 26 | 26 | 1803 | 1803 | 1803 | 0.042929 | 701 | 0.01669 | 2054 | 0.048905 | 1.362 | A04 | MICL0.01941026/RMN
Build-In Floor | Mini Canal | MICL.01941026/RMV | 19 | 410 | 26 | 26 | 1803 | 1803 | 1803 | 0.042929 | 701 | 0.01669 | 2054 | 0.048905 | 1.362 | A04 | MICL0.01941026/RMV
Build-In Floor | Mini Canal | MICL.01941026/RNA | 19 | 410 | 26 | 26 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.01941026/RNA
Build-In Floor | Mini Canal | MICL.01941026/RON | 19 | 410 | 26 | 26 | 1803 | 1803 | 1803 | 0.042929 | 701 | 0.01669 | 2054 | 0.048905 | 1.362 | A04 | MICL0.01941026/RON
Build-In Floor | Mini Canal | MICL.01941026/ROV | 19 | 410 | 26 | 26 | 1803 | 1803 | 1803 | 0.042929 | 701 | 0.01669 | 2054 | 0.048905 | 1.362 | A04 | MICL0.01941026/ROV
Build-In Floor | Mini Canal | MICL.01941026/RSS | 19 | 410 | 26 | 26 | 1785 | 1785 | 1785 | 0.0425 | 694 | 0.016524 | 2033 | 0.048405 | 1.362 | A04 | MICL0.01941026/RSS
Build-In Floor | Mini Canal | MICL.01941026/SBL | 19 | 410 | 26 | 26 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.01941026/SBL
Build-In Floor | Mini Canal | MICL.01941026/SBR | 19 | 410 | 26 | 26 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.01941026/SBR
Build-In Floor | Mini Canal | MICL.01941026/SDB | 19 | 410 | 26 | 26 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.01941026/SDB
Build-In Floor | Mini Canal | MICL.01941026/SNA | 19 | 410 | 26 | 26 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.01941026/SNA
Build-In Floor | Mini Canal | MICL.01941026/SNC | 19 | 410 | 26 | 26 | 1859 | 1859 | 1859 | 0.044262 | 723 | 0.017214 | 2117 | 0.050405 | 1.362 | A04 | MICL0.01941026/SNC
Build-In Floor | Mini Canal | MICL.01941034/ANA | 19 | 410 | 34 | 34 | 1887 | 1887 | 1887 | 0.044929 | 734 | 0.017476 | 2149 | 0.051167 | 1.362 | A04 | MICL0.01941034/ANA
Build-In Floor | Mini Canal | MICL.01941034/DBL | 19 | 410 | 34 | 34 | 2441 | 2441 | 2441 | 0.058119 | 950 | 0.022619 | 2780 | 0.06619 | 1.362 | A04 | MICL0.01941034/DBL
Build-In Floor | Mini Canal | MICL.01941034/DBN | 19 | 410 | 34 | 34 | 2340 | 2340 | 2340 | 0.055714 | 910 | 0.021667 | 2665 | 0.063452 | 1.362 | A04 | MICL0.01941034/DBN
Build-In Floor | Mini Canal | MICL.01941034/DBR | 19 | 410 | 34 | 34 | 2441 | 2441 | 2441 | 0.058119 | 950 | 0.022619 | 2780 | 0.06619 | 1.362 | A04 | MICL0.01941034/DBR
Build-In Floor | Mini Canal | MICL.01941034/DBV | 19 | 410 | 34 | 34 | 2340 | 2340 | 2340 | 0.055714 | 910 | 0.021667 | 2665 | 0.063452 | 1.362 | A04 | MICL0.01941034/DBV
Build-In Floor | Mini Canal | MICL.01941034/DDB | 19 | 410 | 34 | 34 | 2441 | 2441 | 2441 | 0.058119 | 950 | 0.022619 | 2780 | 0.06619 | 1.362 | A04 | MICL0.01941034/DDB
Build-In Floor | Mini Canal | MICL.01941034/DMN | 19 | 410 | 34 | 34 | 2340 | 2340 | 2340 | 0.055714 | 910 | 0.021667 | 2665 | 0.063452 | 1.362 | A04 | MICL0.01941034/DMN
Build-In Floor | Mini Canal | MICL.01941034/DMV | 19 | 410 | 34 | 34 | 2340 | 2340 | 2340 | 0.055714 | 910 | 0.021667 | 2665 | 0.063452 | 1.362 | A04 | MICL0.01941034/DMV
Build-In Floor | Mini Canal | MICL.01941034/DNA | 19 | 410 | 34 | 34 | 2441 | 2441 | 2441 | 0.058119 | 950 | 0.022619 | 2780 | 0.06619 | 1.362 | A04 | MICL0.01941034/DNA
Build-In Floor | Mini Canal | MICL.01941034/DNC | 19 | 410 | 34 | 34 | 2441 | 2441 | 2441 | 0.058119 | 950 | 0.022619 | 2780 | 0.06619 | 1.362 | A04 | MICL0.01941034/DNC
Build-In Floor | Mini Canal | MICL.01941034/DON | 19 | 410 | 34 | 34 | 2340 | 2340 | 2340 | 0.055714 | 910 | 0.021667 | 2665 | 0.063452 | 1.362 | A04 | MICL0.01941034/DON
Build-In Floor | Mini Canal | MICL.01941034/DOV | 19 | 410 | 34 | 34 | 2340 | 2340 | 2340 | 0.055714 | 910 | 0.021667 | 2665 | 0.063452 | 1.362 | A04 | MICL0.01941034/DOV
Build-In Floor | Mini Canal | MICL.01941034/PNC | 19 | 410 | 34 | 34 | 2139 | 2139 | 2139 | 0.050929 | 832 | 0.01981 | 2436 | 0.058 | 1.362 | A04 | MICL0.01941034/PNC
Build-In Floor | Mini Canal | MICL.01941034/RBL | 19 | 410 | 34 | 34 | 2516 | 2516 | 2516 | 0.059905 | 979 | 0.02331 | 2866 | 0.068238 | 1.362 | A04 | MICL0.01941034/RBL
Build-In Floor | Mini Canal | MICL.01941034/RBN | 19 | 410 | 34 | 34 | 2441 | 2441 | 2441 | 0.058119 | 950 | 0.022619 | 2780 | 0.06619 | 1.362 | A04 | MICL0.01941034/RBN
Build-In Floor | Mini Canal | MICL.01941034/RBR | 19 | 410 | 34 | 34 | 2516 | 2516 | 2516 | 0.059905 | 979 | 0.02331 | 2866 | 0.068238 | 1.362 | A04 | MICL0.01941034/RBR
Build-In Floor | Mini Canal | MICL.01941034/RBV | 19 | 410 | 34 | 34 | 2441 | 2441 | 2441 | 0.058119 | 950 | 0.022619 | 2780 | 0.06619 | 1.362 | A04 | MICL0.01941034/RBV
Build-In Floor | Mini Canal | MICL.01941034/RDB | 19 | 410 | 34 | 34 | 2516 | 2516 | 2516 | 0.059905 | 979 | 0.02331 | 2866 | 0.068238 | 1.362 | A04 | MICL0.01941034/RDB
Build-In Floor | Mini Canal | MICL.01941034/RMN | 19 | 410 | 34 | 34 | 2441 | 2441 | 2441 | 0.058119 | 950 | 0.022619 | 2780 | 0.06619 | 1.362 | A04 | MICL0.01941034/RMN
Build-In Floor | Mini Canal | MICL.01941034/RMV | 19 | 410 | 34 | 34 | 2441 | 2441 | 2441 | 0.058119 | 950 | 0.022619 | 2780 | 0.06619 | 1.362 | A04 | MICL0.01941034/RMV
Build-In Floor | Mini Canal | MICL.01941034/RNA | 19 | 410 | 34 | 34 | 2516 | 2516 | 2516 | 0.059905 | 979 | 0.02331 | 2866 | 0.068238 | 1.362 | A04 | MICL0.01941034/RNA
Build-In Floor | Mini Canal | MICL.01941034/RON | 19 | 410 | 34 | 34 | 2441 | 2441 | 2441 | 0.058119 | 950 | 0.022619 | 2780 | 0.06619 | 1.362 | A04 | MICL0.01941034/RON
Build-In Floor | Mini Canal | MICL.01941034/ROV | 19 | 410 | 34 | 34 | 2441 | 2441 | 2441 | 0.058119 | 950 | 0.022619 | 2780 | 0.06619 | 1.362 | A04 | MICL0.01941034/ROV
Build-In Floor | Mini Canal | MICL.01941034/RSS | 19 | 410 | 34 | 34 | 2415 | 2415 | 2415 | 0.0575 | 939 | 0.022357 | 2751 | 0.0655 | 1.362 | A04 | MICL0.01941034/RSS
Build-In Floor | Mini Canal | MICL.01941034/SBL | 19 | 410 | 34 | 34 | 2516 | 2516 | 2516 | 0.059905 | 979 | 0.02331 | 2866 | 0.068238 | 1.362 | A04 | MICL0.01941034/SBL
Build-In Floor | Mini Canal | MICL.01941034/SBR | 19 | 410 | 34 | 34 | 2516 | 2516 | 2516 | 0.059905 | 979 | 0.02331 | 2866 | 0.068238 | 1.362 | A04 | MICL0.01941034/SBR
Build-In Floor | Mini Canal | MICL.01941034/SDB | 19 | 410 | 34 | 34 | 2516 | 2516 | 2516 | 0.059905 | 979 | 0.02331 | 2866 | 0.068238 | 1.362 | A04 | MICL0.01941034/SDB
Build-In Floor | Mini Canal | MICL.01941034/SNA | 19 | 410 | 34 | 34 | 2516 | 2516 | 2516 | 0.059905 | 979 | 0.02331 | 2866 | 0.068238 | 1.362 | A04 | MICL0.01941034/SNA
Build-In Floor | Mini Canal | MICL.01941034/SNC | 19 | 410 | 34 | 34 | 2516 | 2516 | 2516 | 0.059905 | 979 | 0.02331 | 2866 | 0.068238 | 1.362 | A04 | MICL0.01941034/SNC
Build-In Floor | Mini Canal | MICL.01941042/ANA | 19 | 410 | 42 | 42 | 2592 | 2592 | 2592 | 0.061714 | 1008 | 0.024 | 2952 | 0.070286 | 1.362 | A04 | MICL0.01941042/ANA
Build-In Floor | Mini Canal | MICL.01941042/DBL | 19 | 410 | 42 | 42 | 3352 | 3352 | 3352 | 0.07981 | 1304 | 0.031048 | 3818 | 0.090905 | 1.362 | A04 | MICL0.01941042/DBL
Build-In Floor | Mini Canal | MICL.01941042/DBN | 19 | 410 | 42 | 42 | 3214 | 3214 | 3214 | 0.076524 | 1250 | 0.029762 | 3661 | 0.087167 | 1.362 | A04 | MICL0.01941042/DBN
Build-In Floor | Mini Canal | MICL.01941042/DBR | 19 | 410 | 42 | 42 | 3352 | 3352 | 3352 | 0.07981 | 1304 | 0.031048 | 3818 | 0.090905 | 1.362 | A04 | MICL0.01941042/DBR
Build-In Floor | Mini Canal | MICL.01941042/DBV | 19 | 410 | 42 | 42 | 3214 | 3214 | 3214 | 0.076524 | 1250 | 0.029762 | 3661 | 0.087167 | 1.362 | A04 | MICL0.01941042/DBV
Build-In Floor | Mini Canal | MICL.01941042/DDB | 19 | 410 | 42 | 42 | 3352 | 3352 | 3352 | 0.07981 | 1304 | 0.031048 | 3818 | 0.090905 | 1.362 | A04 | MICL0.01941042/DDB
Build-In Floor | Mini Canal | MICL.01941042/DMN | 19 | 410 | 42 | 42 | 3214 | 3214 | 3214 | 0.076524 | 1250 | 0.029762 | 3661 | 0.087167 | 1.362 | A04 | MICL0.01941042/DMN
Build-In Floor | Mini Canal | MICL.01941042/DMV | 19 | 410 | 42 | 42 | 3214 | 3214 | 3214 | 0.076524 | 1250 | 0.029762 | 3661 | 0.087167 | 1.362 | A04 | MICL0.01941042/DMV
Build-In Floor | Mini Canal | MICL.01941042/DNA | 19 | 410 | 42 | 42 | 3352 | 3352 | 3352 | 0.07981 | 1304 | 0.031048 | 3818 | 0.090905 | 1.362 | A04 | MICL0.01941042/DNA
Build-In Floor | Mini Canal | MICL.01941042/DNC | 19 | 410 | 42 | 42 | 3352 | 3352 | 3352 | 0.07981 | 1304 | 0.031048 | 3818 | 0.090905 | 1.362 | A04 | MICL0.01941042/DNC
Build-In Floor | Mini Canal | MICL.01941042/DON | 19 | 410 | 42 | 42 | 3214 | 3214 | 3214 | 0.076524 | 1250 | 0.029762 | 3661 | 0.087167 | 1.362 | A04 | MICL0.01941042/DON
Build-In Floor | Mini Canal | MICL.01941042/DOV | 19 | 410 | 42 | 42 | 3214 | 3214 | 3214 | 0.076524 | 1250 | 0.029762 | 3661 | 0.087167 | 1.362 | A04 | MICL0.01941042/DOV
Build-In Floor | Mini Canal | MICL.01941042/PNC | 19 | 410 | 42 | 42 | 2938 | 2938 | 2938 | 0.069952 | 1143 | 0.027214 | 3346 | 0.079667 | 1.362 | A04 | MICL0.01941042/PNC
Build-In Floor | Mini Canal | MICL.01941042/RBL | 19 | 410 | 42 | 42 | 3456 | 3456 | 3456 | 0.082286 | 1344 | 0.032 | 3936 | 0.093714 | 1.362 | A04 | MICL0.01941042/RBL
Build-In Floor | Mini Canal | MICL.01941042/RBN | 19 | 410 | 42 | 42 | 3352 | 3352 | 3352 | 0.07981 | 1304 | 0.031048 | 3818 | 0.090905 | 1.362 | A04 | MICL0.01941042/RBN
Build-In Floor | Mini Canal | MICL.01941042/RBR | 19 | 410 | 42 | 42 | 3456 | 3456 | 3456 | 0.082286 | 1344 | 0.032 | 3936 | 0.093714 | 1.362 | A04 | MICL0.01941042/RBR
Build-In Floor | Mini Canal | MICL.01941042/RBV | 19 | 410 | 42 | 42 | 3352 | 3352 | 3352 | 0.07981 | 1304 | 0.031048 | 3818 | 0.090905 | 1.362 | A04 | MICL0.01941042/RBV
Build-In Floor | Mini Canal | MICL.01941042/RDB | 19 | 410 | 42 | 42 | 3456 | 3456 | 3456 | 0.082286 | 1344 | 0.032 | 3936 | 0.093714 | 1.362 | A04 | MICL0.01941042/RDB
Build-In Floor | Mini Canal | MICL.01941042/RMN | 19 | 410 | 42 | 42 | 3352 | 3352 | 3352 | 0.07981 | 1304 | 0.031048 | 3818 | 0.090905 | 1.362 | A04 | MICL0.01941042/RMN
Build-In Floor | Mini Canal | MICL.01941042/RMV | 19 | 410 | 42 | 42 | 3352 | 3352 | 3352 | 0.07981 | 1304 | 0.031048 | 3818 | 0.090905 | 1.362 | A04 | MICL0.01941042/RMV
Build-In Floor | Mini Canal | MICL.01941042/RNA | 19 | 410 | 42 | 42 | 3456 | 3456 | 3456 | 0.082286 | 1344 | 0.032 | 3936 | 0.093714 | 1.362 | A04 | MICL0.01941042/RNA
Build-In Floor | Mini Canal | MICL.01941042/RON | 19 | 410 | 42 | 42 | 3352 | 3352 | 3352 | 0.07981 | 1304 | 0.031048 | 3818 | 0.090905 | 1.362 | A04 | MICL0.01941042/RON
Build-In Floor | Mini Canal | MICL.01941042/ROV | 19 | 410 | 42 | 42 | 3352 | 3352 | 3352 | 0.07981 | 1304 | 0.031048 | 3818 | 0.090905 | 1.362 | A04 | MICL0.01941042/ROV
Build-In Floor | Mini Canal | MICL.01941042/RSS | 19 | 410 | 42 | 42 | 3318 | 3318 | 3318 | 0.079 | 1291 | 0.030738 | 3779 | 0.089976 | 1.362 | A04 | MICL0.01941042/RSS
Build-In Floor | Mini Canal | MICL.01941042/SBL | 19 | 410 | 42 | 42 | 3456 | 3456 | 3456 | 0.082286 | 1344 | 0.032 | 3936 | 0.093714 | 1.362 | A04 | MICL0.01941042/SBL
Build-In Floor | Mini Canal | MICL.01941042/SBR | 19 | 410 | 42 | 42 | 3456 | 3456 | 3456 | 0.082286 | 1344 | 0.032 | 3936 | 0.093714 | 1.362 | A04 | MICL0.01941042/SBR
Build-In Floor | Mini Canal | MICL.01941042/SDB | 19 | 410 | 42 | 42 | 3456 | 3456 | 3456 | 0.082286 | 1344 | 0.032 | 3936 | 0.093714 | 1.362 | A04 | MICL0.01941042/SDB
Build-In Floor | Mini Canal | MICL.01941042/SNA | 19 | 410 | 42 | 42 | 3456 | 3456 | 3456 | 0.082286 | 1344 | 0.032 | 3936 | 0.093714 | 1.362 | A04 | MICL0.01941042/SNA
Build-In Floor | Mini Canal | MICL.01941042/SNC | 19 | 410 | 42 | 42 | 3456 | 3456 | 3456 | 0.082286 | 1344 | 0.032 | 3936 | 0.093714 | 1.362 | A04 | MICL0.01941042/SNC
Build-In Floor | Mini Canal | MICL.01943026/ANA | 19 | 430 | 26 | 26 | 1467 | 1467 | 1467 | 0.034929 | 571 | 0.013595 | 1671 | 0.039786 | 1.362 | A04 | MICL0.01943026/ANA
Build-In Floor | Mini Canal | MICL.01943026/DBL | 19 | 430 | 26 | 26 | 1897 | 1897 | 1897 | 0.045167 | 738 | 0.017571 | 2161 | 0.051452 | 1.362 | A04 | MICL0.01943026/DBL
Build-In Floor | Mini Canal | MICL.01943026/DBN | 19 | 430 | 26 | 26 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01943026/DBN
Build-In Floor | Mini Canal | MICL.01943026/DBR | 19 | 430 | 26 | 26 | 1897 | 1897 | 1897 | 0.045167 | 738 | 0.017571 | 2161 | 0.051452 | 1.362 | A04 | MICL0.01943026/DBR
Build-In Floor | Mini Canal | MICL.01943026/DBV | 19 | 430 | 26 | 26 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01943026/DBV
Build-In Floor | Mini Canal | MICL.01943026/DDB | 19 | 430 | 26 | 26 | 1897 | 1897 | 1897 | 0.045167 | 738 | 0.017571 | 2161 | 0.051452 | 1.362 | A04 | MICL0.01943026/DDB
Build-In Floor | Mini Canal | MICL.01943026/DMN | 19 | 430 | 26 | 26 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01943026/DMN
Build-In Floor | Mini Canal | MICL.01943026/DMV | 19 | 430 | 26 | 26 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01943026/DMV
Build-In Floor | Mini Canal | MICL.01943026/DNA | 19 | 430 | 26 | 26 | 1897 | 1897 | 1897 | 0.045167 | 738 | 0.017571 | 2161 | 0.051452 | 1.362 | A04 | MICL0.01943026/DNA
Build-In Floor | Mini Canal | MICL.01943026/DNC | 19 | 430 | 26 | 26 | 1897 | 1897 | 1897 | 0.045167 | 738 | 0.017571 | 2161 | 0.051452 | 1.362 | A04 | MICL0.01943026/DNC
Build-In Floor | Mini Canal | MICL.01943026/DON | 19 | 430 | 26 | 26 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01943026/DON
Build-In Floor | Mini Canal | MICL.01943026/DOV | 19 | 430 | 26 | 26 | 1819 | 1819 | 1819 | 0.04331 | 708 | 0.016857 | 2072 | 0.049333 | 1.362 | A04 | MICL0.01943026/DOV
Build-In Floor | Mini Canal | MICL.01943026/PNC | 19 | 430 | 26 | 26 | 1663 | 1663 | 1663 | 0.039595 | 647 | 0.015405 | 1894 | 0.045095 | 1.362 | A04 | MICL0.01943026/PNC
Build-In Floor | Mini Canal | MICL.01943026/RBL | 19 | 430 | 26 | 26 | 1956 | 1956 | 1956 | 0.046571 | 761 | 0.018119 | 2228 | 0.053048 | 1.362 | A04 | MICL0.01943026/RBL
Build-In Floor | Mini Canal | MICL.01943026/RBN | 19 | 430 | 26 | 26 | 1897 | 1897 | 1897 | 0.045167 | 738 | 0.017571 | 2161 | 0.051452 | 1.362 | A04 | MICL0.01943026/RBN
Build-In Floor | Mini Canal | MICL.01943026/RBR | 19 | 430 | 26 | 26 | 1956 | 1956 | 1956 | 0.046571 | 761 | 0.018119 | 2228 | 0.053048 | 1.362 | A04 | MICL0.01943026/RBR
Build-In Floor | Mini Canal | MICL.01943026/RBV | 19 | 430 | 26 | 26 | 1897 | 1897 | 1897 | 0.045167 | 738 | 0.017571 | 2161 | 0.051452 | 1.362 | A04 | MICL0.01943026/RBV
Build-In Floor | Mini Canal | MICL.01943026/RDB | 19 | 430 | 26 | 26 | 1956 | 1956 | 1956 | 0.046571 | 761 | 0.018119 | 2228 | 0.053048 | 1.362 | A04 | MICL0.01943026/RDB
Build-In Floor | Mini Canal | MICL.01943026/RMN | 19 | 430 | 26 | 26 | 1897 | 1897 | 1897 | 0.045167 | 738 | 0.017571 | 2161 | 0.051452 | 1.362 | A04 | MICL0.01943026/RMN
Build-In Floor | Mini Canal | MICL.01943026/RMV | 19 | 430 | 26 | 26 | 1897 | 1897 | 1897 | 0.045167 | 738 | 0.017571 | 2161 | 0.051452 | 1.362 | A04 | MICL0.01943026/RMV
Build-In Floor | Mini Canal | MICL.01943026/RNA | 19 | 430 | 26 | 26 | 1956 | 1956 | 1956 | 0.046571 | 761 | 0.018119 | 2228 | 0.053048 | 1.362 | A04 | MICL0.01943026/RNA
Build-In Floor | Mini Canal | MICL.01943026/RON | 19 | 430 | 26 | 26 | 1897 | 1897 | 1897 | 0.045167 | 738 | 0.017571 | 2161 | 0.051452 | 1.362 | A04 | MICL0.01943026/RON
Build-In Floor | Mini Canal | MICL.01943026/ROV | 19 | 430 | 26 | 26 | 1897 | 1897 | 1897 | 0.045167 | 738 | 0.017571 | 2161 | 0.051452 | 1.362 | A04 | MICL0.01943026/ROV
Build-In Floor | Mini Canal | MICL.01943026/RSS | 19 | 430 | 26 | 26 | 1878 | 1878 | 1878 | 0.044714 | 731 | 0.017405 | 2139 | 0.050929 | 1.362 | A04 | MICL0.01943026/RSS
Build-In Floor | Mini Canal | MICL.01943026/SBL | 19 | 430 | 26 | 26 | 1956 | 1956 | 1956 | 0.046571 | 761 | 0.018119 | 2228 | 0.053048 | 1.362 | A04 | MICL0.01943026/SBL
Build-In Floor | Mini Canal | MICL.01943026/SBR | 19 | 430 | 26 | 26 | 1956 | 1956 | 1956 | 0.046571 | 761 | 0.018119 | 2228 | 0.053048 | 1.362 | A04 | MICL0.01943026/SBR
Build-In Floor | Mini Canal | MICL.01943026/SDB | 19 | 430 | 26 | 26 | 1956 | 1956 | 1956 | 0.046571 | 761 | 0.018119 | 2228 | 0.053048 | 1.362 | A04 | MICL0.01943026/SDB
Build-In Floor | Mini Canal | MICL.01943026/SNA | 19 | 430 | 26 | 26 | 1956 | 1956 | 1956 | 0.046571 | 761 | 0.018119 | 2228 | 0.053048 | 1.362 | A04 | MICL0.01943026/SNA
Build-In Floor | Mini Canal | MICL.01943026/SNC | 19 | 430 | 26 | 26 | 1956 | 1956 | 1956 | 0.046571 | 761 | 0.018119 | 2228 | 0.053048 | 1.362 | A04 | MICL0.01943026/SNC
Build-In Floor | Mini Canal | MICL.01943034/ANA | 19 | 430 | 34 | 34 | 1987 | 1987 | 1987 | 0.04731 | 773 | 0.018405 | 2263 | 0.053881 | 1.362 | A04 | MICL0.01943034/ANA
Build-In Floor | Mini Canal | MICL.01943034/DBL | 19 | 430 | 34 | 34 | 2570 | 2570 | 2570 | 0.06119 | 1000 | 0.02381 | 2927 | 0.06969 | 1.362 | A04 | MICL0.01943034/DBL
Build-In Floor | Mini Canal | MICL.01943034/DBN | 19 | 430 | 34 | 34 | 2464 | 2464 | 2464 | 0.058667 | 958 | 0.02281 | 2806 | 0.06681 | 1.362 | A04 | MICL0.01943034/DBN
Build-In Floor | Mini Canal | MICL.01943034/DBR | 19 | 430 | 34 | 34 | 2570 | 2570 | 2570 | 0.06119 | 1000 | 0.02381 | 2927 | 0.06969 | 1.362 | A04 | MICL0.01943034/DBR
Build-In Floor | Mini Canal | MICL.01943034/DBV | 19 | 430 | 34 | 34 | 2464 | 2464 | 2464 | 0.058667 | 958 | 0.02281 | 2806 | 0.06681 | 1.362 | A04 | MICL0.01943034/DBV
Build-In Floor | Mini Canal | MICL.01943034/DDB | 19 | 430 | 34 | 34 | 2570 | 2570 | 2570 | 0.06119 | 1000 | 0.02381 | 2927 | 0.06969 | 1.362 | A04 | MICL0.01943034/DDB
Build-In Floor | Mini Canal | MICL.01943034/DMN | 19 | 430 | 34 | 34 | 2464 | 2464 | 2464 | 0.058667 | 958 | 0.02281 | 2806 | 0.06681 | 1.362 | A04 | MICL0.01943034/DMN
Build-In Floor | Mini Canal | MICL.01943034/DMV | 19 | 430 | 34 | 34 | 2464 | 2464 | 2464 | 0.058667 | 958 | 0.02281 | 2806 | 0.06681 | 1.362 | A04 | MICL0.01943034/DMV
Build-In Floor | Mini Canal | MICL.01943034/DNA | 19 | 430 | 34 | 34 | 2570 | 2570 | 2570 | 0.06119 | 1000 | 0.02381 | 2927 | 0.06969 | 1.362 | A04 | MICL0.01943034/DNA
Build-In Floor | Mini Canal | MICL.01943034/DNC | 19 | 430 | 34 | 34 | 2570 | 2570 | 2570 | 0.06119 | 1000 | 0.02381 | 2927 | 0.06969 | 1.362 | A04 | MICL0.01943034/DNC
Build-In Floor | Mini Canal | MICL.01943034/DON | 19 | 430 | 34 | 34 | 2464 | 2464 | 2464 | 0.058667 | 958 | 0.02281 | 2806 | 0.06681 | 1.362 | A04 | MICL0.01943034/DON
Build-In Floor | Mini Canal | MICL.01943034/DOV | 19 | 430 | 34 | 34 | 2464 | 2464 | 2464 | 0.058667 | 958 | 0.02281 | 2806 | 0.06681 | 1.362 | A04 | MICL0.01943034/DOV
Build-In Floor | Mini Canal | MICL.01943034/PNC | 19 | 430 | 34 | 34 | 2252 | 2252 | 2252 | 0.053619 | 876 | 0.020857 | 2565 | 0.061071 | 1.362 | A04 | MICL0.01943034/PNC
Build-In Floor | Mini Canal | MICL.01943034/RBL | 19 | 430 | 34 | 34 | 2649 | 2649 | 2649 | 0.063071 | 1030 | 0.024524 | 3017 | 0.071833 | 1.362 | A04 | MICL0.01943034/RBL
Build-In Floor | Mini Canal | MICL.01943034/RBN | 19 | 430 | 34 | 34 | 2570 | 2570 | 2570 | 0.06119 | 1000 | 0.02381 | 2927 | 0.06969 | 1.362 | A04 | MICL0.01943034/RBN
Build-In Floor | Mini Canal | MICL.01943034/RBR | 19 | 430 | 34 | 34 | 2649 | 2649 | 2649 | 0.063071 | 1030 | 0.024524 | 3017 | 0.071833 | 1.362 | A04 | MICL0.01943034/RBR
Build-In Floor | Mini Canal | MICL.01943034/RBV | 19 | 430 | 34 | 34 | 2570 | 2570 | 2570 | 0.06119 | 1000 | 0.02381 | 2927 | 0.06969 | 1.362 | A04 | MICL0.01943034/RBV
Build-In Floor | Mini Canal | MICL.01943034/RDB | 19 | 430 | 34 | 34 | 2649 | 2649 | 2649 | 0.063071 | 1030 | 0.024524 | 3017 | 0.071833 | 1.362 | A04 | MICL0.01943034/RDB
Build-In Floor | Mini Canal | MICL.01943034/RMN | 19 | 430 | 34 | 34 | 2570 | 2570 | 2570 | 0.06119 | 1000 | 0.02381 | 2927 | 0.06969 | 1.362 | A04 | MICL0.01943034/RMN
Build-In Floor | Mini Canal | MICL.01943034/RMV | 19 | 430 | 34 | 34 | 2570 | 2570 | 2570 | 0.06119 | 1000 | 0.02381 | 2927 | 0.06969 | 1.362 | A04 | MICL0.01943034/RMV
Build-In Floor | Mini Canal | MICL.01943034/RNA | 19 | 430 | 34 | 34 | 2649 | 2649 | 2649 | 0.063071 | 1030 | 0.024524 | 3017 | 0.071833 | 1.362 | A04 | MICL0.01943034/RNA
Build-In Floor | Mini Canal | MICL.01943034/RON | 19 | 430 | 34 | 34 | 2570 | 2570 | 2570 | 0.06119 | 1000 | 0.02381 | 2927 | 0.06969 | 1.362 | A04 | MICL0.01943034/RON
Build-In Floor | Mini Canal | MICL.01943034/ROV | 19 | 430 | 34 | 34 | 2570 | 2570 | 2570 | 0.06119 | 1000 | 0.02381 | 2927 | 0.06969 | 1.362 | A04 | MICL0.01943034/ROV
Build-In Floor | Mini Canal | MICL.01943034/RSS | 19 | 430 | 34 | 34 | 2543 | 2543 | 2543 | 0.060548 | 989 | 0.023548 | 2896 | 0.068952 | 1.362 | A04 | MICL0.01943034/RSS
Build-In Floor | Mini Canal | MICL.01943034/SBL | 19 | 430 | 34 | 34 | 2649 | 2649 | 2649 | 0.063071 | 1030 | 0.024524 | 3017 | 0.071833 | 1.362 | A04 | MICL0.01943034/SBL
Build-In Floor | Mini Canal | MICL.01943034/SBR | 19 | 430 | 34 | 34 | 2649 | 2649 | 2649 | 0.063071 | 1030 | 0.024524 | 3017 | 0.071833 | 1.362 | A04 | MICL0.01943034/SBR
Build-In Floor | Mini Canal | MICL.01943034/SDB | 19 | 430 | 34 | 34 | 2649 | 2649 | 2649 | 0.063071 | 1030 | 0.024524 | 3017 | 0.071833 | 1.362 | A04 | MICL0.01943034/SDB
Build-In Floor | Mini Canal | MICL.01943034/SNA | 19 | 430 | 34 | 34 | 2649 | 2649 | 2649 | 0.063071 | 1030 | 0.024524 | 3017 | 0.071833 | 1.362 | A04 | MICL0.01943034/SNA
Build-In Floor | Mini Canal | MICL.01943034/SNC | 19 | 430 | 34 | 34 | 2649 | 2649 | 2649 | 0.063071 | 1030 | 0.024524 | 3017 | 0.071833 | 1.362 | A04 | MICL0.01943034/SNC
Build-In Floor | Mini Canal | MICL.01943042/ANA | 19 | 430 | 42 | 42 | 2729 | 2729 | 2729 | 0.064976 | 1062 | 0.025286 | 3108 | 0.074 | 1.362 | A04 | MICL0.01943042/ANA
Build-In Floor | Mini Canal | MICL.01943042/DBL | 19 | 430 | 42 | 42 | 3529 | 3529 | 3529 | 0.084024 | 1373 | 0.03269 | 4020 | 0.095714 | 1.362 | A04 | MICL0.01943042/DBL
Build-In Floor | Mini Canal | MICL.01943042/DBN | 19 | 430 | 42 | 42 | 3383 | 3383 | 3383 | 0.080548 | 1316 | 0.031333 | 3853 | 0.091738 | 1.362 | A04 | MICL0.01943042/DBN
Build-In Floor | Mini Canal | MICL.01943042/DBR | 19 | 430 | 42 | 42 | 3529 | 3529 | 3529 | 0.084024 | 1373 | 0.03269 | 4020 | 0.095714 | 1.362 | A04 | MICL0.01943042/DBR
Build-In Floor | Mini Canal | MICL.01943042/DBV | 19 | 430 | 42 | 42 | 3383 | 3383 | 3383 | 0.080548 | 1316 | 0.031333 | 3853 | 0.091738 | 1.362 | A04 | MICL0.01943042/DBV
Build-In Floor | Mini Canal | MICL.01943042/DDB | 19 | 430 | 42 | 42 | 3529 | 3529 | 3529 | 0.084024 | 1373 | 0.03269 | 4020 | 0.095714 | 1.362 | A04 | MICL0.01943042/DDB
Build-In Floor | Mini Canal | MICL.01943042/DMN | 19 | 430 | 42 | 42 | 3383 | 3383 | 3383 | 0.080548 | 1316 | 0.031333 | 3853 | 0.091738 | 1.362 | A04 | MICL0.01943042/DMN
Build-In Floor | Mini Canal | MICL.01943042/DMV | 19 | 430 | 42 | 42 | 3383 | 3383 | 3383 | 0.080548 | 1316 | 0.031333 | 3853 | 0.091738 | 1.362 | A04 | MICL0.01943042/DMV
Build-In Floor | Mini Canal | MICL.01943042/DNA | 19 | 430 | 42 | 42 | 3529 | 3529 | 3529 | 0.084024 | 1373 | 0.03269 | 4020 | 0.095714 | 1.362 | A04 | MICL0.01943042/DNA
Build-In Floor | Mini Canal | MICL.01943042/DNC | 19 | 430 | 42 | 42 | 3529 | 3529 | 3529 | 0.084024 | 1373 | 0.03269 | 4020 | 0.095714 | 1.362 | A04 | MICL0.01943042/DNC
Build-In Floor | Mini Canal | MICL.01943042/DON | 19 | 430 | 42 | 42 | 3383 | 3383 | 3383 | 0.080548 | 1316 | 0.031333 | 3853 | 0.091738 | 1.362 | A04 | MICL0.01943042/DON
Build-In Floor | Mini Canal | MICL.01943042/DOV | 19 | 430 | 42 | 42 | 3383 | 3383 | 3383 | 0.080548 | 1316 | 0.031333 | 3853 | 0.091738 | 1.362 | A04 | MICL0.01943042/DOV
Build-In Floor | Mini Canal | MICL.01943042/PNC | 19 | 430 | 42 | 42 | 3092 | 3092 | 3092 | 0.073619 | 1203 | 0.028643 | 3522 | 0.083857 | 1.362 | A04 | MICL0.01943042/PNC
Build-In Floor | Mini Canal | MICL.01943042/RBL | 19 | 430 | 42 | 42 | 3638 | 3638 | 3638 | 0.086619 | 1415 | 0.03369 | 4144 | 0.098667 | 1.362 | A04 | MICL0.01943042/RBL
Build-In Floor | Mini Canal | MICL.01943042/RBN | 19 | 430 | 42 | 42 | 3529 | 3529 | 3529 | 0.084024 | 1373 | 0.03269 | 4020 | 0.095714 | 1.362 | A04 | MICL0.01943042/RBN
Build-In Floor | Mini Canal | MICL.01943042/RBR | 19 | 430 | 42 | 42 | 3638 | 3638 | 3638 | 0.086619 | 1415 | 0.03369 | 4144 | 0.098667 | 1.362 | A04 | MICL0.01943042/RBR
Build-In Floor | Mini Canal | MICL.01943042/RBV | 19 | 430 | 42 | 42 | 3529 | 3529 | 3529 | 0.084024 | 1373 | 0.03269 | 4020 | 0.095714 | 1.362 | A04 | MICL0.01943042/RBV
Build-In Floor | Mini Canal | MICL.01943042/RDB | 19 | 430 | 42 | 42 | 3638 | 3638 | 3638 | 0.086619 | 1415 | 0.03369 | 4144 | 0.098667 | 1.362 | A04 | MICL0.01943042/RDB
Build-In Floor | Mini Canal | MICL.01943042/RMN | 19 | 430 | 42 | 42 | 3529 | 3529 | 3529 | 0.084024 | 1373 | 0.03269 | 4020 | 0.095714 | 1.362 | A04 | MICL0.01943042/RMN
Build-In Floor | Mini Canal | MICL.01943042/RMV | 19 | 430 | 42 | 42 | 3529 | 3529 | 3529 | 0.084024 | 1373 | 0.03269 | 4020 | 0.095714 | 1.362 | A04 | MICL0.01943042/RMV
Build-In Floor | Mini Canal | MICL.01943042/RNA | 19 | 430 | 42 | 42 | 3638 | 3638 | 3638 | 0.086619 | 1415 | 0.03369 | 4144 | 0.098667 | 1.362 | A04 | MICL0.01943042/RNA
Build-In Floor | Mini Canal | MICL.01943042/RON | 19 | 430 | 42 | 42 | 3529 | 3529 | 3529 | 0.084024 | 1373 | 0.03269 | 4020 | 0.095714 | 1.362 | A04 | MICL0.01943042/RON
Build-In Floor | Mini Canal | MICL.01943042/ROV | 19 | 430 | 42 | 42 | 3529 | 3529 | 3529 | 0.084024 | 1373 | 0.03269 | 4020 | 0.095714 | 1.362 | A04 | MICL0.01943042/ROV
Build-In Floor | Mini Canal | MICL.01943042/RSS | 19 | 430 | 42 | 42 | 3492 | 3492 | 3492 | 0.083143 | 1358 | 0.032333 | 3977 | 0.09469 | 1.362 | A04 | MICL0.01943042/RSS
Build-In Floor | Mini Canal | MICL.01943042/SBL | 19 | 430 | 42 | 42 | 3638 | 3638 | 3638 | 0.086619 | 1415 | 0.03369 | 4144 | 0.098667 | 1.362 | A04 | MICL0.01943042/SBL
Build-In Floor | Mini Canal | MICL.01943042/SBR | 19 | 430 | 42 | 42 | 3638 | 3638 | 3638 | 0.086619 | 1415 | 0.03369 | 4144 | 0.098667 | 1.362 | A04 | MICL0.01943042/SBR
Build-In Floor | Mini Canal | MICL.01943042/SDB | 19 | 430 | 42 | 42 | 3638 | 3638 | 3638 | 0.086619 | 1415 | 0.03369 | 4144 | 0.098667 | 1.362 | A04 | MICL0.01943042/SDB
Build-In Floor | Mini Canal | MICL.01943042/SNA | 19 | 430 | 42 | 42 | 3638 | 3638 | 3638 | 0.086619 | 1415 | 0.03369 | 4144 | 0.098667 | 1.362 | A04 | MICL0.01943042/SNA
Build-In Floor | Mini Canal | MICL.01943042/SNC | 19 | 430 | 42 | 42 | 3638 | 3638 | 3638 | 0.086619 | 1415 | 0.03369 | 4144 | 0.098667 | 1.362 | A04 | MICL0.01943042/SNC
Build-In Floor | Mini Canal | MICL.01945026/ANA | 19 | 450 | 26 | 26 | 1541 | 1541 | 1541 | 0.03669 | 599 | 0.014262 | 1755 | 0.041786 | 1.362 | A04 | MICL0.01945026/ANA
Build-In Floor | Mini Canal | MICL.01945026/DBL | 19 | 450 | 26 | 26 | 1992 | 1992 | 1992 | 0.047429 | 775 | 0.018452 | 2269 | 0.054024 | 1.362 | A04 | MICL0.01945026/DBL
Build-In Floor | Mini Canal | MICL.01945026/DBN | 19 | 450 | 26 | 26 | 1910 | 1910 | 1910 | 0.045476 | 743 | 0.01769 | 2175 | 0.051786 | 1.362 | A04 | MICL0.01945026/DBN
Build-In Floor | Mini Canal | MICL.01945026/DBR | 19 | 450 | 26 | 26 | 1992 | 1992 | 1992 | 0.047429 | 775 | 0.018452 | 2269 | 0.054024 | 1.362 | A04 | MICL0.01945026/DBR
Build-In Floor | Mini Canal | MICL.01945026/DBV | 19 | 450 | 26 | 26 | 1910 | 1910 | 1910 | 0.045476 | 743 | 0.01769 | 2175 | 0.051786 | 1.362 | A04 | MICL0.01945026/DBV
Build-In Floor | Mini Canal | MICL.01945026/DDB | 19 | 450 | 26 | 26 | 1992 | 1992 | 1992 | 0.047429 | 775 | 0.018452 | 2269 | 0.054024 | 1.362 | A04 | MICL0.01945026/DDB
Build-In Floor | Mini Canal | MICL.01945026/DMN | 19 | 450 | 26 | 26 | 1910 | 1910 | 1910 | 0.045476 | 743 | 0.01769 | 2175 | 0.051786 | 1.362 | A04 | MICL0.01945026/DMN
Build-In Floor | Mini Canal | MICL.01945026/DMV | 19 | 450 | 26 | 26 | 1910 | 1910 | 1910 | 0.045476 | 743 | 0.01769 | 2175 | 0.051786 | 1.362 | A04 | MICL0.01945026/DMV
Build-In Floor | Mini Canal | MICL.01945026/DNA | 19 | 450 | 26 | 26 | 1992 | 1992 | 1992 | 0.047429 | 775 | 0.018452 | 2269 | 0.054024 | 1.362 | A04 | MICL0.01945026/DNA
Build-In Floor | Mini Canal | MICL.01945026/DNC | 19 | 450 | 26 | 26 | 1992 | 1992 | 1992 | 0.047429 | 775 | 0.018452 | 2269 | 0.054024 | 1.362 | A04 | MICL0.01945026/DNC
Build-In Floor | Mini Canal | MICL.01945026/DON | 19 | 450 | 26 | 26 | 1910 | 1910 | 1910 | 0.045476 | 743 | 0.01769 | 2175 | 0.051786 | 1.362 | A04 | MICL0.01945026/DON
Build-In Floor | Mini Canal | MICL.01945026/DOV | 19 | 450 | 26 | 26 | 1910 | 1910 | 1910 | 0.045476 | 743 | 0.01769 | 2175 | 0.051786 | 1.362 | A04 | MICL0.01945026/DOV
Build-In Floor | Mini Canal | MICL.01945026/PNC | 19 | 450 | 26 | 26 | 1746 | 1746 | 1746 | 0.041571 | 679 | 0.016167 | 1989 | 0.047357 | 1.362 | A04 | MICL0.01945026/PNC
Build-In Floor | Mini Canal | MICL.01945026/RBL | 19 | 450 | 26 | 26 | 2054 | 2054 | 2054 | 0.048905 | 799 | 0.019024 | 2340 | 0.055714 | 1.362 | A04 | MICL0.01945026/RBL
Build-In Floor | Mini Canal | MICL.01945026/RBN | 19 | 450 | 26 | 26 | 1992 | 1992 | 1992 | 0.047429 | 775 | 0.018452 | 2269 | 0.054024 | 1.362 | A04 | MICL0.01945026/RBN
Build-In Floor | Mini Canal | MICL.01945026/RBR | 19 | 450 | 26 | 26 | 2054 | 2054 | 2054 | 0.048905 | 799 | 0.019024 | 2340 | 0.055714 | 1.362 | A04 | MICL0.01945026/RBR
Build-In Floor | Mini Canal | MICL.01945026/RBV | 19 | 450 | 26 | 26 | 1992 | 1992 | 1992 | 0.047429 | 775 | 0.018452 | 2269 | 0.054024 | 1.362 | A04 | MICL0.01945026/RBV
Build-In Floor | Mini Canal | MICL.01945026/RDB | 19 | 450 | 26 | 26 | 2054 | 2054 | 2054 | 0.048905 | 799 | 0.019024 | 2340 | 0.055714 | 1.362 | A04 | MICL0.01945026/RDB
Build-In Floor | Mini Canal | MICL.01945026/RMN | 19 | 450 | 26 | 26 | 1992 | 1992 | 1992 | 0.047429 | 775 | 0.018452 | 2269 | 0.054024 | 1.362 | A04 | MICL0.01945026/RMN
Build-In Floor | Mini Canal | MICL.01945026/RMV | 19 | 450 | 26 | 26 | 1992 | 1992 | 1992 | 0.047429 | 775 | 0.018452 | 2269 | 0.054024 | 1.362 | A04 | MICL0.01945026/RMV
Build-In Floor | Mini Canal | MICL.01945026/RNA | 19 | 450 | 26 | 26 | 2054 | 2054 | 2054 | 0.048905 | 799 | 0.019024 | 2340 | 0.055714 | 1.362 | A04 | MICL0.01945026/RNA
Build-In Floor | Mini Canal | MICL.01945026/RON | 19 | 450 | 26 | 26 | 1992 | 1992 | 1992 | 0.047429 | 775 | 0.018452 | 2269 | 0.054024 | 1.362 | A04 | MICL0.01945026/RON
Build-In Floor | Mini Canal | MICL.01945026/ROV | 19 | 450 | 26 | 26 | 1992 | 1992 | 1992 | 0.047429 | 775 | 0.018452 | 2269 | 0.054024 | 1.362 | A04 | MICL0.01945026/ROV
Build-In Floor | Mini Canal | MICL.01945026/RSS | 19 | 450 | 26 | 26 | 1972 | 1972 | 1972 | 0.046952 | 767 | 0.018262 | 2246 | 0.053476 | 1.362 | A04 | MICL0.01945026/RSS
Build-In Floor | Mini Canal | MICL.01945026/SBL | 19 | 450 | 26 | 26 | 2054 | 2054 | 2054 | 0.048905 | 799 | 0.019024 | 2340 | 0.055714 | 1.362 | A04 | MICL0.01945026/SBL
Build-In Floor | Mini Canal | MICL.01945026/SBR | 19 | 450 | 26 | 26 | 2054 | 2054 | 2054 | 0.048905 | 799 | 0.019024 | 2340 | 0.055714 | 1.362 | A04 | MICL0.01945026/SBR
Build-In Floor | Mini Canal | MICL.01945026/SDB | 19 | 450 | 26 | 26 | 2054 | 2054 | 2054 | 0.048905 | 799 | 0.019024 | 2340 | 0.055714 | 1.362 | A04 | MICL0.01945026/SDB
Build-In Floor | Mini Canal | MICL.01945026/SNA | 19 | 450 | 26 | 26 | 2054 | 2054 | 2054 | 0.048905 | 799 | 0.019024 | 2340 | 0.055714 | 1.362 | A04 | MICL0.01945026/SNA
Build-In Floor | Mini Canal | MICL.01945026/SNC | 19 | 450 | 26 | 26 | 2054 | 2054 | 2054 | 0.048905 | 799 | 0.019024 | 2340 | 0.055714 | 1.362 | A04 | MICL0.01945026/SNC
Build-In Floor | Mini Canal | MICL.01945034/ANA | 19 | 450 | 34 | 34 | 2086 | 2086 | 2086 | 0.049667 | 811 | 0.01931 | 2376 | 0.056571 | 1.362 | A04 | MICL0.01945034/ANA
Build-In Floor | Mini Canal | MICL.01945034/DBL | 19 | 450 | 34 | 34 | 2698 | 2698 | 2698 | 0.064238 | 1050 | 0.025 | 3073 | 0.073167 | 1.362 | A04 | MICL0.01945034/DBL
Build-In Floor | Mini Canal | MICL.01945034/DBN | 19 | 450 | 34 | 34 | 2586 | 2586 | 2586 | 0.061571 | 1006 | 0.023952 | 2945 | 0.070119 | 1.362 | A04 | MICL0.01945034/DBN
Build-In Floor | Mini Canal | MICL.01945034/DBR | 19 | 450 | 34 | 34 | 2698 | 2698 | 2698 | 0.064238 | 1050 | 0.025 | 3073 | 0.073167 | 1.362 | A04 | MICL0.01945034/DBR
Build-In Floor | Mini Canal | MICL.01945034/DBV | 19 | 450 | 34 | 34 | 2586 | 2586 | 2586 | 0.061571 | 1006 | 0.023952 | 2945 | 0.070119 | 1.362 | A04 | MICL0.01945034/DBV
Build-In Floor | Mini Canal | MICL.01945034/DDB | 19 | 450 | 34 | 34 | 2698 | 2698 | 2698 | 0.064238 | 1050 | 0.025 | 3073 | 0.073167 | 1.362 | A04 | MICL0.01945034/DDB
Build-In Floor | Mini Canal | MICL.01945034/DMN | 19 | 450 | 34 | 34 | 2586 | 2586 | 2586 | 0.061571 | 1006 | 0.023952 | 2945 | 0.070119 | 1.362 | A04 | MICL0.01945034/DMN
Build-In Floor | Mini Canal | MICL.01945034/DMV | 19 | 450 | 34 | 34 | 2586 | 2586 | 2586 | 0.061571 | 1006 | 0.023952 | 2945 | 0.070119 | 1.362 | A04 | MICL0.01945034/DMV
Build-In Floor | Mini Canal | MICL.01945034/DNA | 19 | 450 | 34 | 34 | 2698 | 2698 | 2698 | 0.064238 | 1050 | 0.025 | 3073 | 0.073167 | 1.362 | A04 | MICL0.01945034/DNA
Build-In Floor | Mini Canal | MICL.01945034/DNC | 19 | 450 | 34 | 34 | 2698 | 2698 | 2698 | 0.064238 | 1050 | 0.025 | 3073 | 0.073167 | 1.362 | A04 | MICL0.01945034/DNC
Build-In Floor | Mini Canal | MICL.01945034/DON | 19 | 450 | 34 | 34 | 2586 | 2586 | 2586 | 0.061571 | 1006 | 0.023952 | 2945 | 0.070119 | 1.362 | A04 | MICL0.01945034/DON
Build-In Floor | Mini Canal | MICL.01945034/DOV | 19 | 450 | 34 | 34 | 2586 | 2586 | 2586 | 0.061571 | 1006 | 0.023952 | 2945 | 0.070119 | 1.362 | A04 | MICL0.01945034/DOV
Build-In Floor | Mini Canal | MICL.01945034/PNC | 19 | 450 | 34 | 34 | 2364 | 2364 | 2364 | 0.056286 | 920 | 0.021905 | 2693 | 0.064119 | 1.362 | A04 | MICL0.01945034/PNC
Build-In Floor | Mini Canal | MICL.01945034/RBL | 19 | 450 | 34 | 34 | 2781 | 2781 | 2781 | 0.066214 | 1082 | 0.025762 | 3168 | 0.075429 | 1.362 | A04 | MICL0.01945034/RBL
Build-In Floor | Mini Canal | MICL.01945034/RBN | 19 | 450 | 34 | 34 | 2698 | 2698 | 2698 | 0.064238 | 1050 | 0.025 | 3073 | 0.073167 | 1.362 | A04 | MICL0.01945034/RBN
Build-In Floor | Mini Canal | MICL.01945034/RBR | 19 | 450 | 34 | 34 | 2781 | 2781 | 2781 | 0.066214 | 1082 | 0.025762 | 3168 | 0.075429 | 1.362 | A04 | MICL0.01945034/RBR
Build-In Floor | Mini Canal | MICL.01945034/RBV | 19 | 450 | 34 | 34 | 2698 | 2698 | 2698 | 0.064238 | 1050 | 0.025 | 3073 | 0.073167 | 1.362 | A04 | MICL0.01945034/RBV
Build-In Floor | Mini Canal | MICL.01945034/RDB | 19 | 450 | 34 | 34 | 2781 | 2781 | 2781 | 0.066214 | 1082 | 0.025762 | 3168 | 0.075429 | 1.362 | A04 | MICL0.01945034/RDB
Build-In Floor | Mini Canal | MICL.01945034/RMN | 19 | 450 | 34 | 34 | 2698 | 2698 | 2698 | 0.064238 | 1050 | 0.025 | 3073 | 0.073167 | 1.362 | A04 | MICL0.01945034/RMN
Build-In Floor | Mini Canal | MICL.01945034/RMV | 19 | 450 | 34 | 34 | 2698 | 2698 | 2698 | 0.064238 | 1050 | 0.025 | 3073 | 0.073167 | 1.362 | A04 | MICL0.01945034/RMV
Build-In Floor | Mini Canal | MICL.01945034/RNA | 19 | 450 | 34 | 34 | 2781 | 2781 | 2781 | 0.066214 | 1082 | 0.025762 | 3168 | 0.075429 | 1.362 | A04 | MICL0.01945034/RNA
Build-In Floor | Mini Canal | MICL.01945034/RON | 19 | 450 | 34 | 34 | 2698 | 2698 | 2698 | 0.064238 | 1050 | 0.025 | 3073 | 0.073167 | 1.362 | A04 | MICL0.01945034/RON
Build-In Floor | Mini Canal | MICL.01945034/ROV | 19 | 450 | 34 | 34 | 2698 | 2698 | 2698 | 0.064238 | 1050 | 0.025 | 3073 | 0.073167 | 1.362 | A04 | MICL0.01945034/ROV
Build-In Floor | Mini Canal | MICL.01945034/RSS | 19 | 450 | 34 | 34 | 2670 | 2670 | 2670 | 0.063571 | 1039 | 0.024738 | 3041 | 0.072405 | 1.362 | A04 | MICL0.01945034/RSS
Build-In Floor | Mini Canal | MICL.01945034/SBL | 19 | 450 | 34 | 34 | 2781 | 2781 | 2781 | 0.066214 | 1082 | 0.025762 | 3168 | 0.075429 | 1.362 | A04 | MICL0.01945034/SBL
Build-In Floor | Mini Canal | MICL.01945034/SBR | 19 | 450 | 34 | 34 | 2781 | 2781 | 2781 | 0.066214 | 1082 | 0.025762 | 3168 | 0.075429 | 1.362 | A04 | MICL0.01945034/SBR
Build-In Floor | Mini Canal | MICL.01945034/SDB | 19 | 450 | 34 | 34 | 2781 | 2781 | 2781 | 0.066214 | 1082 | 0.025762 | 3168 | 0.075429 | 1.362 | A04 | MICL0.01945034/SDB
Build-In Floor | Mini Canal | MICL.01945034/SNA | 19 | 450 | 34 | 34 | 2781 | 2781 | 2781 | 0.066214 | 1082 | 0.025762 | 3168 | 0.075429 | 1.362 | A04 | MICL0.01945034/SNA
Build-In Floor | Mini Canal | MICL.01945034/SNC | 19 | 450 | 34 | 34 | 2781 | 2781 | 2781 | 0.066214 | 1082 | 0.025762 | 3168 | 0.075429 | 1.362 | A04 | MICL0.01945034/SNC
Build-In Floor | Mini Canal | MICL.01945042/ANA | 19 | 450 | 42 | 42 | 2865 | 2865 | 2865 | 0.068214 | 1114 | 0.026524 | 3263 | 0.07769 | 1.362 | A04 | MICL0.01945042/ANA
Build-In Floor | Mini Canal | MICL.01945042/DBL | 19 | 450 | 42 | 42 | 3705 | 3705 | 3705 | 0.088214 | 1441 | 0.03431 | 4220 | 0.10048 | 1.362 | A04 | MICL0.01945042/DBL
Build-In Floor | Mini Canal | MICL.01945042/DBN | 19 | 450 | 42 | 42 | 3553 | 3553 | 3553 | 0.084595 | 1382 | 0.032905 | 4047 | 0.096357 | 1.362 | A04 | MICL0.01945042/DBN
Build-In Floor | Mini Canal | MICL.01945042/DBR | 19 | 450 | 42 | 42 | 3705 | 3705 | 3705 | 0.088214 | 1441 | 0.03431 | 4220 | 0.10048 | 1.362 | A04 | MICL0.01945042/DBR
Build-In Floor | Mini Canal | MICL.01945042/DBV | 19 | 450 | 42 | 42 | 3553 | 3553 | 3553 | 0.084595 | 1382 | 0.032905 | 4047 | 0.096357 | 1.362 | A04 | MICL0.01945042/DBV
Build-In Floor | Mini Canal | MICL.01945042/DDB | 19 | 450 | 42 | 42 | 3705 | 3705 | 3705 | 0.088214 | 1441 | 0.03431 | 4220 | 0.10048 | 1.362 | A04 | MICL0.01945042/DDB
Build-In Floor | Mini Canal | MICL.01945042/DMN | 19 | 450 | 42 | 42 | 3553 | 3553 | 3553 | 0.084595 | 1382 | 0.032905 | 4047 | 0.096357 | 1.362 | A04 | MICL0.01945042/DMN
Build-In Floor | Mini Canal | MICL.01945042/DMV | 19 | 450 | 42 | 42 | 3553 | 3553 | 3553 | 0.084595 | 1382 | 0.032905 | 4047 | 0.096357 | 1.362 | A04 | MICL0.01945042/DMV
Build-In Floor | Mini Canal | MICL.01945042/DNA | 19 | 450 | 42 | 42 | 3705 | 3705 | 3705 | 0.088214 | 1441 | 0.03431 | 4220 | 0.10048 | 1.362 | A04 | MICL0.01945042/DNA
Build-In Floor | Mini Canal | MICL.01945042/DNC | 19 | 450 | 42 | 42 | 3705 | 3705 | 3705 | 0.088214 | 1441 | 0.03431 | 4220 | 0.10048 | 1.362 | A04 | MICL0.01945042/DNC
Build-In Floor | Mini Canal | MICL.01945042/DON | 19 | 450 | 42 | 42 | 3553 | 3553 | 3553 | 0.084595 | 1382 | 0.032905 | 4047 | 0.096357 | 1.362 | A04 | MICL0.01945042/DON
Build-In Floor | Mini Canal | MICL.01945042/DOV | 19 | 450 | 42 | 42 | 3553 | 3553 | 3553 | 0.084595 | 1382 | 0.032905 | 4047 | 0.096357 | 1.362 | A04 | MICL0.01945042/DOV
Build-In Floor | Mini Canal | MICL.01945042/PNC | 19 | 450 | 42 | 42 | 3247 | 3247 | 3247 | 0.07731 | 1263 | 0.030071 | 3698 | 0.088048 | 1.362 | A04 | MICL0.01945042/PNC
Build-In Floor | Mini Canal | MICL.01945042/RBL | 19 | 450 | 42 | 42 | 3820 | 3820 | 3820 | 0.090952 | 1486 | 0.035381 | 4351 | 0.1036 | 1.362 | A04 | MICL0.01945042/RBL
Build-In Floor | Mini Canal | MICL.01945042/RBN | 19 | 450 | 42 | 42 | 3705 | 3705 | 3705 | 0.088214 | 1441 | 0.03431 | 4220 | 0.10048 | 1.362 | A04 | MICL0.01945042/RBN
Build-In Floor | Mini Canal | MICL.01945042/RBR | 19 | 450 | 42 | 42 | 3820 | 3820 | 3820 | 0.090952 | 1486 | 0.035381 | 4351 | 0.1036 | 1.362 | A04 | MICL0.01945042/RBR
Build-In Floor | Mini Canal | MICL.01945042/RBV | 19 | 450 | 42 | 42 | 3705 | 3705 | 3705 | 0.088214 | 1441 | 0.03431 | 4220 | 0.10048 | 1.362 | A04 | MICL0.01945042/RBV
Build-In Floor | Mini Canal | MICL.01945042/RDB | 19 | 450 | 42 | 42 | 3820 | 3820 | 3820 | 0.090952 | 1486 | 0.035381 | 4351 | 0.1036 | 1.362 | A04 | MICL0.01945042/RDB
Build-In Floor | Mini Canal | MICL.01945042/RMN | 19 | 450 | 42 | 42 | 3705 | 3705 | 3705 | 0.088214 | 1441 | 0.03431 | 4220 | 0.10048 | 1.362 | A04 | MICL0.01945042/RMN
Build-In Floor | Mini Canal | MICL.01945042/RMV | 19 | 450 | 42 | 42 | 3705 | 3705 | 3705 | 0.088214 | 1441 | 0.03431 | 4220 | 0.10048 | 1.362 | A04 | MICL0.01945042/RMV
Build-In Floor | Mini Canal | MICL.01945042/RNA | 19 | 450 | 42 | 42 | 3820 | 3820 | 3820 | 0.090952 | 1486 | 0.035381 | 4351 | 0.1036 | 1.362 | A04 | MICL0.01945042/RNA
Build-In Floor | Mini Canal | MICL.01945042/RON | 19 | 450 | 42 | 42 | 3705 | 3705 | 3705 | 0.088214 | 1441 | 0.03431 | 4220 | 0.10048 | 1.362 | A04 | MICL0.01945042/RON
Build-In Floor | Mini Canal | MICL.01945042/ROV | 19 | 450 | 42 | 42 | 3705 | 3705 | 3705 | 0.088214 | 1441 | 0.03431 | 4220 | 0.10048 | 1.362 | A04 | MICL0.01945042/ROV
Build-In Floor | Mini Canal | MICL.01945042/RSS | 19 | 450 | 42 | 42 | 3667 | 3667 | 3667 | 0.08731 | 1426 | 0.033952 | 4177 | 0.099452 | 1.362 | A04 | MICL0.01945042/RSS
Build-In Floor | Mini Canal | MICL.01945042/SBL | 19 | 450 | 42 | 42 | 3820 | 3820 | 3820 | 0.090952 | 1486 | 0.035381 | 4351 | 0.1036 | 1.362 | A04 | MICL0.01945042/SBL
Build-In Floor | Mini Canal | MICL.01945042/SBR | 19 | 450 | 42 | 42 | 3820 | 3820 | 3820 | 0.090952 | 1486 | 0.035381 | 4351 | 0.1036 | 1.362 | A04 | MICL0.01945042/SBR
Build-In Floor | Mini Canal | MICL.01945042/SDB | 19 | 450 | 42 | 42 | 3820 | 3820 | 3820 | 0.090952 | 1486 | 0.035381 | 4351 | 0.1036 | 1.362 | A04 | MICL0.01945042/SDB
Build-In Floor | Mini Canal | MICL.01945042/SNA | 19 | 450 | 42 | 42 | 3820 | 3820 | 3820 | 0.090952 | 1486 | 0.035381 | 4351 | 0.1036 | 1.362 | A04 | MICL0.01945042/SNA
Build-In Floor | Mini Canal | MICL.01945042/SNC | 19 | 450 | 42 | 42 | 3820 | 3820 | 3820 | 0.090952 | 1486 | 0.035381 | 4351 | 0.1036 | 1.362 | A04 | MICL0.01945042/SNC
Build-In Floor | Mini Canal | MICL.01947026/ANA | 19 | 470 | 26 | 26 | 1614 | 1614 | 1614 | 0.038429 | 628 | 0.014952 | 1838 | 0.043762 | 1.362 | A04 | MICL0.01947026/ANA
Build-In Floor | Mini Canal | MICL.01947026/DBL | 19 | 470 | 26 | 26 | 2087 | 2087 | 2087 | 0.04969 | 812 | 0.019333 | 2377 | 0.056595 | 1.362 | A04 | MICL0.01947026/DBL
Build-In Floor | Mini Canal | MICL.01947026/DBN | 19 | 470 | 26 | 26 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01947026/DBN
Build-In Floor | Mini Canal | MICL.01947026/DBR | 19 | 470 | 26 | 26 | 2087 | 2087 | 2087 | 0.04969 | 812 | 0.019333 | 2377 | 0.056595 | 1.362 | A04 | MICL0.01947026/DBR
Build-In Floor | Mini Canal | MICL.01947026/DBV | 19 | 470 | 26 | 26 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01947026/DBV
Build-In Floor | Mini Canal | MICL.01947026/DDB | 19 | 470 | 26 | 26 | 2087 | 2087 | 2087 | 0.04969 | 812 | 0.019333 | 2377 | 0.056595 | 1.362 | A04 | MICL0.01947026/DDB
Build-In Floor | Mini Canal | MICL.01947026/DMN | 19 | 470 | 26 | 26 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01947026/DMN
Build-In Floor | Mini Canal | MICL.01947026/DMV | 19 | 470 | 26 | 26 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01947026/DMV
Build-In Floor | Mini Canal | MICL.01947026/DNA | 19 | 470 | 26 | 26 | 2087 | 2087 | 2087 | 0.04969 | 812 | 0.019333 | 2377 | 0.056595 | 1.362 | A04 | MICL0.01947026/DNA
Build-In Floor | Mini Canal | MICL.01947026/DNC | 19 | 470 | 26 | 26 | 2087 | 2087 | 2087 | 0.04969 | 812 | 0.019333 | 2377 | 0.056595 | 1.362 | A04 | MICL0.01947026/DNC
Build-In Floor | Mini Canal | MICL.01947026/DON | 19 | 470 | 26 | 26 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01947026/DON
Build-In Floor | Mini Canal | MICL.01947026/DOV | 19 | 470 | 26 | 26 | 2001 | 2001 | 2001 | 0.047643 | 778 | 0.018524 | 2279 | 0.054262 | 1.362 | A04 | MICL0.01947026/DOV
Build-In Floor | Mini Canal | MICL.01947026/PNC | 19 | 470 | 26 | 26 | 1829 | 1829 | 1829 | 0.043548 | 711 | 0.016929 | 2083 | 0.049595 | 1.362 | A04 | MICL0.01947026/PNC
Build-In Floor | Mini Canal | MICL.01947026/RBL | 19 | 470 | 26 | 26 | 2152 | 2152 | 2152 | 0.051238 | 837 | 0.019929 | 2451 | 0.058357 | 1.362 | A04 | MICL0.01947026/RBL
Build-In Floor | Mini Canal | MICL.01947026/RBN | 19 | 470 | 26 | 26 | 2087 | 2087 | 2087 | 0.04969 | 812 | 0.019333 | 2377 | 0.056595 | 1.362 | A04 | MICL0.01947026/RBN
Build-In Floor | Mini Canal | MICL.01947026/RBR | 19 | 470 | 26 | 26 | 2152 | 2152 | 2152 | 0.051238 | 837 | 0.019929 | 2451 | 0.058357 | 1.362 | A04 | MICL0.01947026/RBR
Build-In Floor | Mini Canal | MICL.01947026/RBV | 19 | 470 | 26 | 26 | 2087 | 2087 | 2087 | 0.04969 | 812 | 0.019333 | 2377 | 0.056595 | 1.362 | A04 | MICL0.01947026/RBV
Build-In Floor | Mini Canal | MICL.01947026/RDB | 19 | 470 | 26 | 26 | 2152 | 2152 | 2152 | 0.051238 | 837 | 0.019929 | 2451 | 0.058357 | 1.362 | A04 | MICL0.01947026/RDB
Build-In Floor | Mini Canal | MICL.01947026/RMN | 19 | 470 | 26 | 26 | 2087 | 2087 | 2087 | 0.04969 | 812 | 0.019333 | 2377 | 0.056595 | 1.362 | A04 | MICL0.01947026/RMN
Build-In Floor | Mini Canal | MICL.01947026/RMV | 19 | 470 | 26 | 26 | 2087 | 2087 | 2087 | 0.04969 | 812 | 0.019333 | 2377 | 0.056595 | 1.362 | A04 | MICL0.01947026/RMV
Build-In Floor | Mini Canal | MICL.01947026/RNA | 19 | 470 | 26 | 26 | 2152 | 2152 | 2152 | 0.051238 | 837 | 0.019929 | 2451 | 0.058357 | 1.362 | A04 | MICL0.01947026/RNA
Build-In Floor | Mini Canal | MICL.01947026/RON | 19 | 470 | 26 | 26 | 2087 | 2087 | 2087 | 0.04969 | 812 | 0.019333 | 2377 | 0.056595 | 1.362 | A04 | MICL0.01947026/RON
Build-In Floor | Mini Canal | MICL.01947026/ROV | 19 | 470 | 26 | 26 | 2087 | 2087 | 2087 | 0.04969 | 812 | 0.019333 | 2377 | 0.056595 | 1.362 | A04 | MICL0.01947026/ROV
Build-In Floor | Mini Canal | MICL.01947026/RSS | 19 | 470 | 26 | 26 | 2066 | 2066 | 2066 | 0.04919 | 804 | 0.019143 | 2353 | 0.056024 | 1.362 | A04 | MICL0.01947026/RSS
Build-In Floor | Mini Canal | MICL.01947026/SBL | 19 | 470 | 26 | 26 | 2152 | 2152 | 2152 | 0.051238 | 837 | 0.019929 | 2451 | 0.058357 | 1.362 | A04 | MICL0.01947026/SBL
Build-In Floor | Mini Canal | MICL.01947026/SBR | 19 | 470 | 26 | 26 | 2152 | 2152 | 2152 | 0.051238 | 837 | 0.019929 | 2451 | 0.058357 | 1.362 | A04 | MICL0.01947026/SBR
Build-In Floor | Mini Canal | MICL.01947026/SDB | 19 | 470 | 26 | 26 | 2152 | 2152 | 2152 | 0.051238 | 837 | 0.019929 | 2451 | 0.058357 | 1.362 | A04 | MICL0.01947026/SDB
Build-In Floor | Mini Canal | MICL.01947026/SNA | 19 | 470 | 26 | 26 | 2152 | 2152 | 2152 | 0.051238 | 837 | 0.019929 | 2451 | 0.058357 | 1.362 | A04 | MICL0.01947026/SNA
Build-In Floor | Mini Canal | MICL.01947026/SNC | 19 | 470 | 26 | 26 | 2152 | 2152 | 2152 | 0.051238 | 837 | 0.019929 | 2451 | 0.058357 | 1.362 | A04 | MICL0.01947026/SNC
Build-In Floor | Mini Canal | MICL.01947034/ANA | 19 | 470 | 34 | 34 | 2186 | 2186 | 2186 | 0.052048 | 850 | 0.020238 | 2490 | 0.059286 | 1.362 | A04 | MICL0.01947034/ANA
Build-In Floor | Mini Canal | MICL.01947034/DBL | 19 | 470 | 34 | 34 | 2827 | 2827 | 2827 | 0.06731 | 1100 | 0.02619 | 3220 | 0.076667 | 1.362 | A04 | MICL0.01947034/DBL
Build-In Floor | Mini Canal | MICL.01947034/DBN | 19 | 470 | 34 | 34 | 2710 | 2710 | 2710 | 0.064524 | 1054 | 0.025095 | 3087 | 0.0735 | 1.362 | A04 | MICL0.01947034/DBN
Build-In Floor | Mini Canal | MICL.01947034/DBR | 19 | 470 | 34 | 34 | 2827 | 2827 | 2827 | 0.06731 | 1100 | 0.02619 | 3220 | 0.076667 | 1.362 | A04 | MICL0.01947034/DBR
Build-In Floor | Mini Canal | MICL.01947034/DBV | 19 | 470 | 34 | 34 | 2710 | 2710 | 2710 | 0.064524 | 1054 | 0.025095 | 3087 | 0.0735 | 1.362 | A04 | MICL0.01947034/DBV
Build-In Floor | Mini Canal | MICL.01947034/DDB | 19 | 470 | 34 | 34 | 2827 | 2827 | 2827 | 0.06731 | 1100 | 0.02619 | 3220 | 0.076667 | 1.362 | A04 | MICL0.01947034/DDB
Build-In Floor | Mini Canal | MICL.01947034/DMN | 19 | 470 | 34 | 34 | 2710 | 2710 | 2710 | 0.064524 | 1054 | 0.025095 | 3087 | 0.0735 | 1.362 | A04 | MICL0.01947034/DMN
Build-In Floor | Mini Canal | MICL.01947034/DMV | 19 | 470 | 34 | 34 | 2710 | 2710 | 2710 | 0.064524 | 1054 | 0.025095 | 3087 | 0.0735 | 1.362 | A04 | MICL0.01947034/DMV
Build-In Floor | Mini Canal | MICL.01947034/DNA | 19 | 470 | 34 | 34 | 2827 | 2827 | 2827 | 0.06731 | 1100 | 0.02619 | 3220 | 0.076667 | 1.362 | A04 | MICL0.01947034/DNA
Build-In Floor | Mini Canal | MICL.01947034/DNC | 19 | 470 | 34 | 34 | 2827 | 2827 | 2827 | 0.06731 | 1100 | 0.02619 | 3220 | 0.076667 | 1.362 | A04 | MICL0.01947034/DNC
Build-In Floor | Mini Canal | MICL.01947034/DON | 19 | 470 | 34 | 34 | 2710 | 2710 | 2710 | 0.064524 | 1054 | 0.025095 | 3087 | 0.0735 | 1.362 | A04 | MICL0.01947034/DON
Build-In Floor | Mini Canal | MICL.01947034/DOV | 19 | 470 | 34 | 34 | 2710 | 2710 | 2710 | 0.064524 | 1054 | 0.025095 | 3087 | 0.0735 | 1.362 | A04 | MICL0.01947034/DOV
Build-In Floor | Mini Canal | MICL.01947034/PNC | 19 | 470 | 34 | 34 | 2477 | 2477 | 2477 | 0.058976 | 964 | 0.022952 | 2821 | 0.067167 | 1.362 | A04 | MICL0.01947034/PNC
Build-In Floor | Mini Canal | MICL.01947034/RBL | 19 | 470 | 34 | 34 | 2914 | 2914 | 2914 | 0.069381 | 1134 | 0.027 | 3319 | 0.079024 | 1.362 | A04 | MICL0.01947034/RBL
Build-In Floor | Mini Canal | MICL.01947034/RBN | 19 | 470 | 34 | 34 | 2827 | 2827 | 2827 | 0.06731 | 1100 | 0.02619 | 3220 | 0.076667 | 1.362 | A04 | MICL0.01947034/RBN
Build-In Floor | Mini Canal | MICL.01947034/RBR | 19 | 470 | 34 | 34 | 2914 | 2914 | 2914 | 0.069381 | 1134 | 0.027 | 3319 | 0.079024 | 1.362 | A04 | MICL0.01947034/RBR
Build-In Floor | Mini Canal | MICL.01947034/RBV | 19 | 470 | 34 | 34 | 2827 | 2827 | 2827 | 0.06731 | 1100 | 0.02619 | 3220 | 0.076667 | 1.362 | A04 | MICL0.01947034/RBV
Build-In Floor | Mini Canal | MICL.01947034/RDB | 19 | 470 | 34 | 34 | 2914 | 2914 | 2914 | 0.069381 | 1134 | 0.027 | 3319 | 0.079024 | 1.362 | A04 | MICL0.01947034/RDB
Build-In Floor | Mini Canal | MICL.01947034/RMN | 19 | 470 | 34 | 34 | 2827 | 2827 | 2827 | 0.06731 | 1100 | 0.02619 | 3220 | 0.076667 | 1.362 | A04 | MICL0.01947034/RMN
Build-In Floor | Mini Canal | MICL.01947034/RMV | 19 | 470 | 34 | 34 | 2827 | 2827 | 2827 | 0.06731 | 1100 | 0.02619 | 3220 | 0.076667 | 1.362 | A04 | MICL0.01947034/RMV
Build-In Floor | Mini Canal | MICL.01947034/RNA | 19 | 470 | 34 | 34 | 2914 | 2914 | 2914 | 0.069381 | 1134 | 0.027 | 3319 | 0.079024 | 1.362 | A04 | MICL0.01947034/RNA
Build-In Floor | Mini Canal | MICL.01947034/RON | 19 | 470 | 34 | 34 | 2827 | 2827 | 2827 | 0.06731 | 1100 | 0.02619 | 3220 | 0.076667 | 1.362 | A04 | MICL0.01947034/RON
Build-In Floor | Mini Canal | MICL.01947034/ROV | 19 | 470 | 34 | 34 | 2827 | 2827 | 2827 | 0.06731 | 1100 | 0.02619 | 3220 | 0.076667 | 1.362 | A04 | MICL0.01947034/ROV
Build-In Floor | Mini Canal | MICL.01947034/RSS | 19 | 470 | 34 | 34 | 2797 | 2797 | 2797 | 0.066595 | 1088 | 0.025905 | 3186 | 0.075857 | 1.362 | A04 | MICL0.01947034/RSS
Build-In Floor | Mini Canal | MICL.01947034/SBL | 19 | 470 | 34 | 34 | 2914 | 2914 | 2914 | 0.069381 | 1134 | 0.027 | 3319 | 0.079024 | 1.362 | A04 | MICL0.01947034/SBL
Build-In Floor | Mini Canal | MICL.01947034/SBR | 19 | 470 | 34 | 34 | 2914 | 2914 | 2914 | 0.069381 | 1134 | 0.027 | 3319 | 0.079024 | 1.362 | A04 | MICL0.01947034/SBR
Build-In Floor | Mini Canal | MICL.01947034/SDB | 19 | 470 | 34 | 34 | 2914 | 2914 | 2914 | 0.069381 | 1134 | 0.027 | 3319 | 0.079024 | 1.362 | A04 | MICL0.01947034/SDB
Build-In Floor | Mini Canal | MICL.01947034/SNA | 19 | 470 | 34 | 34 | 2914 | 2914 | 2914 | 0.069381 | 1134 | 0.027 | 3319 | 0.079024 | 1.362 | A04 | MICL0.01947034/SNA
Build-In Floor | Mini Canal | MICL.01947034/SNC | 19 | 470 | 34 | 34 | 2914 | 2914 | 2914 | 0.069381 | 1134 | 0.027 | 3319 | 0.079024 | 1.362 | A04 | MICL0.01947034/SNC
Build-In Floor | Mini Canal | MICL.01947042/ANA | 19 | 470 | 42 | 42 | 3001 | 3001 | 3001 | 0.071452 | 1167 | 0.027786 | 3418 | 0.081381 | 1.362 | A04 | MICL0.01947042/ANA
Build-In Floor | Mini Canal | MICL.01947042/DBL | 19 | 470 | 42 | 42 | 3881 | 3881 | 3881 | 0.092405 | 1510 | 0.035952 | 4420 | 0.10524 | 1.362 | A04 | MICL0.01947042/DBL
Build-In Floor | Mini Canal | MICL.01947042/DBN | 19 | 470 | 42 | 42 | 3721 | 3721 | 3721 | 0.088595 | 1447 | 0.034452 | 4238 | 0.1009 | 1.362 | A04 | MICL0.01947042/DBN
Build-In Floor | Mini Canal | MICL.01947042/DBR | 19 | 470 | 42 | 42 | 3881 | 3881 | 3881 | 0.092405 | 1510 | 0.035952 | 4420 | 0.10524 | 1.362 | A04 | MICL0.01947042/DBR
Build-In Floor | Mini Canal | MICL.01947042/DBV | 19 | 470 | 42 | 42 | 3721 | 3721 | 3721 | 0.088595 | 1447 | 0.034452 | 4238 | 0.1009 | 1.362 | A04 | MICL0.01947042/DBV
Build-In Floor | Mini Canal | MICL.01947042/DDB | 19 | 470 | 42 | 42 | 3881 | 3881 | 3881 | 0.092405 | 1510 | 0.035952 | 4420 | 0.10524 | 1.362 | A04 | MICL0.01947042/DDB
Build-In Floor | Mini Canal | MICL.01947042/DMN | 19 | 470 | 42 | 42 | 3721 | 3721 | 3721 | 0.088595 | 1447 | 0.034452 | 4238 | 0.1009 | 1.362 | A04 | MICL0.01947042/DMN
Build-In Floor | Mini Canal | MICL.01947042/DMV | 19 | 470 | 42 | 42 | 3721 | 3721 | 3721 | 0.088595 | 1447 | 0.034452 | 4238 | 0.1009 | 1.362 | A04 | MICL0.01947042/DMV
Build-In Floor | Mini Canal | MICL.01947042/DNA | 19 | 470 | 42 | 42 | 3881 | 3881 | 3881 | 0.092405 | 1510 | 0.035952 | 4420 | 0.10524 | 1.362 | A04 | MICL0.01947042/DNA
Build-In Floor | Mini Canal | MICL.01947042/DNC | 19 | 470 | 42 | 42 | 3881 | 3881 | 3881 | 0.092405 | 1510 | 0.035952 | 4420 | 0.10524 | 1.362 | A04 | MICL0.01947042/DNC
Build-In Floor | Mini Canal | MICL.01947042/DON | 19 | 470 | 42 | 42 | 3721 | 3721 | 3721 | 0.088595 | 1447 | 0.034452 | 4238 | 0.1009 | 1.362 | A04 | MICL0.01947042/DON
Build-In Floor | Mini Canal | MICL.01947042/DOV | 19 | 470 | 42 | 42 | 3721 | 3721 | 3721 | 0.088595 | 1447 | 0.034452 | 4238 | 0.1009 | 1.362 | A04 | MICL0.01947042/DOV
Build-In Floor | Mini Canal | MICL.01947042/PNC | 19 | 470 | 42 | 42 | 3401 | 3401 | 3401 | 0.080976 | 1323 | 0.0315 | 3874 | 0.092238 | 1.362 | A04 | MICL0.01947042/PNC
Build-In Floor | Mini Canal | MICL.01947042/RBL | 19 | 470 | 42 | 42 | 4001 | 4001 | 4001 | 0.095262 | 1556 | 0.037048 | 4557 | 0.1085 | 1.362 | A04 | MICL0.01947042/RBL
Build-In Floor | Mini Canal | MICL.01947042/RBN | 19 | 470 | 42 | 42 | 3881 | 3881 | 3881 | 0.092405 | 1510 | 0.035952 | 4420 | 0.10524 | 1.362 | A04 | MICL0.01947042/RBN
Build-In Floor | Mini Canal | MICL.01947042/RBR | 19 | 470 | 42 | 42 | 4001 | 4001 | 4001 | 0.095262 | 1556 | 0.037048 | 4557 | 0.1085 | 1.362 | A04 | MICL0.01947042/RBR
Build-In Floor | Mini Canal | MICL.01947042/RBV | 19 | 470 | 42 | 42 | 3881 | 3881 | 3881 | 0.092405 | 1510 | 0.035952 | 4420 | 0.10524 | 1.362 | A04 | MICL0.01947042/RBV
Build-In Floor | Mini Canal | MICL.01947042/RDB | 19 | 470 | 42 | 42 | 4001 | 4001 | 4001 | 0.095262 | 1556 | 0.037048 | 4557 | 0.1085 | 1.362 | A04 | MICL0.01947042/RDB
Build-In Floor | Mini Canal | MICL.01947042/RMN | 19 | 470 | 42 | 42 | 3881 | 3881 | 3881 | 0.092405 | 1510 | 0.035952 | 4420 | 0.10524 | 1.362 | A04 | MICL0.01947042/RMN
Build-In Floor | Mini Canal | MICL.01947042/RMV | 19 | 470 | 42 | 42 | 3881 | 3881 | 3881 | 0.092405 | 1510 | 0.035952 | 4420 | 0.10524 | 1.362 | A04 | MICL0.01947042/RMV
Build-In Floor | Mini Canal | MICL.01947042/RNA | 19 | 470 | 42 | 42 | 4001 | 4001 | 4001 | 0.095262 | 1556 | 0.037048 | 4557 | 0.1085 | 1.362 | A04 | MICL0.01947042/RNA
Build-In Floor | Mini Canal | MICL.01947042/RON | 19 | 470 | 42 | 42 | 3881 | 3881 | 3881 | 0.092405 | 1510 | 0.035952 | 4420 | 0.10524 | 1.362 | A04 | MICL0.01947042/RON
Build-In Floor | Mini Canal | MICL.01947042/ROV | 19 | 470 | 42 | 42 | 3881 | 3881 | 3881 | 0.092405 | 1510 | 0.035952 | 4420 | 0.10524 | 1.362 | A04 | MICL0.01947042/ROV
Build-In Floor | Mini Canal | MICL.01947042/RSS | 19 | 470 | 42 | 42 | 3841 | 3841 | 3841 | 0.091452 | 1494 | 0.035571 | 4375 | 0.10417 | 1.362 | A04 | MICL0.01947042/RSS
Build-In Floor | Mini Canal | MICL.01947042/SBL | 19 | 470 | 42 | 42 | 4001 | 4001 | 4001 | 0.095262 | 1556 | 0.037048 | 4557 | 0.1085 | 1.362 | A04 | MICL0.01947042/SBL
Build-In Floor | Mini Canal | MICL.01947042/SBR | 19 | 470 | 42 | 42 | 4001 | 4001 | 4001 | 0.095262 | 1556 | 0.037048 | 4557 | 0.1085 | 1.362 | A04 | MICL0.01947042/SBR
Build-In Floor | Mini Canal | MICL.01947042/SDB | 19 | 470 | 42 | 42 | 4001 | 4001 | 4001 | 0.095262 | 1556 | 0.037048 | 4557 | 0.1085 | 1.362 | A04 | MICL0.01947042/SDB
Build-In Floor | Mini Canal | MICL.01947042/SNA | 19 | 470 | 42 | 42 | 4001 | 4001 | 4001 | 0.095262 | 1556 | 0.037048 | 4557 | 0.1085 | 1.362 | A04 | MICL0.01947042/SNA
Build-In Floor | Mini Canal | MICL.01947042/SNC | 19 | 470 | 42 | 42 | 4001 | 4001 | 4001 | 0.095262 | 1556 | 0.037048 | 4557 | 0.1085 | 1.362 | A04 | MICL0.01947042/SNC
Build-In Floor | Mini Canal | MICL.01949026/ANA | 19 | 490 | 26 | 26 | 1688 | 1688 | 1688 | 0.04019 | 657 | 0.015643 | 1923 | 0.045786 | 1.362 | A04 | MICL0.01949026/ANA
Build-In Floor | Mini Canal | MICL.01949026/DBL | 19 | 490 | 26 | 26 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01949026/DBL
Build-In Floor | Mini Canal | MICL.01949026/DBN | 19 | 490 | 26 | 26 | 2092 | 2092 | 2092 | 0.04981 | 814 | 0.019381 | 2383 | 0.056738 | 1.362 | A04 | MICL0.01949026/DBN
Build-In Floor | Mini Canal | MICL.01949026/DBR | 19 | 490 | 26 | 26 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01949026/DBR
Build-In Floor | Mini Canal | MICL.01949026/DBV | 19 | 490 | 26 | 26 | 2092 | 2092 | 2092 | 0.04981 | 814 | 0.019381 | 2383 | 0.056738 | 1.362 | A04 | MICL0.01949026/DBV
Build-In Floor | Mini Canal | MICL.01949026/DDB | 19 | 490 | 26 | 26 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01949026/DDB
Build-In Floor | Mini Canal | MICL.01949026/DMN | 19 | 490 | 26 | 26 | 2092 | 2092 | 2092 | 0.04981 | 814 | 0.019381 | 2383 | 0.056738 | 1.362 | A04 | MICL0.01949026/DMN
Build-In Floor | Mini Canal | MICL.01949026/DMV | 19 | 490 | 26 | 26 | 2092 | 2092 | 2092 | 0.04981 | 814 | 0.019381 | 2383 | 0.056738 | 1.362 | A04 | MICL0.01949026/DMV
Build-In Floor | Mini Canal | MICL.01949026/DNA | 19 | 490 | 26 | 26 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01949026/DNA
Build-In Floor | Mini Canal | MICL.01949026/DNC | 19 | 490 | 26 | 26 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01949026/DNC
Build-In Floor | Mini Canal | MICL.01949026/DON | 19 | 490 | 26 | 26 | 2092 | 2092 | 2092 | 0.04981 | 814 | 0.019381 | 2383 | 0.056738 | 1.362 | A04 | MICL0.01949026/DON
Build-In Floor | Mini Canal | MICL.01949026/DOV | 19 | 490 | 26 | 26 | 2092 | 2092 | 2092 | 0.04981 | 814 | 0.019381 | 2383 | 0.056738 | 1.362 | A04 | MICL0.01949026/DOV
Build-In Floor | Mini Canal | MICL.01949026/PNC | 19 | 490 | 26 | 26 | 1913 | 1913 | 1913 | 0.045548 | 744 | 0.017714 | 2179 | 0.051881 | 1.362 | A04 | MICL0.01949026/PNC
Build-In Floor | Mini Canal | MICL.01949026/RBL | 19 | 490 | 26 | 26 | 2250 | 2250 | 2250 | 0.053571 | 875 | 0.020833 | 2563 | 0.061024 | 1.362 | A04 | MICL0.01949026/RBL
Build-In Floor | Mini Canal | MICL.01949026/RBN | 19 | 490 | 26 | 26 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01949026/RBN
Build-In Floor | Mini Canal | MICL.01949026/RBR | 19 | 490 | 26 | 26 | 2250 | 2250 | 2250 | 0.053571 | 875 | 0.020833 | 2563 | 0.061024 | 1.362 | A04 | MICL0.01949026/RBR
Build-In Floor | Mini Canal | MICL.01949026/RBV | 19 | 490 | 26 | 26 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01949026/RBV
Build-In Floor | Mini Canal | MICL.01949026/RDB | 19 | 490 | 26 | 26 | 2250 | 2250 | 2250 | 0.053571 | 875 | 0.020833 | 2563 | 0.061024 | 1.362 | A04 | MICL0.01949026/RDB
Build-In Floor | Mini Canal | MICL.01949026/RMN | 19 | 490 | 26 | 26 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01949026/RMN
Build-In Floor | Mini Canal | MICL.01949026/RMV | 19 | 490 | 26 | 26 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01949026/RMV
Build-In Floor | Mini Canal | MICL.01949026/RNA | 19 | 490 | 26 | 26 | 2250 | 2250 | 2250 | 0.053571 | 875 | 0.020833 | 2563 | 0.061024 | 1.362 | A04 | MICL0.01949026/RNA
Build-In Floor | Mini Canal | MICL.01949026/RON | 19 | 490 | 26 | 26 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01949026/RON
Build-In Floor | Mini Canal | MICL.01949026/ROV | 19 | 490 | 26 | 26 | 2182 | 2182 | 2182 | 0.051952 | 849 | 0.020214 | 2485 | 0.059167 | 1.362 | A04 | MICL0.01949026/ROV
Build-In Floor | Mini Canal | MICL.01949026/RSS | 19 | 490 | 26 | 26 | 2160 | 2160 | 2160 | 0.051429 | 840 | 0.02 | 2460 | 0.058571 | 1.362 | A04 | MICL0.01949026/RSS
Build-In Floor | Mini Canal | MICL.01949026/SBL | 19 | 490 | 26 | 26 | 2250 | 2250 | 2250 | 0.053571 | 875 | 0.020833 | 2563 | 0.061024 | 1.362 | A04 | MICL0.01949026/SBL
Build-In Floor | Mini Canal | MICL.01949026/SBR | 19 | 490 | 26 | 26 | 2250 | 2250 | 2250 | 0.053571 | 875 | 0.020833 | 2563 | 0.061024 | 1.362 | A04 | MICL0.01949026/SBR
Build-In Floor | Mini Canal | MICL.01949026/SDB | 19 | 490 | 26 | 26 | 2250 | 2250 | 2250 | 0.053571 | 875 | 0.020833 | 2563 | 0.061024 | 1.362 | A04 | MICL0.01949026/SDB
Build-In Floor | Mini Canal | MICL.01949026/SNA | 19 | 490 | 26 | 26 | 2250 | 2250 | 2250 | 0.053571 | 875 | 0.020833 | 2563 | 0.061024 | 1.362 | A04 | MICL0.01949026/SNA
Build-In Floor | Mini Canal | MICL.01949026/SNC | 19 | 490 | 26 | 26 | 2250 | 2250 | 2250 | 0.053571 | 875 | 0.020833 | 2563 | 0.061024 | 1.362 | A04 | MICL0.01949026/SNC
Build-In Floor | Mini Canal | MICL.01949034/ANA | 19 | 490 | 34 | 34 | 2285 | 2285 | 2285 | 0.054405 | 889 | 0.021167 | 2603 | 0.061976 | 1.362 | A04 | MICL0.01949034/ANA
Build-In Floor | Mini Canal | MICL.01949034/DBL | 19 | 490 | 34 | 34 | 2955 | 2955 | 2955 | 0.070357 | 1149 | 0.027357 | 3366 | 0.080143 | 1.362 | A04 | MICL0.01949034/DBL
Build-In Floor | Mini Canal | MICL.01949034/DBN | 19 | 490 | 34 | 34 | 2833 | 2833 | 2833 | 0.067452 | 1102 | 0.026238 | 3227 | 0.076833 | 1.362 | A04 | MICL0.01949034/DBN
Build-In Floor | Mini Canal | MICL.01949034/DBR | 19 | 490 | 34 | 34 | 2955 | 2955 | 2955 | 0.070357 | 1149 | 0.027357 | 3366 | 0.080143 | 1.362 | A04 | MICL0.01949034/DBR
Build-In Floor | Mini Canal | MICL.01949034/DBV | 19 | 490 | 34 | 34 | 2833 | 2833 | 2833 | 0.067452 | 1102 | 0.026238 | 3227 | 0.076833 | 1.362 | A04 | MICL0.01949034/DBV
Build-In Floor | Mini Canal | MICL.01949034/DDB | 19 | 490 | 34 | 34 | 2955 | 2955 | 2955 | 0.070357 | 1149 | 0.027357 | 3366 | 0.080143 | 1.362 | A04 | MICL0.01949034/DDB
Build-In Floor | Mini Canal | MICL.01949034/DMN | 19 | 490 | 34 | 34 | 2833 | 2833 | 2833 | 0.067452 | 1102 | 0.026238 | 3227 | 0.076833 | 1.362 | A04 | MICL0.01949034/DMN
Build-In Floor | Mini Canal | MICL.01949034/DMV | 19 | 490 | 34 | 34 | 2833 | 2833 | 2833 | 0.067452 | 1102 | 0.026238 | 3227 | 0.076833 | 1.362 | A04 | MICL0.01949034/DMV
Build-In Floor | Mini Canal | MICL.01949034/DNA | 19 | 490 | 34 | 34 | 2955 | 2955 | 2955 | 0.070357 | 1149 | 0.027357 | 3366 | 0.080143 | 1.362 | A04 | MICL0.01949034/DNA
Build-In Floor | Mini Canal | MICL.01949034/DNC | 19 | 490 | 34 | 34 | 2955 | 2955 | 2955 | 0.070357 | 1149 | 0.027357 | 3366 | 0.080143 | 1.362 | A04 | MICL0.01949034/DNC
Build-In Floor | Mini Canal | MICL.01949034/DON | 19 | 490 | 34 | 34 | 2833 | 2833 | 2833 | 0.067452 | 1102 | 0.026238 | 3227 | 0.076833 | 1.362 | A04 | MICL0.01949034/DON
Build-In Floor | Mini Canal | MICL.01949034/DOV | 19 | 490 | 34 | 34 | 2833 | 2833 | 2833 | 0.067452 | 1102 | 0.026238 | 3227 | 0.076833 | 1.362 | A04 | MICL0.01949034/DOV
Build-In Floor | Mini Canal | MICL.01949034/PNC | 19 | 490 | 34 | 34 | 2589 | 2589 | 2589 | 0.061643 | 1007 | 0.023976 | 2949 | 0.070214 | 1.362 | A04 | MICL0.01949034/PNC
Build-In Floor | Mini Canal | MICL.01949034/RBL | 19 | 490 | 34 | 34 | 3046 | 3046 | 3046 | 0.072524 | 1185 | 0.028214 | 3469 | 0.082595 | 1.362 | A04 | MICL0.01949034/RBL
Build-In Floor | Mini Canal | MICL.01949034/RBN | 19 | 490 | 34 | 34 | 2955 | 2955 | 2955 | 0.070357 | 1149 | 0.027357 | 3366 | 0.080143 | 1.362 | A04 | MICL0.01949034/RBN
Build-In Floor | Mini Canal | MICL.01949034/RBR | 19 | 490 | 34 | 34 | 3046 | 3046 | 3046 | 0.072524 | 1185 | 0.028214 | 3469 | 0.082595 | 1.362 | A04 | MICL0.01949034/RBR
Build-In Floor | Mini Canal | MICL.01949034/RBV | 19 | 490 | 34 | 34 | 2955 | 2955 | 2955 | 0.070357 | 1149 | 0.027357 | 3366 | 0.080143 | 1.362 | A04 | MICL0.01949034/RBV
Build-In Floor | Mini Canal | MICL.01949034/RDB | 19 | 490 | 34 | 34 | 3046 | 3046 | 3046 | 0.072524 | 1185 | 0.028214 | 3469 | 0.082595 | 1.362 | A04 | MICL0.01949034/RDB
Build-In Floor | Mini Canal | MICL.01949034/RMN | 19 | 490 | 34 | 34 | 2955 | 2955 | 2955 | 0.070357 | 1149 | 0.027357 | 3366 | 0.080143 | 1.362 | A04 | MICL0.01949034/RMN
Build-In Floor | Mini Canal | MICL.01949034/RMV | 19 | 490 | 34 | 34 | 2955 | 2955 | 2955 | 0.070357 | 1149 | 0.027357 | 3366 | 0.080143 | 1.362 | A04 | MICL0.01949034/RMV
Build-In Floor | Mini Canal | MICL.01949034/RNA | 19 | 490 | 34 | 34 | 3046 | 3046 | 3046 | 0.072524 | 1185 | 0.028214 | 3469 | 0.082595 | 1.362 | A04 | MICL0.01949034/RNA
Build-In Floor | Mini Canal | MICL.01949034/RON | 19 | 490 | 34 | 34 | 2955 | 2955 | 2955 | 0.070357 | 1149 | 0.027357 | 3366 | 0.080143 | 1.362 | A04 | MICL0.01949034/RON
Build-In Floor | Mini Canal | MICL.01949034/ROV | 19 | 490 | 34 | 34 | 2955 | 2955 | 2955 | 0.070357 | 1149 | 0.027357 | 3366 | 0.080143 | 1.362 | A04 | MICL0.01949034/ROV
Build-In Floor | Mini Canal | MICL.01949034/RSS | 19 | 490 | 34 | 34 | 2924 | 2924 | 2924 | 0.069619 | 1137 | 0.027071 | 3330 | 0.079286 | 1.362 | A04 | MICL0.01949034/RSS
Build-In Floor | Mini Canal | MICL.01949034/SBL | 19 | 490 | 34 | 34 | 3046 | 3046 | 3046 | 0.072524 | 1185 | 0.028214 | 3469 | 0.082595 | 1.362 | A04 | MICL0.01949034/SBL
Build-In Floor | Mini Canal | MICL.01949034/SBR | 19 | 490 | 34 | 34 | 3046 | 3046 | 3046 | 0.072524 | 1185 | 0.028214 | 3469 | 0.082595 | 1.362 | A04 | MICL0.01949034/SBR
Build-In Floor | Mini Canal | MICL.01949034/SDB | 19 | 490 | 34 | 34 | 3046 | 3046 | 3046 | 0.072524 | 1185 | 0.028214 | 3469 | 0.082595 | 1.362 | A04 | MICL0.01949034/SDB
Build-In Floor | Mini Canal | MICL.01949034/SNA | 19 | 490 | 34 | 34 | 3046 | 3046 | 3046 | 0.072524 | 1185 | 0.028214 | 3469 | 0.082595 | 1.362 | A04 | MICL0.01949034/SNA
Build-In Floor | Mini Canal | MICL.01949034/SNC | 19 | 490 | 34 | 34 | 3046 | 3046 | 3046 | 0.072524 | 1185 | 0.028214 | 3469 | 0.082595 | 1.362 | A04 | MICL0.01949034/SNC
Build-In Floor | Mini Canal | MICL.01949042/ANA | 19 | 490 | 42 | 42 | 3138 | 3138 | 3138 | 0.074714 | 1221 | 0.029071 | 3574 | 0.085095 | 1.362 | A04 | MICL0.01949042/ANA
Build-In Floor | Mini Canal | MICL.01949042/DBL | 19 | 490 | 42 | 42 | 4058 | 4058 | 4058 | 0.096619 | 1579 | 0.037595 | 4622 | 0.11005 | 1.362 | A04 | MICL0.01949042/DBL
Build-In Floor | Mini Canal | MICL.01949042/DBN | 19 | 490 | 42 | 42 | 3891 | 3891 | 3891 | 0.092643 | 1514 | 0.036048 | 4432 | 0.10552 | 1.362 | A04 | MICL0.01949042/DBN
Build-In Floor | Mini Canal | MICL.01949042/DBR | 19 | 490 | 42 | 42 | 4058 | 4058 | 4058 | 0.096619 | 1579 | 0.037595 | 4622 | 0.11005 | 1.362 | A04 | MICL0.01949042/DBR
Build-In Floor | Mini Canal | MICL.01949042/DBV | 19 | 490 | 42 | 42 | 3891 | 3891 | 3891 | 0.092643 | 1514 | 0.036048 | 4432 | 0.10552 | 1.362 | A04 | MICL0.01949042/DBV
Build-In Floor | Mini Canal | MICL.01949042/DDB | 19 | 490 | 42 | 42 | 4058 | 4058 | 4058 | 0.096619 | 1579 | 0.037595 | 4622 | 0.11005 | 1.362 | A04 | MICL0.01949042/DDB
Build-In Floor | Mini Canal | MICL.01949042/DMN | 19 | 490 | 42 | 42 | 3891 | 3891 | 3891 | 0.092643 | 1514 | 0.036048 | 4432 | 0.10552 | 1.362 | A04 | MICL0.01949042/DMN
Build-In Floor | Mini Canal | MICL.01949042/DMV | 19 | 490 | 42 | 42 | 3891 | 3891 | 3891 | 0.092643 | 1514 | 0.036048 | 4432 | 0.10552 | 1.362 | A04 | MICL0.01949042/DMV
Build-In Floor | Mini Canal | MICL.01949042/DNA | 19 | 490 | 42 | 42 | 4058 | 4058 | 4058 | 0.096619 | 1579 | 0.037595 | 4622 | 0.11005 | 1.362 | A04 | MICL0.01949042/DNA
Build-In Floor | Mini Canal | MICL.01949042/DNC | 19 | 490 | 42 | 42 | 4058 | 4058 | 4058 | 0.096619 | 1579 | 0.037595 | 4622 | 0.11005 | 1.362 | A04 | MICL0.01949042/DNC
Build-In Floor | Mini Canal | MICL.01949042/DON | 19 | 490 | 42 | 42 | 3891 | 3891 | 3891 | 0.092643 | 1514 | 0.036048 | 4432 | 0.10552 | 1.362 | A04 | MICL0.01949042/DON
Build-In Floor | Mini Canal | MICL.01949042/DOV | 19 | 490 | 42 | 42 | 3891 | 3891 | 3891 | 0.092643 | 1514 | 0.036048 | 4432 | 0.10552 | 1.362 | A04 | MICL0.01949042/DOV
Build-In Floor | Mini Canal | MICL.01949042/PNC | 19 | 490 | 42 | 42 | 3556 | 3556 | 3556 | 0.084667 | 1383 | 0.032929 | 4050 | 0.096429 | 1.362 | A04 | MICL0.01949042/PNC
Build-In Floor | Mini Canal | MICL.01949042/RBL | 19 | 490 | 42 | 42 | 4184 | 4184 | 4184 | 0.099619 | 1628 | 0.038762 | 4766 | 0.11348 | 1.362 | A04 | MICL0.01949042/RBL
Build-In Floor | Mini Canal | MICL.01949042/RBN | 19 | 490 | 42 | 42 | 4058 | 4058 | 4058 | 0.096619 | 1579 | 0.037595 | 4622 | 0.11005 | 1.362 | A04 | MICL0.01949042/RBN
Build-In Floor | Mini Canal | MICL.01949042/RBR | 19 | 490 | 42 | 42 | 4184 | 4184 | 4184 | 0.099619 | 1628 | 0.038762 | 4766 | 0.11348 | 1.362 | A04 | MICL0.01949042/RBR
Build-In Floor | Mini Canal | MICL.01949042/RBV | 19 | 490 | 42 | 42 | 4058 | 4058 | 4058 | 0.096619 | 1579 | 0.037595 | 4622 | 0.11005 | 1.362 | A04 | MICL0.01949042/RBV
Build-In Floor | Mini Canal | MICL.01949042/RDB | 19 | 490 | 42 | 42 | 4184 | 4184 | 4184 | 0.099619 | 1628 | 0.038762 | 4766 | 0.11348 | 1.362 | A04 | MICL0.01949042/RDB
Build-In Floor | Mini Canal | MICL.01949042/RMN | 19 | 490 | 42 | 42 | 4058 | 4058 | 4058 | 0.096619 | 1579 | 0.037595 | 4622 | 0.11005 | 1.362 | A04 | MICL0.01949042/RMN
Build-In Floor | Mini Canal | MICL.01949042/RMV | 19 | 490 | 42 | 42 | 4058 | 4058 | 4058 | 0.096619 | 1579 | 0.037595 | 4622 | 0.11005 | 1.362 | A04 | MICL0.01949042/RMV
Build-In Floor | Mini Canal | MICL.01949042/RNA | 19 | 490 | 42 | 42 | 4184 | 4184 | 4184 | 0.099619 | 1628 | 0.038762 | 4766 | 0.11348 | 1.362 | A04 | MICL0.01949042/RNA
Build-In Floor | Mini Canal | MICL.01949042/RON | 19 | 490 | 42 | 42 | 4058 | 4058 | 4058 | 0.096619 | 1579 | 0.037595 | 4622 | 0.11005 | 1.362 | A04 | MICL0.01949042/RON
Build-In Floor | Mini Canal | MICL.01949042/ROV | 19 | 490 | 42 | 42 | 4058 | 4058 | 4058 | 0.096619 | 1579 | 0.037595 | 4622 | 0.11005 | 1.362 | A04 | MICL0.01949042/ROV
Build-In Floor | Mini Canal | MICL.01949042/RSS | 19 | 490 | 42 | 42 | 4017 | 4017 | 4017 | 0.095643 | 1563 | 0.037214 | 4575 | 0.10893 | 1.362 | A04 | MICL0.01949042/RSS
Build-In Floor | Mini Canal | MICL.01949042/SBL | 19 | 490 | 42 | 42 | 4184 | 4184 | 4184 | 0.099619 | 1628 | 0.038762 | 4766 | 0.11348 | 1.362 | A04 | MICL0.01949042/SBL
Build-In Floor | Mini Canal | MICL.01949042/SBR | 19 | 490 | 42 | 42 | 4184 | 4184 | 4184 | 0.099619 | 1628 | 0.038762 | 4766 | 0.11348 | 1.362 | A04 | MICL0.01949042/SBR
Build-In Floor | Mini Canal | MICL.01949042/SDB | 19 | 490 | 42 | 42 | 4184 | 4184 | 4184 | 0.099619 | 1628 | 0.038762 | 4766 | 0.11348 | 1.362 | A04 | MICL0.01949042/SDB
Build-In Floor | Mini Canal | MICL.01949042/SNA | 19 | 490 | 42 | 42 | 4184 | 4184 | 4184 | 0.099619 | 1628 | 0.038762 | 4766 | 0.11348 | 1.362 | A04 | MICL0.01949042/SNA
Build-In Floor | Mini Canal | MICL.01949042/SNC | 19 | 490 | 42 | 42 | 4184 | 4184 | 4184 | 0.099619 | 1628 | 0.038762 | 4766 | 0.11348 | 1.362 | A04 | MICL0.01949042/SNC
Freestanding | Mini Freestanding | MINF.00806009/AS | 8 | 60 | 09 | 13 | 255 | 255 | 255 | 0.0060714 | 95 | 0.0022619 | 292 | 0.0069524 | 1.418 | A03 | MINF0.00806009/AS
Freestanding | Mini Freestanding | MINF.00806009/FS | 8 | 60 | 09 | 13 | 255 | 255 | 255 | 0.0060714 | 95 | 0.0022619 | 292 | 0.0069524 | 1.418 | A03 | MINF0.00806009/FS
Freestanding | Mini Freestanding | MINF.00806014/AS | 8 | 60 | 14 | 18 | 416 | 416 | 416 | 0.0099048 | 156 | 0.0037143 | 476 | 0.011333 | 1.418 | A03 | MINF0.00806014/AS
Freestanding | Mini Freestanding | MINF.00806014/FS | 8 | 60 | 14 | 18 | 416 | 416 | 416 | 0.0099048 | 156 | 0.0037143 | 476 | 0.011333 | 1.418 | A03 | MINF0.00806014/FS
Freestanding | Mini Freestanding | MINF.00806019/AS | 8 | 60 | 19 | 23 | 572 | 572 | 572 | 0.013619 | 214 | 0.0050952 | 655 | 0.015595 | 1.418 | A03 | MINF0.00806019/AS
Freestanding | Mini Freestanding | MINF.00806019/FS | 8 | 60 | 19 | 23 | 572 | 572 | 572 | 0.013619 | 214 | 0.0050952 | 655 | 0.015595 | 1.418 | A03 | MINF0.00806019/FS
Freestanding | Mini Freestanding | MINF.00807009/AS | 8 | 70 | 09 | 13 | 298 | 298 | 298 | 0.0070952 | 111 | 0.0026429 | 341 | 0.008119 | 1.418 | A03 | MINF0.00807009/AS
Freestanding | Mini Freestanding | MINF.00807009/FS | 8 | 70 | 09 | 13 | 298 | 298 | 298 | 0.0070952 | 111 | 0.0026429 | 341 | 0.008119 | 1.418 | A03 | MINF0.00807009/FS
Freestanding | Mini Freestanding | MINF.00807014/AS | 8 | 70 | 14 | 18 | 486 | 486 | 486 | 0.011571 | 182 | 0.0043333 | 556 | 0.013238 | 1.418 | A03 | MINF0.00807014/AS
Freestanding | Mini Freestanding | MINF.00807014/FS | 8 | 70 | 14 | 18 | 486 | 486 | 486 | 0.011571 | 182 | 0.0043333 | 556 | 0.013238 | 1.418 | A03 | MINF0.00807014/FS
Freestanding | Mini Freestanding | MINF.00807019/AS | 8 | 70 | 19 | 23 | 667 | 667 | 667 | 0.015881 | 249 | 0.0059286 | 764 | 0.01819 | 1.418 | A03 | MINF0.00807019/AS
Freestanding | Mini Freestanding | MINF.00807019/FS | 8 | 70 | 19 | 23 | 667 | 667 | 667 | 0.015881 | 249 | 0.0059286 | 764 | 0.01819 | 1.418 | A03 | MINF0.00807019/FS
Freestanding | Mini Freestanding | MINF.00808009/AS | 8 | 80 | 09 | 13 | 340 | 340 | 340 | 0.0080952 | 127 | 0.0030238 | 389 | 0.0092619 | 1.418 | A03 | MINF0.00808009/AS
Freestanding | Mini Freestanding | MINF.00808009/FS | 8 | 80 | 09 | 13 | 340 | 340 | 340 | 0.0080952 | 127 | 0.0030238 | 389 | 0.0092619 | 1.418 | A03 | MINF0.00808009/FS
Freestanding | Mini Freestanding | MINF.00808014/AS | 8 | 80 | 14 | 18 | 555 | 555 | 555 | 0.013214 | 208 | 0.0049524 | 635 | 0.015119 | 1.418 | A03 | MINF0.00808014/AS
Freestanding | Mini Freestanding | MINF.00808014/FS | 8 | 80 | 14 | 18 | 555 | 555 | 555 | 0.013214 | 208 | 0.0049524 | 635 | 0.015119 | 1.418 | A03 | MINF0.00808014/FS
Freestanding | Mini Freestanding | MINF.00808019/AS | 8 | 80 | 19 | 23 | 762 | 762 | 762 | 0.018143 | 285 | 0.0067857 | 872 | 0.020762 | 1.418 | A03 | MINF0.00808019/AS
Freestanding | Mini Freestanding | MINF.00808019/FS | 8 | 80 | 19 | 23 | 762 | 762 | 762 | 0.018143 | 285 | 0.0067857 | 872 | 0.020762 | 1.418 | A03 | MINF0.00808019/FS
Freestanding | Mini Freestanding | MINF.00809009/AS | 8 | 90 | 09 | 13 | 383 | 383 | 383 | 0.009119 | 143 | 0.0034048 | 439 | 0.010452 | 1.418 | A03 | MINF0.00809009/AS
Freestanding | Mini Freestanding | MINF.00809009/FS | 8 | 90 | 09 | 13 | 383 | 383 | 383 | 0.009119 | 143 | 0.0034048 | 439 | 0.010452 | 1.418 | A03 | MINF0.00809009/FS
Freestanding | Mini Freestanding | MINF.00809014/AS | 8 | 90 | 14 | 18 | 625 | 625 | 625 | 0.014881 | 234 | 0.0055714 | 716 | 0.017048 | 1.418 | A03 | MINF0.00809014/AS
Freestanding | Mini Freestanding | MINF.00809014/FS | 8 | 90 | 14 | 18 | 625 | 625 | 625 | 0.014881 | 234 | 0.0055714 | 716 | 0.017048 | 1.418 | A03 | MINF0.00809014/FS
Freestanding | Mini Freestanding | MINF.00809019/AS | 8 | 90 | 19 | 23 | 858 | 858 | 858 | 0.020429 | 321 | 0.0076429 | 982 | 0.023381 | 1.418 | A03 | MINF0.00809019/AS
Freestanding | Mini Freestanding | MINF.00809019/FS | 8 | 90 | 19 | 23 | 858 | 858 | 858 | 0.020429 | 321 | 0.0076429 | 982 | 0.023381 | 1.418 | A03 | MINF0.00809019/FS
Freestanding | Mini Freestanding | MINF.00810009/AS | 8 | 100 | 09 | 13 | 425 | 425 | 425 | 0.010119 | 159 | 0.0037857 | 487 | 0.011595 | 1.418 | A03 | MINF0.00810009/AS
Freestanding | Mini Freestanding | MINF.00810009/FS | 8 | 100 | 09 | 13 | 425 | 425 | 425 | 0.010119 | 159 | 0.0037857 | 487 | 0.011595 | 1.418 | A03 | MINF0.00810009/FS
Freestanding | Mini Freestanding | MINF.00810014/AS | 8 | 100 | 14 | 18 | 694 | 694 | 694 | 0.016524 | 260 | 0.0061905 | 795 | 0.018929 | 1.418 | A03 | MINF0.00810014/AS
Freestanding | Mini Freestanding | MINF.00810014/FS | 8 | 100 | 14 | 18 | 694 | 694 | 694 | 0.016524 | 260 | 0.0061905 | 795 | 0.018929 | 1.418 | A03 | MINF0.00810014/FS
Freestanding | Mini Freestanding | MINF.00810019/AS | 8 | 100 | 19 | 23 | 953 | 953 | 953 | 0.02269 | 356 | 0.0084762 | 1091 | 0.025976 | 1.418 | A03 | MINF0.00810019/AS
Freestanding | Mini Freestanding | MINF.00810019/FS | 8 | 100 | 19 | 23 | 953 | 953 | 953 | 0.02269 | 356 | 0.0084762 | 1091 | 0.025976 | 1.418 | A03 | MINF0.00810019/FS
Freestanding | Mini Freestanding | MINF.00811009/AS | 8 | 110 | 09 | 13 | 468 | 468 | 468 | 0.011143 | 175 | 0.0041667 | 536 | 0.012762 | 1.418 | A03 | MINF0.00811009/AS
Freestanding | Mini Freestanding | MINF.00811009/FS | 8 | 110 | 09 | 13 | 468 | 468 | 468 | 0.011143 | 175 | 0.0041667 | 536 | 0.012762 | 1.418 | A03 | MINF0.00811009/FS
Freestanding | Mini Freestanding | MINF.00811014/AS | 8 | 110 | 14 | 18 | 763 | 763 | 763 | 0.018167 | 285 | 0.0067857 | 874 | 0.02081 | 1.418 | A03 | MINF0.00811014/AS
Freestanding | Mini Freestanding | MINF.00811014/FS | 8 | 110 | 14 | 18 | 763 | 763 | 763 | 0.018167 | 285 | 0.0067857 | 874 | 0.02081 | 1.418 | A03 | MINF0.00811014/FS
Freestanding | Mini Freestanding | MINF.00811019/AS | 8 | 110 | 19 | 23 | 1048 | 1048 | 1048 | 0.024952 | 392 | 0.0093333 | 1200 | 0.028571 | 1.418 | A03 | MINF0.00811019/AS
Freestanding | Mini Freestanding | MINF.00811019/FS | 8 | 110 | 19 | 23 | 1048 | 1048 | 1048 | 0.024952 | 392 | 0.0093333 | 1200 | 0.028571 | 1.418 | A03 | MINF0.00811019/FS
Freestanding | Mini Freestanding | MINF.00812009/AS | 8 | 120 | 09 | 13 | 510 | 510 | 510 | 0.012143 | 191 | 0.0045476 | 584 | 0.013905 | 1.418 | A03 | MINF0.00812009/AS
Freestanding | Mini Freestanding | MINF.00812009/FS | 8 | 120 | 09 | 13 | 510 | 510 | 510 | 0.012143 | 191 | 0.0045476 | 584 | 0.013905 | 1.418 | A03 | MINF0.00812009/FS
Freestanding | Mini Freestanding | MINF.00812014/AS | 8 | 120 | 14 | 18 | 833 | 833 | 833 | 0.019833 | 312 | 0.0074286 | 954 | 0.022714 | 1.418 | A03 | MINF0.00812014/AS
Freestanding | Mini Freestanding | MINF.00812014/FS | 8 | 120 | 14 | 18 | 833 | 833 | 833 | 0.019833 | 312 | 0.0074286 | 954 | 0.022714 | 1.418 | A03 | MINF0.00812014/FS
Freestanding | Mini Freestanding | MINF.00812019/AS | 8 | 120 | 19 | 23 | 1144 | 1144 | 1144 | 0.027238 | 428 | 0.01019 | 1310 | 0.03119 | 1.418 | A03 | MINF0.00812019/AS
Freestanding | Mini Freestanding | MINF.00812019/FS | 8 | 120 | 19 | 23 | 1144 | 1144 | 1144 | 0.027238 | 428 | 0.01019 | 1310 | 0.03119 | 1.418 | A03 | MINF0.00812019/FS
Freestanding | Mini Freestanding | MINF.00814009/AS | 8 | 140 | 09 | 13 | 595 | 595 | 595 | 0.014167 | 223 | 0.0053095 | 681 | 0.016214 | 1.418 | A03 | MINF0.00814009/AS
Freestanding | Mini Freestanding | MINF.00814009/FS | 8 | 140 | 09 | 13 | 595 | 595 | 595 | 0.014167 | 223 | 0.0053095 | 681 | 0.016214 | 1.418 | A03 | MINF0.00814009/FS
Freestanding | Mini Freestanding | MINF.00814014/AS | 8 | 140 | 14 | 18 | 972 | 972 | 972 | 0.023143 | 364 | 0.0086667 | 1113 | 0.0265 | 1.418 | A03 | MINF0.00814014/AS
Freestanding | Mini Freestanding | MINF.00814014/FS | 8 | 140 | 14 | 18 | 972 | 972 | 972 | 0.023143 | 364 | 0.0086667 | 1113 | 0.0265 | 1.418 | A03 | MINF0.00814014/FS
Freestanding | Mini Freestanding | MINF.00814019/AS | 8 | 140 | 19 | 23 | 1334 | 1334 | 1334 | 0.031762 | 499 | 0.011881 | 1527 | 0.036357 | 1.418 | A03 | MINF0.00814019/AS
Freestanding | Mini Freestanding | MINF.00814019/FS | 8 | 140 | 19 | 23 | 1334 | 1334 | 1334 | 0.031762 | 499 | 0.011881 | 1527 | 0.036357 | 1.418 | A03 | MINF0.00814019/FS
Freestanding | Mini Freestanding | MINF.00816009/AS | 8 | 160 | 09 | 13 | 680 | 680 | 680 | 0.01619 | 254 | 0.0060476 | 779 | 0.018548 | 1.418 | A03 | MINF0.00816009/AS
Freestanding | Mini Freestanding | MINF.00816009/FS | 8 | 160 | 09 | 13 | 680 | 680 | 680 | 0.01619 | 254 | 0.0060476 | 779 | 0.018548 | 1.418 | A03 | MINF0.00816009/FS
Freestanding | Mini Freestanding | MINF.00816014/AS | 8 | 160 | 14 | 18 | 1110 | 1110 | 1110 | 0.026429 | 415 | 0.009881 | 1271 | 0.030262 | 1.418 | A03 | MINF0.00816014/AS
Freestanding | Mini Freestanding | MINF.00816014/FS | 8 | 160 | 14 | 18 | 1110 | 1110 | 1110 | 0.026429 | 415 | 0.009881 | 1271 | 0.030262 | 1.418 | A03 | MINF0.00816014/FS
Freestanding | Mini Freestanding | MINF.00816019/AS | 8 | 160 | 19 | 23 | 1525 | 1525 | 1525 | 0.03631 | 570 | 0.013571 | 1746 | 0.041571 | 1.418 | A03 | MINF0.00816019/AS
Freestanding | Mini Freestanding | MINF.00816019/FS | 8 | 160 | 19 | 23 | 1525 | 1525 | 1525 | 0.03631 | 570 | 0.013571 | 1746 | 0.041571 | 1.418 | A03 | MINF0.00816019/FS
Freestanding | Mini Freestanding | MINF.00818009/AS | 8 | 180 | 09 | 13 | 765 | 765 | 765 | 0.018214 | 286 | 0.0068095 | 876 | 0.020857 | 1.418 | A03 | MINF0.00818009/AS
Freestanding | Mini Freestanding | MINF.00818009/FS | 8 | 180 | 09 | 13 | 765 | 765 | 765 | 0.018214 | 286 | 0.0068095 | 876 | 0.020857 | 1.418 | A03 | MINF0.00818009/FS
Freestanding | Mini Freestanding | MINF.00818014/AS | 8 | 180 | 14 | 18 | 1249 | 1249 | 1249 | 0.029738 | 467 | 0.011119 | 1430 | 0.034048 | 1.418 | A03 | MINF0.00818014/AS
Freestanding | Mini Freestanding | MINF.00818014/FS | 8 | 180 | 14 | 18 | 1249 | 1249 | 1249 | 0.029738 | 467 | 0.011119 | 1430 | 0.034048 | 1.418 | A03 | MINF0.00818014/FS
Freestanding | Mini Freestanding | MINF.00818019/AS | 8 | 180 | 19 | 23 | 1715 | 1715 | 1715 | 0.040833 | 641 | 0.015262 | 1964 | 0.046762 | 1.418 | A03 | MINF0.00818019/AS
Freestanding | Mini Freestanding | MINF.00818019/FS | 8 | 180 | 19 | 23 | 1715 | 1715 | 1715 | 0.040833 | 641 | 0.015262 | 1964 | 0.046762 | 1.418 | A03 | MINF0.00818019/FS
Freestanding | Mini Freestanding | MINF.00820009/AS | 8 | 200 | 09 | 13 | 850 | 850 | 850 | 0.020238 | 318 | 0.0075714 | 973 | 0.023167 | 1.418 | A03 | MINF0.00820009/AS
Freestanding | Mini Freestanding | MINF.00820009/FS | 8 | 200 | 09 | 13 | 850 | 850 | 850 | 0.020238 | 318 | 0.0075714 | 973 | 0.023167 | 1.418 | A03 | MINF0.00820009/FS
Freestanding | Mini Freestanding | MINF.00820014/AS | 8 | 200 | 14 | 18 | 1388 | 1388 | 1388 | 0.033048 | 519 | 0.012357 | 1589 | 0.037833 | 1.418 | A03 | MINF0.00820014/AS
Freestanding | Mini Freestanding | MINF.00820014/FS | 8 | 200 | 14 | 18 | 1388 | 1388 | 1388 | 0.033048 | 519 | 0.012357 | 1589 | 0.037833 | 1.418 | A03 | MINF0.00820014/FS
Freestanding | Mini Freestanding | MINF.00820019/AS | 8 | 200 | 19 | 23 | 1906 | 1906 | 1906 | 0.045381 | 713 | 0.016976 | 2182 | 0.051952 | 1.418 | A03 | MINF0.00820019/AS
Freestanding | Mini Freestanding | MINF.00820019/FS | 8 | 200 | 19 | 23 | 1906 | 1906 | 1906 | 0.045381 | 713 | 0.016976 | 2182 | 0.051952 | 1.418 | A03 | MINF0.00820019/FS
Freestanding | Mini Freestanding | MINF.00822009/AS | 8 | 220 | 09 | 13 | 935 | 935 | 935 | 0.022262 | 350 | 0.0083333 | 1071 | 0.0255 | 1.418 | A03 | MINF0.00822009/AS
Freestanding | Mini Freestanding | MINF.00822009/FS | 8 | 220 | 09 | 13 | 935 | 935 | 935 | 0.022262 | 350 | 0.0083333 | 1071 | 0.0255 | 1.418 | A03 | MINF0.00822009/FS
Freestanding | Mini Freestanding | MINF.00822014/AS | 8 | 220 | 14 | 18 | 1527 | 1527 | 1527 | 0.036357 | 571 | 0.013595 | 1748 | 0.041619 | 1.418 | A03 | MINF0.00822014/AS
Freestanding | Mini Freestanding | MINF.00822014/FS | 8 | 220 | 14 | 18 | 1527 | 1527 | 1527 | 0.036357 | 571 | 0.013595 | 1748 | 0.041619 | 1.418 | A03 | MINF0.00822014/FS
Freestanding | Mini Freestanding | MINF.00822019/AS | 8 | 220 | 19 | 23 | 2097 | 2097 | 2097 | 0.049929 | 784 | 0.018667 | 2401 | 0.057167 | 1.418 | A03 | MINF0.00822019/AS
Freestanding | Mini Freestanding | MINF.00822019/FS | 8 | 220 | 19 | 23 | 2097 | 2097 | 2097 | 0.049929 | 784 | 0.018667 | 2401 | 0.057167 | 1.418 | A03 | MINF0.00822019/FS
Freestanding | Mini Freestanding | MINF.00824009/AS | 8 | 240 | 09 | 13 | 1020 | 1020 | 1020 | 0.024286 | 381 | 0.0090714 | 1168 | 0.02781 | 1.418 | A03 | MINF0.00824009/AS
Freestanding | Mini Freestanding | MINF.00824009/FS | 8 | 240 | 09 | 13 | 1020 | 1020 | 1020 | 0.024286 | 381 | 0.0090714 | 1168 | 0.02781 | 1.418 | A03 | MINF0.00824009/FS
Freestanding | Mini Freestanding | MINF.00824014/AS | 8 | 240 | 14 | 18 | 1666 | 1666 | 1666 | 0.039667 | 623 | 0.014833 | 1908 | 0.045429 | 1.418 | A03 | MINF0.00824014/AS
Freestanding | Mini Freestanding | MINF.00824014/FS | 8 | 240 | 14 | 18 | 1666 | 1666 | 1666 | 0.039667 | 623 | 0.014833 | 1908 | 0.045429 | 1.418 | A03 | MINF0.00824014/FS
Freestanding | Mini Freestanding | MINF.00824019/AS | 8 | 240 | 19 | 23 | 2287 | 2287 | 2287 | 0.054452 | 855 | 0.020357 | 2619 | 0.062357 | 1.418 | A03 | MINF0.00824019/AS
Freestanding | Mini Freestanding | MINF.00824019/FS | 8 | 240 | 19 | 23 | 2287 | 2287 | 2287 | 0.054452 | 855 | 0.020357 | 2619 | 0.062357 | 1.418 | A03 | MINF0.00824019/FS
Freestanding | Mini Freestanding | MINF.00826009/AS | 8 | 260 | 09 | 13 | 1105 | 1105 | 1105 | 0.02631 | 413 | 0.0098333 | 1265 | 0.030119 | 1.418 | A03 | MINF0.00826009/AS
Freestanding | Mini Freestanding | MINF.00826009/FS | 8 | 260 | 09 | 13 | 1105 | 1105 | 1105 | 0.02631 | 413 | 0.0098333 | 1265 | 0.030119 | 1.418 | A03 | MINF0.00826009/FS
Freestanding | Mini Freestanding | MINF.00826014/AS | 8 | 260 | 14 | 18 | 1804 | 1804 | 1804 | 0.042952 | 675 | 0.016071 | 2066 | 0.04919 | 1.418 | A03 | MINF0.00826014/AS
Freestanding | Mini Freestanding | MINF.00826014/FS | 8 | 260 | 14 | 18 | 1804 | 1804 | 1804 | 0.042952 | 675 | 0.016071 | 2066 | 0.04919 | 1.418 | A03 | MINF0.00826014/FS
Freestanding | Mini Freestanding | MINF.00826019/AS | 8 | 260 | 19 | 23 | 2478 | 2478 | 2478 | 0.059 | 927 | 0.022071 | 2837 | 0.067548 | 1.418 | A03 | MINF0.00826019/AS
Freestanding | Mini Freestanding | MINF.00826019/FS | 8 | 260 | 19 | 23 | 2478 | 2478 | 2478 | 0.059 | 927 | 0.022071 | 2837 | 0.067548 | 1.418 | A03 | MINF0.00826019/FS
Freestanding | Mini Freestanding | MINF.00828009/AS | 8 | 280 | 09 | 13 | 1190 | 1190 | 1190 | 0.028333 | 445 | 0.010595 | 1363 | 0.032452 | 1.418 | A03 | MINF0.00828009/AS
Freestanding | Mini Freestanding | MINF.00828009/FS | 8 | 280 | 09 | 13 | 1190 | 1190 | 1190 | 0.028333 | 445 | 0.010595 | 1363 | 0.032452 | 1.418 | A03 | MINF0.00828009/FS
Freestanding | Mini Freestanding | MINF.00828014/AS | 8 | 280 | 14 | 18 | 1943 | 1943 | 1943 | 0.046262 | 727 | 0.01731 | 2225 | 0.052976 | 1.418 | A03 | MINF0.00828014/AS
Freestanding | Mini Freestanding | MINF.00828014/FS | 8 | 280 | 14 | 18 | 1943 | 1943 | 1943 | 0.046262 | 727 | 0.01731 | 2225 | 0.052976 | 1.418 | A03 | MINF0.00828014/FS
Freestanding | Mini Freestanding | MINF.00828019/AS | 8 | 280 | 19 | 23 | 2668 | 2668 | 2668 | 0.063524 | 998 | 0.023762 | 3055 | 0.072738 | 1.418 | A03 | MINF0.00828019/AS
Freestanding | Mini Freestanding | MINF.00828019/FS | 8 | 280 | 19 | 23 | 2668 | 2668 | 2668 | 0.063524 | 998 | 0.023762 | 3055 | 0.072738 | 1.418 | A03 | MINF0.00828019/FS
Freestanding | Mini Freestanding | MINF.00830009/AS | 8 | 300 | 09 | 13 | 1275 | 1275 | 1275 | 0.030357 | 477 | 0.011357 | 1460 | 0.034762 | 1.418 | A03 | MINF0.00830009/AS
Freestanding | Mini Freestanding | MINF.00830009/FS | 8 | 300 | 09 | 13 | 1275 | 1275 | 1275 | 0.030357 | 477 | 0.011357 | 1460 | 0.034762 | 1.418 | A03 | MINF0.00830009/FS
Freestanding | Mini Freestanding | MINF.00830014/AS | 8 | 300 | 14 | 18 | 2082 | 2082 | 2082 | 0.049571 | 779 | 0.018548 | 2384 | 0.056762 | 1.418 | A03 | MINF0.00830014/AS
Freestanding | Mini Freestanding | MINF.00830014/FS | 8 | 300 | 14 | 18 | 2082 | 2082 | 2082 | 0.049571 | 779 | 0.018548 | 2384 | 0.056762 | 1.418 | A03 | MINF0.00830014/FS
Freestanding | Mini Freestanding | MINF.00830019/AS | 8 | 300 | 19 | 23 | 2859 | 2859 | 2859 | 0.068071 | 1069 | 0.025452 | 3274 | 0.077952 | 1.418 | A03 | MINF0.00830019/AS
Freestanding | Mini Freestanding | MINF.00830019/FS | 8 | 300 | 19 | 23 | 2859 | 2859 | 2859 | 0.068071 | 1069 | 0.025452 | 3274 | 0.077952 | 1.418 | A03 | MINF0.00830019/FS
Freestanding | Mini Freestanding | MINF.01306005/AS | 13 | 60 | 05 | 8 | 197 | 197 | 197 | 0.0046905 | 74 | 0.0017619 | 225 | 0.0053571 | 1.413 | A03 | MINF0.01306005/AS
Freestanding | Mini Freestanding | MINF.01306005/FS | 13 | 60 | 05 | 8 | 197 | 197 | 197 | 0.0046905 | 74 | 0.0017619 | 225 | 0.0053571 | 1.413 | A03 | MINF0.01306005/FS
Freestanding | Mini Freestanding | MINF.01306010/AS | 13 | 60 | 10 | 13 | 303 | 303 | 303 | 0.0072143 | 113 | 0.0026905 | 347 | 0.0082619 | 1.419 | A03 | MINF0.01306010/AS
Freestanding | Mini Freestanding | MINF.01306010/FS | 13 | 60 | 10 | 13 | 303 | 303 | 303 | 0.0072143 | 113 | 0.0026905 | 347 | 0.0082619 | 1.419 | A03 | MINF0.01306010/FS
Freestanding | Mini Freestanding | MINF.01306015/AS | 13 | 60 | 15 | 18 | 508 | 508 | 508 | 0.012095 | 191 | 0.0045476 | 581 | 0.013833 | 1.416 | A03 | MINF0.01306015/AS
Freestanding | Mini Freestanding | MINF.01306015/FS | 13 | 60 | 15 | 18 | 508 | 508 | 508 | 0.012095 | 191 | 0.0045476 | 581 | 0.013833 | 1.416 | A03 | MINF0.01306015/FS
Freestanding | Mini Freestanding | MINF.01306020/AS | 13 | 60 | 20 | 23 | 717 | 717 | 717 | 0.017071 | 269 | 0.0064048 | 820 | 0.019524 | 1.416 | A03 | MINF0.01306020/AS
Freestanding | Mini Freestanding | MINF.01306020/FS | 13 | 60 | 20 | 23 | 717 | 717 | 717 | 0.017071 | 269 | 0.0064048 | 820 | 0.019524 | 1.416 | A03 | MINF0.01306020/FS
Freestanding | Mini Freestanding | MINF.01307005/AS | 13 | 70 | 05 | 8 | 230 | 230 | 230 | 0.0054762 | 86 | 0.0020476 | 263 | 0.0062619 | 1.413 | A03 | MINF0.01307005/AS
Freestanding | Mini Freestanding | MINF.01307005/FS | 13 | 70 | 05 | 8 | 230 | 230 | 230 | 0.0054762 | 86 | 0.0020476 | 263 | 0.0062619 | 1.413 | A03 | MINF0.01307005/FS
Freestanding | Mini Freestanding | MINF.01307010/AS | 13 | 70 | 10 | 13 | 354 | 354 | 354 | 0.0084286 | 132 | 0.0031429 | 405 | 0.0096429 | 1.419 | A03 | MINF0.01307010/AS
Freestanding | Mini Freestanding | MINF.01307010/FS | 13 | 70 | 10 | 13 | 354 | 354 | 354 | 0.0084286 | 132 | 0.0031429 | 405 | 0.0096429 | 1.419 | A03 | MINF0.01307010/FS
Freestanding | Mini Freestanding | MINF.01307015/AS | 13 | 70 | 15 | 18 | 593 | 593 | 593 | 0.014119 | 222 | 0.0052857 | 678 | 0.016143 | 1.416 | A03 | MINF0.01307015/AS
Freestanding | Mini Freestanding | MINF.01307015/FS | 13 | 70 | 15 | 18 | 593 | 593 | 593 | 0.014119 | 222 | 0.0052857 | 678 | 0.016143 | 1.416 | A03 | MINF0.01307015/FS
Freestanding | Mini Freestanding | MINF.01307020/AS | 13 | 70 | 20 | 23 | 837 | 837 | 837 | 0.019929 | 314 | 0.0074762 | 958 | 0.02281 | 1.416 | A03 | MINF0.01307020/AS
Freestanding | Mini Freestanding | MINF.01307020/FS | 13 | 70 | 20 | 23 | 837 | 837 | 837 | 0.019929 | 314 | 0.0074762 | 958 | 0.02281 | 1.416 | A03 | MINF0.01307020/FS
Freestanding | Mini Freestanding | MINF.01308005/AS | 13 | 80 | 05 | 8 | 263 | 263 | 263 | 0.0062619 | 99 | 0.0023571 | 301 | 0.0071667 | 1.413 | A03 | MINF0.01308005/AS
Freestanding | Mini Freestanding | MINF.01308005/FS | 13 | 80 | 05 | 8 | 263 | 263 | 263 | 0.0062619 | 99 | 0.0023571 | 301 | 0.0071667 | 1.413 | A03 | MINF0.01308005/FS
Freestanding | Mini Freestanding | MINF.01308010/AS | 13 | 80 | 10 | 13 | 404 | 404 | 404 | 0.009619 | 151 | 0.0035952 | 463 | 0.011024 | 1.419 | A03 | MINF0.01308010/AS
Freestanding | Mini Freestanding | MINF.01308010/FS | 13 | 80 | 10 | 13 | 404 | 404 | 404 | 0.009619 | 151 | 0.0035952 | 463 | 0.011024 | 1.419 | A03 | MINF0.01308010/FS
Freestanding | Mini Freestanding | MINF.01308015/AS | 13 | 80 | 15 | 18 | 678 | 678 | 678 | 0.016143 | 254 | 0.0060476 | 776 | 0.018476 | 1.416 | A03 | MINF0.01308015/AS
Freestanding | Mini Freestanding | MINF.01308015/FS | 13 | 80 | 15 | 18 | 678 | 678 | 678 | 0.016143 | 254 | 0.0060476 | 776 | 0.018476 | 1.416 | A03 | MINF0.01308015/FS
Freestanding | Mini Freestanding | MINF.01308020/AS | 13 | 80 | 20 | 23 | 956 | 956 | 956 | 0.022762 | 359 | 0.0085476 | 1094 | 0.026048 | 1.416 | A03 | MINF0.01308020/AS
Freestanding | Mini Freestanding | MINF.01308020/FS | 13 | 80 | 20 | 23 | 956 | 956 | 956 | 0.022762 | 359 | 0.0085476 | 1094 | 0.026048 | 1.416 | A03 | MINF0.01308020/FS
Freestanding | Mini Freestanding | MINF.01309005/AS | 13 | 90 | 05 | 8 | 296 | 296 | 296 | 0.0070476 | 111 | 0.0026429 | 339 | 0.0080714 | 1.413 | A03 | MINF0.01309005/AS
Freestanding | Mini Freestanding | MINF.01309005/FS | 13 | 90 | 05 | 8 | 296 | 296 | 296 | 0.0070476 | 111 | 0.0026429 | 339 | 0.0080714 | 1.413 | A03 | MINF0.01309005/FS
Freestanding | Mini Freestanding | MINF.01309010/AS | 13 | 90 | 10 | 13 | 455 | 455 | 455 | 0.010833 | 170 | 0.0040476 | 521 | 0.012405 | 1.419 | A03 | MINF0.01309010/AS
Freestanding | Mini Freestanding | MINF.01309010/FS | 13 | 90 | 10 | 13 | 455 | 455 | 455 | 0.010833 | 170 | 0.0040476 | 521 | 0.012405 | 1.419 | A03 | MINF0.01309010/FS
Freestanding | Mini Freestanding | MINF.01309015/AS | 13 | 90 | 15 | 18 | 762 | 762 | 762 | 0.018143 | 286 | 0.0068095 | 872 | 0.020762 | 1.416 | A03 | MINF0.01309015/AS
Freestanding | Mini Freestanding | MINF.01309015/FS | 13 | 90 | 15 | 18 | 762 | 762 | 762 | 0.018143 | 286 | 0.0068095 | 872 | 0.020762 | 1.416 | A03 | MINF0.01309015/FS
Freestanding | Mini Freestanding | MINF.01309020/AS | 13 | 90 | 20 | 23 | 1076 | 1076 | 1076 | 0.025619 | 404 | 0.009619 | 1231 | 0.02931 | 1.416 | A03 | MINF0.01309020/AS
Freestanding | Mini Freestanding | MINF.01309020/FS | 13 | 90 | 20 | 23 | 1076 | 1076 | 1076 | 0.025619 | 404 | 0.009619 | 1231 | 0.02931 | 1.416 | A03 | MINF0.01309020/FS
Freestanding | Mini Freestanding | MINF.01310005/AS | 13 | 100 | 05 | 8 | 329 | 329 | 329 | 0.0078333 | 124 | 0.0029524 | 376 | 0.0089524 | 1.413 | A03 | MINF0.01310005/AS
Freestanding | Mini Freestanding | MINF.01310005/FS | 13 | 100 | 05 | 8 | 329 | 329 | 329 | 0.0078333 | 124 | 0.0029524 | 376 | 0.0089524 | 1.413 | A03 | MINF0.01310005/FS
Freestanding | Mini Freestanding | MINF.01310010/AS | 13 | 100 | 10 | 13 | 505 | 505 | 505 | 0.012024 | 189 | 0.0045 | 578 | 0.013762 | 1.419 | A03 | MINF0.01310010/AS
Freestanding | Mini Freestanding | MINF.01310010/FS | 13 | 100 | 10 | 13 | 505 | 505 | 505 | 0.012024 | 189 | 0.0045 | 578 | 0.013762 | 1.419 | A03 | MINF0.01310010/FS
Freestanding | Mini Freestanding | MINF.01310015/AS | 13 | 100 | 15 | 18 | 847 | 847 | 847 | 0.020167 | 318 | 0.0075714 | 969 | 0.023071 | 1.416 | A03 | MINF0.01310015/AS
Freestanding | Mini Freestanding | MINF.01310015/FS | 13 | 100 | 15 | 18 | 847 | 847 | 847 | 0.020167 | 318 | 0.0075714 | 969 | 0.023071 | 1.416 | A03 | MINF0.01310015/FS
Freestanding | Mini Freestanding | MINF.01310020/AS | 13 | 100 | 20 | 23 | 1195 | 1195 | 1195 | 0.028452 | 448 | 0.010667 | 1367 | 0.032548 | 1.416 | A03 | MINF0.01310020/AS
Freestanding | Mini Freestanding | MINF.01310020/FS | 13 | 100 | 20 | 23 | 1195 | 1195 | 1195 | 0.028452 | 448 | 0.010667 | 1367 | 0.032548 | 1.416 | A03 | MINF0.01310020/FS
Freestanding | Mini Freestanding | MINF.01311005/AS | 13 | 110 | 05 | 8 | 362 | 362 | 362 | 0.008619 | 136 | 0.0032381 | 414 | 0.0098571 | 1.413 | A03 | MINF0.01311005/AS
Freestanding | Mini Freestanding | MINF.01311005/FS | 13 | 110 | 05 | 8 | 362 | 362 | 362 | 0.008619 | 136 | 0.0032381 | 414 | 0.0098571 | 1.413 | A03 | MINF0.01311005/FS
Freestanding | Mini Freestanding | MINF.01311010/AS | 13 | 110 | 10 | 13 | 556 | 556 | 556 | 0.013238 | 208 | 0.0049524 | 637 | 0.015167 | 1.419 | A03 | MINF0.01311010/AS
Freestanding | Mini Freestanding | MINF.01311010/FS | 13 | 110 | 10 | 13 | 556 | 556 | 556 | 0.013238 | 208 | 0.0049524 | 637 | 0.015167 | 1.419 | A03 | MINF0.01311010/FS
Freestanding | Mini Freestanding | MINF.01311015/AS | 13 | 110 | 15 | 18 | 932 | 932 | 932 | 0.02219 | 350 | 0.0083333 | 1066 | 0.025381 | 1.416 | A03 | MINF0.01311015/AS
Freestanding | Mini Freestanding | MINF.01311015/FS | 13 | 110 | 15 | 18 | 932 | 932 | 932 | 0.02219 | 350 | 0.0083333 | 1066 | 0.025381 | 1.416 | A03 | MINF0.01311015/FS
Freestanding | Mini Freestanding | MINF.01311020/AS | 13 | 110 | 20 | 23 | 1315 | 1315 | 1315 | 0.03131 | 493 | 0.011738 | 1504 | 0.03581 | 1.416 | A03 | MINF0.01311020/AS
Freestanding | Mini Freestanding | MINF.01311020/FS | 13 | 110 | 20 | 23 | 1315 | 1315 | 1315 | 0.03131 | 493 | 0.011738 | 1504 | 0.03581 | 1.416 | A03 | MINF0.01311020/FS
Freestanding | Mini Freestanding | MINF.01312005/AS | 13 | 120 | 05 | 8 | 395 | 395 | 395 | 0.0094048 | 149 | 0.0035476 | 452 | 0.010762 | 1.413 | A03 | MINF0.01312005/AS
Freestanding | Mini Freestanding | MINF.01312005/FS | 13 | 120 | 05 | 8 | 395 | 395 | 395 | 0.0094048 | 149 | 0.0035476 | 452 | 0.010762 | 1.413 | A03 | MINF0.01312005/FS
Freestanding | Mini Freestanding | MINF.01312010/AS | 13 | 120 | 10 | 13 | 606 | 606 | 606 | 0.014429 | 227 | 0.0054048 | 694 | 0.016524 | 1.419 | A03 | MINF0.01312010/AS
Freestanding | Mini Freestanding | MINF.01312010/FS | 13 | 120 | 10 | 13 | 606 | 606 | 606 | 0.014429 | 227 | 0.0054048 | 694 | 0.016524 | 1.419 | A03 | MINF0.01312010/FS
Freestanding | Mini Freestanding | MINF.01312015/AS | 13 | 120 | 15 | 18 | 1016 | 1016 | 1016 | 0.02419 | 381 | 0.0090714 | 1162 | 0.027667 | 1.416 | A03 | MINF0.01312015/AS
Freestanding | Mini Freestanding | MINF.01312015/FS | 13 | 120 | 15 | 18 | 1016 | 1016 | 1016 | 0.02419 | 381 | 0.0090714 | 1162 | 0.027667 | 1.416 | A03 | MINF0.01312015/FS
Freestanding | Mini Freestanding | MINF.01312020/AS | 13 | 120 | 20 | 23 | 1434 | 1434 | 1434 | 0.034143 | 538 | 0.01281 | 1640 | 0.039048 | 1.416 | A03 | MINF0.01312020/AS
Freestanding | Mini Freestanding | MINF.01312020/FS | 13 | 120 | 20 | 23 | 1434 | 1434 | 1434 | 0.034143 | 538 | 0.01281 | 1640 | 0.039048 | 1.416 | A03 | MINF0.01312020/FS
Freestanding | Mini Freestanding | MINF.01314005/AS | 13 | 140 | 05 | 8 | 461 | 461 | 461 | 0.010976 | 173 | 0.004119 | 527 | 0.012548 | 1.413 | A03 | MINF0.01314005/AS
Freestanding | Mini Freestanding | MINF.01314005/FS | 13 | 140 | 05 | 8 | 461 | 461 | 461 | 0.010976 | 173 | 0.004119 | 527 | 0.012548 | 1.413 | A03 | MINF0.01314005/FS
Freestanding | Mini Freestanding | MINF.01314010/AS | 13 | 140 | 10 | 13 | 707 | 707 | 707 | 0.016833 | 264 | 0.0062857 | 810 | 0.019286 | 1.419 | A03 | MINF0.01314010/AS
Freestanding | Mini Freestanding | MINF.01314010/FS | 13 | 140 | 10 | 13 | 707 | 707 | 707 | 0.016833 | 264 | 0.0062857 | 810 | 0.019286 | 1.419 | A03 | MINF0.01314010/FS
Freestanding | Mini Freestanding | MINF.01314015/AS | 13 | 140 | 15 | 18 | 1186 | 1186 | 1186 | 0.028238 | 445 | 0.010595 | 1357 | 0.03231 | 1.416 | A03 | MINF0.01314015/AS
Freestanding | Mini Freestanding | MINF.01314015/FS | 13 | 140 | 15 | 18 | 1186 | 1186 | 1186 | 0.028238 | 445 | 0.010595 | 1357 | 0.03231 | 1.416 | A03 | MINF0.01314015/FS
Freestanding | Mini Freestanding | MINF.01314020/AS | 13 | 140 | 20 | 23 | 1673 | 1673 | 1673 | 0.039833 | 627 | 0.014929 | 1914 | 0.045571 | 1.416 | A03 | MINF0.01314020/AS
Freestanding | Mini Freestanding | MINF.01314020/FS | 13 | 140 | 20 | 23 | 1673 | 1673 | 1673 | 0.039833 | 627 | 0.014929 | 1914 | 0.045571 | 1.416 | A03 | MINF0.01314020/FS
Freestanding | Mini Freestanding | MINF.01316005/AS | 13 | 160 | 05 | 8 | 526 | 526 | 526 | 0.012524 | 198 | 0.0047143 | 602 | 0.014333 | 1.413 | A03 | MINF0.01316005/AS
Freestanding | Mini Freestanding | MINF.01316005/FS | 13 | 160 | 05 | 8 | 526 | 526 | 526 | 0.012524 | 198 | 0.0047143 | 602 | 0.014333 | 1.413 | A03 | MINF0.01316005/FS
Freestanding | Mini Freestanding | MINF.01316010/AS | 13 | 160 | 10 | 13 | 808 | 808 | 808 | 0.019238 | 302 | 0.0071905 | 925 | 0.022024 | 1.419 | A03 | MINF0.01316010/AS
Freestanding | Mini Freestanding | MINF.01316010/FS | 13 | 160 | 10 | 13 | 808 | 808 | 808 | 0.019238 | 302 | 0.0071905 | 925 | 0.022024 | 1.419 | A03 | MINF0.01316010/FS
Freestanding | Mini Freestanding | MINF.01316015/AS | 13 | 160 | 15 | 18 | 1355 | 1355 | 1355 | 0.032262 | 508 | 0.012095 | 1550 | 0.036905 | 1.416 | A03 | MINF0.01316015/AS
Freestanding | Mini Freestanding | MINF.01316015/FS | 13 | 160 | 15 | 18 | 1355 | 1355 | 1355 | 0.032262 | 508 | 0.012095 | 1550 | 0.036905 | 1.416 | A03 | MINF0.01316015/FS
Freestanding | Mini Freestanding | MINF.01316020/AS | 13 | 160 | 20 | 23 | 1912 | 1912 | 1912 | 0.045524 | 717 | 0.017071 | 2187 | 0.052071 | 1.416 | A03 | MINF0.01316020/AS
Freestanding | Mini Freestanding | MINF.01316020/FS | 13 | 160 | 20 | 23 | 1912 | 1912 | 1912 | 0.045524 | 717 | 0.017071 | 2187 | 0.052071 | 1.416 | A03 | MINF0.01316020/FS
Freestanding | Mini Freestanding | MINF.01318005/AS | 13 | 180 | 05 | 8 | 592 | 592 | 592 | 0.014095 | 223 | 0.0053095 | 677 | 0.016119 | 1.413 | A03 | MINF0.01318005/AS
Freestanding | Mini Freestanding | MINF.01318005/FS | 13 | 180 | 05 | 8 | 592 | 592 | 592 | 0.014095 | 223 | 0.0053095 | 677 | 0.016119 | 1.413 | A03 | MINF0.01318005/FS
Freestanding | Mini Freestanding | MINF.01318010/AS | 13 | 180 | 10 | 13 | 909 | 909 | 909 | 0.021643 | 340 | 0.0080952 | 1041 | 0.024786 | 1.419 | A03 | MINF0.01318010/AS
Freestanding | Mini Freestanding | MINF.01318010/FS | 13 | 180 | 10 | 13 | 909 | 909 | 909 | 0.021643 | 340 | 0.0080952 | 1041 | 0.024786 | 1.419 | A03 | MINF0.01318010/FS
Freestanding | Mini Freestanding | MINF.01318015/AS | 13 | 180 | 15 | 18 | 1525 | 1525 | 1525 | 0.03631 | 572 | 0.013619 | 1745 | 0.041548 | 1.416 | A03 | MINF0.01318015/AS
Freestanding | Mini Freestanding | MINF.01318015/FS | 13 | 180 | 15 | 18 | 1525 | 1525 | 1525 | 0.03631 | 572 | 0.013619 | 1745 | 0.041548 | 1.416 | A03 | MINF0.01318015/FS
Freestanding | Mini Freestanding | MINF.01318020/AS | 13 | 180 | 20 | 23 | 2151 | 2151 | 2151 | 0.051214 | 807 | 0.019214 | 2461 | 0.058595 | 1.416 | A03 | MINF0.01318020/AS
Freestanding | Mini Freestanding | MINF.01318020/FS | 13 | 180 | 20 | 23 | 2151 | 2151 | 2151 | 0.051214 | 807 | 0.019214 | 2461 | 0.058595 | 1.416 | A03 | MINF0.01318020/FS
Freestanding | Mini Freestanding | MINF.01320005/AS | 13 | 200 | 05 | 8 | 658 | 658 | 658 | 0.015667 | 247 | 0.005881 | 753 | 0.017929 | 1.413 | A03 | MINF0.01320005/AS
Freestanding | Mini Freestanding | MINF.01320005/FS | 13 | 200 | 05 | 8 | 658 | 658 | 658 | 0.015667 | 247 | 0.005881 | 753 | 0.017929 | 1.413 | A03 | MINF0.01320005/FS
Freestanding | Mini Freestanding | MINF.01320010/AS | 13 | 200 | 10 | 13 | 1010 | 1010 | 1010 | 0.024048 | 378 | 0.009 | 1156 | 0.027524 | 1.419 | A03 | MINF0.01320010/AS
Freestanding | Mini Freestanding | MINF.01320010/FS | 13 | 200 | 10 | 13 | 1010 | 1010 | 1010 | 0.024048 | 378 | 0.009 | 1156 | 0.027524 | 1.419 | A03 | MINF0.01320010/FS
Freestanding | Mini Freestanding | MINF.01320015/AS | 13 | 200 | 15 | 18 | 1694 | 1694 | 1694 | 0.040333 | 635 | 0.015119 | 1938 | 0.046143 | 1.416 | A03 | MINF0.01320015/AS
Freestanding | Mini Freestanding | MINF.01320015/FS | 13 | 200 | 15 | 18 | 1694 | 1694 | 1694 | 0.040333 | 635 | 0.015119 | 1938 | 0.046143 | 1.416 | A03 | MINF0.01320015/FS
Freestanding | Mini Freestanding | MINF.01320020/AS | 13 | 200 | 20 | 23 | 2390 | 2390 | 2390 | 0.056905 | 896 | 0.021333 | 2734 | 0.065095 | 1.416 | A03 | MINF0.01320020/AS
Freestanding | Mini Freestanding | MINF.01320020/FS | 13 | 200 | 20 | 23 | 2390 | 2390 | 2390 | 0.056905 | 896 | 0.021333 | 2734 | 0.065095 | 1.416 | A03 | MINF0.01320020/FS
Freestanding | Mini Freestanding | MINF.01322005/AS | 13 | 220 | 05 | 8 | 724 | 724 | 724 | 0.017238 | 272 | 0.0064762 | 828 | 0.019714 | 1.413 | A03 | MINF0.01322005/AS
Freestanding | Mini Freestanding | MINF.01322005/FS | 13 | 220 | 05 | 8 | 724 | 724 | 724 | 0.017238 | 272 | 0.0064762 | 828 | 0.019714 | 1.413 | A03 | MINF0.01322005/FS
Freestanding | Mini Freestanding | MINF.01322010/AS | 13 | 220 | 10 | 13 | 1111 | 1111 | 1111 | 0.026452 | 416 | 0.0099048 | 1272 | 0.030286 | 1.419 | A03 | MINF0.01322010/AS
Freestanding | Mini Freestanding | MINF.01322010/FS | 13 | 220 | 10 | 13 | 1111 | 1111 | 1111 | 0.026452 | 416 | 0.0099048 | 1272 | 0.030286 | 1.419 | A03 | MINF0.01322010/FS
Freestanding | Mini Freestanding | MINF.01322015/AS | 13 | 220 | 15 | 18 | 1863 | 1863 | 1863 | 0.044357 | 699 | 0.016643 | 2131 | 0.050738 | 1.416 | A03 | MINF0.01322015/AS
Freestanding | Mini Freestanding | MINF.01322015/FS | 13 | 220 | 15 | 18 | 1863 | 1863 | 1863 | 0.044357 | 699 | 0.016643 | 2131 | 0.050738 | 1.416 | A03 | MINF0.01322015/FS
Freestanding | Mini Freestanding | MINF.01322020/AS | 13 | 220 | 20 | 23 | 2629 | 2629 | 2629 | 0.062595 | 986 | 0.023476 | 3008 | 0.071619 | 1.416 | A03 | MINF0.01322020/AS
Freestanding | Mini Freestanding | MINF.01322020/FS | 13 | 220 | 20 | 23 | 2629 | 2629 | 2629 | 0.062595 | 986 | 0.023476 | 3008 | 0.071619 | 1.416 | A03 | MINF0.01322020/FS
Freestanding | Mini Freestanding | MINF.01324005/AS | 13 | 240 | 05 | 8 | 790 | 790 | 790 | 0.01881 | 297 | 0.0070714 | 904 | 0.021524 | 1.413 | A03 | MINF0.01324005/AS
Freestanding | Mini Freestanding | MINF.01324005/FS | 13 | 240 | 05 | 8 | 790 | 790 | 790 | 0.01881 | 297 | 0.0070714 | 904 | 0.021524 | 1.413 | A03 | MINF0.01324005/FS
Freestanding | Mini Freestanding | MINF.01324010/AS | 13 | 240 | 10 | 13 | 1212 | 1212 | 1212 | 0.028857 | 453 | 0.010786 | 1388 | 0.033048 | 1.419 | A03 | MINF0.01324010/AS
Freestanding | Mini Freestanding | MINF.01324010/FS | 13 | 240 | 10 | 13 | 1212 | 1212 | 1212 | 0.028857 | 453 | 0.010786 | 1388 | 0.033048 | 1.419 | A03 | MINF0.01324010/FS
Freestanding | Mini Freestanding | MINF.01324015/AS | 13 | 240 | 15 | 18 | 2033 | 2033 | 2033 | 0.048405 | 762 | 0.018143 | 2326 | 0.055381 | 1.416 | A03 | MINF0.01324015/AS
Freestanding | Mini Freestanding | MINF.01324015/FS | 13 | 240 | 15 | 18 | 2033 | 2033 | 2033 | 0.048405 | 762 | 0.018143 | 2326 | 0.055381 | 1.416 | A03 | MINF0.01324015/FS
Freestanding | Mini Freestanding | MINF.01324020/AS | 13 | 240 | 20 | 23 | 2868 | 2868 | 2868 | 0.068286 | 1076 | 0.025619 | 3281 | 0.078119 | 1.416 | A03 | MINF0.01324020/AS
Freestanding | Mini Freestanding | MINF.01324020/FS | 13 | 240 | 20 | 23 | 2868 | 2868 | 2868 | 0.068286 | 1076 | 0.025619 | 3281 | 0.078119 | 1.416 | A03 | MINF0.01324020/FS
Freestanding | Mini Freestanding | MINF.01326005/AS | 13 | 260 | 05 | 8 | 855 | 855 | 855 | 0.020357 | 321 | 0.0076429 | 978 | 0.023286 | 1.413 | A03 | MINF0.01326005/AS
Freestanding | Mini Freestanding | MINF.01326005/FS | 13 | 260 | 05 | 8 | 855 | 855 | 855 | 0.020357 | 321 | 0.0076429 | 978 | 0.023286 | 1.413 | A03 | MINF0.01326005/FS
Freestanding | Mini Freestanding | MINF.01326010/AS | 13 | 260 | 10 | 13 | 1313 | 1313 | 1313 | 0.031262 | 491 | 0.01169 | 1503 | 0.035786 | 1.419 | A03 | MINF0.01326010/AS
Freestanding | Mini Freestanding | MINF.01326010/FS | 13 | 260 | 10 | 13 | 1313 | 1313 | 1313 | 0.031262 | 491 | 0.01169 | 1503 | 0.035786 | 1.419 | A03 | MINF0.01326010/FS
Freestanding | Mini Freestanding | MINF.01326015/AS | 13 | 260 | 15 | 18 | 2202 | 2202 | 2202 | 0.052429 | 826 | 0.019667 | 2519 | 0.059976 | 1.416 | A03 | MINF0.01326015/AS
Freestanding | Mini Freestanding | MINF.01326015/FS | 13 | 260 | 15 | 18 | 2202 | 2202 | 2202 | 0.052429 | 826 | 0.019667 | 2519 | 0.059976 | 1.416 | A03 | MINF0.01326015/FS
Freestanding | Mini Freestanding | MINF.01326020/AS | 13 | 260 | 20 | 23 | 3107 | 3107 | 3107 | 0.073976 | 1165 | 0.027738 | 3554 | 0.084619 | 1.416 | A03 | MINF0.01326020/AS
Freestanding | Mini Freestanding | MINF.01326020/FS | 13 | 260 | 20 | 23 | 3107 | 3107 | 3107 | 0.073976 | 1165 | 0.027738 | 3554 | 0.084619 | 1.416 | A03 | MINF0.01326020/FS
Freestanding | Mini Freestanding | MINF.01328005/AS | 13 | 280 | 05 | 8 | 921 | 921 | 921 | 0.021929 | 346 | 0.0082381 | 1054 | 0.025095 | 1.413 | A03 | MINF0.01328005/AS
Freestanding | Mini Freestanding | MINF.01328005/FS | 13 | 280 | 05 | 8 | 921 | 921 | 921 | 0.021929 | 346 | 0.0082381 | 1054 | 0.025095 | 1.413 | A03 | MINF0.01328005/FS
Freestanding | Mini Freestanding | MINF.01328010/AS | 13 | 280 | 10 | 13 | 1414 | 1414 | 1414 | 0.033667 | 529 | 0.012595 | 1619 | 0.038548 | 1.419 | A03 | MINF0.01328010/AS
Freestanding | Mini Freestanding | MINF.01328010/FS | 13 | 280 | 10 | 13 | 1414 | 1414 | 1414 | 0.033667 | 529 | 0.012595 | 1619 | 0.038548 | 1.419 | A03 | MINF0.01328010/FS
Freestanding | Mini Freestanding | MINF.01328015/AS | 13 | 280 | 15 | 18 | 2372 | 2372 | 2372 | 0.056476 | 890 | 0.02119 | 2714 | 0.064619 | 1.416 | A03 | MINF0.01328015/AS
Freestanding | Mini Freestanding | MINF.01328015/FS | 13 | 280 | 15 | 18 | 2372 | 2372 | 2372 | 0.056476 | 890 | 0.02119 | 2714 | 0.064619 | 1.416 | A03 | MINF0.01328015/FS
Freestanding | Mini Freestanding | MINF.01328020/AS | 13 | 280 | 20 | 23 | 3346 | 3346 | 3346 | 0.079667 | 1255 | 0.029881 | 3828 | 0.091143 | 1.416 | A03 | MINF0.01328020/AS
Freestanding | Mini Freestanding | MINF.01328020/FS | 13 | 280 | 20 | 23 | 3346 | 3346 | 3346 | 0.079667 | 1255 | 0.029881 | 3828 | 0.091143 | 1.416 | A03 | MINF0.01328020/FS
Freestanding | Mini Freestanding | MINF.01330005/AS | 13 | 300 | 05 | 8 | 987 | 987 | 987 | 0.0235 | 371 | 0.0088333 | 1129 | 0.026881 | 1.413 | A03 | MINF0.01330005/AS
Freestanding | Mini Freestanding | MINF.01330005/FS | 13 | 300 | 05 | 8 | 987 | 987 | 987 | 0.0235 | 371 | 0.0088333 | 1129 | 0.026881 | 1.413 | A03 | MINF0.01330005/FS
Freestanding | Mini Freestanding | MINF.01330010/AS | 13 | 300 | 10 | 13 | 1515 | 1515 | 1515 | 0.036071 | 567 | 0.0135 | 1735 | 0.04131 | 1.419 | A03 | MINF0.01330010/AS
Freestanding | Mini Freestanding | MINF.01330010/FS | 13 | 300 | 10 | 13 | 1515 | 1515 | 1515 | 0.036071 | 567 | 0.0135 | 1735 | 0.04131 | 1.419 | A03 | MINF0.01330010/FS
Freestanding | Mini Freestanding | MINF.01330015/AS | 13 | 300 | 15 | 18 | 2541 | 2541 | 2541 | 0.0605 | 953 | 0.02269 | 2907 | 0.069214 | 1.416 | A03 | MINF0.01330015/AS
Freestanding | Mini Freestanding | MINF.01330015/FS | 13 | 300 | 15 | 18 | 2541 | 2541 | 2541 | 0.0605 | 953 | 0.02269 | 2907 | 0.069214 | 1.416 | A03 | MINF0.01330015/FS
Freestanding | Mini Freestanding | MINF.01330020/AS | 13 | 300 | 20 | 23 | 3585 | 3585 | 3585 | 0.085357 | 1344 | 0.032 | 4101 | 0.097643 | 1.416 | A03 | MINF0.01330020/AS
Freestanding | Mini Freestanding | MINF.01330020/FS | 13 | 300 | 20 | 23 | 3585 | 3585 | 3585 | 0.085357 | 1344 | 0.032 | 4101 | 0.097643 | 1.416 | A03 | MINF0.01330020/FS
Freestanding | Mini Freestanding | MINF.02306006/AS | 23 | 60 | 06 | 8 | 323 | 323 | 323 | 0.0076905 | 121 | 0.002881 | 370 | 0.0088095 | 1.411 | A03 | MINF0.02306006/AS
Freestanding | Mini Freestanding | MINF.02306006/FM | 23 | 60 | 06 | 8 | 323 | 323 | 323 | 0.0076905 | 121 | 0.002881 | 370 | 0.0088095 | 1.411 | A03 | MINF0.02306006/FM
Freestanding | Mini Freestanding | MINF.02306011/AS | 23 | 60 | 11 | 13 | 601 | 601 | 601 | 0.01431 | 221 | 0.0052619 | 689 | 0.016405 | 1.441 | A03 | MINF0.02306011/AS
Freestanding | Mini Freestanding | MINF.02306011/FM | 23 | 60 | 11 | 13 | 601 | 601 | 601 | 0.01431 | 221 | 0.0052619 | 689 | 0.016405 | 1.441 | A03 | MINF0.02306011/FM
Freestanding | Mini Freestanding | MINF.02306016/AS | 23 | 60 | 16 | 18 | 785 | 785 | 785 | 0.01869 | 287 | 0.0068333 | 902 | 0.021476 | 1.453 | A03 | MINF0.02306016/AS
Freestanding | Mini Freestanding | MINF.02306016/FM | 23 | 60 | 16 | 18 | 785 | 785 | 785 | 0.01869 | 287 | 0.0068333 | 902 | 0.021476 | 1.453 | A03 | MINF0.02306016/FM
Freestanding | Mini Freestanding | MINF.02306021/AS | 23 | 60 | 21 | 23 | 1021 | 1021 | 1021 | 0.02431 | 371 | 0.0088333 | 1174 | 0.027952 | 1.463 | A03 | MINF0.02306021/AS
Freestanding | Mini Freestanding | MINF.02306021/FM | 23 | 60 | 21 | 23 | 1021 | 1021 | 1021 | 0.02431 | 371 | 0.0088333 | 1174 | 0.027952 | 1.463 | A03 | MINF0.02306021/FM
Freestanding | Mini Freestanding | MINF.02307006/AS | 23 | 70 | 06 | 8 | 377 | 377 | 377 | 0.0089762 | 142 | 0.003381 | 431 | 0.010262 | 1.411 | A03 | MINF0.02307006/AS
Freestanding | Mini Freestanding | MINF.02307006/FM | 23 | 70 | 06 | 8 | 377 | 377 | 377 | 0.0089762 | 142 | 0.003381 | 431 | 0.010262 | 1.411 | A03 | MINF0.02307006/FM
Freestanding | Mini Freestanding | MINF.02307011/AS | 23 | 70 | 11 | 13 | 701 | 701 | 701 | 0.01669 | 258 | 0.0061429 | 804 | 0.019143 | 1.441 | A03 | MINF0.02307011/AS
Freestanding | Mini Freestanding | MINF.02307011/FM | 23 | 70 | 11 | 13 | 701 | 701 | 701 | 0.01669 | 258 | 0.0061429 | 804 | 0.019143 | 1.441 | A03 | MINF0.02307011/FM
Freestanding | Mini Freestanding | MINF.02307016/AS | 23 | 70 | 16 | 18 | 916 | 916 | 916 | 0.02181 | 334 | 0.0079524 | 1052 | 0.025048 | 1.453 | A03 | MINF0.02307016/AS
Freestanding | Mini Freestanding | MINF.02307016/FM | 23 | 70 | 16 | 18 | 916 | 916 | 916 | 0.02181 | 334 | 0.0079524 | 1052 | 0.025048 | 1.453 | A03 | MINF0.02307016/FM
Freestanding | Mini Freestanding | MINF.02307021/AS | 23 | 70 | 21 | 23 | 1191 | 1191 | 1191 | 0.028357 | 432 | 0.010286 | 1370 | 0.032619 | 1.463 | A03 | MINF0.02307021/AS
Freestanding | Mini Freestanding | MINF.02307021/FM | 23 | 70 | 21 | 23 | 1191 | 1191 | 1191 | 0.028357 | 432 | 0.010286 | 1370 | 0.032619 | 1.463 | A03 | MINF0.02307021/FM
Freestanding | Mini Freestanding | MINF.02308006/AS | 23 | 80 | 06 | 8 | 431 | 431 | 431 | 0.010262 | 162 | 0.0038571 | 493 | 0.011738 | 1.411 | A03 | MINF0.02308006/AS
Freestanding | Mini Freestanding | MINF.02308006/FM | 23 | 80 | 06 | 8 | 431 | 431 | 431 | 0.010262 | 162 | 0.0038571 | 493 | 0.011738 | 1.411 | A03 | MINF0.02308006/FM
Freestanding | Mini Freestanding | MINF.02308011/AS | 23 | 80 | 11 | 13 | 802 | 802 | 802 | 0.019095 | 295 | 0.0070238 | 920 | 0.021905 | 1.441 | A03 | MINF0.02308011/AS
Freestanding | Mini Freestanding | MINF.02308011/FM | 23 | 80 | 11 | 13 | 802 | 802 | 802 | 0.019095 | 295 | 0.0070238 | 920 | 0.021905 | 1.441 | A03 | MINF0.02308011/FM
Freestanding | Mini Freestanding | MINF.02308016/AS | 23 | 80 | 16 | 18 | 1046 | 1046 | 1046 | 0.024905 | 382 | 0.0090952 | 1202 | 0.028619 | 1.453 | A03 | MINF0.02308016/AS
Freestanding | Mini Freestanding | MINF.02308016/FM | 23 | 80 | 16 | 18 | 1046 | 1046 | 1046 | 0.024905 | 382 | 0.0090952 | 1202 | 0.028619 | 1.453 | A03 | MINF0.02308016/FM
Freestanding | Mini Freestanding | MINF.02308021/AS | 23 | 80 | 21 | 23 | 1361 | 1361 | 1361 | 0.032405 | 494 | 0.011762 | 1565 | 0.037262 | 1.463 | A03 | MINF0.02308021/AS
Freestanding | Mini Freestanding | MINF.02308021/FM | 23 | 80 | 21 | 23 | 1361 | 1361 | 1361 | 0.032405 | 494 | 0.011762 | 1565 | 0.037262 | 1.463 | A03 | MINF0.02308021/FM
Freestanding | Mini Freestanding | MINF.02309006/AS | 23 | 90 | 06 | 8 | 485 | 485 | 485 | 0.011548 | 182 | 0.0043333 | 555 | 0.013214 | 1.411 | A03 | MINF0.02309006/AS
Freestanding | Mini Freestanding | MINF.02309006/FM | 23 | 90 | 06 | 8 | 485 | 485 | 485 | 0.011548 | 182 | 0.0043333 | 555 | 0.013214 | 1.411 | A03 | MINF0.02309006/FM
Freestanding | Mini Freestanding | MINF.02309011/AS | 23 | 90 | 11 | 13 | 902 | 902 | 902 | 0.021476 | 332 | 0.0079048 | 1035 | 0.024643 | 1.441 | A03 | MINF0.02309011/AS
Freestanding | Mini Freestanding | MINF.02309011/FM | 23 | 90 | 11 | 13 | 902 | 902 | 902 | 0.021476 | 332 | 0.0079048 | 1035 | 0.024643 | 1.441 | A03 | MINF0.02309011/FM
Freestanding | Mini Freestanding | MINF.02309016/AS | 23 | 90 | 16 | 18 | 1177 | 1177 | 1177 | 0.028024 | 430 | 0.010238 | 1352 | 0.03219 | 1.453 | A03 | MINF0.02309016/AS
Freestanding | Mini Freestanding | MINF.02309016/FM | 23 | 90 | 16 | 18 | 1177 | 1177 | 1177 | 0.028024 | 430 | 0.010238 | 1352 | 0.03219 | 1.453 | A03 | MINF0.02309016/FM
Freestanding | Mini Freestanding | MINF.02309021/AS | 23 | 90 | 21 | 23 | 1531 | 1531 | 1531 | 0.036452 | 556 | 0.013238 | 1761 | 0.041929 | 1.463 | A03 | MINF0.02309021/AS
Freestanding | Mini Freestanding | MINF.02309021/FM | 23 | 90 | 21 | 23 | 1531 | 1531 | 1531 | 0.036452 | 556 | 0.013238 | 1761 | 0.041929 | 1.463 | A03 | MINF0.02309021/FM
Freestanding | Mini Freestanding | MINF.02310006/AS | 23 | 100 | 06 | 8 | 539 | 539 | 539 | 0.012833 | 203 | 0.0048333 | 617 | 0.01469 | 1.411 | A03 | MINF0.02310006/AS
Freestanding | Mini Freestanding | MINF.02310006/FM | 23 | 100 | 06 | 8 | 539 | 539 | 539 | 0.012833 | 203 | 0.0048333 | 617 | 0.01469 | 1.411 | A03 | MINF0.02310006/FM
Freestanding | Mini Freestanding | MINF.02310011/AS | 23 | 100 | 11 | 13 | 1002 | 1002 | 1002 | 0.023857 | 369 | 0.0087857 | 1149 | 0.027357 | 1.441 | A03 | MINF0.02310011/AS
Freestanding | Mini Freestanding | MINF.02310011/FM | 23 | 100 | 11 | 13 | 1002 | 1002 | 1002 | 0.023857 | 369 | 0.0087857 | 1149 | 0.027357 | 1.441 | A03 | MINF0.02310011/FM
Freestanding | Mini Freestanding | MINF.02310016/AS | 23 | 100 | 16 | 18 | 1308 | 1308 | 1308 | 0.031143 | 477 | 0.011357 | 1503 | 0.035786 | 1.453 | A03 | MINF0.02310016/AS
Freestanding | Mini Freestanding | MINF.02310016/FM | 23 | 100 | 16 | 18 | 1308 | 1308 | 1308 | 0.031143 | 477 | 0.011357 | 1503 | 0.035786 | 1.453 | A03 | MINF0.02310016/FM
Freestanding | Mini Freestanding | MINF.02310021/AS | 23 | 100 | 21 | 23 | 1701 | 1701 | 1701 | 0.0405 | 617 | 0.01469 | 1956 | 0.046571 | 1.463 | A03 | MINF0.02310021/AS
Freestanding | Mini Freestanding | MINF.02310021/FM | 23 | 100 | 21 | 23 | 1701 | 1701 | 1701 | 0.0405 | 617 | 0.01469 | 1956 | 0.046571 | 1.463 | A03 | MINF0.02310021/FM
Freestanding | Mini Freestanding | MINF.02311006/AS | 23 | 110 | 06 | 8 | 593 | 593 | 593 | 0.014119 | 223 | 0.0053095 | 678 | 0.016143 | 1.411 | A03 | MINF0.02311006/AS
Freestanding | Mini Freestanding | MINF.02311006/FM | 23 | 110 | 06 | 8 | 593 | 593 | 593 | 0.014119 | 223 | 0.0053095 | 678 | 0.016143 | 1.411 | A03 | MINF0.02311006/FM
Freestanding | Mini Freestanding | MINF.02311011/AS | 23 | 110 | 11 | 13 | 1102 | 1102 | 1102 | 0.026238 | 406 | 0.0096667 | 1264 | 0.030095 | 1.441 | A03 | MINF0.02311011/AS
Freestanding | Mini Freestanding | MINF.02311011/FM | 23 | 110 | 11 | 13 | 1102 | 1102 | 1102 | 0.026238 | 406 | 0.0096667 | 1264 | 0.030095 | 1.441 | A03 | MINF0.02311011/FM
Freestanding | Mini Freestanding | MINF.02311016/AS | 23 | 110 | 16 | 18 | 1439 | 1439 | 1439 | 0.034262 | 525 | 0.0125 | 1653 | 0.039357 | 1.453 | A03 | MINF0.02311016/AS
Freestanding | Mini Freestanding | MINF.02311016/FM | 23 | 110 | 16 | 18 | 1439 | 1439 | 1439 | 0.034262 | 525 | 0.0125 | 1653 | 0.039357 | 1.453 | A03 | MINF0.02311016/FM
Freestanding | Mini Freestanding | MINF.02311021/AS | 23 | 110 | 21 | 23 | 1871 | 1871 | 1871 | 0.044548 | 679 | 0.016167 | 2152 | 0.051238 | 1.463 | A03 | MINF0.02311021/AS
Freestanding | Mini Freestanding | MINF.02311021/FM | 23 | 110 | 21 | 23 | 1871 | 1871 | 1871 | 0.044548 | 679 | 0.016167 | 2152 | 0.051238 | 1.463 | A03 | MINF0.02311021/FM
Freestanding | Mini Freestanding | MINF.02312006/AS | 23 | 120 | 06 | 8 | 647 | 647 | 647 | 0.015405 | 243 | 0.0057857 | 740 | 0.017619 | 1.411 | A03 | MINF0.02312006/AS
Freestanding | Mini Freestanding | MINF.02312006/FM | 23 | 120 | 06 | 8 | 647 | 647 | 647 | 0.015405 | 243 | 0.0057857 | 740 | 0.017619 | 1.411 | A03 | MINF0.02312006/FM
Freestanding | Mini Freestanding | MINF.02312011/AS | 23 | 120 | 11 | 13 | 1202 | 1202 | 1202 | 0.028619 | 442 | 0.010524 | 1379 | 0.032833 | 1.441 | A03 | MINF0.02312011/AS
Freestanding | Mini Freestanding | MINF.02312011/FM | 23 | 120 | 11 | 13 | 1202 | 1202 | 1202 | 0.028619 | 442 | 0.010524 | 1379 | 0.032833 | 1.441 | A03 | MINF0.02312011/FM
Freestanding | Mini Freestanding | MINF.02312016/AS | 23 | 120 | 16 | 18 | 1570 | 1570 | 1570 | 0.037381 | 573 | 0.013643 | 1804 | 0.042952 | 1.453 | A03 | MINF0.02312016/AS
Freestanding | Mini Freestanding | MINF.02312016/FM | 23 | 120 | 16 | 18 | 1570 | 1570 | 1570 | 0.037381 | 573 | 0.013643 | 1804 | 0.042952 | 1.453 | A03 | MINF0.02312016/FM
Freestanding | Mini Freestanding | MINF.02312021/AS | 23 | 120 | 21 | 23 | 2041 | 2041 | 2041 | 0.048595 | 741 | 0.017643 | 2347 | 0.055881 | 1.463 | A03 | MINF0.02312021/AS
Freestanding | Mini Freestanding | MINF.02312021/FM | 23 | 120 | 21 | 23 | 2041 | 2041 | 2041 | 0.048595 | 741 | 0.017643 | 2347 | 0.055881 | 1.463 | A03 | MINF0.02312021/FM
Freestanding | Mini Freestanding | MINF.02314006/AS | 23 | 140 | 06 | 8 | 755 | 755 | 755 | 0.017976 | 284 | 0.0067619 | 864 | 0.020571 | 1.411 | A03 | MINF0.02314006/AS
Freestanding | Mini Freestanding | MINF.02314006/FM | 23 | 140 | 06 | 8 | 755 | 755 | 755 | 0.017976 | 284 | 0.0067619 | 864 | 0.020571 | 1.411 | A03 | MINF0.02314006/FM
Freestanding | Mini Freestanding | MINF.02314011/AS | 23 | 140 | 11 | 13 | 1403 | 1403 | 1403 | 0.033405 | 516 | 0.012286 | 1609 | 0.03831 | 1.441 | A03 | MINF0.02314011/AS
Freestanding | Mini Freestanding | MINF.02314011/FM | 23 | 140 | 11 | 13 | 1403 | 1403 | 1403 | 0.033405 | 516 | 0.012286 | 1609 | 0.03831 | 1.441 | A03 | MINF0.02314011/FM
Freestanding | Mini Freestanding | MINF.02314016/AS | 23 | 140 | 16 | 18 | 1831 | 1831 | 1831 | 0.043595 | 668 | 0.015905 | 2104 | 0.050095 | 1.453 | A03 | MINF0.02314016/AS
Freestanding | Mini Freestanding | MINF.02314016/FM | 23 | 140 | 16 | 18 | 1831 | 1831 | 1831 | 0.043595 | 668 | 0.015905 | 2104 | 0.050095 | 1.453 | A03 | MINF0.02314016/FM
Freestanding | Mini Freestanding | MINF.02314021/AS | 23 | 140 | 21 | 23 | 2381 | 2381 | 2381 | 0.05669 | 864 | 0.020571 | 2738 | 0.06519 | 1.463 | A03 | MINF0.02314021/AS
Freestanding | Mini Freestanding | MINF.02314021/FM | 23 | 140 | 21 | 23 | 2381 | 2381 | 2381 | 0.05669 | 864 | 0.020571 | 2738 | 0.06519 | 1.463 | A03 | MINF0.02314021/FM
Freestanding | Mini Freestanding | MINF.02316006/AS | 23 | 160 | 06 | 8 | 862 | 862 | 862 | 0.020524 | 324 | 0.0077143 | 986 | 0.023476 | 1.411 | A03 | MINF0.02316006/AS
Freestanding | Mini Freestanding | MINF.02316006/FM | 23 | 160 | 06 | 8 | 862 | 862 | 862 | 0.020524 | 324 | 0.0077143 | 986 | 0.023476 | 1.411 | A03 | MINF0.02316006/FM
Freestanding | Mini Freestanding | MINF.02316011/AS | 23 | 160 | 11 | 13 | 1603 | 1603 | 1603 | 0.038167 | 590 | 0.014048 | 1839 | 0.043786 | 1.441 | A03 | MINF0.02316011/AS
Freestanding | Mini Freestanding | MINF.02316011/FM | 23 | 160 | 11 | 13 | 1603 | 1603 | 1603 | 0.038167 | 590 | 0.014048 | 1839 | 0.043786 | 1.441 | A03 | MINF0.02316011/FM
Freestanding | Mini Freestanding | MINF.02316016/AS | 23 | 160 | 16 | 18 | 2093 | 2093 | 2093 | 0.049833 | 764 | 0.01819 | 2405 | 0.057262 | 1.453 | A03 | MINF0.02316016/AS
Freestanding | Mini Freestanding | MINF.02316016/FM | 23 | 160 | 16 | 18 | 2093 | 2093 | 2093 | 0.049833 | 764 | 0.01819 | 2405 | 0.057262 | 1.453 | A03 | MINF0.02316016/FM
Freestanding | Mini Freestanding | MINF.02316021/AS | 23 | 160 | 21 | 23 | 2722 | 2722 | 2722 | 0.06481 | 988 | 0.023524 | 3130 | 0.074524 | 1.463 | A03 | MINF0.02316021/AS
Freestanding | Mini Freestanding | MINF.02316021/FM | 23 | 160 | 21 | 23 | 2722 | 2722 | 2722 | 0.06481 | 988 | 0.023524 | 3130 | 0.074524 | 1.463 | A03 | MINF0.02316021/FM
Freestanding | Mini Freestanding | MINF.02318006/AS | 23 | 180 | 06 | 8 | 970 | 970 | 970 | 0.023095 | 365 | 0.0086905 | 1110 | 0.026429 | 1.411 | A03 | MINF0.02318006/AS
Freestanding | Mini Freestanding | MINF.02318006/FM | 23 | 180 | 06 | 8 | 970 | 970 | 970 | 0.023095 | 365 | 0.0086905 | 1110 | 0.026429 | 1.411 | A03 | MINF0.02318006/FM
Freestanding | Mini Freestanding | MINF.02318011/AS | 23 | 180 | 11 | 13 | 1804 | 1804 | 1804 | 0.042952 | 664 | 0.01581 | 2069 | 0.049262 | 1.441 | A03 | MINF0.02318011/AS
Freestanding | Mini Freestanding | MINF.02318011/FM | 23 | 180 | 11 | 13 | 1804 | 1804 | 1804 | 0.042952 | 664 | 0.01581 | 2069 | 0.049262 | 1.441 | A03 | MINF0.02318011/FM
Freestanding | Mini Freestanding | MINF.02318016/AS | 23 | 180 | 16 | 18 | 2354 | 2354 | 2354 | 0.056048 | 859 | 0.020452 | 2705 | 0.064405 | 1.453 | A03 | MINF0.02318016/AS
Freestanding | Mini Freestanding | MINF.02318016/FM | 23 | 180 | 16 | 18 | 2354 | 2354 | 2354 | 0.056048 | 859 | 0.020452 | 2705 | 0.064405 | 1.453 | A03 | MINF0.02318016/FM
Freestanding | Mini Freestanding | MINF.02318021/AS | 23 | 180 | 21 | 23 | 3062 | 3062 | 3062 | 0.072905 | 1112 | 0.026476 | 3521 | 0.083833 | 1.463 | A03 | MINF0.02318021/AS
Freestanding | Mini Freestanding | MINF.02318021/FM | 23 | 180 | 21 | 23 | 3062 | 3062 | 3062 | 0.072905 | 1112 | 0.026476 | 3521 | 0.083833 | 1.463 | A03 | MINF0.02318021/FM
Freestanding | Mini Freestanding | MINF.02320006/AS | 23 | 200 | 06 | 8 | 1078 | 1078 | 1078 | 0.025667 | 405 | 0.0096429 | 1233 | 0.029357 | 1.411 | A03 | MINF0.02320006/AS
Freestanding | Mini Freestanding | MINF.02320006/FM | 23 | 200 | 06 | 8 | 1078 | 1078 | 1078 | 0.025667 | 405 | 0.0096429 | 1233 | 0.029357 | 1.411 | A03 | MINF0.02320006/FM
Freestanding | Mini Freestanding | MINF.02320011/AS | 23 | 200 | 11 | 13 | 2004 | 2004 | 2004 | 0.047714 | 737 | 0.017548 | 2299 | 0.054738 | 1.441 | A03 | MINF0.02320011/AS
Freestanding | Mini Freestanding | MINF.02320011/FM | 23 | 200 | 11 | 13 | 2004 | 2004 | 2004 | 0.047714 | 737 | 0.017548 | 2299 | 0.054738 | 1.441 | A03 | MINF0.02320011/FM
Freestanding | Mini Freestanding | MINF.02320016/AS | 23 | 200 | 16 | 18 | 2616 | 2616 | 2616 | 0.062286 | 955 | 0.022738 | 3006 | 0.071571 | 1.453 | A03 | MINF0.02320016/AS
Freestanding | Mini Freestanding | MINF.02320016/FM | 23 | 200 | 16 | 18 | 2616 | 2616 | 2616 | 0.062286 | 955 | 0.022738 | 3006 | 0.071571 | 1.453 | A03 | MINF0.02320016/FM
Freestanding | Mini Freestanding | MINF.02320021/AS | 23 | 200 | 21 | 23 | 3402 | 3402 | 3402 | 0.081 | 1235 | 0.029405 | 3912 | 0.093143 | 1.463 | A03 | MINF0.02320021/AS
Freestanding | Mini Freestanding | MINF.02320021/FM | 23 | 200 | 21 | 23 | 3402 | 3402 | 3402 | 0.081 | 1235 | 0.029405 | 3912 | 0.093143 | 1.463 | A03 | MINF0.02320021/FM
Freestanding | Mini Freestanding | MINF.02322006/AS | 23 | 220 | 06 | 8 | 1186 | 1186 | 1186 | 0.028238 | 446 | 0.010619 | 1357 | 0.03231 | 1.411 | A03 | MINF0.02322006/AS
Freestanding | Mini Freestanding | MINF.02322006/FM | 23 | 220 | 06 | 8 | 1186 | 1186 | 1186 | 0.028238 | 446 | 0.010619 | 1357 | 0.03231 | 1.411 | A03 | MINF0.02322006/FM
Freestanding | Mini Freestanding | MINF.02322011/AS | 23 | 220 | 11 | 13 | 2204 | 2204 | 2204 | 0.052476 | 811 | 0.01931 | 2528 | 0.06019 | 1.441 | A03 | MINF0.02322011/AS
Freestanding | Mini Freestanding | MINF.02322011/FM | 23 | 220 | 11 | 13 | 2204 | 2204 | 2204 | 0.052476 | 811 | 0.01931 | 2528 | 0.06019 | 1.441 | A03 | MINF0.02322011/FM
Freestanding | Mini Freestanding | MINF.02322016/AS | 23 | 220 | 16 | 18 | 2878 | 2878 | 2878 | 0.068524 | 1050 | 0.025 | 3307 | 0.078738 | 1.453 | A03 | MINF0.02322016/AS
Freestanding | Mini Freestanding | MINF.02322016/FM | 23 | 220 | 16 | 18 | 2878 | 2878 | 2878 | 0.068524 | 1050 | 0.025 | 3307 | 0.078738 | 1.453 | A03 | MINF0.02322016/FM
Freestanding | Mini Freestanding | MINF.02322021/AS | 23 | 220 | 21 | 23 | 3742 | 3742 | 3742 | 0.089095 | 1358 | 0.032333 | 4303 | 0.10245 | 1.463 | A03 | MINF0.02322021/AS
Freestanding | Mini Freestanding | MINF.02322021/FM | 23 | 220 | 21 | 23 | 3742 | 3742 | 3742 | 0.089095 | 1358 | 0.032333 | 4303 | 0.10245 | 1.463 | A03 | MINF0.02322021/FM
Freestanding | Mini Freestanding | MINF.02324006/AS | 23 | 240 | 06 | 8 | 1294 | 1294 | 1294 | 0.03081 | 487 | 0.011595 | 1480 | 0.035238 | 1.411 | A03 | MINF0.02324006/AS
Freestanding | Mini Freestanding | MINF.02324006/FM | 23 | 240 | 06 | 8 | 1294 | 1294 | 1294 | 0.03081 | 487 | 0.011595 | 1480 | 0.035238 | 1.411 | A03 | MINF0.02324006/FM
Freestanding | Mini Freestanding | MINF.02324011/AS | 23 | 240 | 11 | 13 | 2405 | 2405 | 2405 | 0.057262 | 885 | 0.021071 | 2759 | 0.06569 | 1.441 | A03 | MINF0.02324011/AS
Freestanding | Mini Freestanding | MINF.02324011/FM | 23 | 240 | 11 | 13 | 2405 | 2405 | 2405 | 0.057262 | 885 | 0.021071 | 2759 | 0.06569 | 1.441 | A03 | MINF0.02324011/FM
Freestanding | Mini Freestanding | MINF.02324016/AS | 23 | 240 | 16 | 18 | 3139 | 3139 | 3139 | 0.074738 | 1146 | 0.027286 | 3607 | 0.085881 | 1.453 | A03 | MINF0.02324016/AS
Freestanding | Mini Freestanding | MINF.02324016/FM | 23 | 240 | 16 | 18 | 3139 | 3139 | 3139 | 0.074738 | 1146 | 0.027286 | 3607 | 0.085881 | 1.453 | A03 | MINF0.02324016/FM
Freestanding | Mini Freestanding | MINF.02324021/AS | 23 | 240 | 21 | 23 | 4082 | 4082 | 4082 | 0.09719 | 1482 | 0.035286 | 4694 | 0.11176 | 1.463 | A03 | MINF0.02324021/AS
Freestanding | Mini Freestanding | MINF.02324021/FM | 23 | 240 | 21 | 23 | 4082 | 4082 | 4082 | 0.09719 | 1482 | 0.035286 | 4694 | 0.11176 | 1.463 | A03 | MINF0.02324021/FM
Freestanding | Mini Freestanding | MINF.02326006/AS | 23 | 260 | 06 | 8 | 1401 | 1401 | 1401 | 0.033357 | 527 | 0.012548 | 1603 | 0.038167 | 1.411 | A03 | MINF0.02326006/AS
Freestanding | Mini Freestanding | MINF.02326006/FM | 23 | 260 | 06 | 8 | 1401 | 1401 | 1401 | 0.033357 | 527 | 0.012548 | 1603 | 0.038167 | 1.411 | A03 | MINF0.02326006/FM
Freestanding | Mini Freestanding | MINF.02326011/AS | 23 | 260 | 11 | 13 | 2605 | 2605 | 2605 | 0.062024 | 959 | 0.022833 | 2988 | 0.071143 | 1.441 | A03 | MINF0.02326011/AS
Freestanding | Mini Freestanding | MINF.02326011/FM | 23 | 260 | 11 | 13 | 2605 | 2605 | 2605 | 0.062024 | 959 | 0.022833 | 2988 | 0.071143 | 1.441 | A03 | MINF0.02326011/FM
Freestanding | Mini Freestanding | MINF.02326016/AS | 23 | 260 | 16 | 18 | 3401 | 3401 | 3401 | 0.080976 | 1241 | 0.029548 | 3908 | 0.093048 | 1.453 | A03 | MINF0.02326016/AS
Freestanding | Mini Freestanding | MINF.02326016/FM | 23 | 260 | 16 | 18 | 3401 | 3401 | 3401 | 0.080976 | 1241 | 0.029548 | 3908 | 0.093048 | 1.453 | A03 | MINF0.02326016/FM
Freestanding | Mini Freestanding | MINF.02326021/AS | 23 | 260 | 21 | 23 | 4423 | 4423 | 4423 | 0.10531 | 1606 | 0.038238 | 5086 | 0.1211 | 1.463 | A03 | MINF0.02326021/AS
Freestanding | Mini Freestanding | MINF.02326021/FM | 23 | 260 | 21 | 23 | 4423 | 4423 | 4423 | 0.10531 | 1606 | 0.038238 | 5086 | 0.1211 | 1.463 | A03 | MINF0.02326021/FM
Freestanding | Mini Freestanding | MINF.02328006/AS | 23 | 280 | 06 | 8 | 1509 | 1509 | 1509 | 0.035929 | 567 | 0.0135 | 1726 | 0.041095 | 1.411 | A03 | MINF0.02328006/AS
Freestanding | Mini Freestanding | MINF.02328006/FM | 23 | 280 | 06 | 8 | 1509 | 1509 | 1509 | 0.035929 | 567 | 0.0135 | 1726 | 0.041095 | 1.411 | A03 | MINF0.02328006/FM
Freestanding | Mini Freestanding | MINF.02328011/AS | 23 | 280 | 11 | 13 | 2806 | 2806 | 2806 | 0.06681 | 1033 | 0.024595 | 3218 | 0.076619 | 1.441 | A03 | MINF0.02328011/AS
Freestanding | Mini Freestanding | MINF.02328011/FM | 23 | 280 | 11 | 13 | 2806 | 2806 | 2806 | 0.06681 | 1033 | 0.024595 | 3218 | 0.076619 | 1.441 | A03 | MINF0.02328011/FM
Freestanding | Mini Freestanding | MINF.02328016/AS | 23 | 280 | 16 | 18 | 3662 | 3662 | 3662 | 0.08719 | 1337 | 0.031833 | 4208 | 0.10019 | 1.453 | A03 | MINF0.02328016/AS
Freestanding | Mini Freestanding | MINF.02328016/FM | 23 | 280 | 16 | 18 | 3662 | 3662 | 3662 | 0.08719 | 1337 | 0.031833 | 4208 | 0.10019 | 1.453 | A03 | MINF0.02328016/FM
Freestanding | Mini Freestanding | MINF.02328021/AS | 23 | 280 | 21 | 23 | 4763 | 4763 | 4763 | 0.1134 | 1729 | 0.041167 | 5477 | 0.1304 | 1.463 | A03 | MINF0.02328021/AS
Freestanding | Mini Freestanding | MINF.02328021/FM | 23 | 280 | 21 | 23 | 4763 | 4763 | 4763 | 0.1134 | 1729 | 0.041167 | 5477 | 0.1304 | 1.463 | A03 | MINF0.02328021/FM
Freestanding | Mini Freestanding | MINF.02330006/AS | 23 | 300 | 06 | 8 | 1617 | 1617 | 1617 | 0.0385 | 608 | 0.014476 | 1850 | 0.044048 | 1.411 | A03 | MINF0.02330006/AS
Freestanding | Mini Freestanding | MINF.02330006/FM | 23 | 300 | 06 | 8 | 1617 | 1617 | 1617 | 0.0385 | 608 | 0.014476 | 1850 | 0.044048 | 1.411 | A03 | MINF0.02330006/FM
Freestanding | Mini Freestanding | MINF.02330011/AS | 23 | 300 | 11 | 13 | 3006 | 3006 | 3006 | 0.071571 | 1106 | 0.026333 | 3448 | 0.082095 | 1.441 | A03 | MINF0.02330011/AS
Freestanding | Mini Freestanding | MINF.02330011/FM | 23 | 300 | 11 | 13 | 3006 | 3006 | 3006 | 0.071571 | 1106 | 0.026333 | 3448 | 0.082095 | 1.441 | A03 | MINF0.02330011/FM
Freestanding | Mini Freestanding | MINF.02330016/AS | 23 | 300 | 16 | 18 | 3924 | 3924 | 3924 | 0.093429 | 1432 | 0.034095 | 4509 | 0.10736 | 1.453 | A03 | MINF0.02330016/AS
Freestanding | Mini Freestanding | MINF.02330016/FM | 23 | 300 | 16 | 18 | 3924 | 3924 | 3924 | 0.093429 | 1432 | 0.034095 | 4509 | 0.10736 | 1.453 | A03 | MINF0.02330016/FM
Freestanding | Mini Freestanding | MINF.02330021/AS | 23 | 300 | 21 | 23 | 5103 | 5103 | 5103 | 0.1215 | 1852 | 0.044095 | 5868 | 0.13971 | 1.463 | A03 | MINF0.02330021/AS
Freestanding | Mini Freestanding | MINF.02330021/FM | 23 | 300 | 21 | 23 | 5103 | 5103 | 5103 | 0.1215 | 1852 | 0.044095 | 5868 | 0.13971 | 1.463 | A03 | MINF0.02330021/FM
Freestanding | Mini Freestanding | MINF.02806006/AS | 28 | 60 | 06 | 8 | 342 | 342 | 342 | 0.0081429 | 129 | 0.0030714 | 391 | 0.0093095 | 1.403 | A03 | MINF0.02806006/AS
Freestanding | Mini Freestanding | MINF.02806006/FM | 28 | 60 | 06 | 8 | 342 | 342 | 342 | 0.0081429 | 129 | 0.0030714 | 391 | 0.0093095 | 1.403 | A03 | MINF0.02806006/FM
Freestanding | Mini Freestanding | MINF.02806011/AS | 28 | 60 | 11 | 13 | 653 | 653 | 653 | 0.015548 | 240 | 0.0057143 | 749 | 0.017833 | 1.441 | A03 | MINF0.02806011/AS
Freestanding | Mini Freestanding | MINF.02806011/FM | 28 | 60 | 11 | 13 | 653 | 653 | 653 | 0.015548 | 240 | 0.0057143 | 749 | 0.017833 | 1.441 | A03 | MINF0.02806011/FM
Freestanding | Mini Freestanding | MINF.02806016/AS | 28 | 60 | 16 | 18 | 860 | 860 | 860 | 0.020476 | 314 | 0.0074762 | 988 | 0.023524 | 1.455 | A03 | MINF0.02806016/AS
Freestanding | Mini Freestanding | MINF.02806016/FM | 28 | 60 | 16 | 18 | 860 | 860 | 860 | 0.020476 | 314 | 0.0074762 | 988 | 0.023524 | 1.455 | A03 | MINF0.02806016/FM
Freestanding | Mini Freestanding | MINF.02806021/AS | 28 | 60 | 21 | 23 | 1127 | 1127 | 1127 | 0.026833 | 408 | 0.0097143 | 1296 | 0.030857 | 1.467 | A03 | MINF0.02806021/AS
Freestanding | Mini Freestanding | MINF.02806021/FM | 28 | 60 | 21 | 23 | 1127 | 1127 | 1127 | 0.026833 | 408 | 0.0097143 | 1296 | 0.030857 | 1.467 | A03 | MINF0.02806021/FM
Freestanding | Mini Freestanding | MINF.02807006/AS | 28 | 70 | 06 | 8 | 399 | 399 | 399 | 0.0095 | 151 | 0.0035952 | 456 | 0.010857 | 1.403 | A03 | MINF0.02807006/AS
Freestanding | Mini Freestanding | MINF.02807006/FM | 28 | 70 | 06 | 8 | 399 | 399 | 399 | 0.0095 | 151 | 0.0035952 | 456 | 0.010857 | 1.403 | A03 | MINF0.02807006/FM
Freestanding | Mini Freestanding | MINF.02807011/AS | 28 | 70 | 11 | 13 | 762 | 762 | 762 | 0.018143 | 280 | 0.0066667 | 874 | 0.02081 | 1.441 | A03 | MINF0.02807011/AS
Freestanding | Mini Freestanding | MINF.02807011/FM | 28 | 70 | 11 | 13 | 762 | 762 | 762 | 0.018143 | 280 | 0.0066667 | 874 | 0.02081 | 1.441 | A03 | MINF0.02807011/FM
Freestanding | Mini Freestanding | MINF.02807016/AS | 28 | 70 | 16 | 18 | 1003 | 1003 | 1003 | 0.023881 | 366 | 0.0087143 | 1152 | 0.027429 | 1.455 | A03 | MINF0.02807016/AS
Freestanding | Mini Freestanding | MINF.02807016/FM | 28 | 70 | 16 | 18 | 1003 | 1003 | 1003 | 0.023881 | 366 | 0.0087143 | 1152 | 0.027429 | 1.455 | A03 | MINF0.02807016/FM
Freestanding | Mini Freestanding | MINF.02807021/AS | 28 | 70 | 21 | 23 | 1315 | 1315 | 1315 | 0.03131 | 476 | 0.011333 | 1512 | 0.036 | 1.467 | A03 | MINF0.02807021/AS
Freestanding | Mini Freestanding | MINF.02807021/FM | 28 | 70 | 21 | 23 | 1315 | 1315 | 1315 | 0.03131 | 476 | 0.011333 | 1512 | 0.036 | 1.467 | A03 | MINF0.02807021/FM
Freestanding | Mini Freestanding | MINF.02808006/AS | 28 | 80 | 06 | 8 | 456 | 456 | 456 | 0.010857 | 172 | 0.0040952 | 521 | 0.012405 | 1.403 | A03 | MINF0.02808006/AS
Freestanding | Mini Freestanding | MINF.02808006/FM | 28 | 80 | 06 | 8 | 456 | 456 | 456 | 0.010857 | 172 | 0.0040952 | 521 | 0.012405 | 1.403 | A03 | MINF0.02808006/FM
Freestanding | Mini Freestanding | MINF.02808011/AS | 28 | 80 | 11 | 13 | 871 | 871 | 871 | 0.020738 | 321 | 0.0076429 | 999 | 0.023786 | 1.441 | A03 | MINF0.02808011/AS
Freestanding | Mini Freestanding | MINF.02808011/FM | 28 | 80 | 11 | 13 | 871 | 871 | 871 | 0.020738 | 321 | 0.0076429 | 999 | 0.023786 | 1.441 | A03 | MINF0.02808011/FM
Freestanding | Mini Freestanding | MINF.02808016/AS | 28 | 80 | 16 | 18 | 1146 | 1146 | 1146 | 0.027286 | 418 | 0.0099524 | 1317 | 0.031357 | 1.455 | A03 | MINF0.02808016/AS
Freestanding | Mini Freestanding | MINF.02808016/FM | 28 | 80 | 16 | 18 | 1146 | 1146 | 1146 | 0.027286 | 418 | 0.0099524 | 1317 | 0.031357 | 1.455 | A03 | MINF0.02808016/FM
Freestanding | Mini Freestanding | MINF.02808021/AS | 28 | 80 | 21 | 23 | 1503 | 1503 | 1503 | 0.035786 | 544 | 0.012952 | 1728 | 0.041143 | 1.467 | A03 | MINF0.02808021/AS
Freestanding | Mini Freestanding | MINF.02808021/FM | 28 | 80 | 21 | 23 | 1503 | 1503 | 1503 | 0.035786 | 544 | 0.012952 | 1728 | 0.041143 | 1.467 | A03 | MINF0.02808021/FM
Freestanding | Mini Freestanding | MINF.02808111/DS/DBE | 28 | 81 | 11 | 13 | 1171 | 1171 | 1171 | 0.027881 | 586 | 0.013952 | 1288 | 0.030667 | 1 | A03 | MINF0.02808111/DS/DBE
Freestanding | Mini Freestanding | MINF.02808116/DS/DBE | 28 | 81 | 16 | 18 | 1626 | 1626 | 1626 | 0.038714 | 813 | 0.019357 | 1789 | 0.042595 | 1 | A03 | MINF0.02808116/DS/DBE
Freestanding | Mini Freestanding | MINF.02809006/AS | 28 | 90 | 06 | 8 | 513 | 513 | 513 | 0.012214 | 194 | 0.004619 | 586 | 0.013952 | 1.403 | A03 | MINF0.02809006/AS
Freestanding | Mini Freestanding | MINF.02809006/FM | 28 | 90 | 06 | 8 | 513 | 513 | 513 | 0.012214 | 194 | 0.004619 | 586 | 0.013952 | 1.403 | A03 | MINF0.02809006/FM
Freestanding | Mini Freestanding | MINF.02809011/AS | 28 | 90 | 11 | 13 | 980 | 980 | 980 | 0.023333 | 361 | 0.0085952 | 1124 | 0.026762 | 1.441 | A03 | MINF0.02809011/AS
Freestanding | Mini Freestanding | MINF.02809011/FM | 28 | 90 | 11 | 13 | 980 | 980 | 980 | 0.023333 | 361 | 0.0085952 | 1124 | 0.026762 | 1.441 | A03 | MINF0.02809011/FM
Freestanding | Mini Freestanding | MINF.02809016/AS | 28 | 90 | 16 | 18 | 1290 | 1290 | 1290 | 0.030714 | 471 | 0.011214 | 1482 | 0.035286 | 1.455 | A03 | MINF0.02809016/AS
Freestanding | Mini Freestanding | MINF.02809016/FM | 28 | 90 | 16 | 18 | 1290 | 1290 | 1290 | 0.030714 | 471 | 0.011214 | 1482 | 0.035286 | 1.455 | A03 | MINF0.02809016/FM
Freestanding | Mini Freestanding | MINF.02809021/AS | 28 | 90 | 21 | 23 | 1691 | 1691 | 1691 | 0.040262 | 612 | 0.014571 | 1945 | 0.04631 | 1.467 | A03 | MINF0.02809021/AS
Freestanding | Mini Freestanding | MINF.02809021/FM | 28 | 90 | 21 | 23 | 1691 | 1691 | 1691 | 0.040262 | 612 | 0.014571 | 1945 | 0.04631 | 1.467 | A03 | MINF0.02809021/FM
Freestanding | Mini Freestanding | MINF.02810006/AS | 28 | 100 | 06 | 8 | 570 | 570 | 570 | 0.013571 | 215 | 0.005119 | 652 | 0.015524 | 1.403 | A03 | MINF0.02810006/AS
Freestanding | Mini Freestanding | MINF.02810006/FM | 28 | 100 | 06 | 8 | 570 | 570 | 570 | 0.013571 | 215 | 0.005119 | 652 | 0.015524 | 1.403 | A03 | MINF0.02810006/FM
Freestanding | Mini Freestanding | MINF.02810011/AS | 28 | 100 | 11 | 13 | 1089 | 1089 | 1089 | 0.025929 | 401 | 0.0095476 | 1249 | 0.029738 | 1.441 | A03 | MINF0.02810011/AS
Freestanding | Mini Freestanding | MINF.02810011/FM | 28 | 100 | 11 | 13 | 1089 | 1089 | 1089 | 0.025929 | 401 | 0.0095476 | 1249 | 0.029738 | 1.441 | A03 | MINF0.02810011/FM
Freestanding | Mini Freestanding | MINF.02810016/AS | 28 | 100 | 16 | 18 | 1433 | 1433 | 1433 | 0.034119 | 523 | 0.012452 | 1647 | 0.039214 | 1.455 | A03 | MINF0.02810016/AS
Freestanding | Mini Freestanding | MINF.02810016/FM | 28 | 100 | 16 | 18 | 1433 | 1433 | 1433 | 0.034119 | 523 | 0.012452 | 1647 | 0.039214 | 1.455 | A03 | MINF0.02810016/FM
Freestanding | Mini Freestanding | MINF.02810021/AS | 28 | 100 | 21 | 23 | 1879 | 1879 | 1879 | 0.044738 | 680 | 0.01619 | 2161 | 0.051452 | 1.467 | A03 | MINF0.02810021/AS
Freestanding | Mini Freestanding | MINF.02810021/FM | 28 | 100 | 21 | 23 | 1879 | 1879 | 1879 | 0.044738 | 680 | 0.01619 | 2161 | 0.051452 | 1.467 | A03 | MINF0.02810021/FM
Freestanding | Mini Freestanding | MINF.02810111/DS/DBE | 28 | 101 | 11 | 13 | 1689 | 1689 | 1689 | 0.040214 | 845 | 0.020119 | 1858 | 0.044238 | 1 | A03 | MINF0.02810111/DS/DBE
Freestanding | Mini Freestanding | MINF.02810116/DS/DBE | 28 | 101 | 16 | 18 | 2393 | 2393 | 2393 | 0.056976 | 1197 | 0.0285 | 2632 | 0.062667 | 1 | A03 | MINF0.02810116/DS/DBE
Freestanding | Mini Freestanding | MINF.02811006/AS | 28 | 110 | 06 | 8 | 627 | 627 | 627 | 0.014929 | 237 | 0.0056429 | 717 | 0.017071 | 1.403 | A03 | MINF0.02811006/AS
Freestanding | Mini Freestanding | MINF.02811006/FM | 28 | 110 | 06 | 8 | 627 | 627 | 627 | 0.014929 | 237 | 0.0056429 | 717 | 0.017071 | 1.403 | A03 | MINF0.02811006/FM
Freestanding | Mini Freestanding | MINF.02811011/AS | 28 | 110 | 11 | 13 | 1198 | 1198 | 1198 | 0.028524 | 441 | 0.0105 | 1374 | 0.032714 | 1.441 | A03 | MINF0.02811011/AS
Freestanding | Mini Freestanding | MINF.02811011/FM | 28 | 110 | 11 | 13 | 1198 | 1198 | 1198 | 0.028524 | 441 | 0.0105 | 1374 | 0.032714 | 1.441 | A03 | MINF0.02811011/FM
Freestanding | Mini Freestanding | MINF.02811016/AS | 28 | 110 | 16 | 18 | 1576 | 1576 | 1576 | 0.037524 | 575 | 0.01369 | 1811 | 0.043119 | 1.455 | A03 | MINF0.02811016/AS
Freestanding | Mini Freestanding | MINF.02811016/FM | 28 | 110 | 16 | 18 | 1576 | 1576 | 1576 | 0.037524 | 575 | 0.01369 | 1811 | 0.043119 | 1.455 | A03 | MINF0.02811016/FM
Freestanding | Mini Freestanding | MINF.02811021/AS | 28 | 110 | 21 | 23 | 2067 | 2067 | 2067 | 0.049214 | 748 | 0.01781 | 2377 | 0.056595 | 1.467 | A03 | MINF0.02811021/AS
Freestanding | Mini Freestanding | MINF.02811021/FM | 28 | 110 | 21 | 23 | 2067 | 2067 | 2067 | 0.049214 | 748 | 0.01781 | 2377 | 0.056595 | 1.467 | A03 | MINF0.02811021/FM
Freestanding | Mini Freestanding | MINF.02812006/AS | 28 | 120 | 06 | 8 | 684 | 684 | 684 | 0.016286 | 259 | 0.0061667 | 782 | 0.018619 | 1.403 | A03 | MINF0.02812006/AS
Freestanding | Mini Freestanding | MINF.02812006/FM | 28 | 120 | 06 | 8 | 684 | 684 | 684 | 0.016286 | 259 | 0.0061667 | 782 | 0.018619 | 1.403 | A03 | MINF0.02812006/FM
Freestanding | Mini Freestanding | MINF.02812011/AS | 28 | 120 | 11 | 13 | 1307 | 1307 | 1307 | 0.031119 | 481 | 0.011452 | 1499 | 0.03569 | 1.441 | A03 | MINF0.02812011/AS
Freestanding | Mini Freestanding | MINF.02812011/FM | 28 | 120 | 11 | 13 | 1307 | 1307 | 1307 | 0.031119 | 481 | 0.011452 | 1499 | 0.03569 | 1.441 | A03 | MINF0.02812011/FM
Freestanding | Mini Freestanding | MINF.02812016/AS | 28 | 120 | 16 | 18 | 1720 | 1720 | 1720 | 0.040952 | 628 | 0.014952 | 1976 | 0.047048 | 1.455 | A03 | MINF0.02812016/AS
Freestanding | Mini Freestanding | MINF.02812016/FM | 28 | 120 | 16 | 18 | 1720 | 1720 | 1720 | 0.040952 | 628 | 0.014952 | 1976 | 0.047048 | 1.455 | A03 | MINF0.02812016/FM
Freestanding | Mini Freestanding | MINF.02812021/AS | 28 | 120 | 21 | 23 | 2255 | 2255 | 2255 | 0.05369 | 816 | 0.019429 | 2593 | 0.061738 | 1.467 | A03 | MINF0.02812021/AS
Freestanding | Mini Freestanding | MINF.02812021/FM | 28 | 120 | 21 | 23 | 2255 | 2255 | 2255 | 0.05369 | 816 | 0.019429 | 2593 | 0.061738 | 1.467 | A03 | MINF0.02812021/FM
Freestanding | Mini Freestanding | MINF.02812111/DS/DBE | 28 | 121 | 11 | 13 | 1907 | 1907 | 1907 | 0.045405 | 954 | 0.022714 | 2098 | 0.049952 | 1 | A03 | MINF0.02812111/DS/DBE
Freestanding | Mini Freestanding | MINF.02812116/DS/DBE | 28 | 121 | 16 | 18 | 2680 | 2680 | 2680 | 0.06381 | 1340 | 0.031905 | 2948 | 0.07019 | 1 | A03 | MINF0.02812116/DS/DBE
Freestanding | Mini Freestanding | MINF.02814006/AS | 28 | 140 | 06 | 8 | 798 | 798 | 798 | 0.019 | 302 | 0.0071905 | 912 | 0.021714 | 1.403 | A03 | MINF0.02814006/AS
Freestanding | Mini Freestanding | MINF.02814006/FM | 28 | 140 | 06 | 8 | 798 | 798 | 798 | 0.019 | 302 | 0.0071905 | 912 | 0.021714 | 1.403 | A03 | MINF0.02814006/FM
Freestanding | Mini Freestanding | MINF.02814011/AS | 28 | 140 | 11 | 13 | 1525 | 1525 | 1525 | 0.03631 | 561 | 0.013357 | 1749 | 0.041643 | 1.441 | A03 | MINF0.02814011/AS
Freestanding | Mini Freestanding | MINF.02814011/FM | 28 | 140 | 11 | 13 | 1525 | 1525 | 1525 | 0.03631 | 561 | 0.013357 | 1749 | 0.041643 | 1.441 | A03 | MINF0.02814011/FM
Freestanding | Mini Freestanding | MINF.02814016/AS | 28 | 140 | 16 | 18 | 2006 | 2006 | 2006 | 0.047762 | 732 | 0.017429 | 2305 | 0.054881 | 1.455 | A03 | MINF0.02814016/AS
Freestanding | Mini Freestanding | MINF.02814016/FM | 28 | 140 | 16 | 18 | 2006 | 2006 | 2006 | 0.047762 | 732 | 0.017429 | 2305 | 0.054881 | 1.455 | A03 | MINF0.02814016/FM
Freestanding | Mini Freestanding | MINF.02814021/AS | 28 | 140 | 21 | 23 | 2631 | 2631 | 2631 | 0.062643 | 952 | 0.022667 | 3026 | 0.072048 | 1.467 | A03 | MINF0.02814021/AS
Freestanding | Mini Freestanding | MINF.02814021/FM | 28 | 140 | 21 | 23 | 2631 | 2631 | 2631 | 0.062643 | 952 | 0.022667 | 3026 | 0.072048 | 1.467 | A03 | MINF0.02814021/FM
Freestanding | Mini Freestanding | MINF.02814111/DS/DBE | 28 | 141 | 11 | 13 | 2425 | 2425 | 2425 | 0.057738 | 1213 | 0.028881 | 2668 | 0.063524 | 1 | A03 | MINF0.02814111/DS/DBE
Freestanding | Mini Freestanding | MINF.02814116/DS/DBE | 28 | 141 | 16 | 18 | 3446 | 3446 | 3446 | 0.082048 | 1723 | 0.041024 | 3791 | 0.090262 | 1 | A03 | MINF0.02814116/DS/DBE
Freestanding | Mini Freestanding | MINF.02816006/AS | 28 | 160 | 06 | 8 | 912 | 912 | 912 | 0.021714 | 345 | 0.0082143 | 1042 | 0.02481 | 1.403 | A03 | MINF0.02816006/AS
Freestanding | Mini Freestanding | MINF.02816006/FM | 28 | 160 | 06 | 8 | 912 | 912 | 912 | 0.021714 | 345 | 0.0082143 | 1042 | 0.02481 | 1.403 | A03 | MINF0.02816006/FM
Freestanding | Mini Freestanding | MINF.02816011/AS | 28 | 160 | 11 | 13 | 1742 | 1742 | 1742 | 0.041476 | 641 | 0.015262 | 1998 | 0.047571 | 1.441 | A03 | MINF0.02816011/AS
Freestanding | Mini Freestanding | MINF.02816011/FM | 28 | 160 | 11 | 13 | 1742 | 1742 | 1742 | 0.041476 | 641 | 0.015262 | 1998 | 0.047571 | 1.441 | A03 | MINF0.02816011/FM
Freestanding | Mini Freestanding | MINF.02816016/AS | 28 | 160 | 16 | 18 | 2293 | 2293 | 2293 | 0.054595 | 837 | 0.019929 | 2635 | 0.062738 | 1.455 | A03 | MINF0.02816016/AS
Freestanding | Mini Freestanding | MINF.02816016/FM | 28 | 160 | 16 | 18 | 2293 | 2293 | 2293 | 0.054595 | 837 | 0.019929 | 2635 | 0.062738 | 1.455 | A03 | MINF0.02816016/FM
Freestanding | Mini Freestanding | MINF.02816021/AS | 28 | 160 | 21 | 23 | 3006 | 3006 | 3006 | 0.071571 | 1088 | 0.025905 | 3457 | 0.08231 | 1.467 | A03 | MINF0.02816021/AS
Freestanding | Mini Freestanding | MINF.02816021/FM | 28 | 160 | 21 | 23 | 3006 | 3006 | 3006 | 0.071571 | 1088 | 0.025905 | 3457 | 0.08231 | 1.467 | A03 | MINF0.02816021/FM
Freestanding | Mini Freestanding | MINF.02818006/AS | 28 | 180 | 06 | 8 | 1026 | 1026 | 1026 | 0.024429 | 388 | 0.0092381 | 1173 | 0.027929 | 1.403 | A03 | MINF0.02818006/AS
Freestanding | Mini Freestanding | MINF.02818006/FM | 28 | 180 | 06 | 8 | 1026 | 1026 | 1026 | 0.024429 | 388 | 0.0092381 | 1173 | 0.027929 | 1.403 | A03 | MINF0.02818006/FM
Freestanding | Mini Freestanding | MINF.02818011/AS | 28 | 180 | 11 | 13 | 1960 | 1960 | 1960 | 0.046667 | 721 | 0.017167 | 2248 | 0.053524 | 1.441 | A03 | MINF0.02818011/AS
Freestanding | Mini Freestanding | MINF.02818011/FM | 28 | 180 | 11 | 13 | 1960 | 1960 | 1960 | 0.046667 | 721 | 0.017167 | 2248 | 0.053524 | 1.441 | A03 | MINF0.02818011/FM
Freestanding | Mini Freestanding | MINF.02818016/AS | 28 | 180 | 16 | 18 | 2579 | 2579 | 2579 | 0.061405 | 941 | 0.022405 | 2963 | 0.070548 | 1.455 | A03 | MINF0.02818016/AS
Freestanding | Mini Freestanding | MINF.02818016/FM | 28 | 180 | 16 | 18 | 2579 | 2579 | 2579 | 0.061405 | 941 | 0.022405 | 2963 | 0.070548 | 1.455 | A03 | MINF0.02818016/FM
Freestanding | Mini Freestanding | MINF.02818021/AS | 28 | 180 | 21 | 23 | 3382 | 3382 | 3382 | 0.080524 | 1224 | 0.029143 | 3889 | 0.092595 | 1.467 | A03 | MINF0.02818021/AS
Freestanding | Mini Freestanding | MINF.02818021/FM | 28 | 180 | 21 | 23 | 3382 | 3382 | 3382 | 0.080524 | 1224 | 0.029143 | 3889 | 0.092595 | 1.467 | A03 | MINF0.02818021/FM
Freestanding | Mini Freestanding | MINF.02818111/DS/DBE | 28 | 181 | 11 | 13 | 3160 | 3160 | 3160 | 0.075238 | 1580 | 0.037619 | 3476 | 0.082762 | 1 | A03 | MINF0.02818111/DS/DBE
Freestanding | Mini Freestanding | MINF.02818116/DS/DBE | 28 | 181 | 16 | 18 | 4499 | 4499 | 4499 | 0.10712 | 2250 | 0.053571 | 4949 | 0.11783 | 1 | A03 | MINF0.02818116/DS/DBE
Freestanding | Mini Freestanding | MINF.02820006/AS | 28 | 200 | 06 | 8 | 1140 | 1140 | 1140 | 0.027143 | 431 | 0.010262 | 1303 | 0.031024 | 1.403 | A03 | MINF0.02820006/AS
Freestanding | Mini Freestanding | MINF.02820006/FM | 28 | 200 | 06 | 8 | 1140 | 1140 | 1140 | 0.027143 | 431 | 0.010262 | 1303 | 0.031024 | 1.403 | A03 | MINF0.02820006/FM
Freestanding | Mini Freestanding | MINF.02820011/AS | 28 | 200 | 11 | 13 | 2178 | 2178 | 2178 | 0.051857 | 802 | 0.019095 | 2498 | 0.059476 | 1.441 | A03 | MINF0.02820011/AS
Freestanding | Mini Freestanding | MINF.02820011/FM | 28 | 200 | 11 | 13 | 2178 | 2178 | 2178 | 0.051857 | 802 | 0.019095 | 2498 | 0.059476 | 1.441 | A03 | MINF0.02820011/FM
Freestanding | Mini Freestanding | MINF.02820016/AS | 28 | 200 | 16 | 18 | 2866 | 2866 | 2866 | 0.068238 | 1046 | 0.024905 | 3293 | 0.078405 | 1.455 | A03 | MINF0.02820016/AS
Freestanding | Mini Freestanding | MINF.02820016/FM | 28 | 200 | 16 | 18 | 2866 | 2866 | 2866 | 0.068238 | 1046 | 0.024905 | 3293 | 0.078405 | 1.455 | A03 | MINF0.02820016/FM
Freestanding | Mini Freestanding | MINF.02820021/AS | 28 | 200 | 21 | 23 | 3758 | 3758 | 3758 | 0.089476 | 1360 | 0.032381 | 4322 | 0.1029 | 1.467 | A03 | MINF0.02820021/AS
Freestanding | Mini Freestanding | MINF.02820021/FM | 28 | 200 | 21 | 23 | 3758 | 3758 | 3758 | 0.089476 | 1360 | 0.032381 | 4322 | 0.1029 | 1.467 | A03 | MINF0.02820021/FM
Freestanding | Mini Freestanding | MINF.02822006/AS | 28 | 220 | 06 | 8 | 1254 | 1254 | 1254 | 0.029857 | 474 | 0.011286 | 1433 | 0.034119 | 1.403 | A03 | MINF0.02822006/AS
Freestanding | Mini Freestanding | MINF.02822006/FM | 28 | 220 | 06 | 8 | 1254 | 1254 | 1254 | 0.029857 | 474 | 0.011286 | 1433 | 0.034119 | 1.403 | A03 | MINF0.02822006/FM
Freestanding | Mini Freestanding | MINF.02822011/AS | 28 | 220 | 11 | 13 | 2396 | 2396 | 2396 | 0.057048 | 882 | 0.021 | 2748 | 0.065429 | 1.441 | A03 | MINF0.02822011/AS
Freestanding | Mini Freestanding | MINF.02822011/FM | 28 | 220 | 11 | 13 | 2396 | 2396 | 2396 | 0.057048 | 882 | 0.021 | 2748 | 0.065429 | 1.441 | A03 | MINF0.02822011/FM
Freestanding | Mini Freestanding | MINF.02822016/AS | 28 | 220 | 16 | 18 | 3153 | 3153 | 3153 | 0.075071 | 1151 | 0.027405 | 3623 | 0.086262 | 1.455 | A03 | MINF0.02822016/AS
Freestanding | Mini Freestanding | MINF.02822016/FM | 28 | 220 | 16 | 18 | 3153 | 3153 | 3153 | 0.075071 | 1151 | 0.027405 | 3623 | 0.086262 | 1.455 | A03 | MINF0.02822016/FM
Freestanding | Mini Freestanding | MINF.02822021/AS | 28 | 220 | 21 | 23 | 4134 | 4134 | 4134 | 0.098429 | 1497 | 0.035643 | 4754 | 0.11319 | 1.467 | A03 | MINF0.02822021/AS
Freestanding | Mini Freestanding | MINF.02822021/FM | 28 | 220 | 21 | 23 | 4134 | 4134 | 4134 | 0.098429 | 1497 | 0.035643 | 4754 | 0.11319 | 1.467 | A03 | MINF0.02822021/FM
Freestanding | Mini Freestanding | MINF.02824006/AS | 28 | 240 | 06 | 8 | 1368 | 1368 | 1368 | 0.032571 | 517 | 0.01231 | 1564 | 0.037238 | 1.403 | A03 | MINF0.02824006/AS
Freestanding | Mini Freestanding | MINF.02824006/FM | 28 | 240 | 06 | 8 | 1368 | 1368 | 1368 | 0.032571 | 517 | 0.01231 | 1564 | 0.037238 | 1.403 | A03 | MINF0.02824006/FM
Freestanding | Mini Freestanding | MINF.02824011/AS | 28 | 240 | 11 | 13 | 2614 | 2614 | 2614 | 0.062238 | 962 | 0.022905 | 2998 | 0.071381 | 1.441 | A03 | MINF0.02824011/AS
Freestanding | Mini Freestanding | MINF.02824011/FM | 28 | 240 | 11 | 13 | 2614 | 2614 | 2614 | 0.062238 | 962 | 0.022905 | 2998 | 0.071381 | 1.441 | A03 | MINF0.02824011/FM
Freestanding | Mini Freestanding | MINF.02824016/AS | 28 | 240 | 16 | 18 | 3439 | 3439 | 3439 | 0.081881 | 1255 | 0.029881 | 3951 | 0.094071 | 1.455 | A03 | MINF0.02824016/AS
Freestanding | Mini Freestanding | MINF.02824016/FM | 28 | 240 | 16 | 18 | 3439 | 3439 | 3439 | 0.081881 | 1255 | 0.029881 | 3951 | 0.094071 | 1.455 | A03 | MINF0.02824016/FM
Freestanding | Mini Freestanding | MINF.02824021/AS | 28 | 240 | 21 | 23 | 4510 | 4510 | 4510 | 0.10738 | 1633 | 0.038881 | 5187 | 0.1235 | 1.467 | A03 | MINF0.02824021/AS
Freestanding | Mini Freestanding | MINF.02824021/FM | 28 | 240 | 21 | 23 | 4510 | 4510 | 4510 | 0.10738 | 1633 | 0.038881 | 5187 | 0.1235 | 1.467 | A03 | MINF0.02824021/FM
Freestanding | Mini Freestanding | MINF.02824111/DS/DBE | 28 | 241 | 11 | 13 | 4414 | 4414 | 4414 | 0.1051 | 2207 | 0.052548 | 4855 | 0.1156 | 1 | A03 | MINF0.02824111/DS/DBE
Freestanding | Mini Freestanding | MINF.02824116/DS/DBE | 28 | 241 | 16 | 18 | 6319 | 6319 | 6319 | 0.15045 | 3160 | 0.075238 | 6951 | 0.1655 | 1 | A03 | MINF0.02824116/DS/DBE
Freestanding | Mini Freestanding | MINF.02826006/AS | 28 | 260 | 06 | 8 | 1482 | 1482 | 1482 | 0.035286 | 560 | 0.013333 | 1694 | 0.040333 | 1.403 | A03 | MINF0.02826006/AS
Freestanding | Mini Freestanding | MINF.02826006/FM | 28 | 260 | 06 | 8 | 1482 | 1482 | 1482 | 0.035286 | 560 | 0.013333 | 1694 | 0.040333 | 1.403 | A03 | MINF0.02826006/FM
Freestanding | Mini Freestanding | MINF.02826011/AS | 28 | 260 | 11 | 13 | 2831 | 2831 | 2831 | 0.067405 | 1042 | 0.02481 | 3247 | 0.07731 | 1.441 | A03 | MINF0.02826011/AS
Freestanding | Mini Freestanding | MINF.02826011/FM | 28 | 260 | 11 | 13 | 2831 | 2831 | 2831 | 0.067405 | 1042 | 0.02481 | 3247 | 0.07731 | 1.441 | A03 | MINF0.02826011/FM
Freestanding | Mini Freestanding | MINF.02826016/AS | 28 | 260 | 16 | 18 | 3726 | 3726 | 3726 | 0.088714 | 1360 | 0.032381 | 4281 | 0.10193 | 1.455 | A03 | MINF0.02826016/AS
Freestanding | Mini Freestanding | MINF.02826016/FM | 28 | 260 | 16 | 18 | 3726 | 3726 | 3726 | 0.088714 | 1360 | 0.032381 | 4281 | 0.10193 | 1.455 | A03 | MINF0.02826016/FM
Freestanding | Mini Freestanding | MINF.02826021/AS | 28 | 260 | 21 | 23 | 4885 | 4885 | 4885 | 0.11631 | 1768 | 0.042095 | 5618 | 0.13376 | 1.467 | A03 | MINF0.02826021/AS
Freestanding | Mini Freestanding | MINF.02826021/FM | 28 | 260 | 21 | 23 | 4885 | 4885 | 4885 | 0.11631 | 1768 | 0.042095 | 5618 | 0.13376 | 1.467 | A03 | MINF0.02826021/FM
Freestanding | Mini Freestanding | MINF.02828006/AS | 28 | 280 | 06 | 8 | 1596 | 1596 | 1596 | 0.038 | 603 | 0.014357 | 1824 | 0.043429 | 1.403 | A03 | MINF0.02828006/AS
Freestanding | Mini Freestanding | MINF.02828006/FM | 28 | 280 | 06 | 8 | 1596 | 1596 | 1596 | 0.038 | 603 | 0.014357 | 1824 | 0.043429 | 1.403 | A03 | MINF0.02828006/FM
Freestanding | Mini Freestanding | MINF.02828011/AS | 28 | 280 | 11 | 13 | 3049 | 3049 | 3049 | 0.072595 | 1122 | 0.026714 | 3497 | 0.083262 | 1.441 | A03 | MINF0.02828011/AS
Freestanding | Mini Freestanding | MINF.02828011/FM | 28 | 280 | 11 | 13 | 3049 | 3049 | 3049 | 0.072595 | 1122 | 0.026714 | 3497 | 0.083262 | 1.441 | A03 | MINF0.02828011/FM
Freestanding | Mini Freestanding | MINF.02828016/AS | 28 | 280 | 16 | 18 | 4012 | 4012 | 4012 | 0.095524 | 1464 | 0.034857 | 4610 | 0.10976 | 1.455 | A03 | MINF0.02828016/AS
Freestanding | Mini Freestanding | MINF.02828016/FM | 28 | 280 | 16 | 18 | 4012 | 4012 | 4012 | 0.095524 | 1464 | 0.034857 | 4610 | 0.10976 | 1.455 | A03 | MINF0.02828016/FM
Freestanding | Mini Freestanding | MINF.02828021/AS | 28 | 280 | 21 | 23 | 5261 | 5261 | 5261 | 0.12526 | 1904 | 0.045333 | 6050 | 0.14405 | 1.467 | A03 | MINF0.02828021/AS
Freestanding | Mini Freestanding | MINF.02828021/FM | 28 | 280 | 21 | 23 | 5261 | 5261 | 5261 | 0.12526 | 1904 | 0.045333 | 6050 | 0.14405 | 1.467 | A03 | MINF0.02828021/FM
Freestanding | Mini Freestanding | MINF.02830006/AS | 28 | 300 | 06 | 8 | 1710 | 1710 | 1710 | 0.040714 | 646 | 0.015381 | 1955 | 0.046548 | 1.403 | A03 | MINF0.02830006/AS
Freestanding | Mini Freestanding | MINF.02830006/FM | 28 | 300 | 06 | 8 | 1710 | 1710 | 1710 | 0.040714 | 646 | 0.015381 | 1955 | 0.046548 | 1.403 | A03 | MINF0.02830006/FM
Freestanding | Mini Freestanding | MINF.02830011/AS | 28 | 300 | 11 | 13 | 3267 | 3267 | 3267 | 0.077786 | 1202 | 0.028619 | 3747 | 0.089214 | 1.441 | A03 | MINF0.02830011/AS
Freestanding | Mini Freestanding | MINF.02830011/FM | 28 | 300 | 11 | 13 | 3267 | 3267 | 3267 | 0.077786 | 1202 | 0.028619 | 3747 | 0.089214 | 1.441 | A03 | MINF0.02830011/FM
Freestanding | Mini Freestanding | MINF.02830016/AS | 28 | 300 | 16 | 18 | 4299 | 4299 | 4299 | 0.10236 | 1569 | 0.037357 | 4940 | 0.11762 | 1.455 | A03 | MINF0.02830016/AS
Freestanding | Mini Freestanding | MINF.02830016/FM | 28 | 300 | 16 | 18 | 4299 | 4299 | 4299 | 0.10236 | 1569 | 0.037357 | 4940 | 0.11762 | 1.455 | A03 | MINF0.02830016/FM
Freestanding | Mini Freestanding | MINF.02830021/AS | 28 | 300 | 21 | 23 | 5637 | 5637 | 5637 | 0.13421 | 2041 | 0.048595 | 6483 | 0.15436 | 1.467 | A03 | MINF0.02830021/AS
Freestanding | Mini Freestanding | MINF.02830021/FM | 28 | 300 | 21 | 23 | 5637 | 5637 | 5637 | 0.13421 | 2041 | 0.048595 | 6483 | 0.15436 | 1.467 | A03 | MINF0.02830021/FM
Horizontal Wall | Play | PLAW.03506010 | 35 | 60 | 10 | 13 | 529 | 529 | 529 | 0.012595 | 203 | 0.0048333 | 603 | 0.014357 | 1.379 | A20 | PLAW0.03506010
Horizontal Wall | Play | PLAW.03506011 | 35 | 60 | 11 | 13 | 583 | 583 | 583 | 0.013881 | 215 | 0.005119 | 669 | 0.015929 | 1.441 | A20 | PLAW0.03506011
Horizontal Wall | Play | PLAW.03506015 | 35 | 60 | 15 | 18 | 805 | 805 | 805 | 0.019167 | 312 | 0.0074286 | 917 | 0.021833 | 1.37 | A20 | PLAW0.03506015
Horizontal Wall | Play | PLAW.03506016 | 35 | 60 | 16 | 18 | 870 | 870 | 870 | 0.020714 | 317 | 0.0075476 | 1000 | 0.02381 | 1.459 | A20 | PLAW0.03506016
Horizontal Wall | Play | PLAW.03506020 | 35 | 60 | 20 | 23 | 1104 | 1104 | 1104 | 0.026286 | 431 | 0.010262 | 1256 | 0.029905 | 1.36 | A20 | PLAW0.03506020
Horizontal Wall | Play | PLAW.03506021 | 35 | 60 | 21 | 23 | 1217 | 1217 | 1217 | 0.028976 | 437 | 0.010405 | 1401 | 0.033357 | 1.476 | A20 | PLAW0.03506021
Horizontal Wall | Play | PLAW.03508010 | 35 | 80 | 10 | 13 | 705 | 705 | 705 | 0.016786 | 271 | 0.0064524 | 804 | 0.019143 | 1.379 | A20 | PLAW0.03508010
Horizontal Wall | Play | PLAW.03508011 | 35 | 80 | 11 | 13 | 777 | 777 | 777 | 0.0185 | 286 | 0.0068095 | 891 | 0.021214 | 1.441 | A20 | PLAW0.03508011
Horizontal Wall | Play | PLAW.03508011/DBE | 35 | 80 | 11 | 13 | 1077 | 1077 | 1077 | 0.025643 | 539 | 0.012833 | 1185 | 0.028214 | 1 | A20 | PLAW0.03508011/DBE
Horizontal Wall | Play | PLAW.03508015 | 35 | 80 | 15 | 18 | 1074 | 1074 | 1074 | 0.025571 | 416 | 0.0099048 | 1223 | 0.029119 | 1.37 | A20 | PLAW0.03508015
Horizontal Wall | Play | PLAW.03508016 | 35 | 80 | 16 | 18 | 1160 | 1160 | 1160 | 0.027619 | 422 | 0.010048 | 1333 | 0.031738 | 1.459 | A20 | PLAW0.03508016
Horizontal Wall | Play | PLAW.03508016/DBE | 35 | 80 | 16 | 18 | 1640 | 1640 | 1640 | 0.039048 | 820 | 0.019524 | 1804 | 0.042952 | 1 | A20 | PLAW0.03508016/DBE
Horizontal Wall | Play | PLAW.03508020 | 35 | 80 | 20 | 23 | 1472 | 1472 | 1472 | 0.035048 | 574 | 0.013667 | 1675 | 0.039881 | 1.36 | A20 | PLAW0.03508020
Horizontal Wall | Play | PLAW.03508021 | 35 | 80 | 21 | 23 | 1622 | 1622 | 1622 | 0.038619 | 582 | 0.013857 | 1867 | 0.044452 | 1.476 | A20 | PLAW0.03508021
Horizontal Wall | Play | PLAW.03508021/DBE | 35 | 80 | 21 | 23 | 2102 | 2102 | 2102 | 0.050048 | 1051 | 0.025024 | 2312 | 0.055048 | 1 | A20 | PLAW0.03508021/DBE
Horizontal Wall | Play | PLAW.03510010 | 35 | 100 | 10 | 13 | 881 | 881 | 881 | 0.020976 | 338 | 0.0080476 | 1004 | 0.023905 | 1.379 | A20 | PLAW0.03510010
Horizontal Wall | Play | PLAW.03510011 | 35 | 100 | 11 | 13 | 971 | 971 | 971 | 0.023119 | 357 | 0.0085 | 1114 | 0.026524 | 1.441 | A20 | PLAW0.03510011
Horizontal Wall | Play | PLAW.03510011/DBE | 35 | 100 | 11 | 13 | 1271 | 1271 | 1271 | 0.030262 | 636 | 0.015143 | 1398 | 0.033286 | 1 | A20 | PLAW0.03510011/DBE
Horizontal Wall | Play | PLAW.03510015 | 35 | 100 | 15 | 18 | 1342 | 1342 | 1342 | 0.031952 | 519 | 0.012357 | 1529 | 0.036405 | 1.37 | A20 | PLAW0.03510015
Horizontal Wall | Play | PLAW.03510016 | 35 | 100 | 16 | 18 | 1450 | 1450 | 1450 | 0.034524 | 528 | 0.012571 | 1666 | 0.039667 | 1.459 | A20 | PLAW0.03510016
Horizontal Wall | Play | PLAW.03510016/DBE | 35 | 100 | 16 | 18 | 1930 | 1930 | 1930 | 0.045952 | 965 | 0.022976 | 2123 | 0.050548 | 1 | A20 | PLAW0.03510016/DBE
Horizontal Wall | Play | PLAW.03510020 | 35 | 100 | 20 | 23 | 1840 | 1840 | 1840 | 0.04381 | 718 | 0.017095 | 2094 | 0.049857 | 1.36 | A20 | PLAW0.03510020
Horizontal Wall | Play | PLAW.03510021 | 35 | 100 | 21 | 23 | 2028 | 2028 | 2028 | 0.048286 | 728 | 0.017333 | 2334 | 0.055571 | 1.476 | A20 | PLAW0.03510021
Horizontal Wall | Play | PLAW.03510021/DBE | 35 | 100 | 21 | 23 | 2508 | 2508 | 2508 | 0.059714 | 1254 | 0.029857 | 2759 | 0.06569 | 1 | A20 | PLAW0.03510021/DBE
Horizontal Wall | Play | PLAW.03512010 | 35 | 120 | 10 | 13 | 1057 | 1057 | 1057 | 0.025167 | 406 | 0.0096667 | 1205 | 0.02869 | 1.379 | A20 | PLAW0.03512010
Horizontal Wall | Play | PLAW.03512011 | 35 | 120 | 11 | 13 | 1165 | 1165 | 1165 | 0.027738 | 429 | 0.010214 | 1336 | 0.03181 | 1.441 | A20 | PLAW0.03512011
Horizontal Wall | Play | PLAW.03512011/DBE | 35 | 120 | 11 | 13 | 1765 | 1765 | 1765 | 0.042024 | 883 | 0.021024 | 1942 | 0.046238 | 1 | A20 | PLAW0.03512011/DBE
Horizontal Wall | Play | PLAW.03512015 | 35 | 120 | 15 | 18 | 1610 | 1610 | 1610 | 0.038333 | 623 | 0.014833 | 1834 | 0.043667 | 1.37 | A20 | PLAW0.03512015
Horizontal Wall | Play | PLAW.03512016 | 35 | 120 | 16 | 18 | 1740 | 1740 | 1740 | 0.041429 | 633 | 0.015071 | 1999 | 0.047595 | 1.459 | A20 | PLAW0.03512016
Horizontal Wall | Play | PLAW.03512016/DBE | 35 | 120 | 16 | 18 | 2700 | 2700 | 2700 | 0.064286 | 1350 | 0.032143 | 2970 | 0.070714 | 1 | A20 | PLAW0.03512016/DBE
Horizontal Wall | Play | PLAW.03512020 | 35 | 120 | 20 | 23 | 2208 | 2208 | 2208 | 0.052571 | 861 | 0.0205 | 2513 | 0.059833 | 1.36 | A20 | PLAW0.03512020
Horizontal Wall | Play | PLAW.03512021 | 35 | 120 | 21 | 23 | 2434 | 2434 | 2434 | 0.057952 | 874 | 0.02081 | 2802 | 0.066714 | 1.476 | A20 | PLAW0.03512021
Horizontal Wall | Play | PLAW.03512021/DBE | 35 | 120 | 21 | 23 | 3394 | 3394 | 3394 | 0.08081 | 1697 | 0.040405 | 3733 | 0.088881 | 1 | A20 | PLAW0.03512021/DBE
Horizontal Wall | Play | PLAW.05006010 | 50 | 60 | 10 | 13 | 591 | 591 | 591 | 0.014071 | 225 | 0.0053571 | 675 | 0.016071 | 1.396 | A20 | PLAW0.05006010
Horizontal Wall | Play | PLAW.05006011 | 50 | 60 | 11 | 13 | 685 | 685 | 685 | 0.01631 | 251 | 0.0059762 | 786 | 0.018714 | 1.449 | A20 | PLAW0.05006011
Horizontal Wall | Play | PLAW.05006015 | 50 | 60 | 15 | 18 | 925 | 925 | 925 | 0.022024 | 354 | 0.0084286 | 1055 | 0.025119 | 1.384 | A20 | PLAW0.05006015
Horizontal Wall | Play | PLAW.05006016 | 50 | 60 | 16 | 18 | 1040 | 1040 | 1040 | 0.024762 | 378 | 0.009 | 1195 | 0.028452 | 1.46 | A20 | PLAW0.05006016
Horizontal Wall | Play | PLAW.05006020 | 50 | 60 | 20 | 23 | 1284 | 1284 | 1284 | 0.030571 | 496 | 0.01181 | 1464 | 0.034857 | 1.372 | A20 | PLAW0.05006020
Horizontal Wall | Play | PLAW.05006021 | 50 | 60 | 21 | 23 | 1461 | 1461 | 1461 | 0.034786 | 527 | 0.012548 | 1682 | 0.040048 | 1.471 | A20 | PLAW0.05006021
Horizontal Wall | Play | PLAW.05008010 | 50 | 80 | 10 | 13 | 788 | 788 | 788 | 0.018762 | 299 | 0.007119 | 900 | 0.021429 | 1.396 | A20 | PLAW0.05008010
Horizontal Wall | Play | PLAW.05008011 | 50 | 80 | 11 | 13 | 913 | 913 | 913 | 0.021738 | 334 | 0.0079524 | 1048 | 0.024952 | 1.449 | A20 | PLAW0.05008011
Horizontal Wall | Play | PLAW.05008011/DBE | 50 | 80 | 11 | 13 | 1213 | 1213 | 1213 | 0.028881 | 607 | 0.014452 | 1334 | 0.031762 | 1 | A20 | PLAW0.05008011/DBE
Horizontal Wall | Play | PLAW.05008015 | 50 | 80 | 15 | 18 | 1234 | 1234 | 1234 | 0.029381 | 473 | 0.011262 | 1408 | 0.033524 | 1.384 | A20 | PLAW0.05008015
Horizontal Wall | Play | PLAW.05008016 | 50 | 80 | 16 | 18 | 1386 | 1386 | 1386 | 0.033 | 503 | 0.011976 | 1593 | 0.037929 | 1.46 | A20 | PLAW0.05008016
Horizontal Wall | Play | PLAW.05008016/DBE | 50 | 80 | 16 | 18 | 1866 | 1866 | 1866 | 0.044429 | 933 | 0.022214 | 2053 | 0.048881 | 1 | A20 | PLAW0.05008016/DBE
Horizontal Wall | Play | PLAW.05008020 | 50 | 80 | 20 | 23 | 1712 | 1712 | 1712 | 0.040762 | 661 | 0.015738 | 1952 | 0.046476 | 1.372 | A20 | PLAW0.05008020
Horizontal Wall | Play | PLAW.05008021 | 50 | 80 | 21 | 23 | 1948 | 1948 | 1948 | 0.046381 | 703 | 0.016738 | 2242 | 0.053381 | 1.471 | A20 | PLAW0.05008021
Horizontal Wall | Play | PLAW.05008021/DBE | 50 | 80 | 21 | 23 | 2428 | 2428 | 2428 | 0.05781 | 1214 | 0.028905 | 2671 | 0.063595 | 1 | A20 | PLAW0.05008021/DBE
Horizontal Wall | Play | PLAW.05010010 | 50 | 100 | 10 | 13 | 985 | 985 | 985 | 0.023452 | 374 | 0.0089048 | 1125 | 0.026786 | 1.396 | A20 | PLAW0.05010010
Horizontal Wall | Play | PLAW.05010011 | 50 | 100 | 11 | 13 | 1141 | 1141 | 1141 | 0.027167 | 418 | 0.0099524 | 1310 | 0.03119 | 1.449 | A20 | PLAW0.05010011
Horizontal Wall | Play | PLAW.05010011/DBE | 50 | 100 | 11 | 13 | 1441 | 1441 | 1441 | 0.03431 | 721 | 0.017167 | 1585 | 0.037738 | 1 | A20 | PLAW0.05010011/DBE
Horizontal Wall | Play | PLAW.05010015 | 50 | 100 | 15 | 18 | 1542 | 1542 | 1542 | 0.036714 | 591 | 0.014071 | 1759 | 0.041881 | 1.384 | A20 | PLAW0.05010015
Horizontal Wall | Play | PLAW.05010016 | 50 | 100 | 16 | 18 | 1733 | 1733 | 1733 | 0.041262 | 629 | 0.014976 | 1991 | 0.047405 | 1.46 | A20 | PLAW0.05010016
Horizontal Wall | Play | PLAW.05010016/DBE | 50 | 100 | 16 | 18 | 2213 | 2213 | 2213 | 0.05269 | 1107 | 0.026357 | 2434 | 0.057952 | 1 | A20 | PLAW0.05010016/DBE
Horizontal Wall | Play | PLAW.05010020 | 50 | 100 | 20 | 23 | 2140 | 2140 | 2140 | 0.050952 | 826 | 0.019667 | 2440 | 0.058095 | 1.372 | A20 | PLAW0.05010020
Horizontal Wall | Play | PLAW.05010021 | 50 | 100 | 21 | 23 | 2435 | 2435 | 2435 | 0.057976 | 879 | 0.020929 | 2803 | 0.066738 | 1.471 | A20 | PLAW0.05010021
Horizontal Wall | Play | PLAW.05010021/DBE | 50 | 100 | 21 | 23 | 2915 | 2915 | 2915 | 0.069405 | 1458 | 0.034714 | 3207 | 0.076357 | 1 | A20 | PLAW0.05010021/DBE
Horizontal Wall | Play | PLAW.05012010 | 50 | 120 | 10 | 13 | 1182 | 1182 | 1182 | 0.028143 | 449 | 0.01069 | 1350 | 0.032143 | 1.396 | A20 | PLAW0.05012010
Horizontal Wall | Play | PLAW.05012011 | 50 | 120 | 11 | 13 | 1369 | 1369 | 1369 | 0.032595 | 501 | 0.011929 | 1572 | 0.037429 | 1.449 | A20 | PLAW0.05012011
Horizontal Wall | Play | PLAW.05012011/DBE | 50 | 120 | 11 | 13 | 1969 | 1969 | 1969 | 0.046881 | 985 | 0.023452 | 2166 | 0.051571 | 1 | A20 | PLAW0.05012011/DBE
Horizontal Wall | Play | PLAW.05012015 | 50 | 120 | 15 | 18 | 1850 | 1850 | 1850 | 0.044048 | 709 | 0.016881 | 2111 | 0.050262 | 1.384 | A20 | PLAW0.05012015
Horizontal Wall | Play | PLAW.05012016 | 50 | 120 | 16 | 18 | 2080 | 2080 | 2080 | 0.049524 | 755 | 0.017976 | 2390 | 0.056905 | 1.46 | A20 | PLAW0.05012016
Horizontal Wall | Play | PLAW.05012016/DBE | 50 | 120 | 16 | 18 | 3040 | 3040 | 3040 | 0.072381 | 1520 | 0.03619 | 3344 | 0.079619 | 1 | A20 | PLAW0.05012016/DBE
Horizontal Wall | Play | PLAW.05012020 | 50 | 120 | 20 | 23 | 2568 | 2568 | 2568 | 0.061143 | 991 | 0.023595 | 2928 | 0.069714 | 1.372 | A20 | PLAW0.05012020
Horizontal Wall | Play | PLAW.05012021 | 50 | 120 | 21 | 23 | 2922 | 2922 | 2922 | 0.069571 | 1055 | 0.025119 | 3363 | 0.080071 | 1.471 | A20 | PLAW0.05012021
Horizontal Wall | Play | PLAW.05012021/DBE | 50 | 120 | 21 | 23 | 3882 | 3882 | 3882 | 0.092429 | 1941 | 0.046214 | 4270 | 0.10167 | 1 | A20 | PLAW0.05012021/DBE
Horizontal Wall | Play | PLAW.06506010 | 65 | 60 | 10 | 13 | 653 | 653 | 653 | 0.015548 | 246 | 0.0058571 | 747 | 0.017786 | 1.413 | A20 | PLAW0.06506010
Horizontal Wall | Play | PLAW.06506011 | 65 | 60 | 11 | 13 | 778 | 778 | 778 | 0.018524 | 283 | 0.0067381 | 894 | 0.021286 | 1.458 | A20 | PLAW0.06506011
Horizontal Wall | Play | PLAW.06506015 | 65 | 60 | 15 | 18 | 1040 | 1040 | 1040 | 0.024762 | 394 | 0.009381 | 1189 | 0.02831 | 1.398 | A20 | PLAW0.06506015
Horizontal Wall | Play | PLAW.06506016 | 65 | 60 | 16 | 18 | 1187 | 1187 | 1187 | 0.028262 | 431 | 0.010262 | 1365 | 0.0325 | 1.462 | A20 | PLAW0.06506016
Horizontal Wall | Play | PLAW.06506020 | 65 | 60 | 20 | 23 | 1454 | 1454 | 1454 | 0.034619 | 557 | 0.013262 | 1659 | 0.0395 | 1.384 | A20 | PLAW0.06506020
Horizontal Wall | Play | PLAW.06506021 | 65 | 60 | 21 | 23 | 1663 | 1663 | 1663 | 0.039595 | 602 | 0.014333 | 1912 | 0.045524 | 1.466 | A20 | PLAW0.06506021
Horizontal Wall | Play | PLAW.06508010 | 65 | 80 | 10 | 13 | 870 | 870 | 870 | 0.020714 | 327 | 0.0077857 | 995 | 0.02369 | 1.413 | A20 | PLAW0.06508010
Horizontal Wall | Play | PLAW.06508011 | 65 | 80 | 11 | 13 | 1037 | 1037 | 1037 | 0.02469 | 377 | 0.0089762 | 1192 | 0.028381 | 1.458 | A20 | PLAW0.06508011
Horizontal Wall | Play | PLAW.06508011/DBE | 65 | 80 | 11 | 13 | 1337 | 1337 | 1337 | 0.031833 | 669 | 0.015929 | 1471 | 0.035024 | 1 | A20 | PLAW0.06508011/DBE
Horizontal Wall | Play | PLAW.06508015 | 65 | 80 | 15 | 18 | 1386 | 1386 | 1386 | 0.033 | 525 | 0.0125 | 1584 | 0.037714 | 1.398 | A20 | PLAW0.06508015
Horizontal Wall | Play | PLAW.06508016 | 65 | 80 | 16 | 18 | 1582 | 1582 | 1582 | 0.037667 | 574 | 0.013667 | 1819 | 0.04331 | 1.462 | A20 | PLAW0.06508016
Horizontal Wall | Play | PLAW.06508016/DBE | 65 | 80 | 16 | 18 | 2062 | 2062 | 2062 | 0.049095 | 1031 | 0.024548 | 2268 | 0.054 | 1 | A20 | PLAW0.06508016/DBE
Horizontal Wall | Play | PLAW.06508020 | 65 | 80 | 20 | 23 | 1938 | 1938 | 1938 | 0.046143 | 742 | 0.017667 | 2211 | 0.052643 | 1.384 | A20 | PLAW0.06508020
Horizontal Wall | Play | PLAW.06508021 | 65 | 80 | 21 | 23 | 2218 | 2218 | 2218 | 0.05281 | 803 | 0.019119 | 2551 | 0.060738 | 1.466 | A20 | PLAW0.06508021
Horizontal Wall | Play | PLAW.06508021/DBE | 65 | 80 | 21 | 23 | 2698 | 2698 | 2698 | 0.064238 | 1349 | 0.032119 | 2968 | 0.070667 | 1 | A20 | PLAW0.06508021/DBE
Horizontal Wall | Play | PLAW.06510010 | 65 | 100 | 10 | 13 | 1088 | 1088 | 1088 | 0.025905 | 409 | 0.0097381 | 1245 | 0.029643 | 1.413 | A20 | PLAW0.06510010
Horizontal Wall | Play | PLAW.06510011 | 65 | 100 | 11 | 13 | 1296 | 1296 | 1296 | 0.030857 | 472 | 0.011238 | 1489 | 0.035452 | 1.458 | A20 | PLAW0.06510011
Horizontal Wall | Play | PLAW.06510011/DBE | 65 | 100 | 11 | 13 | 1596 | 1596 | 1596 | 0.038 | 798 | 0.019 | 1756 | 0.04181 | 1 | A20 | PLAW0.06510011/DBE
Horizontal Wall | Play | PLAW.06510015 | 65 | 100 | 15 | 18 | 1733 | 1733 | 1733 | 0.041262 | 657 | 0.015643 | 1981 | 0.047167 | 1.398 | A20 | PLAW0.06510015
Horizontal Wall | Play | PLAW.06510016 | 65 | 100 | 16 | 18 | 1978 | 1978 | 1978 | 0.047095 | 718 | 0.017095 | 2275 | 0.054167 | 1.462 | A20 | PLAW0.06510016
Horizontal Wall | Play | PLAW.06510016/DBE | 65 | 100 | 16 | 18 | 2458 | 2458 | 2458 | 0.058524 | 1229 | 0.029262 | 2704 | 0.064381 | 1 | A20 | PLAW0.06510016/DBE
Horizontal Wall | Play | PLAW.06510020 | 65 | 100 | 20 | 23 | 2423 | 2423 | 2423 | 0.05769 | 928 | 0.022095 | 2765 | 0.065833 | 1.384 | A20 | PLAW0.06510020
Horizontal Wall | Play | PLAW.06510021 | 65 | 100 | 21 | 23 | 2772 | 2772 | 2772 | 0.066 | 1003 | 0.023881 | 3188 | 0.075905 | 1.466 | A20 | PLAW0.06510021
Horizontal Wall | Play | PLAW.06510021/DBE | 65 | 100 | 21 | 23 | 3252 | 3252 | 3252 | 0.077429 | 1626 | 0.038714 | 3577 | 0.085167 | 1 | A20 | PLAW0.06510021/DBE
Horizontal Wall | Play | PLAW.06512010 | 65 | 120 | 10 | 13 | 1306 | 1306 | 1306 | 0.031095 | 491 | 0.01169 | 1494 | 0.035571 | 1.413 | A20 | PLAW0.06512010
Horizontal Wall | Play | PLAW.06512011 | 65 | 120 | 11 | 13 | 1555 | 1555 | 1555 | 0.037024 | 566 | 0.013476 | 1787 | 0.042548 | 1.458 | A20 | PLAW0.06512011
Horizontal Wall | Play | PLAW.06512011/DBE | 65 | 120 | 11 | 13 | 2155 | 2155 | 2155 | 0.05131 | 1078 | 0.025667 | 2371 | 0.056452 | 1 | A20 | PLAW0.06512011/DBE
Horizontal Wall | Play | PLAW.06512015 | 65 | 120 | 15 | 18 | 2080 | 2080 | 2080 | 0.049524 | 788 | 0.018762 | 2377 | 0.056595 | 1.398 | A20 | PLAW0.06512015
Horizontal Wall | Play | PLAW.06512016 | 65 | 120 | 16 | 18 | 2374 | 2374 | 2374 | 0.056524 | 862 | 0.020524 | 2730 | 0.065 | 1.462 | A20 | PLAW0.06512016
Horizontal Wall | Play | PLAW.06512016/DBE | 65 | 120 | 16 | 18 | 3334 | 3334 | 3334 | 0.079381 | 1667 | 0.03969 | 3667 | 0.08731 | 1 | A20 | PLAW0.06512016/DBE
Horizontal Wall | Play | PLAW.06512020 | 65 | 120 | 20 | 23 | 2908 | 2908 | 2908 | 0.069238 | 1114 | 0.026524 | 3318 | 0.079 | 1.384 | A20 | PLAW0.06512020
Horizontal Wall | Play | PLAW.06512021 | 65 | 120 | 21 | 23 | 3326 | 3326 | 3326 | 0.07919 | 1204 | 0.028667 | 3825 | 0.091071 | 1.466 | A20 | PLAW0.06512021
Horizontal Wall | Play | PLAW.06512021/DBE | 65 | 120 | 21 | 23 | 4286 | 4286 | 4286 | 0.10205 | 2143 | 0.051024 | 4715 | 0.11226 | 1 | A20 | PLAW0.06512021/DBE
Horizontal Wall | Strada | STRW.02005006 | 20 | 50 | 06 | 9 | 269 | 269 | 269 | 0.0064048 | 101 | 0.0024048 | 308 | 0.0073333 | 1.41 | A09 | STRW0.02005006
Horizontal Wall | Strada | STRW.02005010 | 20 | 50 | 10 | 12 | 328 | 328 | 328 | 0.0078095 | 123 | 0.0029286 | 375 | 0.0089286 | 1.413 | A09 | STRW0.02005010
Horizontal Wall | Strada | STRW.02005015 | 20 | 50 | 15 | 17 | 545 | 545 | 545 | 0.012976 | 205 | 0.004881 | 623 | 0.014833 | 1.408 | A09 | STRW0.02005015
Horizontal Wall | Strada | STRW.02005020 | 20 | 50 | 20 | 22 | 766 | 766 | 766 | 0.018238 | 289 | 0.006881 | 876 | 0.020857 | 1.408 | A09 | STRW0.02005020
Horizontal Wall | Strada | STRW.02006006 | 20 | 60 | 06 | 9 | 323 | 323 | 323 | 0.0076905 | 121 | 0.002881 | 370 | 0.0088095 | 1.41 | A09 | STRW0.02006006
Horizontal Wall | Strada | STRW.02006010 | 20 | 60 | 10 | 12 | 393 | 393 | 393 | 0.0093571 | 148 | 0.0035238 | 450 | 0.010714 | 1.413 | A09 | STRW0.02006010
Horizontal Wall | Strada | STRW.02006010/DBE | 20 | 60 | 10 | 12 | 543 | 543 | 543 | 0.012929 | 272 | 0.0064762 | 597 | 0.014214 | 1 | A09 | STRW0.02006010/DBE
Horizontal Wall | Strada | STRW.02006015 | 20 | 60 | 15 | 17 | 654 | 654 | 654 | 0.015571 | 247 | 0.005881 | 748 | 0.01781 | 1.408 | A09 | STRW0.02006015
Horizontal Wall | Strada | STRW.02006015/DBE | 20 | 60 | 15 | 17 | 904 | 904 | 904 | 0.021524 | 452 | 0.010762 | 994 | 0.023667 | 1 | A09 | STRW0.02006015/DBE
Horizontal Wall | Strada | STRW.02006020 | 20 | 60 | 20 | 22 | 919 | 919 | 919 | 0.021881 | 346 | 0.0082381 | 1051 | 0.025024 | 1.408 | A09 | STRW0.02006020
Horizontal Wall | Strada | STRW.02006020/DBE | 20 | 60 | 20 | 22 | 1169 | 1169 | 1169 | 0.027833 | 585 | 0.013929 | 1286 | 0.030619 | 1 | A09 | STRW0.02006020/DBE
Horizontal Wall | Strada | STRW.02007006 | 20 | 70 | 06 | 9 | 377 | 377 | 377 | 0.0089762 | 142 | 0.003381 | 431 | 0.010262 | 1.41 | A09 | STRW0.02007006
Horizontal Wall | Strada | STRW.02007010 | 20 | 70 | 10 | 12 | 459 | 459 | 459 | 0.010929 | 173 | 0.004119 | 525 | 0.0125 | 1.413 | A09 | STRW0.02007010
Horizontal Wall | Strada | STRW.02007010/DBE | 20 | 70 | 10 | 12 | 609 | 609 | 609 | 0.0145 | 305 | 0.0072619 | 670 | 0.015952 | 1 | A09 | STRW0.02007010/DBE
Horizontal Wall | Strada | STRW.02007015 | 20 | 70 | 15 | 17 | 763 | 763 | 763 | 0.018167 | 288 | 0.0068571 | 873 | 0.020786 | 1.408 | A09 | STRW0.02007015
Horizontal Wall | Strada | STRW.02007015/DBE | 20 | 70 | 15 | 17 | 1013 | 1013 | 1013 | 0.024119 | 507 | 0.012071 | 1114 | 0.026524 | 1 | A09 | STRW0.02007015/DBE
Horizontal Wall | Strada | STRW.02007020 | 20 | 70 | 20 | 22 | 1072 | 1072 | 1072 | 0.025524 | 404 | 0.009619 | 1226 | 0.02919 | 1.408 | A09 | STRW0.02007020
Horizontal Wall | Strada | STRW.02007020/DBE | 20 | 70 | 20 | 22 | 1322 | 1322 | 1322 | 0.031476 | 661 | 0.015738 | 1454 | 0.034619 | 1 | A09 | STRW0.02007020/DBE
Horizontal Wall | Strada | STRW.02008006 | 20 | 80 | 06 | 9 | 430 | 430 | 430 | 0.010238 | 162 | 0.0038571 | 492 | 0.011714 | 1.41 | A09 | STRW0.02008006
Horizontal Wall | Strada | STRW.02008010 | 20 | 80 | 10 | 12 | 524 | 524 | 524 | 0.012476 | 197 | 0.0046905 | 599 | 0.014262 | 1.413 | A09 | STRW0.02008010
Horizontal Wall | Strada | STRW.02008010/DBE | 20 | 80 | 10 | 12 | 674 | 674 | 674 | 0.016048 | 337 | 0.0080238 | 741 | 0.017643 | 1 | A09 | STRW0.02008010/DBE
Horizontal Wall | Strada | STRW.02008015 | 20 | 80 | 15 | 17 | 872 | 872 | 872 | 0.020762 | 329 | 0.0078333 | 998 | 0.023762 | 1.408 | A09 | STRW0.02008015
Horizontal Wall | Strada | STRW.02008015/DBE | 20 | 80 | 15 | 17 | 1122 | 1122 | 1122 | 0.026714 | 561 | 0.013357 | 1234 | 0.029381 | 1 | A09 | STRW0.02008015/DBE
Horizontal Wall | Strada | STRW.02008020 | 20 | 80 | 20 | 22 | 1226 | 1226 | 1226 | 0.02919 | 462 | 0.011 | 1403 | 0.033405 | 1.408 | A09 | STRW0.02008020
Horizontal Wall | Strada | STRW.02008020/DBE | 20 | 80 | 20 | 22 | 1476 | 1476 | 1476 | 0.035143 | 738 | 0.017571 | 1624 | 0.038667 | 1 | A09 | STRW0.02008020/DBE
Horizontal Wall | Strada | STRW.02009006 | 20 | 90 | 06 | 9 | 484 | 484 | 484 | 0.011524 | 182 | 0.0043333 | 554 | 0.01319 | 1.41 | A09 | STRW0.02009006
Horizontal Wall | Strada | STRW.02009010 | 20 | 90 | 10 | 12 | 590 | 590 | 590 | 0.014048 | 222 | 0.0052857 | 675 | 0.016071 | 1.413 | A09 | STRW0.02009010
Horizontal Wall | Strada | STRW.02009010/DBE | 20 | 90 | 10 | 12 | 890 | 890 | 890 | 0.02119 | 445 | 0.010595 | 979 | 0.02331 | 1 | A09 | STRW0.02009010/DBE
Horizontal Wall | Strada | STRW.02009015 | 20 | 90 | 15 | 17 | 981 | 981 | 981 | 0.023357 | 370 | 0.0088095 | 1122 | 0.026714 | 1.408 | A09 | STRW0.02009015
Horizontal Wall | Strada | STRW.02009015/DBE | 20 | 90 | 15 | 17 | 1481 | 1481 | 1481 | 0.035262 | 741 | 0.017643 | 1629 | 0.038786 | 1 | A09 | STRW0.02009015/DBE
Horizontal Wall | Strada | STRW.02009020 | 20 | 90 | 20 | 22 | 1379 | 1379 | 1379 | 0.032833 | 520 | 0.012381 | 1578 | 0.037571 | 1.408 | A09 | STRW0.02009020
Horizontal Wall | Strada | STRW.02009020/DBE | 20 | 90 | 20 | 22 | 1879 | 1879 | 1879 | 0.044738 | 940 | 0.022381 | 2067 | 0.049214 | 1 | A09 | STRW0.02009020/DBE
Horizontal Wall | Strada | STRW.02010006 | 20 | 100 | 06 | 9 | 538 | 538 | 538 | 0.01281 | 202 | 0.0048095 | 615 | 0.014643 | 1.41 | A09 | STRW0.02010006
Horizontal Wall | Strada | STRW.02010010 | 20 | 100 | 10 | 12 | 655 | 655 | 655 | 0.015595 | 246 | 0.0058571 | 749 | 0.017833 | 1.413 | A09 | STRW0.02010010
Horizontal Wall | Strada | STRW.02010010/DBE | 20 | 100 | 10 | 12 | 955 | 955 | 955 | 0.022738 | 478 | 0.011381 | 1051 | 0.025024 | 1 | A09 | STRW0.02010010/DBE
Horizontal Wall | Strada | STRW.02010015 | 20 | 100 | 15 | 17 | 1090 | 1090 | 1090 | 0.025952 | 411 | 0.0097857 | 1247 | 0.02969 | 1.408 | A09 | STRW0.02010015
Horizontal Wall | Strada | STRW.02010015/DBE | 20 | 100 | 15 | 17 | 1590 | 1590 | 1590 | 0.037857 | 795 | 0.018929 | 1749 | 0.041643 | 1 | A09 | STRW0.02010015/DBE
Horizontal Wall | Strada | STRW.02010020 | 20 | 100 | 20 | 22 | 1532 | 1532 | 1532 | 0.036476 | 578 | 0.013762 | 1753 | 0.041738 | 1.408 | A09 | STRW0.02010020
Horizontal Wall | Strada | STRW.02010020/DBE | 20 | 100 | 20 | 22 | 2032 | 2032 | 2032 | 0.048381 | 1016 | 0.02419 | 2235 | 0.053214 | 1 | A09 | STRW0.02010020/DBE
Horizontal Wall | Strada | STRW.02011006 | 20 | 110 | 06 | 9 | 592 | 592 | 592 | 0.014095 | 223 | 0.0053095 | 677 | 0.016119 | 1.41 | A09 | STRW0.02011006
Horizontal Wall | Strada | STRW.02011010 | 20 | 110 | 10 | 12 | 721 | 721 | 721 | 0.017167 | 271 | 0.0064524 | 825 | 0.019643 | 1.413 | A09 | STRW0.02011010
Horizontal Wall | Strada | STRW.02011010/DBE | 20 | 110 | 10 | 12 | 1021 | 1021 | 1021 | 0.02431 | 511 | 0.012167 | 1123 | 0.026738 | 1 | A09 | STRW0.02011010/DBE
Horizontal Wall | Strada | STRW.02011015 | 20 | 110 | 15 | 17 | 1199 | 1199 | 1199 | 0.028548 | 452 | 0.010762 | 1372 | 0.032667 | 1.408 | A09 | STRW0.02011015
Horizontal Wall | Strada | STRW.02011015/DBE | 20 | 110 | 15 | 17 | 1699 | 1699 | 1699 | 0.040452 | 850 | 0.020238 | 1869 | 0.0445 | 1 | A09 | STRW0.02011015/DBE
Horizontal Wall | Strada | STRW.02011020 | 20 | 110 | 20 | 22 | 1685 | 1685 | 1685 | 0.040119 | 635 | 0.015119 | 1928 | 0.045905 | 1.408 | A09 | STRW0.02011020
Horizontal Wall | Strada | STRW.02011020/DBE | 20 | 110 | 20 | 22 | 2185 | 2185 | 2185 | 0.052024 | 1093 | 0.026024 | 2404 | 0.057238 | 1 | A09 | STRW0.02011020/DBE
Horizontal Wall | Strada | STRW.02012006 | 20 | 120 | 06 | 9 | 646 | 646 | 646 | 0.015381 | 243 | 0.0057857 | 739 | 0.017595 | 1.41 | A09 | STRW0.02012006
Horizontal Wall | Strada | STRW.02012010 | 20 | 120 | 10 | 12 | 786 | 786 | 786 | 0.018714 | 296 | 0.0070476 | 899 | 0.021405 | 1.413 | A09 | STRW0.02012010
Horizontal Wall | Strada | STRW.02012010/DBE | 20 | 120 | 10 | 12 | 1086 | 1086 | 1086 | 0.025857 | 543 | 0.012929 | 1195 | 0.028452 | 1 | A09 | STRW0.02012010/DBE
Horizontal Wall | Strada | STRW.02012015 | 20 | 120 | 15 | 17 | 1308 | 1308 | 1308 | 0.031143 | 493 | 0.011738 | 1496 | 0.035619 | 1.408 | A09 | STRW0.02012015
Horizontal Wall | Strada | STRW.02012015/DBE | 20 | 120 | 15 | 17 | 1808 | 1808 | 1808 | 0.043048 | 904 | 0.021524 | 1989 | 0.047357 | 1 | A09 | STRW0.02012015/DBE
Horizontal Wall | Strada | STRW.02012020 | 20 | 120 | 20 | 22 | 1838 | 1838 | 1838 | 0.043762 | 693 | 0.0165 | 2103 | 0.050071 | 1.408 | A09 | STRW0.02012020
Horizontal Wall | Strada | STRW.02012020/DBE | 20 | 120 | 20 | 22 | 2338 | 2338 | 2338 | 0.055667 | 1169 | 0.027833 | 2572 | 0.061238 | 1 | A09 | STRW0.02012020/DBE
Horizontal Wall | Strada | STRW.02014006 | 20 | 140 | 06 | 9 | 753 | 753 | 753 | 0.017929 | 283 | 0.0067381 | 861 | 0.0205 | 1.41 | A09 | STRW0.02014006
Horizontal Wall | Strada | STRW.02014010 | 20 | 140 | 10 | 12 | 917 | 917 | 917 | 0.021833 | 345 | 0.0082143 | 1049 | 0.024976 | 1.413 | A09 | STRW0.02014010
Horizontal Wall | Strada | STRW.02014010/DBE | 20 | 140 | 10 | 12 | 1217 | 1217 | 1217 | 0.028976 | 609 | 0.0145 | 1339 | 0.031881 | 1 | A09 | STRW0.02014010/DBE
Horizontal Wall | Strada | STRW.02014015 | 20 | 140 | 15 | 17 | 1526 | 1526 | 1526 | 0.036333 | 575 | 0.01369 | 1746 | 0.041571 | 1.408 | A09 | STRW0.02014015
Horizontal Wall | Strada | STRW.02014015/DBE | 20 | 140 | 15 | 17 | 2026 | 2026 | 2026 | 0.048238 | 1013 | 0.024119 | 2229 | 0.053071 | 1 | A09 | STRW0.02014015/DBE
Horizontal Wall | Strada | STRW.02014020 | 20 | 140 | 20 | 22 | 2145 | 2145 | 2145 | 0.051071 | 809 | 0.019262 | 2454 | 0.058429 | 1.408 | A09 | STRW0.02014020
Horizontal Wall | Strada | STRW.02014020/DBE | 20 | 140 | 20 | 22 | 2645 | 2645 | 2645 | 0.062976 | 1323 | 0.0315 | 2910 | 0.069286 | 1 | A09 | STRW0.02014020/DBE
Horizontal Wall | Strada | STRW.02016006 | 20 | 160 | 06 | 9 | 861 | 861 | 861 | 0.0205 | 324 | 0.0077143 | 985 | 0.023452 | 1.41 | A09 | STRW0.02016006
Horizontal Wall | Strada | STRW.02016010 | 20 | 160 | 10 | 12 | 1048 | 1048 | 1048 | 0.024952 | 394 | 0.009381 | 1199 | 0.028548 | 1.413 | A09 | STRW0.02016010
Horizontal Wall | Strada | STRW.02016010/DBE | 20 | 160 | 10 | 12 | 1648 | 1648 | 1648 | 0.039238 | 824 | 0.019619 | 1813 | 0.043167 | 1 | A09 | STRW0.02016010/DBE
Horizontal Wall | Strada | STRW.02016015 | 20 | 160 | 15 | 17 | 1744 | 1744 | 1744 | 0.041524 | 657 | 0.015643 | 1995 | 0.0475 | 1.408 | A09 | STRW0.02016015
Horizontal Wall | Strada | STRW.02016015/DBE | 20 | 160 | 15 | 17 | 2744 | 2744 | 2744 | 0.065333 | 1372 | 0.032667 | 3018 | 0.071857 | 1 | A09 | STRW0.02016015/DBE
Horizontal Wall | Strada | STRW.02016020 | 20 | 160 | 20 | 22 | 2451 | 2451 | 2451 | 0.058357 | 924 | 0.022 | 2804 | 0.066762 | 1.408 | A09 | STRW0.02016020
Horizontal Wall | Strada | STRW.02016020/DBE | 20 | 160 | 20 | 22 | 3451 | 3451 | 3451 | 0.082167 | 1726 | 0.041095 | 3796 | 0.090381 | 1 | A09 | STRW0.02016020/DBE
Horizontal Wall | Strada | STRW.02018006 | 20 | 180 | 06 | 9 | 968 | 968 | 968 | 0.023048 | 364 | 0.0086667 | 1107 | 0.026357 | 1.41 | A09 | STRW0.02018006
Horizontal Wall | Strada | STRW.02018010 | 20 | 180 | 10 | 12 | 1179 | 1179 | 1179 | 0.028071 | 443 | 0.010548 | 1349 | 0.032119 | 1.413 | A09 | STRW0.02018010
Horizontal Wall | Strada | STRW.02018010/DBE | 20 | 180 | 10 | 12 | 1779 | 1779 | 1779 | 0.042357 | 890 | 0.02119 | 1957 | 0.046595 | 1 | A09 | STRW0.02018010/DBE
Horizontal Wall | Strada | STRW.02018015 | 20 | 180 | 15 | 17 | 1962 | 1962 | 1962 | 0.046714 | 740 | 0.017619 | 2245 | 0.053452 | 1.408 | A09 | STRW0.02018015
Horizontal Wall | Strada | STRW.02018015/DBE | 20 | 180 | 15 | 17 | 2962 | 2962 | 2962 | 0.070524 | 1481 | 0.035262 | 3258 | 0.077571 | 1 | A09 | STRW0.02018015/DBE
Horizontal Wall | Strada | STRW.02018020 | 20 | 180 | 20 | 22 | 2758 | 2758 | 2758 | 0.065667 | 1040 | 0.024762 | 3155 | 0.075119 | 1.408 | A09 | STRW0.02018020
Horizontal Wall | Strada | STRW.02018020/DBE | 20 | 180 | 20 | 22 | 3758 | 3758 | 3758 | 0.089476 | 1879 | 0.044738 | 4134 | 0.098429 | 1 | A09 | STRW0.02018020/DBE
Horizontal Wall | Strada | STRW.02020006 | 20 | 200 | 06 | 9 | 1076 | 1076 | 1076 | 0.025619 | 405 | 0.0096429 | 1231 | 0.02931 | 1.41 | A09 | STRW0.02020006
Horizontal Wall | Strada | STRW.02020010 | 20 | 200 | 10 | 12 | 1310 | 1310 | 1310 | 0.03119 | 493 | 0.011738 | 1499 | 0.03569 | 1.413 | A09 | STRW0.02020010
Horizontal Wall | Strada | STRW.02020010/DBE | 20 | 200 | 10 | 12 | 1910 | 1910 | 1910 | 0.045476 | 955 | 0.022738 | 2101 | 0.050024 | 1 | A09 | STRW0.02020010/DBE
Horizontal Wall | Strada | STRW.02020015 | 20 | 200 | 15 | 17 | 2180 | 2180 | 2180 | 0.051905 | 822 | 0.019571 | 2494 | 0.059381 | 1.408 | A09 | STRW0.02020015
Horizontal Wall | Strada | STRW.02020015/DBE | 20 | 200 | 15 | 17 | 3180 | 3180 | 3180 | 0.075714 | 1590 | 0.037857 | 3498 | 0.083286 | 1 | A09 | STRW0.02020015/DBE
Horizontal Wall | Strada | STRW.02020020 | 20 | 200 | 20 | 22 | 3064 | 3064 | 3064 | 0.072952 | 1155 | 0.0275 | 3505 | 0.083452 | 1.408 | A09 | STRW0.02020020
Horizontal Wall | Strada | STRW.02020020/DBE | 20 | 200 | 20 | 22 | 4064 | 4064 | 4064 | 0.096762 | 2032 | 0.048381 | 4470 | 0.10643 | 1 | A09 | STRW0.02020020/DBE
Horizontal Wall | Strada | STRW.02024006 | 20 | 240 | 06 | 9 | 1291 | 1291 | 1291 | 0.030738 | 485 | 0.011548 | 1477 | 0.035167 | 1.41 | A09 | STRW0.02024006
Horizontal Wall | Strada | STRW.02024010 | 20 | 240 | 10 | 12 | 1572 | 1572 | 1572 | 0.037429 | 591 | 0.014071 | 1798 | 0.04281 | 1.413 | A09 | STRW0.02024010
Horizontal Wall | Strada | STRW.02024010/DBE | 20 | 240 | 10 | 12 | 2472 | 2472 | 2472 | 0.058857 | 1236 | 0.029429 | 2719 | 0.064738 | 1 | A09 | STRW0.02024010/DBE
Horizontal Wall | Strada | STRW.02024015 | 20 | 240 | 15 | 17 | 2616 | 2616 | 2616 | 0.062286 | 986 | 0.023476 | 2993 | 0.071262 | 1.408 | A09 | STRW0.02024015
Horizontal Wall | Strada | STRW.02024015/DBE | 20 | 240 | 15 | 17 | 4116 | 4116 | 4116 | 0.098 | 2058 | 0.049 | 4528 | 0.10781 | 1 | A09 | STRW0.02024015/DBE
Horizontal Wall | Strada | STRW.02024020 | 20 | 240 | 20 | 22 | 3677 | 3677 | 3677 | 0.087548 | 1386 | 0.033 | 4206 | 0.10014 | 1.408 | A09 | STRW0.02024020
Horizontal Wall | Strada | STRW.02024020/DBE | 20 | 240 | 20 | 22 | 5177 | 5177 | 5177 | 0.12326 | 2589 | 0.061643 | 5695 | 0.1356 | 1 | A09 | STRW0.02024020/DBE
Horizontal Wall | Strada | STRW.02028006 | 20 | 280 | 06 | 9 | 1506 | 1506 | 1506 | 0.035857 | 566 | 0.013476 | 1723 | 0.041024 | 1.41 | A09 | STRW0.02028006
Horizontal Wall | Strada | STRW.02028010 | 20 | 280 | 10 | 12 | 1834 | 1834 | 1834 | 0.043667 | 690 | 0.016429 | 2098 | 0.049952 | 1.413 | A09 | STRW0.02028010
Horizontal Wall | Strada | STRW.02028010/DBE | 20 | 280 | 10 | 12 | 2734 | 2734 | 2734 | 0.065095 | 1367 | 0.032548 | 3007 | 0.071595 | 1 | A09 | STRW0.02028010/DBE
Horizontal Wall | Strada | STRW.02028015 | 20 | 280 | 15 | 17 | 3052 | 3052 | 3052 | 0.072667 | 1151 | 0.027405 | 3491 | 0.083119 | 1.408 | A09 | STRW0.02028015
Horizontal Wall | Strada | STRW.02028015/DBE | 20 | 280 | 15 | 17 | 4552 | 4552 | 4552 | 0.10838 | 2276 | 0.05419 | 5007 | 0.11921 | 1 | A09 | STRW0.02028015/DBE
Horizontal Wall | Strada | STRW.02028020 | 20 | 280 | 20 | 22 | 4290 | 4290 | 4290 | 0.10214 | 1617 | 0.0385 | 4908 | 0.11686 | 1.408 | A09 | STRW0.02028020
Horizontal Wall | Strada | STRW.02028020/DBE | 20 | 280 | 20 | 22 | 5790 | 5790 | 5790 | 0.13786 | 2895 | 0.068929 | 6369 | 0.15164 | 1 | A09 | STRW0.02028020/DBE
Horizontal Wall | Strada | STRW.03505006 | 35 | 50 | 06 | 9 | 395 | 395 | 395 | 0.0094048 | 150 | 0.0035714 | 451 | 0.010738 | 1.393 | A09 | STRW0.03505006
Horizontal Wall | Strada | STRW.03505010 | 35 | 50 | 10 | 12 | 449 | 449 | 449 | 0.01069 | 170 | 0.0040476 | 513 | 0.012214 | 1.399 | A09 | STRW0.03505010
Horizontal Wall | Strada | STRW.03505011 | 35 | 50 | 11 | 12 | 598 | 598 | 598 | 0.014238 | 221 | 0.0052619 | 686 | 0.016333 | 1.44 | A09 | STRW0.03505011
Horizontal Wall | Strada | STRW.03505015 | 35 | 50 | 15 | 17 | 735 | 735 | 735 | 0.0175 | 281 | 0.0066905 | 839 | 0.019976 | 1.39 | A09 | STRW0.03505015
Horizontal Wall | Strada | STRW.03505016 | 35 | 50 | 16 | 17 | 797 | 797 | 797 | 0.018976 | 290 | 0.0069048 | 916 | 0.02181 | 1.458 | A09 | STRW0.03505016
Horizontal Wall | Strada | STRW.03505020 | 35 | 50 | 20 | 22 | 1030 | 1030 | 1030 | 0.024524 | 393 | 0.0093571 | 1176 | 0.028 | 1.39 | A09 | STRW0.03505020
Horizontal Wall | Strada | STRW.03505021 | 35 | 50 | 21 | 22 | 1057 | 1057 | 1057 | 0.025167 | 381 | 0.0090714 | 1217 | 0.028976 | 1.472 | A09 | STRW0.03505021
Horizontal Wall | Strada | STRW.03506006 | 35 | 60 | 06 | 9 | 474 | 474 | 474 | 0.011286 | 181 | 0.0043095 | 541 | 0.012881 | 1.393 | A09 | STRW0.03506006
Horizontal Wall | Strada | STRW.03506010 | 35 | 60 | 10 | 12 | 539 | 539 | 539 | 0.012833 | 204 | 0.0048571 | 616 | 0.014667 | 1.399 | A09 | STRW0.03506010
Horizontal Wall | Strada | STRW.03506010/DBE | 35 | 60 | 10 | #N/A | 689 | 689 | 689 | 0.016405 | 345 | 0.0082143 | 758 | 0.018048 | 1 | A09 | STRW0.03506010/DBE
Horizontal Wall | Strada | STRW.03506011 | 35 | 60 | 11 | 12 | 718 | 718 | 718 | 0.017095 | 265 | 0.0063095 | 824 | 0.019619 | 1.44 | A09 | STRW0.03506011
Horizontal Wall | Strada | STRW.03506011/DBE | 35 | 60 | 11 | 12 | 1018 | 1018 | 1018 | 0.024238 | 509 | 0.012119 | 1120 | 0.026667 | 1 | A09 | STRW0.03506011/DBE
Horizontal Wall | Strada | STRW.03506015 | 35 | 60 | 15 | 17 | 882 | 882 | 882 | 0.021 | 337 | 0.0080238 | 1007 | 0.023976 | 1.39 | A09 | STRW0.03506015
Horizontal Wall | Strada | STRW.03506015/DBE | 35 | 60 | 15 | #N/A | 1132 | 1132 | 1132 | 0.026952 | 566 | 0.013476 | 1245 | 0.029643 | 1 | A09 | STRW0.03506015/DBE
Horizontal Wall | Strada | STRW.03506016 | 35 | 60 | 16 | 17 | 956 | 956 | 956 | 0.022762 | 348 | 0.0082857 | 1098 | 0.026143 | 1.458 | A09 | STRW0.03506016
Horizontal Wall | Strada | STRW.03506016/DBE | 35 | 60 | 16 | 17 | 1436 | 1436 | 1436 | 0.03419 | 718 | 0.017095 | 1580 | 0.037619 | 1 | A09 | STRW0.03506016/DBE
Horizontal Wall | Strada | STRW.03506020 | 35 | 60 | 20 | 22 | 1236 | 1236 | 1236 | 0.029429 | 472 | 0.011238 | 1412 | 0.033619 | 1.39 | A09 | STRW0.03506020
Horizontal Wall | Strada | STRW.03506020/DBE | 35 | 60 | 20 | #N/A | 1486 | 1486 | 1486 | 0.035381 | 743 | 0.01769 | 1635 | 0.038929 | 1 | A09 | STRW0.03506020/DBE
Horizontal Wall | Strada | STRW.03506021 | 35 | 60 | 21 | 22 | 1268 | 1268 | 1268 | 0.03019 | 456 | 0.010857 | 1459 | 0.034738 | 1.472 | A09 | STRW0.03506021
Horizontal Wall | Strada | STRW.03506021/DBE | 35 | 60 | 21 | 22 | 1748 | 1748 | 1748 | 0.041619 | 874 | 0.02081 | 1923 | 0.045786 | 1 | A09 | STRW0.03506021/DBE
Horizontal Wall | Strada | STRW.03507006 | 35 | 70 | 06 | 9 | 553 | 553 | 553 | 0.013167 | 211 | 0.0050238 | 632 | 0.015048 | 1.393 | A09 | STRW0.03507006
Horizontal Wall | Strada | STRW.03507010 | 35 | 70 | 10 | 12 | 629 | 629 | 629 | 0.014976 | 238 | 0.0056667 | 719 | 0.017119 | 1.399 | A09 | STRW0.03507010
Horizontal Wall | Strada | STRW.03507010/DBE | 35 | 70 | 10 | #N/A | 779 | 779 | 779 | 0.018548 | 390 | 0.0092857 | 857 | 0.020405 | 1 | A09 | STRW0.03507010/DBE
Horizontal Wall | Strada | STRW.03507011 | 35 | 70 | 11 | 12 | 837 | 837 | 837 | 0.019929 | 309 | 0.0073571 | 960 | 0.022857 | 1.44 | A09 | STRW0.03507011
Horizontal Wall | Strada | STRW.03507011/DBE | 35 | 70 | 11 | 12 | 1137 | 1137 | 1137 | 0.027071 | 569 | 0.013548 | 1251 | 0.029786 | 1 | A09 | STRW0.03507011/DBE
Horizontal Wall | Strada | STRW.03507015 | 35 | 70 | 15 | 17 | 1029 | 1029 | 1029 | 0.0245 | 393 | 0.0093571 | 1175 | 0.027976 | 1.39 | A09 | STRW0.03507015
Horizontal Wall | Strada | STRW.03507015/DBE | 35 | 70 | 15 | #N/A | 1279 | 1279 | 1279 | 0.030452 | 640 | 0.015238 | 1407 | 0.0335 | 1 | A09 | STRW0.03507015/DBE
Horizontal Wall | Strada | STRW.03507016 | 35 | 70 | 16 | 17 | 1115 | 1115 | 1115 | 0.026548 | 406 | 0.0096667 | 1281 | 0.0305 | 1.458 | A09 | STRW0.03507016
Horizontal Wall | Strada | STRW.03507016/DBE | 35 | 70 | 16 | 17 | 1595 | 1595 | 1595 | 0.037976 | 798 | 0.019 | 1755 | 0.041786 | 1 | A09 | STRW0.03507016/DBE
Horizontal Wall | Strada | STRW.03507020 | 35 | 70 | 20 | 22 | 1442 | 1442 | 1442 | 0.034333 | 551 | 0.013119 | 1647 | 0.039214 | 1.39 | A09 | STRW0.03507020
Horizontal Wall | Strada | STRW.03507020/DBE | 35 | 70 | 20 | #N/A | 1692 | 1692 | 1692 | 0.040286 | 846 | 0.020143 | 1861 | 0.04431 | 1 | A09 | STRW0.03507020/DBE
Horizontal Wall | Strada | STRW.03507021 | 35 | 70 | 21 | 22 | 1480 | 1480 | 1480 | 0.035238 | 533 | 0.01269 | 1703 | 0.040548 | 1.472 | A09 | STRW0.03507021
Horizontal Wall | Strada | STRW.03507021/DBE | 35 | 70 | 21 | 22 | 1960 | 1960 | 1960 | 0.046667 | 980 | 0.023333 | 2156 | 0.051333 | 1 | A09 | STRW0.03507021/DBE
Horizontal Wall | Strada | STRW.03508006 | 35 | 80 | 06 | 9 | 632 | 632 | 632 | 0.015048 | 241 | 0.0057381 | 722 | 0.01719 | 1.393 | A09 | STRW0.03508006
Horizontal Wall | Strada | STRW.03508010 | 35 | 80 | 10 | 12 | 718 | 718 | 718 | 0.017095 | 272 | 0.0064762 | 821 | 0.019548 | 1.399 | A09 | STRW0.03508010
Horizontal Wall | Strada | STRW.03508010/DBE | 35 | 80 | 10 | #N/A | 868 | 868 | 868 | 0.020667 | 434 | 0.010333 | 955 | 0.022738 | 1 | A09 | STRW0.03508010/DBE
Horizontal Wall | Strada | STRW.03508011 | 35 | 80 | 11 | 12 | 957 | 957 | 957 | 0.022786 | 353 | 0.0084048 | 1098 | 0.026143 | 1.44 | A09 | STRW0.03508011
Horizontal Wall | Strada | STRW.03508011/DBE | 35 | 80 | 11 | 12 | 1257 | 1257 | 1257 | 0.029929 | 629 | 0.014976 | 1383 | 0.032929 | 1 | A09 | STRW0.03508011/DBE
Horizontal Wall | Strada | STRW.03508015 | 35 | 80 | 15 | 17 | 1176 | 1176 | 1176 | 0.028 | 449 | 0.01069 | 1343 | 0.031976 | 1.39 | A09 | STRW0.03508015
Horizontal Wall | Strada | STRW.03508015/DBE | 35 | 80 | 15 | #N/A | 1426 | 1426 | 1426 | 0.033952 | 713 | 0.016976 | 1569 | 0.037357 | 1 | A09 | STRW0.03508015/DBE
Horizontal Wall | Strada | STRW.03508016 | 35 | 80 | 16 | 17 | 1274 | 1274 | 1274 | 0.030333 | 464 | 0.011048 | 1464 | 0.034857 | 1.458 | A09 | STRW0.03508016
Horizontal Wall | Strada | STRW.03508016/DBE | 35 | 80 | 16 | 17 | 1754 | 1754 | 1754 | 0.041762 | 877 | 0.020881 | 1929 | 0.045929 | 1 | A09 | STRW0.03508016/DBE
Horizontal Wall | Strada | STRW.03508020 | 35 | 80 | 20 | 22 | 1648 | 1648 | 1648 | 0.039238 | 630 | 0.015 | 1882 | 0.04481 | 1.39 | A09 | STRW0.03508020
Horizontal Wall | Strada | STRW.03508020/DBE | 35 | 80 | 20 | #N/A | 1898 | 1898 | 1898 | 0.04519 | 949 | 0.022595 | 2088 | 0.049714 | 1 | A09 | STRW0.03508020/DBE
Horizontal Wall | Strada | STRW.03508021 | 35 | 80 | 21 | 22 | 1691 | 1691 | 1691 | 0.040262 | 609 | 0.0145 | 1946 | 0.046333 | 1.472 | A09 | STRW0.03508021
Horizontal Wall | Strada | STRW.03508021/DBE | 35 | 80 | 21 | 22 | 2171 | 2171 | 2171 | 0.05169 | 1086 | 0.025857 | 2388 | 0.056857 | 1 | A09 | STRW0.03508021/DBE
Horizontal Wall | Strada | STRW.03509006 | 35 | 90 | 06 | 9 | 711 | 711 | 711 | 0.016929 | 271 | 0.0064524 | 812 | 0.019333 | 1.393 | A09 | STRW0.03509006
Horizontal Wall | Strada | STRW.03509010 | 35 | 90 | 10 | 12 | 808 | 808 | 808 | 0.019238 | 306 | 0.0072857 | 924 | 0.022 | 1.399 | A09 | STRW0.03509010
Horizontal Wall | Strada | STRW.03509010/DBE | 35 | 90 | 10 | #N/A | 1108 | 1108 | 1108 | 0.026381 | 554 | 0.01319 | 1219 | 0.029024 | 1 | A09 | STRW0.03509010/DBE
Horizontal Wall | Strada | STRW.03509011 | 35 | 90 | 11 | 12 | 1076 | 1076 | 1076 | 0.025619 | 397 | 0.0094524 | 1234 | 0.029381 | 1.44 | A09 | STRW0.03509011
Horizontal Wall | Strada | STRW.03509011/DBE | 35 | 90 | 11 | 12 | 1676 | 1676 | 1676 | 0.039905 | 838 | 0.019952 | 1844 | 0.043905 | 1 | A09 | STRW0.03509011/DBE
Horizontal Wall | Strada | STRW.03509015 | 35 | 90 | 15 | 17 | 1323 | 1323 | 1323 | 0.0315 | 505 | 0.012024 | 1511 | 0.035976 | 1.39 | A09 | STRW0.03509015
Horizontal Wall | Strada | STRW.03509015/DBE | 35 | 90 | 15 | #N/A | 1823 | 1823 | 1823 | 0.043405 | 912 | 0.021714 | 2005 | 0.047738 | 1 | A09 | STRW0.03509015/DBE
Horizontal Wall | Strada | STRW.03509016 | 35 | 90 | 16 | 17 | 1434 | 1434 | 1434 | 0.034143 | 522 | 0.012429 | 1648 | 0.039238 | 1.458 | A09 | STRW0.03509016
Horizontal Wall | Strada | STRW.03509016/DBE | 35 | 90 | 16 | 17 | 2394 | 2394 | 2394 | 0.057 | 1197 | 0.0285 | 2633 | 0.06269 | 1 | A09 | STRW0.03509016/DBE
Horizontal Wall | Strada | STRW.03509020 | 35 | 90 | 20 | 22 | 1854 | 1854 | 1854 | 0.044143 | 708 | 0.016857 | 2117 | 0.050405 | 1.39 | A09 | STRW0.03509020
Horizontal Wall | Strada | STRW.03509020/DBE | 35 | 90 | 20 | #N/A | 2354 | 2354 | 2354 | 0.056048 | 1177 | 0.028024 | 2589 | 0.061643 | 1 | A09 | STRW0.03509020/DBE
Horizontal Wall | Strada | STRW.03509021 | 35 | 90 | 21 | 22 | 1903 | 1903 | 1903 | 0.04531 | 685 | 0.01631 | 2190 | 0.052143 | 1.472 | A09 | STRW0.03509021
Horizontal Wall | Strada | STRW.03509021/DBE | 35 | 90 | 21 | 22 | 2863 | 2863 | 2863 | 0.068167 | 1432 | 0.034095 | 3149 | 0.074976 | 1 | A09 | STRW0.03509021/DBE
Horizontal Wall | Strada | STRW.03510006 | 35 | 100 | 06 | 9 | 790 | 790 | 790 | 0.01881 | 301 | 0.0071667 | 902 | 0.021476 | 1.393 | A09 | STRW0.03510006
Horizontal Wall | Strada | STRW.03510010 | 35 | 100 | 10 | 12 | 898 | 898 | 898 | 0.021381 | 340 | 0.0080952 | 1026 | 0.024429 | 1.399 | A09 | STRW0.03510010
Horizontal Wall | Strada | STRW.03510010/DBE | 35 | 100 | 10 | #N/A | 1198 | 1198 | 1198 | 0.028524 | 599 | 0.014262 | 1318 | 0.031381 | 1 | A09 | STRW0.03510010/DBE
Horizontal Wall | Strada | STRW.03510011 | 35 | 100 | 11 | 12 | 1196 | 1196 | 1196 | 0.028476 | 441 | 0.0105 | 1372 | 0.032667 | 1.44 | A09 | STRW0.03510011
Horizontal Wall | Strada | STRW.03510011/DBE | 35 | 100 | 11 | 12 | 1796 | 1796 | 1796 | 0.042762 | 898 | 0.021381 | 1976 | 0.047048 | 1 | A09 | STRW0.03510011/DBE
Horizontal Wall | Strada | STRW.03510015 | 35 | 100 | 15 | 17 | 1470 | 1470 | 1470 | 0.035 | 562 | 0.013381 | 1679 | 0.039976 | 1.39 | A09 | STRW0.03510015
Horizontal Wall | Strada | STRW.03510015/DBE | 35 | 100 | 15 | #N/A | 1970 | 1970 | 1970 | 0.046905 | 985 | 0.023452 | 2167 | 0.051595 | 1 | A09 | STRW0.03510015/DBE
Horizontal Wall | Strada | STRW.03510016 | 35 | 100 | 16 | 17 | 1593 | 1593 | 1593 | 0.037929 | 580 | 0.01381 | 1830 | 0.043571 | 1.458 | A09 | STRW0.03510016
Horizontal Wall | Strada | STRW.03510016/DBE | 35 | 100 | 16 | 17 | 2553 | 2553 | 2553 | 0.060786 | 1277 | 0.030405 | 2808 | 0.066857 | 1 | A09 | STRW0.03510016/DBE
Horizontal Wall | Strada | STRW.03510020 | 35 | 100 | 20 | 22 | 2060 | 2060 | 2060 | 0.049048 | 787 | 0.018738 | 2353 | 0.056024 | 1.39 | A09 | STRW0.03510020
Horizontal Wall | Strada | STRW.03510020/DBE | 35 | 100 | 20 | #N/A | 2560 | 2560 | 2560 | 0.060952 | 1280 | 0.030476 | 2816 | 0.067048 | 1 | A09 | STRW0.03510020/DBE
Horizontal Wall | Strada | STRW.03510021 | 35 | 100 | 21 | 22 | 2114 | 2114 | 2114 | 0.050333 | 761 | 0.018119 | 2433 | 0.057929 | 1.472 | A09 | STRW0.03510021
Horizontal Wall | Strada | STRW.03510021/DBE | 35 | 100 | 21 | 22 | 3074 | 3074 | 3074 | 0.07319 | 1537 | 0.036595 | 3381 | 0.0805 | 1 | A09 | STRW0.03510021/DBE
Horizontal Wall | Strada | STRW.03511006 | 35 | 110 | 06 | 9 | 869 | 869 | 869 | 0.02069 | 331 | 0.007881 | 992 | 0.023619 | 1.393 | A09 | STRW0.03511006
Horizontal Wall | Strada | STRW.03511010 | 35 | 110 | 10 | 12 | 988 | 988 | 988 | 0.023524 | 374 | 0.0089048 | 1129 | 0.026881 | 1.399 | A09 | STRW0.03511010
Horizontal Wall | Strada | STRW.03511010/DBE | 35 | 110 | 10 | #N/A | 1288 | 1288 | 1288 | 0.030667 | 644 | 0.015333 | 1417 | 0.033738 | 1 | A09 | STRW0.03511010/DBE
Horizontal Wall | Strada | STRW.03511011 | 35 | 110 | 11 | 12 | 1316 | 1316 | 1316 | 0.031333 | 486 | 0.011571 | 1509 | 0.035929 | 1.44 | A09 | STRW0.03511011
Horizontal Wall | Strada | STRW.03511011/DBE | 35 | 110 | 11 | 12 | 1916 | 1916 | 1916 | 0.045619 | 958 | 0.02281 | 2108 | 0.05019 | 1 | A09 | STRW0.03511011/DBE
Horizontal Wall | Strada | STRW.03511015 | 35 | 110 | 15 | 17 | 1617 | 1617 | 1617 | 0.0385 | 618 | 0.014714 | 1847 | 0.043976 | 1.39 | A09 | STRW0.03511015
Horizontal Wall | Strada | STRW.03511015/DBE | 35 | 110 | 15 | #N/A | 2117 | 2117 | 2117 | 0.050405 | 1059 | 0.025214 | 2329 | 0.055452 | 1 | A09 | STRW0.03511015/DBE
Horizontal Wall | Strada | STRW.03511016 | 35 | 110 | 16 | 17 | 1752 | 1752 | 1752 | 0.041714 | 638 | 0.01519 | 2013 | 0.047929 | 1.458 | A09 | STRW0.03511016
Horizontal Wall | Strada | STRW.03511016/DBE | 35 | 110 | 16 | 17 | 2712 | 2712 | 2712 | 0.064571 | 1356 | 0.032286 | 2983 | 0.071024 | 1 | A09 | STRW0.03511016/DBE
Horizontal Wall | Strada | STRW.03511020 | 35 | 110 | 20 | 22 | 2266 | 2266 | 2266 | 0.053952 | 866 | 0.020619 | 2588 | 0.061619 | 1.39 | A09 | STRW0.03511020
Horizontal Wall | Strada | STRW.03511020/DBE | 35 | 110 | 20 | #N/A | 2766 | 2766 | 2766 | 0.065857 | 1383 | 0.032929 | 3043 | 0.072452 | 1 | A09 | STRW0.03511020/DBE
Horizontal Wall | Strada | STRW.03511021 | 35 | 110 | 21 | 22 | 2325 | 2325 | 2325 | 0.055357 | 837 | 0.019929 | 2676 | 0.063714 | 1.472 | A09 | STRW0.03511021
Horizontal Wall | Strada | STRW.03511021/DBE | 35 | 110 | 21 | 22 | 3285 | 3285 | 3285 | 0.078214 | 1643 | 0.039119 | 3614 | 0.086048 | 1 | A09 | STRW0.03511021/DBE
Horizontal Wall | Strada | STRW.03512006 | 35 | 120 | 06 | 9 | 948 | 948 | 948 | 0.022571 | 361 | 0.0085952 | 1083 | 0.025786 | 1.393 | A09 | STRW0.03512006
Horizontal Wall | Strada | STRW.03512010 | 35 | 120 | 10 | 12 | 1078 | 1078 | 1078 | 0.025667 | 409 | 0.0097381 | 1232 | 0.029333 | 1.399 | A09 | STRW0.03512010
Horizontal Wall | Strada | STRW.03512010/DBE | 35 | 120 | 10 | #N/A | 1378 | 1378 | 1378 | 0.03281 | 689 | 0.016405 | 1516 | 0.036095 | 1 | A09 | STRW0.03512010/DBE
Horizontal Wall | Strada | STRW.03512011 | 35 | 120 | 11 | 12 | 1435 | 1435 | 1435 | 0.034167 | 530 | 0.012619 | 1646 | 0.03919 | 1.44 | A09 | STRW0.03512011
Horizontal Wall | Strada | STRW.03512011/DBE | 35 | 120 | 11 | 12 | 2035 | 2035 | 2035 | 0.048452 | 1018 | 0.024238 | 2239 | 0.05331 | 1 | A09 | STRW0.03512011/DBE
Horizontal Wall | Strada | STRW.03512015 | 35 | 120 | 15 | 17 | 1764 | 1764 | 1764 | 0.042 | 674 | 0.016048 | 2014 | 0.047952 | 1.39 | A09 | STRW0.03512015
Horizontal Wall | Strada | STRW.03512015/DBE | 35 | 120 | 15 | #N/A | 2264 | 2264 | 2264 | 0.053905 | 1132 | 0.026952 | 2490 | 0.059286 | 1 | A09 | STRW0.03512015/DBE
Horizontal Wall | Strada | STRW.03512016 | 35 | 120 | 16 | 17 | 1912 | 1912 | 1912 | 0.045524 | 696 | 0.016571 | 2197 | 0.05231 | 1.458 | A09 | STRW0.03512016
Horizontal Wall | Strada | STRW.03512016/DBE | 35 | 120 | 16 | 17 | 2872 | 2872 | 2872 | 0.068381 | 1436 | 0.03419 | 3159 | 0.075214 | 1 | A09 | STRW0.03512016/DBE
Horizontal Wall | Strada | STRW.03512020 | 35 | 120 | 20 | 22 | 2472 | 2472 | 2472 | 0.058857 | 944 | 0.022476 | 2823 | 0.067214 | 1.39 | A09 | STRW0.03512020
Horizontal Wall | Strada | STRW.03512020/DBE | 35 | 120 | 20 | #N/A | 2972 | 2972 | 2972 | 0.070762 | 1486 | 0.035381 | 3269 | 0.077833 | 1 | A09 | STRW0.03512020/DBE
Horizontal Wall | Strada | STRW.03512021 | 35 | 120 | 21 | 22 | 2537 | 2537 | 2537 | 0.060405 | 913 | 0.021738 | 2920 | 0.069524 | 1.472 | A09 | STRW0.03512021
Horizontal Wall | Strada | STRW.03512021/DBE | 35 | 120 | 21 | 22 | 3497 | 3497 | 3497 | 0.083262 | 1749 | 0.041643 | 3847 | 0.091595 | 1 | A09 | STRW0.03512021/DBE
Horizontal Wall | Strada | STRW.03514006 | 35 | 140 | 06 | 9 | 1106 | 1106 | 1106 | 0.026333 | 421 | 0.010024 | 1263 | 0.030071 | 1.393 | A09 | STRW0.03514006
Horizontal Wall | Strada | STRW.03514010 | 35 | 140 | 10 | 12 | 1257 | 1257 | 1257 | 0.029929 | 476 | 0.011333 | 1437 | 0.034214 | 1.399 | A09 | STRW0.03514010
Horizontal Wall | Strada | STRW.03514010/DBE | 35 | 140 | 10 | #N/A | 1557 | 1557 | 1557 | 0.037071 | 779 | 0.018548 | 1713 | 0.040786 | 1 | A09 | STRW0.03514010/DBE
Horizontal Wall | Strada | STRW.03514011 | 35 | 140 | 11 | 12 | 1674 | 1674 | 1674 | 0.039857 | 618 | 0.014714 | 1920 | 0.045714 | 1.44 | A09 | STRW0.03514011
Horizontal Wall | Strada | STRW.03514011/DBE | 35 | 140 | 11 | 12 | 2274 | 2274 | 2274 | 0.054143 | 1137 | 0.027071 | 2501 | 0.059548 | 1 | A09 | STRW0.03514011/DBE
Horizontal Wall | Strada | STRW.03514015 | 35 | 140 | 15 | 17 | 2058 | 2058 | 2058 | 0.049 | 786 | 0.018714 | 2350 | 0.055952 | 1.39 | A09 | STRW0.03514015
Horizontal Wall | Strada | STRW.03514015/DBE | 35 | 140 | 15 | #N/A | 2558 | 2558 | 2558 | 0.060905 | 1279 | 0.030452 | 2814 | 0.067 | 1 | A09 | STRW0.03514015/DBE
Horizontal Wall | Strada | STRW.03514016 | 35 | 140 | 16 | 17 | 2230 | 2230 | 2230 | 0.053095 | 812 | 0.019333 | 2562 | 0.061 | 1.458 | A09 | STRW0.03514016
Horizontal Wall | Strada | STRW.03514016/DBE | 35 | 140 | 16 | 17 | 3190 | 3190 | 3190 | 0.075952 | 1595 | 0.037976 | 3509 | 0.083548 | 1 | A09 | STRW0.03514016/DBE
Horizontal Wall | Strada | STRW.03514020 | 35 | 140 | 20 | 22 | 2884 | 2884 | 2884 | 0.068667 | 1102 | 0.026238 | 3294 | 0.078429 | 1.39 | A09 | STRW0.03514020
Horizontal Wall | Strada | STRW.03514020/DBE | 35 | 140 | 20 | #N/A | 3384 | 3384 | 3384 | 0.080571 | 1692 | 0.040286 | 3722 | 0.088619 | 1 | A09 | STRW0.03514020/DBE
Horizontal Wall | Strada | STRW.03514021 | 35 | 140 | 21 | 22 | 2960 | 2960 | 2960 | 0.070476 | 1066 | 0.025381 | 3407 | 0.081119 | 1.472 | A09 | STRW0.03514021
Horizontal Wall | Strada | STRW.03514021/DBE | 35 | 140 | 21 | 22 | 3920 | 3920 | 3920 | 0.093333 | 1960 | 0.046667 | 4312 | 0.10267 | 1 | A09 | STRW0.03514021/DBE
Horizontal Wall | Strada | STRW.03516006 | 35 | 160 | 06 | 9 | 1264 | 1264 | 1264 | 0.030095 | 482 | 0.011476 | 1443 | 0.034357 | 1.393 | A09 | STRW0.03516006
Horizontal Wall | Strada | STRW.03516010 | 35 | 160 | 10 | 12 | 1437 | 1437 | 1437 | 0.034214 | 545 | 0.012976 | 1642 | 0.039095 | 1.399 | A09 | STRW0.03516010
Horizontal Wall | Strada | STRW.03516010/DBE | 35 | 160 | 10 | #N/A | 2037 | 2037 | 2037 | 0.0485 | 1019 | 0.024262 | 2241 | 0.053357 | 1 | A09 | STRW0.03516010/DBE
Horizontal Wall | Strada | STRW.03516011 | 35 | 160 | 11 | 12 | 1914 | 1914 | 1914 | 0.045571 | 706 | 0.01681 | 2195 | 0.052262 | 1.44 | A09 | STRW0.03516011
Horizontal Wall | Strada | STRW.03516011/DBE | 35 | 160 | 11 | 12 | 3114 | 3114 | 3114 | 0.074143 | 1557 | 0.037071 | 3425 | 0.081548 | 1 | A09 | STRW0.03516011/DBE
Horizontal Wall | Strada | STRW.03516015 | 35 | 160 | 15 | 17 | 2352 | 2352 | 2352 | 0.056 | 898 | 0.021381 | 2686 | 0.063952 | 1.39 | A09 | STRW0.03516015
Horizontal Wall | Strada | STRW.03516015/DBE | 35 | 160 | 15 | #N/A | 3352 | 3352 | 3352 | 0.07981 | 1676 | 0.039905 | 3687 | 0.087786 | 1 | A09 | STRW0.03516015/DBE
Horizontal Wall | Strada | STRW.03516016 | 35 | 160 | 16 | 17 | 2549 | 2549 | 2549 | 0.06069 | 928 | 0.022095 | 2929 | 0.069738 | 1.458 | A09 | STRW0.03516016
Horizontal Wall | Strada | STRW.03516016/DBE | 35 | 160 | 16 | 17 | 4469 | 4469 | 4469 | 0.1064 | 2235 | 0.053214 | 4916 | 0.11705 | 1 | A09 | STRW0.03516016/DBE
Horizontal Wall | Strada | STRW.03516020 | 35 | 160 | 20 | 22 | 3296 | 3296 | 3296 | 0.078476 | 1259 | 0.029976 | 3764 | 0.089619 | 1.39 | A09 | STRW0.03516020
Horizontal Wall | Strada | STRW.03516020/DBE | 35 | 160 | 20 | #N/A | 4296 | 4296 | 4296 | 0.10229 | 2148 | 0.051143 | 4726 | 0.11252 | 1 | A09 | STRW0.03516020/DBE
Horizontal Wall | Strada | STRW.03516021 | 35 | 160 | 21 | 22 | 3382 | 3382 | 3382 | 0.080524 | 1218 | 0.029 | 3893 | 0.09269 | 1.472 | A09 | STRW0.03516021
Horizontal Wall | Strada | STRW.03516021/DBE | 35 | 160 | 21 | 22 | 5302 | 5302 | 5302 | 0.12624 | 2651 | 0.063119 | 5832 | 0.13886 | 1 | A09 | STRW0.03516021/DBE
Horizontal Wall | Strada | STRW.03518006 | 35 | 180 | 06 | 9 | 1422 | 1422 | 1422 | 0.033857 | 542 | 0.012905 | 1624 | 0.038667 | 1.393 | A09 | STRW0.03518006
Horizontal Wall | Strada | STRW.03518010 | 35 | 180 | 10 | 12 | 1616 | 1616 | 1616 | 0.038476 | 612 | 0.014571 | 1847 | 0.043976 | 1.399 | A09 | STRW0.03518010
Horizontal Wall | Strada | STRW.03518010/DBE | 35 | 180 | 10 | #N/A | 2216 | 2216 | 2216 | 0.052762 | 1108 | 0.026381 | 2438 | 0.058048 | 1 | A09 | STRW0.03518010/DBE
Horizontal Wall | Strada | STRW.03518011 | 35 | 180 | 11 | 12 | 2153 | 2153 | 2153 | 0.051262 | 794 | 0.018905 | 2469 | 0.058786 | 1.44 | A09 | STRW0.03518011
Horizontal Wall | Strada | STRW.03518011/DBE | 35 | 180 | 11 | 12 | 3353 | 3353 | 3353 | 0.079833 | 1677 | 0.039929 | 3688 | 0.08781 | 1 | A09 | STRW0.03518011/DBE
Horizontal Wall | Strada | STRW.03518015 | 35 | 180 | 15 | 17 | 2646 | 2646 | 2646 | 0.063 | 1011 | 0.024071 | 3022 | 0.071952 | 1.39 | A09 | STRW0.03518015
Horizontal Wall | Strada | STRW.03518015/DBE | 35 | 180 | 15 | #N/A | 3646 | 3646 | 3646 | 0.08681 | 1823 | 0.043405 | 4011 | 0.0955 | 1 | A09 | STRW0.03518015/DBE
Horizontal Wall | Strada | STRW.03518016 | 35 | 180 | 16 | 17 | 2867 | 2867 | 2867 | 0.068262 | 1044 | 0.024857 | 3294 | 0.078429 | 1.458 | A09 | STRW0.03518016
Horizontal Wall | Strada | STRW.03518016/DBE | 35 | 180 | 16 | 17 | 4787 | 4787 | 4787 | 0.11398 | 2394 | 0.057 | 5266 | 0.12538 | 1 | A09 | STRW0.03518016/DBE
Horizontal Wall | Strada | STRW.03518020 | 35 | 180 | 20 | 22 | 3708 | 3708 | 3708 | 0.088286 | 1416 | 0.033714 | 4235 | 0.10083 | 1.39 | A09 | STRW0.03518020
Horizontal Wall | Strada | STRW.03518020/DBE | 35 | 180 | 20 | #N/A | 4708 | 4708 | 4708 | 0.1121 | 2354 | 0.056048 | 5179 | 0.12331 | 1 | A09 | STRW0.03518020/DBE
Horizontal Wall | Strada | STRW.03518021 | 35 | 180 | 21 | 22 | 3805 | 3805 | 3805 | 0.090595 | 1370 | 0.032619 | 4380 | 0.10429 | 1.472 | A09 | STRW0.03518021
Horizontal Wall | Strada | STRW.03518021/DBE | 35 | 180 | 21 | 22 | 5725 | 5725 | 5725 | 0.13631 | 2863 | 0.068167 | 6298 | 0.14995 | 1 | A09 | STRW0.03518021/DBE
Horizontal Wall | Strada | STRW.03520006 | 35 | 200 | 06 | 9 | 1580 | 1580 | 1580 | 0.037619 | 602 | 0.014333 | 1804 | 0.042952 | 1.393 | A09 | STRW0.03520006
Horizontal Wall | Strada | STRW.03520010 | 35 | 200 | 10 | 12 | 1796 | 1796 | 1796 | 0.042762 | 681 | 0.016214 | 2053 | 0.048881 | 1.399 | A09 | STRW0.03520010
Horizontal Wall | Strada | STRW.03520010/DBE | 35 | 200 | 10 | #N/A | 2396 | 2396 | 2396 | 0.057048 | 1198 | 0.028524 | 2636 | 0.062762 | 1 | A09 | STRW0.03520010/DBE
Horizontal Wall | Strada | STRW.03520011 | 35 | 200 | 11 | 12 | 2392 | 2392 | 2392 | 0.056952 | 883 | 0.021024 | 2744 | 0.065333 | 1.44 | A09 | STRW0.03520011
Horizontal Wall | Strada | STRW.03520011/DBE | 35 | 200 | 11 | 12 | 3592 | 3592 | 3592 | 0.085524 | 1796 | 0.042762 | 3951 | 0.094071 | 1 | A09 | STRW0.03520011/DBE
Horizontal Wall | Strada | STRW.03520015 | 35 | 200 | 15 | 17 | 2940 | 2940 | 2940 | 0.07 | 1123 | 0.026738 | 3357 | 0.079929 | 1.39 | A09 | STRW0.03520015
Horizontal Wall | Strada | STRW.03520015/DBE | 35 | 200 | 15 | #N/A | 3940 | 3940 | 3940 | 0.09381 | 1970 | 0.046905 | 4334 | 0.10319 | 1 | A09 | STRW0.03520015/DBE
Horizontal Wall | Strada | STRW.03520016 | 35 | 200 | 16 | 17 | 3186 | 3186 | 3186 | 0.075857 | 1160 | 0.027619 | 3661 | 0.087167 | 1.458 | A09 | STRW0.03520016
Horizontal Wall | Strada | STRW.03520016/DBE | 35 | 200 | 16 | 17 | 5106 | 5106 | 5106 | 0.12157 | 2553 | 0.060786 | 5617 | 0.13374 | 1 | A09 | STRW0.03520016/DBE
Horizontal Wall | Strada | STRW.03520020 | 35 | 200 | 20 | 22 | 4120 | 4120 | 4120 | 0.098095 | 1574 | 0.037476 | 4705 | 0.11202 | 1.39 | A09 | STRW0.03520020
Horizontal Wall | Strada | STRW.03520020/DBE | 35 | 200 | 20 | #N/A | 5120 | 5120 | 5120 | 0.1219 | 2560 | 0.060952 | 5632 | 0.1341 | 1 | A09 | STRW0.03520020/DBE
Horizontal Wall | Strada | STRW.03520021 | 35 | 200 | 21 | 22 | 4228 | 4228 | 4228 | 0.10067 | 1522 | 0.036238 | 4866 | 0.11586 | 1.472 | A09 | STRW0.03520021
Horizontal Wall | Strada | STRW.03520021/DBE | 35 | 200 | 21 | 22 | 6148 | 6148 | 6148 | 0.14638 | 3074 | 0.07319 | 6763 | 0.16102 | 1 | A09 | STRW0.03520021/DBE
Horizontal Wall | Strada | STRW.03524006 | 35 | 240 | 06 | 9 | 1896 | 1896 | 1896 | 0.045143 | 722 | 0.01719 | 2165 | 0.051548 | 1.393 | A09 | STRW0.03524006
Horizontal Wall | Strada | STRW.03524010 | 35 | 240 | 10 | 12 | 2155 | 2155 | 2155 | 0.05131 | 817 | 0.019452 | 2463 | 0.058643 | 1.399 | A09 | STRW0.03524010
Horizontal Wall | Strada | STRW.03524010/DBE | 35 | 240 | 10 | #N/A | 3055 | 3055 | 3055 | 0.072738 | 1528 | 0.036381 | 3361 | 0.080024 | 1 | A09 | STRW0.03524010/DBE
Horizontal Wall | Strada | STRW.03524011 | 35 | 240 | 11 | 12 | 2870 | 2870 | 2870 | 0.068333 | 1059 | 0.025214 | 3292 | 0.078381 | 1.44 | A09 | STRW0.03524011
Horizontal Wall | Strada | STRW.03524011/DBE | 35 | 240 | 11 | 12 | 4670 | 4670 | 4670 | 0.11119 | 2335 | 0.055595 | 5137 | 0.12231 | 1 | A09 | STRW0.03524011/DBE
Horizontal Wall | Strada | STRW.03524015 | 35 | 240 | 15 | 17 | 3528 | 3528 | 3528 | 0.084 | 1348 | 0.032095 | 4029 | 0.095929 | 1.39 | A09 | STRW0.03524015
Horizontal Wall | Strada | STRW.03524015/DBE | 35 | 240 | 15 | #N/A | 5028 | 5028 | 5028 | 0.11971 | 2514 | 0.059857 | 5531 | 0.13169 | 1 | A09 | STRW0.03524015/DBE
Horizontal Wall | Strada | STRW.03524016 | 35 | 240 | 16 | 17 | 3823 | 3823 | 3823 | 0.091024 | 1392 | 0.033143 | 4393 | 0.1046 | 1.458 | A09 | STRW0.03524016
Horizontal Wall | Strada | STRW.03524016/DBE | 35 | 240 | 16 | 17 | 6703 | 6703 | 6703 | 0.1596 | 3352 | 0.07981 | 7373 | 0.17555 | 1 | A09 | STRW0.03524016/DBE
Horizontal Wall | Strada | STRW.03524020 | 35 | 240 | 20 | 22 | 4944 | 4944 | 4944 | 0.11771 | 1889 | 0.044976 | 5646 | 0.13443 | 1.39 | A09 | STRW0.03524020
Horizontal Wall | Strada | STRW.03524020/DBE | 35 | 240 | 20 | #N/A | 6444 | 6444 | 6444 | 0.15343 | 3222 | 0.076714 | 7088 | 0.16876 | 1 | A09 | STRW0.03524020/DBE
Horizontal Wall | Strada | STRW.03524021 | 35 | 240 | 21 | 22 | 5074 | 5074 | 5074 | 0.12081 | 1827 | 0.0435 | 5840 | 0.13905 | 1.472 | A09 | STRW0.03524021
Horizontal Wall | Strada | STRW.03524021/DBE | 35 | 240 | 21 | 22 | 7954 | 7954 | 7954 | 0.18938 | 3977 | 0.09469 | 8749 | 0.20831 | 1 | A09 | STRW0.03524021/DBE
Horizontal Wall | Strada | STRW.03528006 | 35 | 280 | 06 | 9 | 2212 | 2212 | 2212 | 0.052667 | 843 | 0.020071 | 2526 | 0.060143 | 1.393 | A09 | STRW0.03528006
Horizontal Wall | Strada | STRW.03528010 | 35 | 280 | 10 | 12 | 2514 | 2514 | 2514 | 0.059857 | 953 | 0.02269 | 2874 | 0.068429 | 1.399 | A09 | STRW0.03528010
Horizontal Wall | Strada | STRW.03528010/DBE | 35 | 280 | 10 | #N/A | 3414 | 3414 | 3414 | 0.081286 | 1707 | 0.040643 | 3755 | 0.089405 | 1 | A09 | STRW0.03528010/DBE
Horizontal Wall | Strada | STRW.03528011 | 35 | 280 | 11 | 12 | 3349 | 3349 | 3349 | 0.079738 | 1236 | 0.029429 | 3841 | 0.091452 | 1.44 | A09 | STRW0.03528011
Horizontal Wall | Strada | STRW.03528011/DBE | 35 | 280 | 11 | 12 | 5149 | 5149 | 5149 | 0.1226 | 2575 | 0.06131 | 5664 | 0.13486 | 1 | A09 | STRW0.03528011/DBE
Horizontal Wall | Strada | STRW.03528015 | 35 | 280 | 15 | 17 | 4116 | 4116 | 4116 | 0.098 | 1572 | 0.037429 | 4700 | 0.1119 | 1.39 | A09 | STRW0.03528015
Horizontal Wall | Strada | STRW.03528015/DBE | 35 | 280 | 15 | #N/A | 5616 | 5616 | 5616 | 0.13371 | 2808 | 0.066857 | 6178 | 0.1471 | 1 | A09 | STRW0.03528015/DBE
Horizontal Wall | Strada | STRW.03528016 | 35 | 280 | 16 | 17 | 4460 | 4460 | 4460 | 0.10619 | 1623 | 0.038643 | 5125 | 0.12202 | 1.458 | A09 | STRW0.03528016
Horizontal Wall | Strada | STRW.03528016/DBE | 35 | 280 | 16 | 17 | 7340 | 7340 | 7340 | 0.17476 | 3670 | 0.087381 | 8074 | 0.19224 | 1 | A09 | STRW0.03528016/DBE
Horizontal Wall | Strada | STRW.03528020 | 35 | 280 | 20 | 22 | 5768 | 5768 | 5768 | 0.13733 | 2203 | 0.052452 | 6587 | 0.15683 | 1.39 | A09 | STRW0.03528020
Horizontal Wall | Strada | STRW.03528020/DBE | 35 | 280 | 20 | #N/A | 7268 | 7268 | 7268 | 0.17305 | 3634 | 0.086524 | 7995 | 0.19036 | 1 | A09 | STRW0.03528020/DBE
Horizontal Wall | Strada | STRW.03528021 | 35 | 280 | 21 | 22 | 5919 | 5919 | 5919 | 0.14093 | 2131 | 0.050738 | 6813 | 0.16221 | 1.472 | A09 | STRW0.03528021
Horizontal Wall | Strada | STRW.03528021/DBE | 35 | 280 | 21 | 22 | 8799 | 8799 | 8799 | 0.2095 | 4400 | 0.10476 | 9679 | 0.23045 | 1 | A09 | STRW0.03528021/DBE
Horizontal Wall | Strada | STRW.05005006 | 50 | 50 | 06 | 9 | 474 | 474 | 474 | 0.011286 | 183 | 0.0043571 | 540 | 0.012857 | 1.372 | A09 | STRW0.05005006
Horizontal Wall | Strada | STRW.05005010 | 50 | 50 | 10 | 12 | 538 | 538 | 538 | 0.01281 | 206 | 0.0049048 | 614 | 0.014619 | 1.385 | A09 | STRW0.05005010
Horizontal Wall | Strada | STRW.05005011 | 50 | 50 | 11 | 12 | 693 | 693 | 693 | 0.0165 | 256 | 0.0060952 | 795 | 0.018929 | 1.438 | A09 | STRW0.05005011
Horizontal Wall | Strada | STRW.05005015 | 50 | 50 | 15 | 17 | 867 | 867 | 867 | 0.020643 | 335 | 0.0079762 | 988 | 0.023524 | 1.373 | A09 | STRW0.05005015
Horizontal Wall | Strada | STRW.05005016 | 50 | 50 | 16 | 17 | 949 | 949 | 949 | 0.022595 | 344 | 0.0081905 | 1091 | 0.025976 | 1.464 | A09 | STRW0.05005016
Horizontal Wall | Strada | STRW.05005020 | 50 | 50 | 20 | 22 | 1213 | 1213 | 1213 | 0.028881 | 468 | 0.011143 | 1383 | 0.032929 | 1.373 | A09 | STRW0.05005020
Horizontal Wall | Strada | STRW.05005021 | 50 | 50 | 21 | 22 | 1291 | 1291 | 1291 | 0.030738 | 461 | 0.010976 | 1487 | 0.035405 | 1.485 | A09 | STRW0.05005021
Horizontal Wall | Strada | STRW.05006006 | 50 | 60 | 06 | 9 | 568 | 568 | 568 | 0.013524 | 219 | 0.0052143 | 648 | 0.015429 | 1.372 | A09 | STRW0.05006006
Horizontal Wall | Strada | STRW.05006010 | 50 | 60 | 10 | 12 | 646 | 646 | 646 | 0.015381 | 247 | 0.005881 | 737 | 0.017548 | 1.385 | A09 | STRW0.05006010
Horizontal Wall | Strada | STRW.05006010/DBE | 50 | 60 | 10 | #N/A | 796 | 796 | 796 | 0.018952 | 398 | 0.0094762 | 876 | 0.020857 | 1 | A09 | STRW0.05006010/DBE
Horizontal Wall | Strada | STRW.05006011 | 50 | 60 | 11 | 12 | 832 | 832 | 832 | 0.01981 | 307 | 0.0073095 | 954 | 0.022714 | 1.438 | A09 | STRW0.05006011
Horizontal Wall | Strada | STRW.05006011/DBE | 50 | 60 | 11 | 12 | 1132 | 1132 | 1132 | 0.026952 | 566 | 0.013476 | 1245 | 0.029643 | 1 | A09 | STRW0.05006011/DBE
Horizontal Wall | Strada | STRW.05006015 | 50 | 60 | 15 | 17 | 1040 | 1040 | 1040 | 0.024762 | 401 | 0.0095476 | 1186 | 0.028238 | 1.373 | A09 | STRW0.05006015
Horizontal Wall | Strada | STRW.05006015/DBE | 50 | 60 | 15 | #N/A | 1290 | 1290 | 1290 | 0.030714 | 645 | 0.015357 | 1419 | 0.033786 | 1 | A09 | STRW0.05006015/DBE
Horizontal Wall | Strada | STRW.05006016 | 50 | 60 | 16 | 17 | 1139 | 1139 | 1139 | 0.027119 | 412 | 0.0098095 | 1310 | 0.03119 | 1.464 | A09 | STRW0.05006016
Horizontal Wall | Strada | STRW.05006016/DBE | 50 | 60 | 16 | 17 | 1619 | 1619 | 1619 | 0.038548 | 810 | 0.019286 | 1781 | 0.042405 | 1 | A09 | STRW0.05006016/DBE
Horizontal Wall | Strada | STRW.05006020 | 50 | 60 | 20 | 22 | 1455 | 1455 | 1455 | 0.034643 | 562 | 0.013381 | 1659 | 0.0395 | 1.373 | A09 | STRW0.05006020
Horizontal Wall | Strada | STRW.05006020/DBE | 50 | 60 | 20 | #N/A | 1705 | 1705 | 1705 | 0.040595 | 853 | 0.02031 | 1876 | 0.044667 | 1 | A09 | STRW0.05006020/DBE
Horizontal Wall | Strada | STRW.05006021 | 50 | 60 | 21 | 22 | 1549 | 1549 | 1549 | 0.036881 | 553 | 0.013167 | 1784 | 0.042476 | 1.485 | A09 | STRW0.05006021
Horizontal Wall | Strada | STRW.05006021/DBE | 50 | 60 | 21 | 22 | 2029 | 2029 | 2029 | 0.04831 | 1015 | 0.024167 | 2232 | 0.053143 | 1 | A09 | STRW0.05006021/DBE
Horizontal Wall | Strada | STRW.05007006 | 50 | 70 | 06 | 9 | 663 | 663 | 663 | 0.015786 | 256 | 0.0060952 | 756 | 0.018 | 1.372 | A09 | STRW0.05007006
Horizontal Wall | Strada | STRW.05007010 | 50 | 70 | 10 | 12 | 753 | 753 | 753 | 0.017929 | 288 | 0.0068571 | 859 | 0.020452 | 1.385 | A09 | STRW0.05007010
Horizontal Wall | Strada | STRW.05007010/DBE | 50 | 70 | 10 | #N/A | 903 | 903 | 903 | 0.0215 | 452 | 0.010762 | 993 | 0.023643 | 1 | A09 | STRW0.05007010/DBE
Horizontal Wall | Strada | STRW.05007011 | 50 | 70 | 11 | 12 | 970 | 970 | 970 | 0.023095 | 358 | 0.0085238 | 1113 | 0.0265 | 1.438 | A09 | STRW0.05007011
Horizontal Wall | Strada | STRW.05007011/DBE | 50 | 70 | 11 | 12 | 1270 | 1270 | 1270 | 0.030238 | 635 | 0.015119 | 1397 | 0.033262 | 1 | A09 | STRW0.05007011/DBE
Horizontal Wall | Strada | STRW.05007015 | 50 | 70 | 15 | 17 | 1214 | 1214 | 1214 | 0.028905 | 469 | 0.011167 | 1384 | 0.032952 | 1.373 | A09 | STRW0.05007015
Horizontal Wall | Strada | STRW.05007015/DBE | 50 | 70 | 15 | #N/A | 1464 | 1464 | 1464 | 0.034857 | 732 | 0.017429 | 1610 | 0.038333 | 1 | A09 | STRW0.05007015/DBE
Horizontal Wall | Strada | STRW.05007016 | 50 | 70 | 16 | 17 | 1329 | 1329 | 1329 | 0.031643 | 481 | 0.011452 | 1528 | 0.036381 | 1.464 | A09 | STRW0.05007016
Horizontal Wall | Strada | STRW.05007016/DBE | 50 | 70 | 16 | 17 | 1809 | 1809 | 1809 | 0.043071 | 905 | 0.021548 | 1990 | 0.047381 | 1 | A09 | STRW0.05007016/DBE
Horizontal Wall | Strada | STRW.05007020 | 50 | 70 | 20 | 22 | 1698 | 1698 | 1698 | 0.040429 | 655 | 0.015595 | 1936 | 0.046095 | 1.373 | A09 | STRW0.05007020
Horizontal Wall | Strada | STRW.05007020/DBE | 50 | 70 | 20 | #N/A | 1948 | 1948 | 1948 | 0.046381 | 974 | 0.02319 | 2143 | 0.051024 | 1 | A09 | STRW0.05007020/DBE
Horizontal Wall | Strada | STRW.05007021 | 50 | 70 | 21 | 22 | 1807 | 1807 | 1807 | 0.043024 | 645 | 0.015357 | 2082 | 0.049571 | 1.485 | A09 | STRW0.05007021
Horizontal Wall | Strada | STRW.05007021/DBE | 50 | 70 | 21 | 22 | 2287 | 2287 | 2287 | 0.054452 | 1144 | 0.027238 | 2516 | 0.059905 | 1 | A09 | STRW0.05007021/DBE
Horizontal Wall | Strada | STRW.05008006 | 50 | 80 | 06 | 9 | 758 | 758 | 758 | 0.018048 | 293 | 0.0069762 | 864 | 0.020571 | 1.372 | A09 | STRW0.05008006
Horizontal Wall | Strada | STRW.05008010 | 50 | 80 | 10 | 12 | 861 | 861 | 861 | 0.0205 | 330 | 0.0078571 | 982 | 0.023381 | 1.385 | A09 | STRW0.05008010
Horizontal Wall | Strada | STRW.05008010/DBE | 50 | 80 | 10 | #N/A | 1011 | 1011 | 1011 | 0.024071 | 506 | 0.012048 | 1112 | 0.026476 | 1 | A09 | STRW0.05008010/DBE
Horizontal Wall | Strada | STRW.05008011 | 50 | 80 | 11 | 12 | 1109 | 1109 | 1109 | 0.026405 | 409 | 0.0097381 | 1272 | 0.030286 | 1.438 | A09 | STRW0.05008011
Horizontal Wall | Strada | STRW.05008011/DBE | 50 | 80 | 11 | 12 | 1409 | 1409 | 1409 | 0.033548 | 705 | 0.016786 | 1550 | 0.036905 | 1 | A09 | STRW0.05008011/DBE
Horizontal Wall | Strada | STRW.05008015 | 50 | 80 | 15 | 17 | 1387 | 1387 | 1387 | 0.033024 | 535 | 0.012738 | 1581 | 0.037643 | 1.373 | A09 | STRW0.05008015
Horizontal Wall | Strada | STRW.05008015/DBE | 50 | 80 | 15 | #N/A | 1637 | 1637 | 1637 | 0.038976 | 819 | 0.0195 | 1801 | 0.042881 | 1 | A09 | STRW0.05008015/DBE
Horizontal Wall | Strada | STRW.05008016 | 50 | 80 | 16 | 17 | 1518 | 1518 | 1518 | 0.036143 | 550 | 0.013095 | 1746 | 0.041571 | 1.464 | A09 | STRW0.05008016
Horizontal Wall | Strada | STRW.05008016/DBE | 50 | 80 | 16 | 17 | 1998 | 1998 | 1998 | 0.047571 | 999 | 0.023786 | 2198 | 0.052333 | 1 | A09 | STRW0.05008016/DBE
Horizontal Wall | Strada | STRW.05008020 | 50 | 80 | 20 | 22 | 1940 | 1940 | 1940 | 0.04619 | 749 | 0.017833 | 2212 | 0.052667 | 1.373 | A09 | STRW0.05008020
Horizontal Wall | Strada | STRW.05008020/DBE | 50 | 80 | 20 | #N/A | 2190 | 2190 | 2190 | 0.052143 | 1095 | 0.026071 | 2409 | 0.057357 | 1 | A09 | STRW0.05008020/DBE
Horizontal Wall | Strada | STRW.05008021 | 50 | 80 | 21 | 22 | 2066 | 2066 | 2066 | 0.04919 | 738 | 0.017571 | 2380 | 0.056667 | 1.485 | A09 | STRW0.05008021
Horizontal Wall | Strada | STRW.05008021/DBE | 50 | 80 | 21 | 22 | 2546 | 2546 | 2546 | 0.060619 | 1273 | 0.03031 | 2801 | 0.06669 | 1 | A09 | STRW0.05008021/DBE
Horizontal Wall | Strada | STRW.05009006 | 50 | 90 | 06 | 9 | 852 | 852 | 852 | 0.020286 | 329 | 0.0078333 | 971 | 0.023119 | 1.372 | A09 | STRW0.05009006
Horizontal Wall | Strada | STRW.05009010 | 50 | 90 | 10 | 12 | 968 | 968 | 968 | 0.023048 | 371 | 0.0088333 | 1104 | 0.026286 | 1.385 | A09 | STRW0.05009010
Horizontal Wall | Strada | STRW.05009010/DBE | 50 | 90 | 10 | #N/A | 1268 | 1268 | 1268 | 0.03019 | 634 | 0.015095 | 1395 | 0.033214 | 1 | A09 | STRW0.05009010/DBE
Horizontal Wall | Strada | STRW.05009011 | 50 | 90 | 11 | 12 | 1247 | 1247 | 1247 | 0.02969 | 460 | 0.010952 | 1430 | 0.034048 | 1.438 | A09 | STRW0.05009011
Horizontal Wall | Strada | STRW.05009011/DBE | 50 | 90 | 11 | 12 | 1847 | 1847 | 1847 | 0.043976 | 924 | 0.022 | 2032 | 0.048381 | 1 | A09 | STRW0.05009011/DBE
Horizontal Wall | Strada | STRW.05009015 | 50 | 90 | 15 | 17 | 1561 | 1561 | 1561 | 0.037167 | 603 | 0.014357 | 1780 | 0.042381 | 1.373 | A09 | STRW0.05009015
Horizontal Wall | Strada | STRW.05009015/DBE | 50 | 90 | 15 | #N/A | 2061 | 2061 | 2061 | 0.049071 | 1031 | 0.024548 | 2267 | 0.053976 | 1 | A09 | STRW0.05009015/DBE
Horizontal Wall | Strada | STRW.05009016 | 50 | 90 | 16 | 17 | 1708 | 1708 | 1708 | 0.040667 | 618 | 0.014714 | 1964 | 0.046762 | 1.464 | A09 | STRW0.05009016
Horizontal Wall | Strada | STRW.05009016/DBE | 50 | 90 | 16 | 17 | 2668 | 2668 | 2668 | 0.063524 | 1334 | 0.031762 | 2935 | 0.069881 | 1 | A09 | STRW0.05009016/DBE
Horizontal Wall | Strada | STRW.05009020 | 50 | 90 | 20 | 22 | 2183 | 2183 | 2183 | 0.051976 | 843 | 0.020071 | 2489 | 0.059262 | 1.373 | A09 | STRW0.05009020
Horizontal Wall | Strada | STRW.05009020/DBE | 50 | 90 | 20 | #N/A | 2683 | 2683 | 2683 | 0.063881 | 1342 | 0.031952 | 2951 | 0.070262 | 1 | A09 | STRW0.05009020/DBE
Horizontal Wall | Strada | STRW.05009021 | 50 | 90 | 21 | 22 | 2324 | 2324 | 2324 | 0.055333 | 830 | 0.019762 | 2677 | 0.063738 | 1.485 | A09 | STRW0.05009021
Horizontal Wall | Strada | STRW.05009021/DBE | 50 | 90 | 21 | 22 | 3284 | 3284 | 3284 | 0.07819 | 1642 | 0.039095 | 3612 | 0.086 | 1 | A09 | STRW0.05009021/DBE
Horizontal Wall | Strada | STRW.05010006 | 50 | 100 | 06 | 9 | 947 | 947 | 947 | 0.022548 | 366 | 0.0087143 | 1080 | 0.025714 | 1.372 | A09 | STRW0.05010006
Horizontal Wall | Strada | STRW.05010010 | 50 | 100 | 10 | 12 | 1076 | 1076 | 1076 | 0.025619 | 412 | 0.0098095 | 1228 | 0.029238 | 1.385 | A09 | STRW0.05010010
Horizontal Wall | Strada | STRW.05010010/DBE | 50 | 100 | 10 | #N/A | 1376 | 1376 | 1376 | 0.032762 | 688 | 0.016381 | 1514 | 0.036048 | 1 | A09 | STRW0.05010010/DBE
Horizontal Wall | Strada | STRW.05010011 | 50 | 100 | 11 | 12 | 1386 | 1386 | 1386 | 0.033 | 511 | 0.012167 | 1590 | 0.037857 | 1.438 | A09 | STRW0.05010011
Horizontal Wall | Strada | STRW.05010011/DBE | 50 | 100 | 11 | 12 | 1986 | 1986 | 1986 | 0.047286 | 993 | 0.023643 | 2185 | 0.052024 | 1 | A09 | STRW0.05010011/DBE
Horizontal Wall | Strada | STRW.05010015 | 50 | 100 | 15 | 17 | 1734 | 1734 | 1734 | 0.041286 | 669 | 0.015929 | 1977 | 0.047071 | 1.373 | A09 | STRW0.05010015
Horizontal Wall | Strada | STRW.05010015/DBE | 50 | 100 | 15 | #N/A | 2234 | 2234 | 2234 | 0.05319 | 1117 | 0.026595 | 2457 | 0.0585 | 1 | A09 | STRW0.05010015/DBE
Horizontal Wall | Strada | STRW.05010016 | 50 | 100 | 16 | 17 | 1898 | 1898 | 1898 | 0.04519 | 687 | 0.016357 | 2183 | 0.051976 | 1.464 | A09 | STRW0.05010016
Horizontal Wall | Strada | STRW.05010016/DBE | 50 | 100 | 16 | 17 | 2858 | 2858 | 2858 | 0.068048 | 1429 | 0.034024 | 3144 | 0.074857 | 1 | A09 | STRW0.05010016/DBE
Horizontal Wall | Strada | STRW.05010020 | 50 | 100 | 20 | 22 | 2425 | 2425 | 2425 | 0.057738 | 936 | 0.022286 | 2765 | 0.065833 | 1.373 | A09 | STRW0.05010020
Horizontal Wall | Strada | STRW.05010020/DBE | 50 | 100 | 20 | #N/A | 2925 | 2925 | 2925 | 0.069643 | 1463 | 0.034833 | 3218 | 0.076619 | 1 | A09 | STRW0.05010020/DBE
Horizontal Wall | Strada | STRW.05010021 | 50 | 100 | 21 | 22 | 2582 | 2582 | 2582 | 0.061476 | 922 | 0.021952 | 2974 | 0.07081 | 1.485 | A09 | STRW0.05010021
Horizontal Wall | Strada | STRW.05010021/DBE | 50 | 100 | 21 | 22 | 3542 | 3542 | 3542 | 0.084333 | 1771 | 0.042167 | 3896 | 0.092762 | 1 | A09 | STRW0.05010021/DBE
Horizontal Wall | Strada | STRW.05011006 | 50 | 110 | 06 | 9 | 1042 | 1042 | 1042 | 0.02481 | 402 | 0.0095714 | 1188 | 0.028286 | 1.372 | A09 | STRW0.05011006
Horizontal Wall | Strada | STRW.05011010 | 50 | 110 | 10 | 12 | 1184 | 1184 | 1184 | 0.02819 | 453 | 0.010786 | 1351 | 0.032167 | 1.385 | A09 | STRW0.05011010
Horizontal Wall | Strada | STRW.05011010/DBE | 50 | 110 | 10 | #N/A | 1484 | 1484 | 1484 | 0.035333 | 742 | 0.017667 | 1632 | 0.038857 | 1 | A09 | STRW0.05011010/DBE
Horizontal Wall | Strada | STRW.05011011 | 50 | 110 | 11 | 12 | 1525 | 1525 | 1525 | 0.03631 | 563 | 0.013405 | 1749 | 0.041643 | 1.438 | A09 | STRW0.05011011
Horizontal Wall | Strada | STRW.05011011/DBE | 50 | 110 | 11 | 12 | 2125 | 2125 | 2125 | 0.050595 | 1063 | 0.02531 | 2338 | 0.055667 | 1 | A09 | STRW0.05011011/DBE
Horizontal Wall | Strada | STRW.05011015 | 50 | 110 | 15 | 17 | 1907 | 1907 | 1907 | 0.045405 | 736 | 0.017524 | 2174 | 0.051762 | 1.373 | A09 | STRW0.05011015
Horizontal Wall | Strada | STRW.05011015/DBE | 50 | 110 | 15 | #N/A | 2407 | 2407 | 2407 | 0.05731 | 1204 | 0.028667 | 2648 | 0.063048 | 1 | A09 | STRW0.05011015/DBE
Horizontal Wall | Strada | STRW.05011016 | 50 | 110 | 16 | 17 | 2088 | 2088 | 2088 | 0.049714 | 756 | 0.018 | 2401 | 0.057167 | 1.464 | A09 | STRW0.05011016
Horizontal Wall | Strada | STRW.05011016/DBE | 50 | 110 | 16 | 17 | 3048 | 3048 | 3048 | 0.072571 | 1524 | 0.036286 | 3353 | 0.079833 | 1 | A09 | STRW0.05011016/DBE
Horizontal Wall | Strada | STRW.05011020 | 50 | 110 | 20 | 22 | 2668 | 2668 | 2668 | 0.063524 | 1030 | 0.024524 | 3042 | 0.072429 | 1.373 | A09 | STRW0.05011020
Horizontal Wall | Strada | STRW.05011020/DBE | 50 | 110 | 20 | #N/A | 3168 | 3168 | 3168 | 0.075429 | 1584 | 0.037714 | 3485 | 0.082976 | 1 | A09 | STRW0.05011020/DBE
Horizontal Wall | Strada | STRW.05011021 | 50 | 110 | 21 | 22 | 2840 | 2840 | 2840 | 0.067619 | 1014 | 0.024143 | 3272 | 0.077905 | 1.485 | A09 | STRW0.05011021
Horizontal Wall | Strada | STRW.05011021/DBE | 50 | 110 | 21 | 22 | 3800 | 3800 | 3800 | 0.090476 | 1900 | 0.045238 | 4180 | 0.099524 | 1 | A09 | STRW0.05011021/DBE
Horizontal Wall | Strada | STRW.05012006 | 50 | 120 | 06 | 9 | 1136 | 1136 | 1136 | 0.027048 | 438 | 0.010429 | 1295 | 0.030833 | 1.372 | A09 | STRW0.05012006
Horizontal Wall | Strada | STRW.05012010 | 50 | 120 | 10 | 12 | 1291 | 1291 | 1291 | 0.030738 | 494 | 0.011762 | 1473 | 0.035071 | 1.385 | A09 | STRW0.05012010
Horizontal Wall | Strada | STRW.05012010/DBE | 50 | 120 | 10 | #N/A | 1591 | 1591 | 1591 | 0.037881 | 796 | 0.018952 | 1750 | 0.041667 | 1 | A09 | STRW0.05012010/DBE
Horizontal Wall | Strada | STRW.05012011 | 50 | 120 | 11 | 12 | 1663 | 1663 | 1663 | 0.039595 | 614 | 0.014619 | 1907 | 0.045405 | 1.438 | A09 | STRW0.05012011
Horizontal Wall | Strada | STRW.05012011/DBE | 50 | 120 | 11 | 12 | 2263 | 2263 | 2263 | 0.053881 | 1132 | 0.026952 | 2489 | 0.059262 | 1 | A09 | STRW0.05012011/DBE
Horizontal Wall | Strada | STRW.05012015 | 50 | 120 | 15 | 17 | 2081 | 2081 | 2081 | 0.049548 | 803 | 0.019119 | 2372 | 0.056476 | 1.373 | A09 | STRW0.05012015
Horizontal Wall | Strada | STRW.05012015/DBE | 50 | 120 | 15 | #N/A | 2581 | 2581 | 2581 | 0.061452 | 1291 | 0.030738 | 2839 | 0.067595 | 1 | A09 | STRW0.05012015/DBE
Horizontal Wall | Strada | STRW.05012016 | 50 | 120 | 16 | 17 | 2278 | 2278 | 2278 | 0.054238 | 825 | 0.019643 | 2620 | 0.062381 | 1.464 | A09 | STRW0.05012016
Horizontal Wall | Strada | STRW.05012016/DBE | 50 | 120 | 16 | 17 | 3238 | 3238 | 3238 | 0.077095 | 1619 | 0.038548 | 3562 | 0.08481 | 1 | A09 | STRW0.05012016/DBE
Horizontal Wall | Strada | STRW.05012020 | 50 | 120 | 20 | 22 | 2910 | 2910 | 2910 | 0.069286 | 1123 | 0.026738 | 3317 | 0.078976 | 1.373 | A09 | STRW0.05012020
Horizontal Wall | Strada | STRW.05012020/DBE | 50 | 120 | 20 | #N/A | 3410 | 3410 | 3410 | 0.08119 | 1705 | 0.040595 | 3751 | 0.08931 | 1 | A09 | STRW0.05012020/DBE
Horizontal Wall | Strada | STRW.05012021 | 50 | 120 | 21 | 22 | 3098 | 3098 | 3098 | 0.073762 | 1106 | 0.026333 | 3569 | 0.084976 | 1.485 | A09 | STRW0.05012021
Horizontal Wall | Strada | STRW.05012021/DBE | 50 | 120 | 21 | 22 | 4058 | 4058 | 4058 | 0.096619 | 2029 | 0.04831 | 4464 | 0.10629 | 1 | A09 | STRW0.05012021/DBE
Horizontal Wall | Strada | STRW.05014006 | 50 | 140 | 06 | 9 | 1326 | 1326 | 1326 | 0.031571 | 512 | 0.01219 | 1512 | 0.036 | 1.372 | A09 | STRW0.05014006
Horizontal Wall | Strada | STRW.05014010 | 50 | 140 | 10 | 12 | 1506 | 1506 | 1506 | 0.035857 | 577 | 0.013738 | 1718 | 0.040905 | 1.385 | A09 | STRW0.05014010
Horizontal Wall | Strada | STRW.05014010/DBE | 50 | 140 | 10 | #N/A | 1806 | 1806 | 1806 | 0.043 | 903 | 0.0215 | 1987 | 0.04731 | 1 | A09 | STRW0.05014010/DBE
Horizontal Wall | Strada | STRW.05014011 | 50 | 140 | 11 | 12 | 1940 | 1940 | 1940 | 0.04619 | 716 | 0.017048 | 2225 | 0.052976 | 1.438 | A09 | STRW0.05014011
Horizontal Wall | Strada | STRW.05014011/DBE | 50 | 140 | 11 | 12 | 2540 | 2540 | 2540 | 0.060476 | 1270 | 0.030238 | 2794 | 0.066524 | 1 | A09 | STRW0.05014011/DBE
Horizontal Wall | Strada | STRW.05014015 | 50 | 140 | 15 | 17 | 2428 | 2428 | 2428 | 0.05781 | 937 | 0.02231 | 2768 | 0.065905 | 1.373 | A09 | STRW0.05014015
Horizontal Wall | Strada | STRW.05014015/DBE | 50 | 140 | 15 | #N/A | 2928 | 2928 | 2928 | 0.069714 | 1464 | 0.034857 | 3221 | 0.07669 | 1 | A09 | STRW0.05014015/DBE
Horizontal Wall | Strada | STRW.05014016 | 50 | 140 | 16 | 17 | 2657 | 2657 | 2657 | 0.063262 | 962 | 0.022905 | 3056 | 0.072762 | 1.464 | A09 | STRW0.05014016
Horizontal Wall | Strada | STRW.05014016/DBE | 50 | 140 | 16 | 17 | 3617 | 3617 | 3617 | 0.086119 | 1809 | 0.043071 | 3979 | 0.094738 | 1 | A09 | STRW0.05014016/DBE
Horizontal Wall | Strada | STRW.05014020 | 50 | 140 | 20 | 22 | 3395 | 3395 | 3395 | 0.080833 | 1310 | 0.03119 | 3870 | 0.092143 | 1.373 | A09 | STRW0.05014020
Horizontal Wall | Strada | STRW.05014020/DBE | 50 | 140 | 20 | #N/A | 3895 | 3895 | 3895 | 0.092738 | 1948 | 0.046381 | 4285 | 0.10202 | 1 | A09 | STRW0.05014020/DBE
Horizontal Wall | Strada | STRW.05014021 | 50 | 140 | 21 | 22 | 3615 | 3615 | 3615 | 0.086071 | 1291 | 0.030738 | 4164 | 0.099143 | 1.485 | A09 | STRW0.05014021
Horizontal Wall | Strada | STRW.05014021/DBE | 50 | 140 | 21 | 22 | 4575 | 4575 | 4575 | 0.10893 | 2288 | 0.054476 | 5033 | 0.11983 | 1 | A09 | STRW0.05014021/DBE
Horizontal Wall | Strada | STRW.05016006 | 50 | 160 | 06 | 9 | 1515 | 1515 | 1515 | 0.036071 | 585 | 0.013929 | 1727 | 0.041119 | 1.372 | A09 | STRW0.05016006
Horizontal Wall | Strada | STRW.05016010 | 50 | 160 | 10 | 12 | 1722 | 1722 | 1722 | 0.041 | 660 | 0.015714 | 1965 | 0.046786 | 1.385 | A09 | STRW0.05016010
Horizontal Wall | Strada | STRW.05016010/DBE | 50 | 160 | 10 | #N/A | 2322 | 2322 | 2322 | 0.055286 | 1161 | 0.027643 | 2554 | 0.06081 | 1 | A09 | STRW0.05016010/DBE
Horizontal Wall | Strada | STRW.05016011 | 50 | 160 | 11 | 12 | 2218 | 2218 | 2218 | 0.05281 | 818 | 0.019476 | 2544 | 0.060571 | 1.438 | A09 | STRW0.05016011
Horizontal Wall | Strada | STRW.05016011/DBE | 50 | 160 | 11 | 12 | 3418 | 3418 | 3418 | 0.081381 | 1709 | 0.04069 | 3760 | 0.089524 | 1 | A09 | STRW0.05016011/DBE
Horizontal Wall | Strada | STRW.05016015 | 50 | 160 | 15 | 17 | 2774 | 2774 | 2774 | 0.066048 | 1071 | 0.0255 | 3162 | 0.075286 | 1.373 | A09 | STRW0.05016015
Horizontal Wall | Strada | STRW.05016015/DBE | 50 | 160 | 15 | #N/A | 3774 | 3774 | 3774 | 0.089857 | 1887 | 0.044929 | 4151 | 0.098833 | 1 | A09 | STRW0.05016015/DBE
Horizontal Wall | Strada | STRW.05016016 | 50 | 160 | 16 | 17 | 3037 | 3037 | 3037 | 0.07231 | 1099 | 0.026167 | 3493 | 0.083167 | 1.464 | A09 | STRW0.05016016
Horizontal Wall | Strada | STRW.05016016/DBE | 50 | 160 | 16 | 17 | 4957 | 4957 | 4957 | 0.11802 | 2479 | 0.059024 | 5453 | 0.12983 | 1 | A09 | STRW0.05016016/DBE
Horizontal Wall | Strada | STRW.05016020 | 50 | 160 | 20 | 22 | 3880 | 3880 | 3880 | 0.092381 | 1498 | 0.035667 | 4423 | 0.10531 | 1.373 | A09 | STRW0.05016020
Horizontal Wall | Strada | STRW.05016020/DBE | 50 | 160 | 20 | #N/A | 4880 | 4880 | 4880 | 0.11619 | 2440 | 0.058095 | 5368 | 0.12781 | 1 | A09 | STRW0.05016020/DBE
Horizontal Wall | Strada | STRW.05016021 | 50 | 160 | 21 | 22 | 4131 | 4131 | 4131 | 0.098357 | 1475 | 0.035119 | 4759 | 0.11331 | 1.485 | A09 | STRW0.05016021
Horizontal Wall | Strada | STRW.05016021/DBE | 50 | 160 | 21 | 22 | 6051 | 6051 | 6051 | 0.14407 | 3026 | 0.072048 | 6656 | 0.15848 | 1 | A09 | STRW0.05016021/DBE
Horizontal Wall | Strada | STRW.05018006 | 50 | 180 | 06 | 9 | 1705 | 1705 | 1705 | 0.040595 | 658 | 0.015667 | 1944 | 0.046286 | 1.372 | A09 | STRW0.05018006
Horizontal Wall | Strada | STRW.05018010 | 50 | 180 | 10 | 12 | 1937 | 1937 | 1937 | 0.046119 | 742 | 0.017667 | 2210 | 0.052619 | 1.385 | A09 | STRW0.05018010
Horizontal Wall | Strada | STRW.05018010/DBE | 50 | 180 | 10 | #N/A | 2537 | 2537 | 2537 | 0.060405 | 1269 | 0.030214 | 2791 | 0.066452 | 1 | A09 | STRW0.05018010/DBE
Horizontal Wall | Strada | STRW.05018011 | 50 | 180 | 11 | 12 | 2495 | 2495 | 2495 | 0.059405 | 921 | 0.021929 | 2862 | 0.068143 | 1.438 | A09 | STRW0.05018011
Horizontal Wall | Strada | STRW.05018011/DBE | 50 | 180 | 11 | 12 | 3695 | 3695 | 3695 | 0.087976 | 1848 | 0.044 | 4065 | 0.096786 | 1 | A09 | STRW0.05018011/DBE
Horizontal Wall | Strada | STRW.05018015 | 50 | 180 | 15 | 17 | 3121 | 3121 | 3121 | 0.07431 | 1205 | 0.02869 | 3558 | 0.084714 | 1.373 | A09 | STRW0.05018015
Horizontal Wall | Strada | STRW.05018015/DBE | 50 | 180 | 15 | #N/A | 4121 | 4121 | 4121 | 0.098119 | 2061 | 0.049071 | 4533 | 0.10793 | 1 | A09 | STRW0.05018015/DBE
Horizontal Wall | Strada | STRW.05018016 | 50 | 180 | 16 | 17 | 3416 | 3416 | 3416 | 0.081333 | 1237 | 0.029452 | 3928 | 0.093524 | 1.464 | A09 | STRW0.05018016
Horizontal Wall | Strada | STRW.05018016/DBE | 50 | 180 | 16 | 17 | 5336 | 5336 | 5336 | 0.12705 | 2668 | 0.063524 | 5870 | 0.13976 | 1 | A09 | STRW0.05018016/DBE
Horizontal Wall | Strada | STRW.05018020 | 50 | 180 | 20 | 22 | 4365 | 4365 | 4365 | 0.10393 | 1685 | 0.040119 | 4976 | 0.11848 | 1.373 | A09 | STRW0.05018020
Horizontal Wall | Strada | STRW.05018020/DBE | 50 | 180 | 20 | #N/A | 5365 | 5365 | 5365 | 0.12774 | 2683 | 0.063881 | 5902 | 0.14052 | 1 | A09 | STRW0.05018020/DBE
Horizontal Wall | Strada | STRW.05018021 | 50 | 180 | 21 | 22 | 4648 | 4648 | 4648 | 0.11067 | 1659 | 0.0395 | 5354 | 0.12748 | 1.485 | A09 | STRW0.05018021
Horizontal Wall | Strada | STRW.05018021/DBE | 50 | 180 | 21 | 22 | 6568 | 6568 | 6568 | 0.15638 | 3284 | 0.07819 | 7225 | 0.17202 | 1 | A09 | STRW0.05018021/DBE
Horizontal Wall | Strada | STRW.05020006 | 50 | 200 | 06 | 9 | 1894 | 1894 | 1894 | 0.045095 | 731 | 0.017405 | 2159 | 0.051405 | 1.372 | A09 | STRW0.05020006
Horizontal Wall | Strada | STRW.05020010 | 50 | 200 | 10 | 12 | 2152 | 2152 | 2152 | 0.051238 | 824 | 0.019619 | 2455 | 0.058452 | 1.385 | A09 | STRW0.05020010
Horizontal Wall | Strada | STRW.05020010/DBE | 50 | 200 | 10 | #N/A | 2752 | 2752 | 2752 | 0.065524 | 1376 | 0.032762 | 3027 | 0.072071 | 1 | A09 | STRW0.05020010/DBE
Horizontal Wall | Strada | STRW.05020011 | 50 | 200 | 11 | 12 | 2772 | 2772 | 2772 | 0.066 | 1023 | 0.024357 | 3179 | 0.07569 | 1.438 | A09 | STRW0.05020011
Horizontal Wall | Strada | STRW.05020011/DBE | 50 | 200 | 11 | 12 | 3972 | 3972 | 3972 | 0.094571 | 1986 | 0.047286 | 4369 | 0.10402 | 1 | A09 | STRW0.05020011/DBE
Horizontal Wall | Strada | STRW.05020015 | 50 | 200 | 15 | 17 | 3468 | 3468 | 3468 | 0.082571 | 1339 | 0.031881 | 3954 | 0.094143 | 1.373 | A09 | STRW0.05020015
Horizontal Wall | Strada | STRW.05020015/DBE | 50 | 200 | 15 | #N/A | 4468 | 4468 | 4468 | 0.10638 | 2234 | 0.05319 | 4915 | 0.11702 | 1 | A09 | STRW0.05020015/DBE
Horizontal Wall | Strada | STRW.05020016 | 50 | 200 | 16 | 17 | 3796 | 3796 | 3796 | 0.090381 | 1374 | 0.032714 | 4365 | 0.10393 | 1.464 | A09 | STRW0.05020016
Horizontal Wall | Strada | STRW.05020016/DBE | 50 | 200 | 16 | 17 | 5716 | 5716 | 5716 | 0.1361 | 2858 | 0.068048 | 6288 | 0.14971 | 1 | A09 | STRW0.05020016/DBE
Horizontal Wall | Strada | STRW.05020020 | 50 | 200 | 20 | 22 | 4850 | 4850 | 4850 | 0.11548 | 1872 | 0.044571 | 5529 | 0.13164 | 1.373 | A09 | STRW0.05020020
Horizontal Wall | Strada | STRW.05020020/DBE | 50 | 200 | 20 | #N/A | 5850 | 5850 | 5850 | 0.13929 | 2925 | 0.069643 | 6435 | 0.15321 | 1 | A09 | STRW0.05020020/DBE
Horizontal Wall | Strada | STRW.05020021 | 50 | 200 | 21 | 22 | 5164 | 5164 | 5164 | 0.12295 | 1844 | 0.043905 | 5949 | 0.14164 | 1.485 | A09 | STRW0.05020021
Horizontal Wall | Strada | STRW.05020021/DBE | 50 | 200 | 21 | 22 | 7084 | 7084 | 7084 | 0.16867 | 3542 | 0.084333 | 7792 | 0.18552 | 1 | A09 | STRW0.05020021/DBE
Horizontal Wall | Strada | STRW.05024006 | 50 | 240 | 06 | 9 | 2273 | 2273 | 2273 | 0.054119 | 877 | 0.020881 | 2591 | 0.06169 | 1.372 | A09 | STRW0.05024006
Horizontal Wall | Strada | STRW.05024010 | 50 | 240 | 10 | 12 | 2582 | 2582 | 2582 | 0.061476 | 989 | 0.023548 | 2946 | 0.070143 | 1.385 | A09 | STRW0.05024010
Horizontal Wall | Strada | STRW.05024010/DBE | 50 | 240 | 10 | #N/A | 3482 | 3482 | 3482 | 0.082905 | 1741 | 0.041452 | 3830 | 0.09119 | 1 | A09 | STRW0.05024010/DBE
Horizontal Wall | Strada | STRW.05024011 | 50 | 240 | 11 | 12 | 3326 | 3326 | 3326 | 0.07919 | 1227 | 0.029214 | 3815 | 0.090833 | 1.438 | A09 | STRW0.05024011
Horizontal Wall | Strada | STRW.05024011/DBE | 50 | 240 | 11 | 12 | 5126 | 5126 | 5126 | 0.12205 | 2563 | 0.061024 | 5639 | 0.13426 | 1 | A09 | STRW0.05024011/DBE
Horizontal Wall | Strada | STRW.05024015 | 50 | 240 | 15 | 17 | 4162 | 4162 | 4162 | 0.099095 | 1607 | 0.038262 | 4745 | 0.11298 | 1.373 | A09 | STRW0.05024015
Horizontal Wall | Strada | STRW.05024015/DBE | 50 | 240 | 15 | #N/A | 5662 | 5662 | 5662 | 0.13481 | 2831 | 0.067405 | 6228 | 0.14829 | 1 | A09 | STRW0.05024015/DBE
Horizontal Wall | Strada | STRW.05024016 | 50 | 240 | 16 | 17 | 4555 | 4555 | 4555 | 0.10845 | 1649 | 0.039262 | 5238 | 0.12471 | 1.464 | A09 | STRW0.05024016
Horizontal Wall | Strada | STRW.05024016/DBE | 50 | 240 | 16 | 17 | 7435 | 7435 | 7435 | 0.17702 | 3718 | 0.088524 | 8179 | 0.19474 | 1 | A09 | STRW0.05024016/DBE
Horizontal Wall | Strada | STRW.05024020 | 50 | 240 | 20 | 22 | 5820 | 5820 | 5820 | 0.13857 | 2247 | 0.0535 | 6635 | 0.15798 | 1.373 | A09 | STRW0.05024020
Horizontal Wall | Strada | STRW.05024020/DBE | 50 | 240 | 20 | #N/A | 7320 | 7320 | 7320 | 0.17429 | 3660 | 0.087143 | 8052 | 0.19171 | 1 | A09 | STRW0.05024020/DBE
Horizontal Wall | Strada | STRW.05024021 | 50 | 240 | 21 | 22 | 6197 | 6197 | 6197 | 0.14755 | 2212 | 0.052667 | 7139 | 0.16998 | 1.485 | A09 | STRW0.05024021
Horizontal Wall | Strada | STRW.05024021/DBE | 50 | 240 | 21 | 22 | 9077 | 9077 | 9077 | 0.21612 | 4539 | 0.10807 | 9985 | 0.23774 | 1 | A09 | STRW0.05024021/DBE
Horizontal Wall | Strada | STRW.05028006 | 50 | 280 | 06 | 9 | 2652 | 2652 | 2652 | 0.063143 | 1024 | 0.024381 | 3023 | 0.071976 | 1.372 | A09 | STRW0.05028006
Horizontal Wall | Strada | STRW.05028010 | 50 | 280 | 10 | 12 | 3013 | 3013 | 3013 | 0.071738 | 1154 | 0.027476 | 3438 | 0.081857 | 1.385 | A09 | STRW0.05028010
Horizontal Wall | Strada | STRW.05028010/DBE | 50 | 280 | 10 | #N/A | 3913 | 3913 | 3913 | 0.093167 | 1957 | 0.046595 | 4304 | 0.10248 | 1 | A09 | STRW0.05028010/DBE
Horizontal Wall | Strada | STRW.05028011 | 50 | 280 | 11 | 12 | 3881 | 3881 | 3881 | 0.092405 | 1432 | 0.034095 | 4452 | 0.106 | 1.438 | A09 | STRW0.05028011
Horizontal Wall | Strada | STRW.05028011/DBE | 50 | 280 | 11 | 12 | 5681 | 5681 | 5681 | 0.13526 | 2841 | 0.067643 | 6249 | 0.14879 | 1 | A09 | STRW0.05028011/DBE
Horizontal Wall | Strada | STRW.05028015 | 50 | 280 | 15 | 17 | 4855 | 4855 | 4855 | 0.1156 | 1874 | 0.044619 | 5535 | 0.13179 | 1.373 | A09 | STRW0.05028015
Horizontal Wall | Strada | STRW.05028015/DBE | 50 | 280 | 15 | #N/A | 6355 | 6355 | 6355 | 0.15131 | 3178 | 0.075667 | 6991 | 0.16645 | 1 | A09 | STRW0.05028015/DBE
Horizontal Wall | Strada | STRW.05028016 | 50 | 280 | 16 | 17 | 5314 | 5314 | 5314 | 0.12652 | 1924 | 0.04581 | 6111 | 0.1455 | 1.464 | A09 | STRW0.05028016
Horizontal Wall | Strada | STRW.05028016/DBE | 50 | 280 | 16 | 17 | 8194 | 8194 | 8194 | 0.1951 | 4097 | 0.097548 | 9013 | 0.2146 | 1 | A09 | STRW0.05028016/DBE
Horizontal Wall | Strada | STRW.05028020 | 50 | 280 | 20 | 22 | 6790 | 6790 | 6790 | 0.16167 | 2621 | 0.062405 | 7741 | 0.18431 | 1.373 | A09 | STRW0.05028020
Horizontal Wall | Strada | STRW.05028020/DBE | 50 | 280 | 20 | #N/A | 8290 | 8290 | 8290 | 0.19738 | 4145 | 0.09869 | 9119 | 0.21712 | 1 | A09 | STRW0.05028020/DBE
Horizontal Wall | Strada | STRW.05028021 | 50 | 280 | 21 | 22 | 7230 | 7230 | 7230 | 0.17214 | 2581 | 0.061452 | 8329 | 0.19831 | 1.485 | A09 | STRW0.05028021
Horizontal Wall | Strada | STRW.05028021/DBE | 50 | 280 | 21 | 22 | 10110 | 10110 | 10110 | 0.24071 | 5055 | 0.12036 | 11121 | 0.26479 | 1 | A09 | STRW0.05028021/DBE
Horizontal Wall | Strada | STRW.06505006 | 65 | 50 | 06 | 9 | 533 | 533 | 533 | 0.01269 | 209 | 0.0049762 | 606 | 0.014429 | 1.35 | A09 | STRW0.06505006
Horizontal Wall | Strada | STRW.06505010 | 65 | 50 | 10 | 12 | 606 | 606 | 606 | 0.014429 | 235 | 0.0055952 | 691 | 0.016452 | 1.371 | A09 | STRW0.06505010
Horizontal Wall | Strada | STRW.06505011 | 65 | 50 | 11 | 12 | 772 | 772 | 772 | 0.018381 | 285 | 0.0067857 | 885 | 0.021071 | 1.437 | A09 | STRW0.06505011
Horizontal Wall | Strada | STRW.06505015 | 65 | 50 | 15 | 17 | 961 | 961 | 961 | 0.022881 | 376 | 0.0089524 | 1094 | 0.026048 | 1.355 | A09 | STRW0.06505015
Horizontal Wall | Strada | STRW.06505016 | 65 | 50 | 16 | 17 | 1087 | 1087 | 1087 | 0.025881 | 392 | 0.0093333 | 1250 | 0.029762 | 1.47 | A09 | STRW0.06505016
Horizontal Wall | Strada | STRW.06505020 | 65 | 50 | 20 | 22 | 1343 | 1343 | 1343 | 0.031976 | 525 | 0.0125 | 1528 | 0.036381 | 1.355 | A09 | STRW0.06505020
Horizontal Wall | Strada | STRW.06505021 | 65 | 50 | 21 | 22 | 1515 | 1515 | 1515 | 0.036071 | 536 | 0.012762 | 1747 | 0.041595 | 1.497 | A09 | STRW0.06505021
Horizontal Wall | Strada | STRW.06506006 | 65 | 60 | 06 | 9 | 640 | 640 | 640 | 0.015238 | 251 | 0.0059762 | 728 | 0.017333 | 1.35 | A09 | STRW0.06506006
Horizontal Wall | Strada | STRW.06506010 | 65 | 60 | 10 | 12 | 727 | 727 | 727 | 0.01731 | 281 | 0.0066905 | 829 | 0.019738 | 1.371 | A09 | STRW0.06506010
Horizontal Wall | Strada | STRW.06506010/DBE | 65 | 60 | 10 | #N/A | 877 | 877 | 877 | 0.020881 | 439 | 0.010452 | 965 | 0.022976 | 1 | A09 | STRW0.06506010/DBE
Horizontal Wall | Strada | STRW.06506011 | 65 | 60 | 11 | 12 | 926 | 926 | 926 | 0.022048 | 342 | 0.0081429 | 1062 | 0.025286 | 1.437 | A09 | STRW0.06506011
Horizontal Wall | Strada | STRW.06506011/DBE | 65 | 60 | 11 | 12 | 1226 | 1226 | 1226 | 0.02919 | 613 | 0.014595 | 1349 | 0.032119 | 1 | A09 | STRW0.06506011/DBE
Horizontal Wall | Strada | STRW.06506015 | 65 | 60 | 15 | 17 | 1153 | 1153 | 1153 | 0.027452 | 451 | 0.010738 | 1312 | 0.031238 | 1.355 | A09 | STRW0.06506015
Horizontal Wall | Strada | STRW.06506015/DBE | 65 | 60 | 15 | #N/A | 1403 | 1403 | 1403 | 0.033405 | 702 | 0.016714 | 1543 | 0.036738 | 1 | A09 | STRW0.06506015/DBE
Horizontal Wall | Strada | STRW.06506016 | 65 | 60 | 16 | 17 | 1304 | 1304 | 1304 | 0.031048 | 471 | 0.011214 | 1500 | 0.035714 | 1.47 | A09 | STRW0.06506016
Horizontal Wall | Strada | STRW.06506016/DBE | 65 | 60 | 16 | 17 | 1784 | 1784 | 1784 | 0.042476 | 892 | 0.021238 | 1962 | 0.046714 | 1 | A09 | STRW0.06506016/DBE
Horizontal Wall | Strada | STRW.06506020 | 65 | 60 | 20 | 22 | 1611 | 1611 | 1611 | 0.038357 | 630 | 0.015 | 1833 | 0.043643 | 1.355 | A09 | STRW0.06506020
Horizontal Wall | Strada | STRW.06506020/DBE | 65 | 60 | 20 | #N/A | 1861 | 1861 | 1861 | 0.04431 | 931 | 0.022167 | 2047 | 0.048738 | 1 | A09 | STRW0.06506020/DBE
Horizontal Wall | Strada | STRW.06506021 | 65 | 60 | 21 | 22 | 1818 | 1818 | 1818 | 0.043286 | 644 | 0.015333 | 2096 | 0.049905 | 1.497 | A09 | STRW0.06506021
Horizontal Wall | Strada | STRW.06506021/DBE | 65 | 60 | 21 | 22 | 2298 | 2298 | 2298 | 0.054714 | 1149 | 0.027357 | 2528 | 0.06019 | 1 | A09 | STRW0.06506021/DBE
Horizontal Wall | Strada | STRW.06507006 | 65 | 70 | 06 | 9 | 746 | 746 | 746 | 0.017762 | 292 | 0.0069524 | 848 | 0.02019 | 1.35 | A09 | STRW0.06507006
Horizontal Wall | Strada | STRW.06507010 | 65 | 70 | 10 | 12 | 848 | 848 | 848 | 0.02019 | 328 | 0.0078095 | 967 | 0.023024 | 1.371 | A09 | STRW0.06507010
Horizontal Wall | Strada | STRW.06507010/DBE | 65 | 70 | 10 | #N/A | 998 | 998 | 998 | 0.023762 | 499 | 0.011881 | 1098 | 0.026143 | 1 | A09 | STRW0.06507010/DBE
Horizontal Wall | Strada | STRW.06507011 | 65 | 70 | 11 | 12 | 1080 | 1080 | 1080 | 0.025714 | 399 | 0.0095 | 1239 | 0.0295 | 1.437 | A09 | STRW0.06507011
Horizontal Wall | Strada | STRW.06507011/DBE | 65 | 70 | 11 | 12 | 1380 | 1380 | 1380 | 0.032857 | 690 | 0.016429 | 1518 | 0.036143 | 1 | A09 | STRW0.06507011/DBE
Horizontal Wall | Strada | STRW.06507015 | 65 | 70 | 15 | 17 | 1345 | 1345 | 1345 | 0.032024 | 526 | 0.012524 | 1531 | 0.036452 | 1.355 | A09 | STRW0.06507015
Horizontal Wall | Strada | STRW.06507015/DBE | 65 | 70 | 15 | #N/A | 1595 | 1595 | 1595 | 0.037976 | 798 | 0.019 | 1755 | 0.041786 | 1 | A09 | STRW0.06507015/DBE
Horizontal Wall | Strada | STRW.06507016 | 65 | 70 | 16 | 17 | 1521 | 1521 | 1521 | 0.036214 | 549 | 0.013071 | 1749 | 0.041643 | 1.47 | A09 | STRW0.06507016
Horizontal Wall | Strada | STRW.06507016/DBE | 65 | 70 | 16 | 17 | 2001 | 2001 | 2001 | 0.047643 | 1001 | 0.023833 | 2201 | 0.052405 | 1 | A09 | STRW0.06507016/DBE
Horizontal Wall | Strada | STRW.06507020 | 65 | 70 | 20 | 22 | 1880 | 1880 | 1880 | 0.044762 | 735 | 0.0175 | 2139 | 0.050929 | 1.355 | A09 | STRW0.06507020
Horizontal Wall | Strada | STRW.06507020/DBE | 65 | 70 | 20 | #N/A | 2130 | 2130 | 2130 | 0.050714 | 1065 | 0.025357 | 2343 | 0.055786 | 1 | A09 | STRW0.06507020/DBE
Horizontal Wall | Strada | STRW.06507021 | 65 | 70 | 21 | 22 | 2121 | 2121 | 2121 | 0.0505 | 751 | 0.017881 | 2446 | 0.058238 | 1.497 | A09 | STRW0.06507021
Horizontal Wall | Strada | STRW.06507021/DBE | 65 | 70 | 21 | 22 | 2601 | 2601 | 2601 | 0.061929 | 1301 | 0.030976 | 2861 | 0.068119 | 1 | A09 | STRW0.06507021/DBE
Horizontal Wall | Strada | STRW.06508006 | 65 | 80 | 06 | 9 | 853 | 853 | 853 | 0.02031 | 334 | 0.0079524 | 970 | 0.023095 | 1.35 | A09 | STRW0.06508006
Horizontal Wall | Strada | STRW.06508010 | 65 | 80 | 10 | 12 | 969 | 969 | 969 | 0.023071 | 375 | 0.0089286 | 1105 | 0.02631 | 1.371 | A09 | STRW0.06508010
Horizontal Wall | Strada | STRW.06508010/DBE | 65 | 80 | 10 | #N/A | 1119 | 1119 | 1119 | 0.026643 | 560 | 0.013333 | 1231 | 0.02931 | 1 | A09 | STRW0.06508010/DBE
Horizontal Wall | Strada | STRW.06508011 | 65 | 80 | 11 | 12 | 1234 | 1234 | 1234 | 0.029381 | 455 | 0.010833 | 1415 | 0.03369 | 1.437 | A09 | STRW0.06508011
Horizontal Wall | Strada | STRW.06508011/DBE | 65 | 80 | 11 | 12 | 1534 | 1534 | 1534 | 0.036524 | 767 | 0.018262 | 1687 | 0.040167 | 1 | A09 | STRW0.06508011/DBE
Horizontal Wall | Strada | STRW.06508015 | 65 | 80 | 15 | 17 | 1538 | 1538 | 1538 | 0.036619 | 601 | 0.01431 | 1750 | 0.041667 | 1.355 | A09 | STRW0.06508015
Horizontal Wall | Strada | STRW.06508015/DBE | 65 | 80 | 15 | #N/A | 1788 | 1788 | 1788 | 0.042571 | 894 | 0.021286 | 1967 | 0.046833 | 1 | A09 | STRW0.06508015/DBE
Horizontal Wall | Strada | STRW.06508016 | 65 | 80 | 16 | 17 | 1738 | 1738 | 1738 | 0.041381 | 627 | 0.014929 | 1999 | 0.047595 | 1.47 | A09 | STRW0.06508016
Horizontal Wall | Strada | STRW.06508016/DBE | 65 | 80 | 16 | 17 | 2218 | 2218 | 2218 | 0.05281 | 1109 | 0.026405 | 2440 | 0.058095 | 1 | A09 | STRW0.06508016/DBE
Horizontal Wall | Strada | STRW.06508020 | 65 | 80 | 20 | 22 | 2148 | 2148 | 2148 | 0.051143 | 840 | 0.02 | 2444 | 0.05819 | 1.355 | A09 | STRW0.06508020
Horizontal Wall | Strada | STRW.06508020/DBE | 65 | 80 | 20 | #N/A | 2398 | 2398 | 2398 | 0.057095 | 1199 | 0.028548 | 2638 | 0.06281 | 1 | A09 | STRW0.06508020/DBE
Horizontal Wall | Strada | STRW.06508021 | 65 | 80 | 21 | 22 | 2424 | 2424 | 2424 | 0.057714 | 858 | 0.020429 | 2795 | 0.066548 | 1.497 | A09 | STRW0.06508021
Horizontal Wall | Strada | STRW.06508021/DBE | 65 | 80 | 21 | 22 | 2904 | 2904 | 2904 | 0.069143 | 1452 | 0.034571 | 3194 | 0.076048 | 1 | A09 | STRW0.06508021/DBE
Horizontal Wall | Strada | STRW.06509006 | 65 | 90 | 06 | 9 | 959 | 959 | 959 | 0.022833 | 376 | 0.0089524 | 1090 | 0.025952 | 1.35 | A09 | STRW0.06509006
Horizontal Wall | Strada | STRW.06509010 | 65 | 90 | 10 | 12 | 1090 | 1090 | 1090 | 0.025952 | 422 | 0.010048 | 1243 | 0.029595 | 1.371 | A09 | STRW0.06509010
Horizontal Wall | Strada | STRW.06509010/DBE | 65 | 90 | 10 | #N/A | 1390 | 1390 | 1390 | 0.033095 | 695 | 0.016548 | 1529 | 0.036405 | 1 | A09 | STRW0.06509010/DBE
Horizontal Wall | Strada | STRW.06509011 | 65 | 90 | 11 | 12 | 1389 | 1389 | 1389 | 0.033071 | 513 | 0.012214 | 1593 | 0.037929 | 1.437 | A09 | STRW0.06509011
Horizontal Wall | Strada | STRW.06509011/DBE | 65 | 90 | 11 | 12 | 1989 | 1989 | 1989 | 0.047357 | 995 | 0.02369 | 2188 | 0.052095 | 1 | A09 | STRW0.06509011/DBE
Horizontal Wall | Strada | STRW.06509015 | 65 | 90 | 15 | 17 | 1730 | 1730 | 1730 | 0.04119 | 676 | 0.016095 | 1969 | 0.046881 | 1.355 | A09 | STRW0.06509015
Horizontal Wall | Strada | STRW.06509015/DBE | 65 | 90 | 15 | #N/A | 2230 | 2230 | 2230 | 0.053095 | 1115 | 0.026548 | 2453 | 0.058405 | 1 | A09 | STRW0.06509015/DBE
Horizontal Wall | Strada | STRW.06509016 | 65 | 90 | 16 | 17 | 1956 | 1956 | 1956 | 0.046571 | 706 | 0.01681 | 2249 | 0.053548 | 1.47 | A09 | STRW0.06509016
Horizontal Wall | Strada | STRW.06509016/DBE | 65 | 90 | 16 | 17 | 2916 | 2916 | 2916 | 0.069429 | 1458 | 0.034714 | 3208 | 0.076381 | 1 | A09 | STRW0.06509016/DBE
Horizontal Wall | Strada | STRW.06509020 | 65 | 90 | 20 | 22 | 2417 | 2417 | 2417 | 0.057548 | 945 | 0.0225 | 2751 | 0.0655 | 1.355 | A09 | STRW0.06509020
Horizontal Wall | Strada | STRW.06509020/DBE | 65 | 90 | 20 | #N/A | 2917 | 2917 | 2917 | 0.069452 | 1459 | 0.034738 | 3209 | 0.076405 | 1 | A09 | STRW0.06509020/DBE
Horizontal Wall | Strada | STRW.06509021 | 65 | 90 | 21 | 22 | 2727 | 2727 | 2727 | 0.064929 | 965 | 0.022976 | 3144 | 0.074857 | 1.497 | A09 | STRW0.06509021
Horizontal Wall | Strada | STRW.06509021/DBE | 65 | 90 | 21 | 22 | 3687 | 3687 | 3687 | 0.087786 | 1844 | 0.043905 | 4056 | 0.096571 | 1 | A09 | STRW0.06509021/DBE
Horizontal Wall | Strada | STRW.06510006 | 65 | 100 | 06 | 9 | 1066 | 1066 | 1066 | 0.025381 | 418 | 0.0099524 | 1212 | 0.028857 | 1.35 | A09 | STRW0.06510006
Horizontal Wall | Strada | STRW.06510010 | 65 | 100 | 10 | 12 | 1211 | 1211 | 1211 | 0.028833 | 469 | 0.011167 | 1381 | 0.032881 | 1.371 | A09 | STRW0.06510010
Horizontal Wall | Strada | STRW.06510010/DBE | 65 | 100 | 10 | #N/A | 1511 | 1511 | 1511 | 0.035976 | 756 | 0.018 | 1662 | 0.039571 | 1 | A09 | STRW0.06510010/DBE
Horizontal Wall | Strada | STRW.06510011 | 65 | 100 | 11 | 12 | 1543 | 1543 | 1543 | 0.036738 | 569 | 0.013548 | 1770 | 0.042143 | 1.437 | A09 | STRW0.06510011
Horizontal Wall | Strada | STRW.06510011/DBE | 65 | 100 | 11 | 12 | 2143 | 2143 | 2143 | 0.051024 | 1072 | 0.025524 | 2357 | 0.056119 | 1 | A09 | STRW0.06510011/DBE
Horizontal Wall | Strada | STRW.06510015 | 65 | 100 | 15 | 17 | 1922 | 1922 | 1922 | 0.045762 | 752 | 0.017905 | 2187 | 0.052071 | 1.355 | A09 | STRW0.06510015
Horizontal Wall | Strada | STRW.06510015/DBE | 65 | 100 | 15 | #N/A | 2422 | 2422 | 2422 | 0.057667 | 1211 | 0.028833 | 2664 | 0.063429 | 1 | A09 | STRW0.06510015/DBE
Horizontal Wall | Strada | STRW.06510016 | 65 | 100 | 16 | 17 | 2173 | 2173 | 2173 | 0.051738 | 784 | 0.018667 | 2499 | 0.0595 | 1.47 | A09 | STRW0.06510016
Horizontal Wall | Strada | STRW.06510016/DBE | 65 | 100 | 16 | 17 | 3133 | 3133 | 3133 | 0.074595 | 1567 | 0.03731 | 3446 | 0.082048 | 1 | A09 | STRW0.06510016/DBE
Horizontal Wall | Strada | STRW.06510020 | 65 | 100 | 20 | 22 | 2685 | 2685 | 2685 | 0.063929 | 1050 | 0.025 | 3056 | 0.072762 | 1.355 | A09 | STRW0.06510020
Horizontal Wall | Strada | STRW.06510020/DBE | 65 | 100 | 20 | #N/A | 3185 | 3185 | 3185 | 0.075833 | 1593 | 0.037929 | 3504 | 0.083429 | 1 | A09 | STRW0.06510020/DBE
Horizontal Wall | Strada | STRW.06510021 | 65 | 100 | 21 | 22 | 3030 | 3030 | 3030 | 0.072143 | 1073 | 0.025548 | 3494 | 0.08319 | 1.497 | A09 | STRW0.06510021
Horizontal Wall | Strada | STRW.06510021/DBE | 65 | 100 | 21 | 22 | 3990 | 3990 | 3990 | 0.095 | 1995 | 0.0475 | 4389 | 0.1045 | 1 | A09 | STRW0.06510021/DBE
Horizontal Wall | Strada | STRW.06511006 | 65 | 110 | 06 | 9 | 1173 | 1173 | 1173 | 0.027929 | 460 | 0.010952 | 1334 | 0.031762 | 1.35 | A09 | STRW0.06511006
Horizontal Wall | Strada | STRW.06511010 | 65 | 110 | 10 | 12 | 1332 | 1332 | 1332 | 0.031714 | 515 | 0.012262 | 1518 | 0.036143 | 1.371 | A09 | STRW0.06511010
Horizontal Wall | Strada | STRW.06511010/DBE | 65 | 110 | 10 | #N/A | 1632 | 1632 | 1632 | 0.038857 | 816 | 0.019429 | 1795 | 0.042738 | 1 | A09 | STRW0.06511010/DBE
Horizontal Wall | Strada | STRW.06511011 | 65 | 110 | 11 | 12 | 1697 | 1697 | 1697 | 0.040405 | 626 | 0.014905 | 1946 | 0.046333 | 1.437 | A09 | STRW0.06511011
Horizontal Wall | Strada | STRW.06511011/DBE | 65 | 110 | 11 | 12 | 2297 | 2297 | 2297 | 0.05469 | 1149 | 0.027357 | 2527 | 0.060167 | 1 | A09 | STRW0.06511011/DBE
Horizontal Wall | Strada | STRW.06511015 | 65 | 110 | 15 | 17 | 2114 | 2114 | 2114 | 0.050333 | 827 | 0.01969 | 2406 | 0.057286 | 1.355 | A09 | STRW0.06511015
Horizontal Wall | Strada | STRW.06511015/DBE | 65 | 110 | 15 | #N/A | 2614 | 2614 | 2614 | 0.062238 | 1307 | 0.031119 | 2875 | 0.068452 | 1 | A09 | STRW0.06511015/DBE
Horizontal Wall | Strada | STRW.06511016 | 65 | 110 | 16 | 17 | 2390 | 2390 | 2390 | 0.056905 | 863 | 0.020548 | 2749 | 0.065452 | 1.47 | A09 | STRW0.06511016
Horizontal Wall | Strada | STRW.06511016/DBE | 65 | 110 | 16 | 17 | 3350 | 3350 | 3350 | 0.079762 | 1675 | 0.039881 | 3685 | 0.087738 | 1 | A09 | STRW0.06511016/DBE
Horizontal Wall | Strada | STRW.06511020 | 65 | 110 | 20 | 22 | 2954 | 2954 | 2954 | 0.070333 | 1155 | 0.0275 | 3362 | 0.080048 | 1.355 | A09 | STRW0.06511020
Horizontal Wall | Strada | STRW.06511020/DBE | 65 | 110 | 20 | #N/A | 3454 | 3454 | 3454 | 0.082238 | 1727 | 0.041119 | 3799 | 0.090452 | 1 | A09 | STRW0.06511020/DBE
Horizontal Wall | Strada | STRW.06511021 | 65 | 110 | 21 | 22 | 3333 | 3333 | 3333 | 0.079357 | 1180 | 0.028095 | 3843 | 0.0915 | 1.497 | A09 | STRW0.06511021
Horizontal Wall | Strada | STRW.06511021/DBE | 65 | 110 | 21 | 22 | 4293 | 4293 | 4293 | 0.10221 | 2147 | 0.051119 | 4722 | 0.11243 | 1 | A09 | STRW0.06511021/DBE
Horizontal Wall | Strada | STRW.06512006 | 65 | 120 | 06 | 9 | 1279 | 1279 | 1279 | 0.030452 | 501 | 0.011929 | 1454 | 0.034619 | 1.35 | A09 | STRW0.06512006
Horizontal Wall | Strada | STRW.06512010 | 65 | 120 | 10 | 12 | 1453 | 1453 | 1453 | 0.034595 | 562 | 0.013381 | 1656 | 0.039429 | 1.371 | A09 | STRW0.06512010
Horizontal Wall | Strada | STRW.06512010/DBE | 65 | 120 | 10 | #N/A | 1753 | 1753 | 1753 | 0.041738 | 877 | 0.020881 | 1928 | 0.045905 | 1 | A09 | STRW0.06512010/DBE
Horizontal Wall | Strada | STRW.06512011 | 65 | 120 | 11 | 12 | 1852 | 1852 | 1852 | 0.044095 | 683 | 0.016262 | 2124 | 0.050571 | 1.437 | A09 | STRW0.06512011
Horizontal Wall | Strada | STRW.06512011/DBE | 65 | 120 | 11 | 12 | 2452 | 2452 | 2452 | 0.058381 | 1226 | 0.02919 | 2697 | 0.064214 | 1 | A09 | STRW0.06512011/DBE
Horizontal Wall | Strada | STRW.06512015 | 65 | 120 | 15 | 17 | 2306 | 2306 | 2306 | 0.054905 | 902 | 0.021476 | 2624 | 0.062476 | 1.355 | A09 | STRW0.06512015
Horizontal Wall | Strada | STRW.06512015/DBE | 65 | 120 | 15 | #N/A | 2806 | 2806 | 2806 | 0.06681 | 1403 | 0.033405 | 3087 | 0.0735 | 1 | A09 | STRW0.06512015/DBE
Horizontal Wall | Strada | STRW.06512016 | 65 | 120 | 16 | 17 | 2608 | 2608 | 2608 | 0.062095 | 941 | 0.022405 | 2999 | 0.071405 | 1.47 | A09 | STRW0.06512016
Horizontal Wall | Strada | STRW.06512016/DBE | 65 | 120 | 16 | 17 | 3568 | 3568 | 3568 | 0.084952 | 1784 | 0.042476 | 3925 | 0.093452 | 1 | A09 | STRW0.06512016/DBE
Horizontal Wall | Strada | STRW.06512020 | 65 | 120 | 20 | 22 | 3222 | 3222 | 3222 | 0.076714 | 1260 | 0.03 | 3667 | 0.08731 | 1.355 | A09 | STRW0.06512020
Horizontal Wall | Strada | STRW.06512020/DBE | 65 | 120 | 20 | #N/A | 3722 | 3722 | 3722 | 0.088619 | 1861 | 0.04431 | 4094 | 0.097476 | 1 | A09 | STRW0.06512020/DBE
Horizontal Wall | Strada | STRW.06512021 | 65 | 120 | 21 | 22 | 3636 | 3636 | 3636 | 0.086571 | 1287 | 0.030643 | 4192 | 0.09981 | 1.497 | A09 | STRW0.06512021
Horizontal Wall | Strada | STRW.06512021/DBE | 65 | 120 | 21 | 22 | 4596 | 4596 | 4596 | 0.10943 | 2298 | 0.054714 | 5056 | 0.12038 | 1 | A09 | STRW0.06512021/DBE
Horizontal Wall | Strada | STRW.06514006 | 65 | 140 | 06 | 9 | 1492 | 1492 | 1492 | 0.035524 | 585 | 0.013929 | 1696 | 0.040381 | 1.35 | A09 | STRW0.06514006
Horizontal Wall | Strada | STRW.06514010 | 65 | 140 | 10 | 12 | 1695 | 1695 | 1695 | 0.040357 | 656 | 0.015619 | 1932 | 0.046 | 1.371 | A09 | STRW0.06514010
Horizontal Wall | Strada | STRW.06514010/DBE | 65 | 140 | 10 | #N/A | 1995 | 1995 | 1995 | 0.0475 | 998 | 0.023762 | 2195 | 0.052262 | 1 | A09 | STRW0.06514010/DBE
Horizontal Wall | Strada | STRW.06514011 | 65 | 140 | 11 | 12 | 2160 | 2160 | 2160 | 0.051429 | 797 | 0.018976 | 2478 | 0.059 | 1.437 | A09 | STRW0.06514011
Horizontal Wall | Strada | STRW.06514011/DBE | 65 | 140 | 11 | 12 | 2760 | 2760 | 2760 | 0.065714 | 1380 | 0.032857 | 3036 | 0.072286 | 1 | A09 | STRW0.06514011/DBE
Horizontal Wall | Strada | STRW.06514015 | 65 | 140 | 15 | 17 | 2691 | 2691 | 2691 | 0.064071 | 1052 | 0.025048 | 3062 | 0.072905 | 1.355 | A09 | STRW0.06514015
Horizontal Wall | Strada | STRW.06514015/DBE | 65 | 140 | 15 | #N/A | 3191 | 3191 | 3191 | 0.075976 | 1596 | 0.038 | 3510 | 0.083571 | 1 | A09 | STRW0.06514015/DBE
Horizontal Wall | Strada | STRW.06514016 | 65 | 140 | 16 | 17 | 3042 | 3042 | 3042 | 0.072429 | 1098 | 0.026143 | 3498 | 0.083286 | 1.47 | A09 | STRW0.06514016
Horizontal Wall | Strada | STRW.06514016/DBE | 65 | 140 | 16 | 17 | 4002 | 4002 | 4002 | 0.095286 | 2001 | 0.047643 | 4402 | 0.10481 | 1 | A09 | STRW0.06514016/DBE
Horizontal Wall | Strada | STRW.06514020 | 65 | 140 | 20 | 22 | 3759 | 3759 | 3759 | 0.0895 | 1470 | 0.035 | 4278 | 0.10186 | 1.355 | A09 | STRW0.06514020
Horizontal Wall | Strada | STRW.06514020/DBE | 65 | 140 | 20 | #N/A | 4259 | 4259 | 4259 | 0.1014 | 2130 | 0.050714 | 4685 | 0.11155 | 1 | A09 | STRW0.06514020/DBE
Horizontal Wall | Strada | STRW.06514021 | 65 | 140 | 21 | 22 | 4242 | 4242 | 4242 | 0.101 | 1502 | 0.035762 | 4891 | 0.11645 | 1.497 | A09 | STRW0.06514021
Horizontal Wall | Strada | STRW.06514021/DBE | 65 | 140 | 21 | 22 | 5202 | 5202 | 5202 | 0.12386 | 2601 | 0.061929 | 5722 | 0.13624 | 1 | A09 | STRW0.06514021/DBE
Horizontal Wall | Strada | STRW.06516006 | 65 | 160 | 06 | 9 | 1706 | 1706 | 1706 | 0.040619 | 669 | 0.015929 | 1940 | 0.04619 | 1.35 | A09 | STRW0.06516006
Horizontal Wall | Strada | STRW.06516010 | 65 | 160 | 10 | 12 | 1938 | 1938 | 1938 | 0.046143 | 750 | 0.017857 | 2209 | 0.052595 | 1.371 | A09 | STRW0.06516010
Horizontal Wall | Strada | STRW.06516010/DBE | 65 | 160 | 10 | #N/A | 2538 | 2538 | 2538 | 0.060429 | 1269 | 0.030214 | 2792 | 0.066476 | 1 | A09 | STRW0.06516010/DBE
Horizontal Wall | Strada | STRW.06516011 | 65 | 160 | 11 | 12 | 2469 | 2469 | 2469 | 0.058786 | 911 | 0.02169 | 2832 | 0.067429 | 1.437 | A09 | STRW0.06516011
Horizontal Wall | Strada | STRW.06516011/DBE | 65 | 160 | 11 | 12 | 3669 | 3669 | 3669 | 0.087357 | 1835 | 0.04369 | 4036 | 0.096095 | 1 | A09 | STRW0.06516011/DBE
Horizontal Wall | Strada | STRW.06516015 | 65 | 160 | 15 | 17 | 3075 | 3075 | 3075 | 0.073214 | 1202 | 0.028619 | 3499 | 0.08331 | 1.355 | A09 | STRW0.06516015
Horizontal Wall | Strada | STRW.06516015/DBE | 65 | 160 | 15 | #N/A | 4075 | 4075 | 4075 | 0.097024 | 2038 | 0.048524 | 4483 | 0.10674 | 1 | A09 | STRW0.06516015/DBE
Horizontal Wall | Strada | STRW.06516016 | 65 | 160 | 16 | 17 | 3477 | 3477 | 3477 | 0.082786 | 1255 | 0.029881 | 3999 | 0.095214 | 1.47 | A09 | STRW0.06516016
Horizontal Wall | Strada | STRW.06516016/DBE | 65 | 160 | 16 | 17 | 5397 | 5397 | 5397 | 0.1285 | 2699 | 0.064262 | 5937 | 0.14136 | 1 | A09 | STRW0.06516016/DBE
Horizontal Wall | Strada | STRW.06516020 | 65 | 160 | 20 | 22 | 4296 | 4296 | 4296 | 0.10229 | 1680 | 0.04 | 4889 | 0.1164 | 1.355 | A09 | STRW0.06516020
Horizontal Wall | Strada | STRW.06516020/DBE | 65 | 160 | 20 | #N/A | 5296 | 5296 | 5296 | 0.1261 | 2648 | 0.063048 | 5826 | 0.13871 | 1 | A09 | STRW0.06516020/DBE
Horizontal Wall | Strada | STRW.06516021 | 65 | 160 | 21 | 22 | 4848 | 4848 | 4848 | 0.11543 | 1716 | 0.040857 | 5590 | 0.1331 | 1.497 | A09 | STRW0.06516021
Horizontal Wall | Strada | STRW.06516021/DBE | 65 | 160 | 21 | 22 | 6768 | 6768 | 6768 | 0.16114 | 3384 | 0.080571 | 7445 | 0.17726 | 1 | A09 | STRW0.06516021/DBE
Horizontal Wall | Strada | STRW.06518006 | 65 | 180 | 06 | 9 | 1919 | 1919 | 1919 | 0.04569 | 752 | 0.017905 | 2182 | 0.051952 | 1.35 | A09 | STRW0.06518006
Horizontal Wall | Strada | STRW.06518010 | 65 | 180 | 10 | 12 | 2180 | 2180 | 2180 | 0.051905 | 844 | 0.020095 | 2485 | 0.059167 | 1.371 | A09 | STRW0.06518010
Horizontal Wall | Strada | STRW.06518010/DBE | 65 | 180 | 10 | #N/A | 2780 | 2780 | 2780 | 0.06619 | 1390 | 0.033095 | 3058 | 0.07281 | 1 | A09 | STRW0.06518010/DBE
Horizontal Wall | Strada | STRW.06518011 | 65 | 180 | 11 | 12 | 2777 | 2777 | 2777 | 0.066119 | 1025 | 0.024405 | 3185 | 0.075833 | 1.437 | A09 | STRW0.06518011
Horizontal Wall | Strada | STRW.06518011/DBE | 65 | 180 | 11 | 12 | 3977 | 3977 | 3977 | 0.09469 | 1989 | 0.047357 | 4375 | 0.10417 | 1 | A09 | STRW0.06518011/DBE
Horizontal Wall | Strada | STRW.06518015 | 65 | 180 | 15 | 17 | 3460 | 3460 | 3460 | 0.082381 | 1353 | 0.032214 | 3937 | 0.093738 | 1.355 | A09 | STRW0.06518015
Horizontal Wall | Strada | STRW.06518015/DBE | 65 | 180 | 15 | #N/A | 4460 | 4460 | 4460 | 0.10619 | 2230 | 0.053095 | 4906 | 0.11681 | 1 | A09 | STRW0.06518015/DBE
Horizontal Wall | Strada | STRW.06518016 | 65 | 180 | 16 | 17 | 3911 | 3911 | 3911 | 0.093119 | 1412 | 0.033619 | 4498 | 0.1071 | 1.47 | A09 | STRW0.06518016
Horizontal Wall | Strada | STRW.06518016/DBE | 65 | 180 | 16 | 17 | 5831 | 5831 | 5831 | 0.13883 | 2916 | 0.069429 | 6414 | 0.15271 | 1 | A09 | STRW0.06518016/DBE
Horizontal Wall | Strada | STRW.06518020 | 65 | 180 | 20 | 22 | 4833 | 4833 | 4833 | 0.11507 | 1890 | 0.045 | 5500 | 0.13095 | 1.355 | A09 | STRW0.06518020
Horizontal Wall | Strada | STRW.06518020/DBE | 65 | 180 | 20 | #N/A | 5833 | 5833 | 5833 | 0.13888 | 2917 | 0.069452 | 6416 | 0.15276 | 1 | A09 | STRW0.06518020/DBE
Horizontal Wall | Strada | STRW.06518021 | 65 | 180 | 21 | 22 | 5454 | 5454 | 5454 | 0.12986 | 1931 | 0.045976 | 6288 | 0.14971 | 1.497 | A09 | STRW0.06518021
Horizontal Wall | Strada | STRW.06518021/DBE | 65 | 180 | 21 | 22 | 7374 | 7374 | 7374 | 0.17557 | 3687 | 0.087786 | 8111 | 0.19312 | 1 | A09 | STRW0.06518021/DBE
Horizontal Wall | Strada | STRW.06520006 | 65 | 200 | 06 | 9 | 2132 | 2132 | 2132 | 0.050762 | 836 | 0.019905 | 2424 | 0.057714 | 1.35 | A09 | STRW0.06520006
Horizontal Wall | Strada | STRW.06520010 | 65 | 200 | 10 | 12 | 2422 | 2422 | 2422 | 0.057667 | 937 | 0.02231 | 2761 | 0.065738 | 1.371 | A09 | STRW0.06520010
Horizontal Wall | Strada | STRW.06520010/DBE | 65 | 200 | 10 | #N/A | 3022 | 3022 | 3022 | 0.071952 | 1511 | 0.035976 | 3324 | 0.079143 | 1 | A09 | STRW0.06520010/DBE
Horizontal Wall | Strada | STRW.06520011 | 65 | 200 | 11 | 12 | 3086 | 3086 | 3086 | 0.073476 | 1139 | 0.027119 | 3540 | 0.084286 | 1.437 | A09 | STRW0.06520011
Horizontal Wall | Strada | STRW.06520011/DBE | 65 | 200 | 11 | 12 | 4286 | 4286 | 4286 | 0.10205 | 2143 | 0.051024 | 4715 | 0.11226 | 1 | A09 | STRW0.06520011/DBE
Horizontal Wall | Strada | STRW.06520015 | 65 | 200 | 15 | 17 | 3844 | 3844 | 3844 | 0.091524 | 1503 | 0.035786 | 4374 | 0.10414 | 1.355 | A09 | STRW0.06520015
Horizontal Wall | Strada | STRW.06520015/DBE | 65 | 200 | 15 | #N/A | 4844 | 4844 | 4844 | 0.11533 | 2422 | 0.057667 | 5328 | 0.12686 | 1 | A09 | STRW0.06520015/DBE
Horizontal Wall | Strada | STRW.06520016 | 65 | 200 | 16 | 17 | 4346 | 4346 | 4346 | 0.10348 | 1569 | 0.037357 | 4998 | 0.119 | 1.47 | A09 | STRW0.06520016
Horizontal Wall | Strada | STRW.06520016/DBE | 65 | 200 | 16 | 17 | 6266 | 6266 | 6266 | 0.14919 | 3133 | 0.074595 | 6893 | 0.16412 | 1 | A09 | STRW0.06520016/DBE
Horizontal Wall | Strada | STRW.06520020 | 65 | 200 | 20 | 22 | 5370 | 5370 | 5370 | 0.12786 | 2100 | 0.05 | 6111 | 0.1455 | 1.355 | A09 | STRW0.06520020
Horizontal Wall | Strada | STRW.06520020/DBE | 65 | 200 | 20 | #N/A | 6370 | 6370 | 6370 | 0.15167 | 3185 | 0.075833 | 7007 | 0.16683 | 1 | A09 | STRW0.06520020/DBE
Horizontal Wall | Strada | STRW.06520021 | 65 | 200 | 21 | 22 | 6060 | 6060 | 6060 | 0.14429 | 2145 | 0.051071 | 6987 | 0.16636 | 1.497 | A09 | STRW0.06520021
Horizontal Wall | Strada | STRW.06520021/DBE | 65 | 200 | 21 | 22 | 7980 | 7980 | 7980 | 0.19 | 3990 | 0.095 | 8778 | 0.209 | 1 | A09 | STRW0.06520021/DBE
Horizontal Wall | Strada | STRW.06524006 | 65 | 240 | 06 | 9 | 2558 | 2558 | 2558 | 0.060905 | 1003 | 0.023881 | 2908 | 0.069238 | 1.35 | A09 | STRW0.06524006
Horizontal Wall | Strada | STRW.06524010 | 65 | 240 | 10 | 12 | 2906 | 2906 | 2906 | 0.06919 | 1125 | 0.026786 | 3313 | 0.078881 | 1.371 | A09 | STRW0.06524010
Horizontal Wall | Strada | STRW.06524010/DBE | 65 | 240 | 10 | #N/A | 3806 | 3806 | 3806 | 0.090619 | 1903 | 0.04531 | 4187 | 0.09969 | 1 | A09 | STRW0.06524010/DBE
Horizontal Wall | Strada | STRW.06524011 | 65 | 240 | 11 | 12 | 3703 | 3703 | 3703 | 0.088167 | 1366 | 0.032524 | 4247 | 0.10112 | 1.437 | A09 | STRW0.06524011
Horizontal Wall | Strada | STRW.06524011/DBE | 65 | 240 | 11 | 12 | 5503 | 5503 | 5503 | 0.13102 | 2752 | 0.065524 | 6053 | 0.14412 | 1 | A09 | STRW0.06524011/DBE
Horizontal Wall | Strada | STRW.06524015 | 65 | 240 | 15 | 17 | 4613 | 4613 | 4613 | 0.10983 | 1804 | 0.042952 | 5250 | 0.125 | 1.355 | A09 | STRW0.06524015
Horizontal Wall | Strada | STRW.06524015/DBE | 65 | 240 | 15 | #N/A | 6113 | 6113 | 6113 | 0.14555 | 3057 | 0.072786 | 6724 | 0.1601 | 1 | A09 | STRW0.06524015/DBE
Horizontal Wall | Strada | STRW.06524016 | 65 | 240 | 16 | 17 | 5215 | 5215 | 5215 | 0.12417 | 1883 | 0.044833 | 5997 | 0.14279 | 1.47 | A09 | STRW0.06524016
Horizontal Wall | Strada | STRW.06524016/DBE | 65 | 240 | 16 | 17 | 8095 | 8095 | 8095 | 0.19274 | 4048 | 0.096381 | 8905 | 0.21202 | 1 | A09 | STRW0.06524016/DBE
Horizontal Wall | Strada | STRW.06524020 | 65 | 240 | 20 | 22 | 6444 | 6444 | 6444 | 0.15343 | 2520 | 0.06 | 7333 | 0.1746 | 1.355 | A09 | STRW0.06524020
Horizontal Wall | Strada | STRW.06524020/DBE | 65 | 240 | 20 | #N/A | 7944 | 7944 | 7944 | 0.18914 | 3972 | 0.094571 | 8738 | 0.20805 | 1 | A09 | STRW0.06524020/DBE
Horizontal Wall | Strada | STRW.06524021 | 65 | 240 | 21 | 22 | 7272 | 7272 | 7272 | 0.17314 | 2574 | 0.061286 | 8385 | 0.19964 | 1.497 | A09 | STRW0.06524021
Horizontal Wall | Strada | STRW.06524021/DBE | 65 | 240 | 21 | 22 | 10152 | 10152 | 10152 | 0.24171 | 5076 | 0.12086 | 11167 | 0.26588 | 1 | A09 | STRW0.06524021/DBE
Horizontal Wall | Strada | STRW.06528006 | 65 | 280 | 06 | 9 | 2985 | 2985 | 2985 | 0.071071 | 1170 | 0.027857 | 3394 | 0.08081 | 1.35 | A09 | STRW0.06528006
Horizontal Wall | Strada | STRW.06528010 | 65 | 280 | 10 | 12 | 3391 | 3391 | 3391 | 0.080738 | 1312 | 0.031238 | 3866 | 0.092048 | 1.371 | A09 | STRW0.06528010
Horizontal Wall | Strada | STRW.06528010/DBE | 65 | 280 | 10 | #N/A | 4291 | 4291 | 4291 | 0.10217 | 2146 | 0.051095 | 4720 | 0.11238 | 1 | A09 | STRW0.06528010/DBE
Horizontal Wall | Strada | STRW.06528011 | 65 | 280 | 11 | 12 | 4320 | 4320 | 4320 | 0.10286 | 1594 | 0.037952 | 4955 | 0.11798 | 1.437 | A09 | STRW0.06528011
Horizontal Wall | Strada | STRW.06528011/DBE | 65 | 280 | 11 | 12 | 6120 | 6120 | 6120 | 0.14571 | 3060 | 0.072857 | 6732 | 0.16029 | 1 | A09 | STRW0.06528011/DBE
Horizontal Wall | Strada | STRW.06528015 | 65 | 280 | 15 | 17 | 5382 | 5382 | 5382 | 0.12814 | 2104 | 0.050095 | 6125 | 0.14583 | 1.355 | A09 | STRW0.06528015
Horizontal Wall | Strada | STRW.06528015/DBE | 65 | 280 | 15 | #N/A | 6882 | 6882 | 6882 | 0.16386 | 3441 | 0.081929 | 7570 | 0.18024 | 1 | A09 | STRW0.06528015/DBE
Horizontal Wall | Strada | STRW.06528016 | 65 | 280 | 16 | 17 | 6084 | 6084 | 6084 | 0.14486 | 2196 | 0.052286 | 6997 | 0.1666 | 1.47 | A09 | STRW0.06528016
Horizontal Wall | Strada | STRW.06528016/DBE | 65 | 280 | 16 | 17 | 8964 | 8964 | 8964 | 0.21343 | 4482 | 0.10671 | 9860 | 0.23476 | 1 | A09 | STRW0.06528016/DBE
Horizontal Wall | Strada | STRW.06528020 | 65 | 280 | 20 | 22 | 7518 | 7518 | 7518 | 0.179 | 2940 | 0.07 | 8555 | 0.20369 | 1.355 | A09 | STRW0.06528020
Horizontal Wall | Strada | STRW.06528020/DBE | 65 | 280 | 20 | #N/A | 9018 | 9018 | 9018 | 0.21471 | 4509 | 0.10736 | 9920 | 0.23619 | 1 | A09 | STRW0.06528020/DBE
Horizontal Wall | Strada | STRW.06528021 | 65 | 280 | 21 | 22 | 8484 | 8484 | 8484 | 0.202 | 3003 | 0.0715 | 9782 | 0.2329 | 1.497 | A09 | STRW0.06528021
Horizontal Wall | Strada | STRW.06528021/DBE | 65 | 280 | 21 | 22 | 11364 | 11364 | 11364 | 0.27057 | 5682 | 0.13529 | 12500 | 0.29762 | 1 | A09 | STRW0.06528021/DBE
Horizontal Wall | Strada | STRW.09506006 | 95 | 60 | 06 | 9 | 736 | 736 | 736 | 0.017524 | 297 | 0.0070714 | 834 | 0.019857 | 1.307 | A09 | STRW0.09506006
Horizontal Wall | Strada | STRW.09506010 | 95 | 60 | 10 | 12 | 836 | 836 | 836 | 0.019905 | 329 | 0.0078333 | 951 | 0.022643 | 1.343 | A09 | STRW0.09506010
Horizontal Wall | Strada | STRW.09506010/DBE | 95 | 60 | 10 | #N/A | 986 | 986 | 986 | 0.023476 | 493 | 0.011738 | 1085 | 0.025833 | 1 | A09 | STRW0.09506010/DBE
Horizontal Wall | Strada | STRW.09506011 | 95 | 60 | 11 | 12 | 1078 | 1078 | 1078 | 0.025667 | 399 | 0.0095 | 1235 | 0.029405 | 1.434 | A09 | STRW0.09506011
Horizontal Wall | Strada | STRW.09506011/DBE | 95 | 60 | 11 | 12 | 1378 | 1378 | 1378 | 0.03281 | 689 | 0.016405 | 1516 | 0.036095 | 1 | A09 | STRW0.09506011/DBE
Horizontal Wall | Strada | STRW.09506015 | 95 | 60 | 15 | 17 | 1288 | 1288 | 1288 | 0.030667 | 516 | 0.012286 | 1461 | 0.034786 | 1.32 | A09 | STRW0.09506015
Horizontal Wall | Strada | STRW.09506015/DBE | 95 | 60 | 15 | #N/A | 1538 | 1538 | 1538 | 0.036619 | 769 | 0.01831 | 1692 | 0.040286 | 1 | A09 | STRW0.09506015/DBE
Horizontal Wall | Strada | STRW.09506016 | 95 | 60 | 16 | 17 | 1606 | 1606 | 1606 | 0.038238 | 575 | 0.01369 | 1850 | 0.044048 | 1.482 | A09 | STRW0.09506016
Horizontal Wall | Strada | STRW.09506016/DBE | 95 | 60 | 16 | 17 | 2086 | 2086 | 2086 | 0.049667 | 1043 | 0.024833 | 2295 | 0.054643 | 1 | A09 | STRW0.09506016/DBE
Horizontal Wall | Strada | STRW.09506020 | 95 | 60 | 20 | 22 | 1795 | 1795 | 1795 | 0.042738 | 720 | 0.017143 | 2036 | 0.048476 | 1.32 | A09 | STRW0.09506020
Horizontal Wall | Strada | STRW.09506020/DBE | 95 | 60 | 20 | #N/A | 2045 | 2045 | 2045 | 0.04869 | 1023 | 0.024357 | 2250 | 0.053571 | 1 | A09 | STRW0.09506020/DBE
Horizontal Wall | Strada | STRW.09506021 | 95 | 60 | 21 | 22 | 2352 | 2352 | 2352 | 0.056 | 818 | 0.019476 | 2719 | 0.064738 | 1.522 | A09 | STRW0.09506021
Horizontal Wall | Strada | STRW.09506021/DBE | 95 | 60 | 21 | 22 | 2832 | 2832 | 2832 | 0.067429 | 1416 | 0.033714 | 3115 | 0.074167 | 1 | A09 | STRW0.09506021/DBE
Horizontal Wall | Strada | STRW.09507006 | 95 | 70 | 06 | 9 | 858 | 858 | 858 | 0.020429 | 347 | 0.0082619 | 972 | 0.023143 | 1.307 | A09 | STRW0.09507006
Horizontal Wall | Strada | STRW.09507010 | 95 | 70 | 10 | 12 | 975 | 975 | 975 | 0.023214 | 384 | 0.0091429 | 1109 | 0.026405 | 1.343 | A09 | STRW0.09507010
Horizontal Wall | Strada | STRW.09507010/DBE | 95 | 70 | 10 | #N/A | 1125 | 1125 | 1125 | 0.026786 | 563 | 0.013405 | 1238 | 0.029476 | 1 | A09 | STRW0.09507010/DBE
Horizontal Wall | Strada | STRW.09507011 | 95 | 70 | 11 | 12 | 1257 | 1257 | 1257 | 0.029929 | 465 | 0.011071 | 1441 | 0.03431 | 1.434 | A09 | STRW0.09507011
Horizontal Wall | Strada | STRW.09507011/DBE | 95 | 70 | 11 | 12 | 1557 | 1557 | 1557 | 0.037071 | 779 | 0.018548 | 1713 | 0.040786 | 1 | A09 | STRW0.09507011/DBE
Horizontal Wall | Strada | STRW.09507015 | 95 | 70 | 15 | 17 | 1502 | 1502 | 1502 | 0.035762 | 602 | 0.014333 | 1703 | 0.040548 | 1.32 | A09 | STRW0.09507015
Horizontal Wall | Strada | STRW.09507015/DBE | 95 | 70 | 15 | #N/A | 1752 | 1752 | 1752 | 0.041714 | 876 | 0.020857 | 1927 | 0.045881 | 1 | A09 | STRW0.09507015/DBE
Horizontal Wall | Strada | STRW.09507016 | 95 | 70 | 16 | 17 | 1874 | 1874 | 1874 | 0.044619 | 671 | 0.015976 | 2159 | 0.051405 | 1.482 | A09 | STRW0.09507016
Horizontal Wall | Strada | STRW.09507016/DBE | 95 | 70 | 16 | 17 | 2354 | 2354 | 2354 | 0.056048 | 1177 | 0.028024 | 2589 | 0.061643 | 1 | A09 | STRW0.09507016/DBE
Horizontal Wall | Strada | STRW.09507020 | 95 | 70 | 20 | 22 | 2094 | 2094 | 2094 | 0.049857 | 840 | 0.02 | 2375 | 0.056548 | 1.32 | A09 | STRW0.09507020
Horizontal Wall | Strada | STRW.09507020/DBE | 95 | 70 | 20 | #N/A | 2344 | 2344 | 2344 | 0.05581 | 1172 | 0.027905 | 2578 | 0.061381 | 1 | A09 | STRW0.09507020/DBE
Horizontal Wall | Strada | STRW.09507021 | 95 | 70 | 21 | 22 | 2744 | 2744 | 2744 | 0.065333 | 955 | 0.022738 | 3172 | 0.075524 | 1.522 | A09 | STRW0.09507021
Horizontal Wall | Strada | STRW.09507021/DBE | 95 | 70 | 21 | 22 | 3224 | 3224 | 3224 | 0.076762 | 1612 | 0.038381 | 3546 | 0.084429 | 1 | A09 | STRW0.09507021/DBE
Horizontal Wall | Strada | STRW.09508006 | 95 | 80 | 06 | 9 | 981 | 981 | 981 | 0.023357 | 396 | 0.0094286 | 1111 | 0.026452 | 1.307 | A09 | STRW0.09508006
Horizontal Wall | Strada | STRW.09508010 | 95 | 80 | 10 | 12 | 1114 | 1114 | 1114 | 0.026524 | 439 | 0.010452 | 1267 | 0.030167 | 1.343 | A09 | STRW0.09508010
Horizontal Wall | Strada | STRW.09508010/DBE | 95 | 80 | 10 | #N/A | 1264 | 1264 | 1264 | 0.030095 | 632 | 0.015048 | 1390 | 0.033095 | 1 | A09 | STRW0.09508010/DBE
Horizontal Wall | Strada | STRW.09508011 | 95 | 80 | 11 | 12 | 1437 | 1437 | 1437 | 0.034214 | 532 | 0.012667 | 1647 | 0.039214 | 1.434 | A09 | STRW0.09508011
Horizontal Wall | Strada | STRW.09508011/DBE | 95 | 80 | 11 | 12 | 1737 | 1737 | 1737 | 0.041357 | 869 | 0.02069 | 1911 | 0.0455 | 1 | A09 | STRW0.09508011/DBE
Horizontal Wall | Strada | STRW.09508015 | 95 | 80 | 15 | 17 | 1717 | 1717 | 1717 | 0.040881 | 689 | 0.016405 | 1947 | 0.046357 | 1.32 | A09 | STRW0.09508015
Horizontal Wall | Strada | STRW.09508015/DBE | 95 | 80 | 15 | #N/A | 1967 | 1967 | 1967 | 0.046833 | 984 | 0.023429 | 2164 | 0.051524 | 1 | A09 | STRW0.09508015/DBE
Horizontal Wall | Strada | STRW.09508016 | 95 | 80 | 16 | 17 | 2142 | 2142 | 2142 | 0.051 | 767 | 0.018262 | 2468 | 0.058762 | 1.482 | A09 | STRW0.09508016
Horizontal Wall | Strada | STRW.09508016/DBE | 95 | 80 | 16 | 17 | 2622 | 2622 | 2622 | 0.062429 | 1311 | 0.031214 | 2884 | 0.068667 | 1 | A09 | STRW0.09508016/DBE
Horizontal Wall | Strada | STRW.09508020 | 95 | 80 | 20 | 22 | 2394 | 2394 | 2394 | 0.057 | 960 | 0.022857 | 2715 | 0.064643 | 1.32 | A09 | STRW0.09508020
Horizontal Wall | Strada | STRW.09508020/DBE | 95 | 80 | 20 | #N/A | 2644 | 2644 | 2644 | 0.062952 | 1322 | 0.031476 | 2908 | 0.069238 | 1 | A09 | STRW0.09508020/DBE
Horizontal Wall | Strada | STRW.09508021 | 95 | 80 | 21 | 22 | 3136 | 3136 | 3136 | 0.074667 | 1091 | 0.025976 | 3625 | 0.08631 | 1.522 | A09 | STRW0.09508021
Horizontal Wall | Strada | STRW.09508021/DBE | 95 | 80 | 21 | 22 | 3616 | 3616 | 3616 | 0.086095 | 1808 | 0.043048 | 3978 | 0.094714 | 1 | A09 | STRW0.09508021/DBE
Horizontal Wall | Strada | STRW.09509006 | 95 | 90 | 06 | 9 | 1103 | 1103 | 1103 | 0.026262 | 446 | 0.010619 | 1250 | 0.029762 | 1.307 | A09 | STRW0.09509006
Horizontal Wall | Strada | STRW.09509010 | 95 | 90 | 10 | 12 | 1254 | 1254 | 1254 | 0.029857 | 494 | 0.011762 | 1426 | 0.033952 | 1.343 | A09 | STRW0.09509010
Horizontal Wall | Strada | STRW.09509010/DBE | 95 | 90 | 10 | #N/A | 1554 | 1554 | 1554 | 0.037 | 777 | 0.0185 | 1709 | 0.04069 | 1 | A09 | STRW0.09509010/DBE
Horizontal Wall | Strada | STRW.09509011 | 95 | 90 | 11 | 12 | 1616 | 1616 | 1616 | 0.038476 | 598 | 0.014238 | 1852 | 0.044095 | 1.434 | A09 | STRW0.09509011
Horizontal Wall | Strada | STRW.09509011/DBE | 95 | 90 | 11 | 12 | 2216 | 2216 | 2216 | 0.052762 | 1108 | 0.026381 | 2438 | 0.058048 | 1 | A09 | STRW0.09509011/DBE
Horizontal Wall | Strada | STRW.09509015 | 95 | 90 | 15 | 17 | 1931 | 1931 | 1931 | 0.045976 | 774 | 0.018429 | 2190 | 0.052143 | 1.32 | A09 | STRW0.09509015
Horizontal Wall | Strada | STRW.09509015/DBE | 95 | 90 | 15 | #N/A | 2431 | 2431 | 2431 | 0.057881 | 1216 | 0.028952 | 2674 | 0.063667 | 1 | A09 | STRW0.09509015/DBE
Horizontal Wall | Strada | STRW.09509016 | 95 | 90 | 16 | 17 | 2409 | 2409 | 2409 | 0.057357 | 862 | 0.020524 | 2775 | 0.066071 | 1.482 | A09 | STRW0.09509016
Horizontal Wall | Strada | STRW.09509016/DBE | 95 | 90 | 16 | 17 | 3369 | 3369 | 3369 | 0.080214 | 1685 | 0.040119 | 3706 | 0.088238 | 1 | A09 | STRW0.09509016/DBE
Horizontal Wall | Strada | STRW.09509020 | 95 | 90 | 20 | 22 | 2693 | 2693 | 2693 | 0.064119 | 1080 | 0.025714 | 3054 | 0.072714 | 1.32 | A09 | STRW0.09509020
Horizontal Wall | Strada | STRW.09509020/DBE | 95 | 90 | 20 | #N/A | 3193 | 3193 | 3193 | 0.076024 | 1597 | 0.038024 | 3512 | 0.083619 | 1 | A09 | STRW0.09509020/DBE
Horizontal Wall | Strada | STRW.09509021 | 95 | 90 | 21 | 22 | 3528 | 3528 | 3528 | 0.084 | 1228 | 0.029238 | 4078 | 0.097095 | 1.522 | A09 | STRW0.09509021
Horizontal Wall | Strada | STRW.09509021/DBE | 95 | 90 | 21 | 22 | 4488 | 4488 | 4488 | 0.10686 | 2244 | 0.053429 | 4937 | 0.11755 | 1 | A09 | STRW0.09509021/DBE
Horizontal Wall | Strada | STRW.09510006 | 95 | 100 | 06 | 9 | 1226 | 1226 | 1226 | 0.02919 | 495 | 0.011786 | 1389 | 0.033071 | 1.307 | A09 | STRW0.09510006
Horizontal Wall | Strada | STRW.09510010 | 95 | 100 | 10 | 12 | 1393 | 1393 | 1393 | 0.033167 | 549 | 0.013071 | 1584 | 0.037714 | 1.343 | A09 | STRW0.09510010
Horizontal Wall | Strada | STRW.09510010/DBE | 95 | 100 | 10 | #N/A | 1693 | 1693 | 1693 | 0.04031 | 847 | 0.020167 | 1862 | 0.044333 | 1 | A09 | STRW0.09510010/DBE
Horizontal Wall | Strada | STRW.09510011 | 95 | 100 | 11 | 12 | 1796 | 1796 | 1796 | 0.042762 | 665 | 0.015833 | 2058 | 0.049 | 1.434 | A09 | STRW0.09510011
Horizontal Wall | Strada | STRW.09510011/DBE | 95 | 100 | 11 | 12 | 2396 | 2396 | 2396 | 0.057048 | 1198 | 0.028524 | 2636 | 0.062762 | 1 | A09 | STRW0.09510011/DBE
Horizontal Wall | Strada | STRW.09510015 | 95 | 100 | 15 | 17 | 2146 | 2146 | 2146 | 0.051095 | 861 | 0.0205 | 2434 | 0.057952 | 1.32 | A09 | STRW0.09510015
Horizontal Wall | Strada | STRW.09510015/DBE | 95 | 100 | 15 | #N/A | 2646 | 2646 | 2646 | 0.063 | 1323 | 0.0315 | 2911 | 0.06931 | 1 | A09 | STRW0.09510015/DBE
Horizontal Wall | Strada | STRW.09510016 | 95 | 100 | 16 | 17 | 2677 | 2677 | 2677 | 0.063738 | 958 | 0.02281 | 3084 | 0.073429 | 1.482 | A09 | STRW0.09510016
Horizontal Wall | Strada | STRW.09510016/DBE | 95 | 100 | 16 | 17 | 3637 | 3637 | 3637 | 0.086595 | 1819 | 0.04331 | 4001 | 0.095262 | 1 | A09 | STRW0.09510016/DBE
Horizontal Wall | Strada | STRW.09510020 | 95 | 100 | 20 | 22 | 2992 | 2992 | 2992 | 0.071238 | 1200 | 0.028571 | 3393 | 0.080786 | 1.32 | A09 | STRW0.09510020
Horizontal Wall | Strada | STRW.09510020/DBE | 95 | 100 | 20 | #N/A | 3492 | 3492 | 3492 | 0.083143 | 1746 | 0.041571 | 3841 | 0.091452 | 1 | A09 | STRW0.09510020/DBE
Horizontal Wall | Strada | STRW.09510021 | 95 | 100 | 21 | 22 | 3920 | 3920 | 3920 | 0.093333 | 1364 | 0.032476 | 4532 | 0.1079 | 1.522 | A09 | STRW0.09510021
Horizontal Wall | Strada | STRW.09510021/DBE | 95 | 100 | 21 | 22 | 4880 | 4880 | 4880 | 0.11619 | 2440 | 0.058095 | 5368 | 0.12781 | 1 | A09 | STRW0.09510021/DBE
Horizontal Wall | Strada | STRW.09511006 | 95 | 110 | 06 | 9 | 1349 | 1349 | 1349 | 0.032119 | 545 | 0.012976 | 1528 | 0.036381 | 1.307 | A09 | STRW0.09511006
Horizontal Wall | Strada | STRW.09511010 | 95 | 110 | 10 | 12 | 1532 | 1532 | 1532 | 0.036476 | 604 | 0.014381 | 1742 | 0.041476 | 1.343 | A09 | STRW0.09511010
Horizontal Wall | Strada | STRW.09511010/DBE | 95 | 110 | 10 | #N/A | 1832 | 1832 | 1832 | 0.043619 | 916 | 0.02181 | 2015 | 0.047976 | 1 | A09 | STRW0.09511010/DBE
Horizontal Wall | Strada | STRW.09511011 | 95 | 110 | 11 | 12 | 1976 | 1976 | 1976 | 0.047048 | 731 | 0.017405 | 2264 | 0.053905 | 1.434 | A09 | STRW0.09511011
Horizontal Wall | Strada | STRW.09511011/DBE | 95 | 110 | 11 | 12 | 2576 | 2576 | 2576 | 0.061333 | 1288 | 0.030667 | 2834 | 0.067476 | 1 | A09 | STRW0.09511011/DBE
Horizontal Wall | Strada | STRW.09511015 | 95 | 110 | 15 | 17 | 2361 | 2361 | 2361 | 0.056214 | 947 | 0.022548 | 2677 | 0.063738 | 1.32 | A09 | STRW0.09511015
Horizontal Wall | Strada | STRW.09511015/DBE | 95 | 110 | 15 | #N/A | 2861 | 2861 | 2861 | 0.068119 | 1431 | 0.034071 | 3147 | 0.074929 | 1 | A09 | STRW0.09511015/DBE
Horizontal Wall | Strada | STRW.09511016 | 95 | 110 | 16 | 17 | 2945 | 2945 | 2945 | 0.070119 | 1054 | 0.025095 | 3393 | 0.080786 | 1.482 | A09 | STRW0.09511016
Horizontal Wall | Strada | STRW.09511016/DBE | 95 | 110 | 16 | 17 | 3905 | 3905 | 3905 | 0.092976 | 1953 | 0.0465 | 4296 | 0.10229 | 1 | A09 | STRW0.09511016/DBE
Horizontal Wall | Strada | STRW.09511020 | 95 | 110 | 20 | 22 | 3291 | 3291 | 3291 | 0.078357 | 1320 | 0.031429 | 3732 | 0.088857 | 1.32 | A09 | STRW0.09511020
Horizontal Wall | Strada | STRW.09511020/DBE | 95 | 110 | 20 | #N/A | 3791 | 3791 | 3791 | 0.090262 | 1896 | 0.045143 | 4170 | 0.099286 | 1 | A09 | STRW0.09511020/DBE
Horizontal Wall | Strada | STRW.09511021 | 95 | 110 | 21 | 22 | 4312 | 4312 | 4312 | 0.10267 | 1501 | 0.035738 | 4985 | 0.11869 | 1.522 | A09 | STRW0.09511021
Horizontal Wall | Strada | STRW.09511021/DBE | 95 | 110 | 21 | 22 | 5272 | 5272 | 5272 | 0.12552 | 2636 | 0.062762 | 5799 | 0.13807 | 1 | A09 | STRW0.09511021/DBE
Horizontal Wall | Strada | STRW.09512006 | 95 | 120 | 06 | 9 | 1471 | 1471 | 1471 | 0.035024 | 594 | 0.014143 | 1667 | 0.03969 | 1.307 | A09 | STRW0.09512006
Horizontal Wall | Strada | STRW.09512010 | 95 | 120 | 10 | 12 | 1672 | 1672 | 1672 | 0.03981 | 659 | 0.01569 | 1901 | 0.045262 | 1.343 | A09 | STRW0.09512010
Horizontal Wall | Strada | STRW.09512010/DBE | 95 | 120 | 10 | #N/A | 1972 | 1972 | 1972 | 0.046952 | 986 | 0.023476 | 2169 | 0.051643 | 1 | A09 | STRW0.09512010/DBE
Horizontal Wall | Strada | STRW.09512011 | 95 | 120 | 11 | 12 | 2155 | 2155 | 2155 | 0.05131 | 797 | 0.018976 | 2470 | 0.05881 | 1.434 | A09 | STRW0.09512011
Horizontal Wall | Strada | STRW.09512011/DBE | 95 | 120 | 11 | 12 | 2755 | 2755 | 2755 | 0.065595 | 1378 | 0.03281 | 3031 | 0.072167 | 1 | A09 | STRW0.09512011/DBE
Horizontal Wall | Strada | STRW.09512015 | 95 | 120 | 15 | 17 | 2575 | 2575 | 2575 | 0.06131 | 1033 | 0.024595 | 2920 | 0.069524 | 1.32 | A09 | STRW0.09512015
Horizontal Wall | Strada | STRW.09512015/DBE | 95 | 120 | 15 | #N/A | 3075 | 3075 | 3075 | 0.073214 | 1538 | 0.036619 | 3383 | 0.080548 | 1 | A09 | STRW0.09512015/DBE
Horizontal Wall | Strada | STRW.09512016 | 95 | 120 | 16 | 17 | 3212 | 3212 | 3212 | 0.076476 | 1150 | 0.027381 | 3700 | 0.088095 | 1.482 | A09 | STRW0.09512016
Horizontal Wall | Strada | STRW.09512016/DBE | 95 | 120 | 16 | 17 | 4172 | 4172 | 4172 | 0.099333 | 2086 | 0.049667 | 4589 | 0.10926 | 1 | A09 | STRW0.09512016/DBE
Horizontal Wall | Strada | STRW.09512020 | 95 | 120 | 20 | 22 | 3590 | 3590 | 3590 | 0.085476 | 1440 | 0.034286 | 4071 | 0.096929 | 1.32 | A09 | STRW0.09512020
Horizontal Wall | Strada | STRW.09512020/DBE | 95 | 120 | 20 | #N/A | 4090 | 4090 | 4090 | 0.097381 | 2045 | 0.04869 | 4499 | 0.10712 | 1 | A09 | STRW0.09512020/DBE
Horizontal Wall | Strada | STRW.09512021 | 95 | 120 | 21 | 22 | 4704 | 4704 | 4704 | 0.112 | 1637 | 0.038976 | 5438 | 0.12948 | 1.522 | A09 | STRW0.09512021
Horizontal Wall | Strada | STRW.09512021/DBE | 95 | 120 | 21 | 22 | 5664 | 5664 | 5664 | 0.13486 | 2832 | 0.067429 | 6230 | 0.14833 | 1 | A09 | STRW0.09512021/DBE
Horizontal Wall | Strada | STRW.09514006 | 95 | 140 | 06 | 9 | 1716 | 1716 | 1716 | 0.040857 | 693 | 0.0165 | 1944 | 0.046286 | 1.307 | A09 | STRW0.09514006
Horizontal Wall | Strada | STRW.09514010 | 95 | 140 | 10 | 12 | 1950 | 1950 | 1950 | 0.046429 | 768 | 0.018286 | 2217 | 0.052786 | 1.343 | A09 | STRW0.09514010
Horizontal Wall | Strada | STRW.09514010/DBE | 95 | 140 | 10 | #N/A | 2250 | 2250 | 2250 | 0.053571 | 1125 | 0.026786 | 2475 | 0.058929 | 1 | A09 | STRW0.09514010/DBE
Horizontal Wall | Strada | STRW.09514011 | 95 | 140 | 11 | 12 | 2514 | 2514 | 2514 | 0.059857 | 930 | 0.022143 | 2881 | 0.068595 | 1.434 | A09 | STRW0.09514011
Horizontal Wall | Strada | STRW.09514011/DBE | 95 | 140 | 11 | 12 | 3114 | 3114 | 3114 | 0.074143 | 1557 | 0.037071 | 3425 | 0.081548 | 1 | A09 | STRW0.09514011/DBE
Horizontal Wall | Strada | STRW.09514015 | 95 | 140 | 15 | 17 | 3004 | 3004 | 3004 | 0.071524 | 1205 | 0.02869 | 3407 | 0.081119 | 1.32 | A09 | STRW0.09514015
Horizontal Wall | Strada | STRW.09514015/DBE | 95 | 140 | 15 | #N/A | 3504 | 3504 | 3504 | 0.083429 | 1752 | 0.041714 | 3854 | 0.091762 | 1 | A09 | STRW0.09514015/DBE
Horizontal Wall | Strada | STRW.09514016 | 95 | 140 | 16 | 17 | 3748 | 3748 | 3748 | 0.089238 | 1342 | 0.031952 | 4318 | 0.10281 | 1.482 | A09 | STRW0.09514016
Horizontal Wall | Strada | STRW.09514016/DBE | 95 | 140 | 16 | 17 | 4708 | 4708 | 4708 | 0.1121 | 2354 | 0.056048 | 5179 | 0.12331 | 1 | A09 | STRW0.09514016/DBE
Horizontal Wall | Strada | STRW.09514020 | 95 | 140 | 20 | 22 | 4189 | 4189 | 4189 | 0.099738 | 1680 | 0.04 | 4750 | 0.1131 | 1.32 | A09 | STRW0.09514020
Horizontal Wall | Strada | STRW.09514020/DBE | 95 | 140 | 20 | #N/A | 4689 | 4689 | 4689 | 0.11164 | 2345 | 0.055833 | 5158 | 0.12281 | 1 | A09 | STRW0.09514020/DBE
Horizontal Wall | Strada | STRW.09514021 | 95 | 140 | 21 | 22 | 5488 | 5488 | 5488 | 0.13067 | 1910 | 0.045476 | 6344 | 0.15105 | 1.522 | A09 | STRW0.09514021
Horizontal Wall | Strada | STRW.09514021/DBE | 95 | 140 | 21 | 22 | 6448 | 6448 | 6448 | 0.15352 | 3224 | 0.076762 | 7093 | 0.16888 | 1 | A09 | STRW0.09514021/DBE
Freestanding | Tempo Freestanding | TEMF.02004010/AS | 20 | 40 | 10 | 13 | 262 | 262 | 262 | 0.0062381 | 99 | 0.0023571 | 300 | 0.0071429 | 1.413 | A02 | TEMF0.02004010/AS
Freestanding | Tempo Freestanding | TEMF.02004015/AS | 20 | 40 | 15 | 18 | 436 | 436 | 436 | 0.010381 | 164 | 0.0039048 | 499 | 0.011881 | 1.408 | A02 | TEMF0.02004015/AS
Freestanding | Tempo Freestanding | TEMF.02004020/AS | 20 | 40 | 20 | 23 | 613 | 613 | 613 | 0.014595 | 231 | 0.0055 | 701 | 0.01669 | 1.408 | A02 | TEMF0.02004020/AS
Freestanding | Tempo Freestanding | TEMF.02005010/AS | 20 | 50 | 10 | 13 | 328 | 328 | 328 | 0.0078095 | 123 | 0.0029286 | 375 | 0.0089286 | 1.413 | A02 | TEMF0.02005010/AS
Freestanding | Tempo Freestanding | TEMF.02005015/AS | 20 | 50 | 15 | 18 | 545 | 545 | 545 | 0.012976 | 205 | 0.004881 | 623 | 0.014833 | 1.408 | A02 | TEMF0.02005015/AS
Freestanding | Tempo Freestanding | TEMF.02005020/AS | 20 | 50 | 20 | 23 | 766 | 766 | 766 | 0.018238 | 289 | 0.006881 | 876 | 0.020857 | 1.408 | A02 | TEMF0.02005020/AS
Freestanding | Tempo Freestanding | TEMF.02006010/AS | 20 | 60 | 10 | 13 | 393 | 393 | 393 | 0.0093571 | 148 | 0.0035238 | 450 | 0.010714 | 1.413 | A02 | TEMF0.02006010/AS
Freestanding | Tempo Freestanding | TEMF.02006015/AS | 20 | 60 | 15 | 18 | 654 | 654 | 654 | 0.015571 | 247 | 0.005881 | 748 | 0.01781 | 1.408 | A02 | TEMF0.02006015/AS
Freestanding | Tempo Freestanding | TEMF.02006020/AS | 20 | 60 | 20 | 23 | 919 | 919 | 919 | 0.021881 | 346 | 0.0082381 | 1051 | 0.025024 | 1.408 | A02 | TEMF0.02006020/AS
Freestanding | Tempo Freestanding | TEMF.02007010/AS | 20 | 70 | 10 | 13 | 459 | 459 | 459 | 0.010929 | 173 | 0.004119 | 525 | 0.0125 | 1.413 | A02 | TEMF0.02007010/AS
Freestanding | Tempo Freestanding | TEMF.02007015/AS | 20 | 70 | 15 | 18 | 763 | 763 | 763 | 0.018167 | 288 | 0.0068571 | 873 | 0.020786 | 1.408 | A02 | TEMF0.02007015/AS
Freestanding | Tempo Freestanding | TEMF.02007020/AS | 20 | 70 | 20 | 23 | 1072 | 1072 | 1072 | 0.025524 | 404 | 0.009619 | 1226 | 0.02919 | 1.408 | A02 | TEMF0.02007020/AS
Freestanding | Tempo Freestanding | TEMF.02008010/AS | 20 | 80 | 10 | 13 | 524 | 524 | 524 | 0.012476 | 197 | 0.0046905 | 599 | 0.014262 | 1.413 | A02 | TEMF0.02008010/AS
Freestanding | Tempo Freestanding | TEMF.02008015/AS | 20 | 80 | 15 | 18 | 872 | 872 | 872 | 0.020762 | 329 | 0.0078333 | 998 | 0.023762 | 1.408 | A02 | TEMF0.02008015/AS
Freestanding | Tempo Freestanding | TEMF.02008020/AS | 20 | 80 | 20 | 23 | 1226 | 1226 | 1226 | 0.02919 | 462 | 0.011 | 1403 | 0.033405 | 1.408 | A02 | TEMF0.02008020/AS
Freestanding | Tempo Freestanding | TEMF.02009010/AS | 20 | 90 | 10 | 13 | 590 | 590 | 590 | 0.014048 | 222 | 0.0052857 | 675 | 0.016071 | 1.413 | A02 | TEMF0.02009010/AS
Freestanding | Tempo Freestanding | TEMF.02009015/AS | 20 | 90 | 15 | 18 | 981 | 981 | 981 | 0.023357 | 370 | 0.0088095 | 1122 | 0.026714 | 1.408 | A02 | TEMF0.02009015/AS
Freestanding | Tempo Freestanding | TEMF.02009020/AS | 20 | 90 | 20 | 23 | 1379 | 1379 | 1379 | 0.032833 | 520 | 0.012381 | 1578 | 0.037571 | 1.408 | A02 | TEMF0.02009020/AS
Freestanding | Tempo Freestanding | TEMF.02010010/AS | 20 | 100 | 10 | 13 | 655 | 655 | 655 | 0.015595 | 246 | 0.0058571 | 749 | 0.017833 | 1.413 | A02 | TEMF0.02010010/AS
Freestanding | Tempo Freestanding | TEMF.02010015/AS | 20 | 100 | 15 | 18 | 1090 | 1090 | 1090 | 0.025952 | 411 | 0.0097857 | 1247 | 0.02969 | 1.408 | A02 | TEMF0.02010015/AS
Freestanding | Tempo Freestanding | TEMF.02010020/AS | 20 | 100 | 20 | 23 | 1532 | 1532 | 1532 | 0.036476 | 578 | 0.013762 | 1753 | 0.041738 | 1.408 | A02 | TEMF0.02010020/AS
Freestanding | Tempo Freestanding | TEMF.02011010/AS | 20 | 110 | 10 | 13 | 721 | 721 | 721 | 0.017167 | 271 | 0.0064524 | 825 | 0.019643 | 1.413 | A02 | TEMF0.02011010/AS
Freestanding | Tempo Freestanding | TEMF.02011015/AS | 20 | 110 | 15 | 18 | 1199 | 1199 | 1199 | 0.028548 | 452 | 0.010762 | 1372 | 0.032667 | 1.408 | A02 | TEMF0.02011015/AS
Freestanding | Tempo Freestanding | TEMF.02011020/AS | 20 | 110 | 20 | 23 | 1685 | 1685 | 1685 | 0.040119 | 635 | 0.015119 | 1928 | 0.045905 | 1.408 | A02 | TEMF0.02011020/AS
Freestanding | Tempo Freestanding | TEMF.02012010/AS | 20 | 120 | 10 | 13 | 786 | 786 | 786 | 0.018714 | 296 | 0.0070476 | 899 | 0.021405 | 1.413 | A02 | TEMF0.02012010/AS
Freestanding | Tempo Freestanding | TEMF.02012015/AS | 20 | 120 | 15 | 18 | 1308 | 1308 | 1308 | 0.031143 | 493 | 0.011738 | 1496 | 0.035619 | 1.408 | A02 | TEMF0.02012015/AS
Freestanding | Tempo Freestanding | TEMF.02012020/AS | 20 | 120 | 20 | 23 | 1838 | 1838 | 1838 | 0.043762 | 693 | 0.0165 | 2103 | 0.050071 | 1.408 | A02 | TEMF0.02012020/AS
Freestanding | Tempo Freestanding | TEMF.02014010/AS | 20 | 140 | 10 | 13 | 917 | 917 | 917 | 0.021833 | 345 | 0.0082143 | 1049 | 0.024976 | 1.413 | A02 | TEMF0.02014010/AS
Freestanding | Tempo Freestanding | TEMF.02014015/AS | 20 | 140 | 15 | 18 | 1526 | 1526 | 1526 | 0.036333 | 575 | 0.01369 | 1746 | 0.041571 | 1.408 | A02 | TEMF0.02014015/AS
Freestanding | Tempo Freestanding | TEMF.02014020/AS | 20 | 140 | 20 | 23 | 2145 | 2145 | 2145 | 0.051071 | 809 | 0.019262 | 2454 | 0.058429 | 1.408 | A02 | TEMF0.02014020/AS
Freestanding | Tempo Freestanding | TEMF.02016010/AS | 20 | 160 | 10 | 13 | 1048 | 1048 | 1048 | 0.024952 | 394 | 0.009381 | 1199 | 0.028548 | 1.413 | A02 | TEMF0.02016010/AS
Freestanding | Tempo Freestanding | TEMF.02016015/AS | 20 | 160 | 15 | 18 | 1744 | 1744 | 1744 | 0.041524 | 657 | 0.015643 | 1995 | 0.0475 | 1.408 | A02 | TEMF0.02016015/AS
Freestanding | Tempo Freestanding | TEMF.02016020/AS | 20 | 160 | 20 | 23 | 2451 | 2451 | 2451 | 0.058357 | 924 | 0.022 | 2804 | 0.066762 | 1.408 | A02 | TEMF0.02016020/AS
Freestanding | Tempo Freestanding | TEMF.02018010/AS | 20 | 180 | 10 | 13 | 1179 | 1179 | 1179 | 0.028071 | 443 | 0.010548 | 1349 | 0.032119 | 1.413 | A02 | TEMF0.02018010/AS
Freestanding | Tempo Freestanding | TEMF.02018015/AS | 20 | 180 | 15 | 18 | 1962 | 1962 | 1962 | 0.046714 | 740 | 0.017619 | 2245 | 0.053452 | 1.408 | A02 | TEMF0.02018015/AS
Freestanding | Tempo Freestanding | TEMF.02018020/AS | 20 | 180 | 20 | 23 | 2758 | 2758 | 2758 | 0.065667 | 1040 | 0.024762 | 3155 | 0.075119 | 1.408 | A02 | TEMF0.02018020/AS
Freestanding | Tempo Freestanding | TEMF.02020010/AS | 20 | 200 | 10 | 13 | 1310 | 1310 | 1310 | 0.03119 | 493 | 0.011738 | 1499 | 0.03569 | 1.413 | A02 | TEMF0.02020010/AS
Freestanding | Tempo Freestanding | TEMF.02020015/AS | 20 | 200 | 15 | 18 | 2180 | 2180 | 2180 | 0.051905 | 822 | 0.019571 | 2494 | 0.059381 | 1.408 | A02 | TEMF0.02020015/AS
Freestanding | Tempo Freestanding | TEMF.02020020/AS | 20 | 200 | 20 | 23 | 3064 | 3064 | 3064 | 0.072952 | 1155 | 0.0275 | 3505 | 0.083452 | 1.408 | A02 | TEMF0.02020020/AS
Freestanding | Tempo Freestanding | TEMF.02022010/AS | 20 | 220 | 10 | 13 | 1441 | 1441 | 1441 | 0.03431 | 542 | 0.012905 | 1649 | 0.039262 | 1.413 | A02 | TEMF0.02022010/AS
Freestanding | Tempo Freestanding | TEMF.02022015/AS | 20 | 220 | 15 | 18 | 2398 | 2398 | 2398 | 0.057095 | 904 | 0.021524 | 2743 | 0.06531 | 1.408 | A02 | TEMF0.02022015/AS
Freestanding | Tempo Freestanding | TEMF.02022020/AS | 20 | 220 | 20 | 23 | 3370 | 3370 | 3370 | 0.080238 | 1270 | 0.030238 | 3855 | 0.091786 | 1.408 | A02 | TEMF0.02022020/AS
Freestanding | Tempo Freestanding | TEMF.02024010/AS | 20 | 240 | 10 | 13 | 1572 | 1572 | 1572 | 0.037429 | 591 | 0.014071 | 1798 | 0.04281 | 1.413 | A02 | TEMF0.02024010/AS
Freestanding | Tempo Freestanding | TEMF.02024015/AS | 20 | 240 | 15 | 18 | 2616 | 2616 | 2616 | 0.062286 | 986 | 0.023476 | 2993 | 0.071262 | 1.408 | A02 | TEMF0.02024015/AS
Freestanding | Tempo Freestanding | TEMF.02024020/AS | 20 | 240 | 20 | 23 | 3677 | 3677 | 3677 | 0.087548 | 1386 | 0.033 | 4206 | 0.10014 | 1.408 | A02 | TEMF0.02024020/AS
Freestanding | Tempo Freestanding | TEMF.02026010/AS | 20 | 260 | 10 | 13 | 1703 | 1703 | 1703 | 0.040548 | 640 | 0.015238 | 1948 | 0.046381 | 1.413 | A02 | TEMF0.02026010/AS
Freestanding | Tempo Freestanding | TEMF.02026015/AS | 20 | 260 | 15 | 18 | 2834 | 2834 | 2834 | 0.067476 | 1068 | 0.025429 | 3242 | 0.07719 | 1.408 | A02 | TEMF0.02026015/AS
Freestanding | Tempo Freestanding | TEMF.02026020/AS | 20 | 260 | 20 | 23 | 3983 | 3983 | 3983 | 0.094833 | 1502 | 0.035762 | 4557 | 0.1085 | 1.408 | A02 | TEMF0.02026020/AS
Freestanding | Tempo Freestanding | TEMF.02028010/AS | 20 | 280 | 10 | 13 | 1834 | 1834 | 1834 | 0.043667 | 690 | 0.016429 | 2098 | 0.049952 | 1.413 | A02 | TEMF0.02028010/AS
Freestanding | Tempo Freestanding | TEMF.02028015/AS | 20 | 280 | 15 | 18 | 3052 | 3052 | 3052 | 0.072667 | 1151 | 0.027405 | 3491 | 0.083119 | 1.408 | A02 | TEMF0.02028015/AS
Freestanding | Tempo Freestanding | TEMF.02028020/AS | 20 | 280 | 20 | 23 | 4290 | 4290 | 4290 | 0.10214 | 1617 | 0.0385 | 4908 | 0.11686 | 1.408 | A02 | TEMF0.02028020/AS
Freestanding | Tempo Freestanding | TEMF.02030010/AS | 20 | 300 | 10 | 13 | 1965 | 1965 | 1965 | 0.046786 | 739 | 0.017595 | 2248 | 0.053524 | 1.413 | A02 | TEMF0.02030010/AS
Freestanding | Tempo Freestanding | TEMF.02030015/AS | 20 | 300 | 15 | 18 | 3270 | 3270 | 3270 | 0.077857 | 1233 | 0.029357 | 3741 | 0.089071 | 1.408 | A02 | TEMF0.02030015/AS
Freestanding | Tempo Freestanding | TEMF.02030020/AS | 20 | 300 | 20 | 23 | 4596 | 4596 | 4596 | 0.10943 | 1733 | 0.041262 | 5258 | 0.12519 | 1.408 | A02 | TEMF0.02030020/AS
Freestanding | Tempo Freestanding | TEMF.03004010/AS | 30 | 40 | 10 | 13 | 330 | 330 | 330 | 0.0078571 | 125 | 0.0029762 | 377 | 0.0089762 | 1.403 | A02 | TEMF0.03004010/AS
Freestanding | Tempo Freestanding | TEMF.03004011/AS | 30 | 40 | 11 | 13 | 448 | 448 | 448 | 0.010667 | 165 | 0.0039286 | 514 | 0.012238 | 1.44 | A02 | TEMF0.03004011/AS
Freestanding | Tempo Freestanding | TEMF.03004015/AS | 30 | 40 | 15 | 18 | 544 | 544 | 544 | 0.012952 | 207 | 0.0049286 | 621 | 0.014786 | 1.396 | A02 | TEMF0.03004015/AS
Freestanding | Tempo Freestanding | TEMF.03004016/AS | 30 | 40 | 16 | 18 | 592 | 592 | 592 | 0.014095 | 216 | 0.0051429 | 680 | 0.01619 | 1.456 | A02 | TEMF0.03004016/AS
Freestanding | Tempo Freestanding | TEMF.03004020/AS | 30 | 40 | 20 | 23 | 762 | 762 | 762 | 0.018143 | 290 | 0.0069048 | 870 | 0.020714 | 1.396 | A02 | TEMF0.03004020/AS
Freestanding | Tempo Freestanding | TEMF.03004021/AS | 30 | 40 | 21 | 23 | 779 | 779 | 779 | 0.018548 | 281 | 0.0066905 | 896 | 0.021333 | 1.468 | A02 | TEMF0.03004021/AS
Freestanding | Tempo Freestanding | TEMF.03005010/AS | 30 | 50 | 10 | 13 | 413 | 413 | 413 | 0.0098333 | 156 | 0.0037143 | 472 | 0.011238 | 1.403 | A02 | TEMF0.03005010/AS
Freestanding | Tempo Freestanding | TEMF.03005011/AS | 30 | 50 | 11 | 13 | 561 | 561 | 561 | 0.013357 | 207 | 0.0049286 | 643 | 0.01531 | 1.44 | A02 | TEMF0.03005011/AS
Freestanding | Tempo Freestanding | TEMF.03005015/AS | 30 | 50 | 15 | 18 | 680 | 680 | 680 | 0.01619 | 258 | 0.0061429 | 777 | 0.0185 | 1.396 | A02 | TEMF0.03005015/AS
Freestanding | Tempo Freestanding | TEMF.03005016/AS | 30 | 50 | 16 | 18 | 740 | 740 | 740 | 0.017619 | 270 | 0.0064286 | 850 | 0.020238 | 1.456 | A02 | TEMF0.03005016/AS
Freestanding | Tempo Freestanding | TEMF.03005020/AS | 30 | 50 | 20 | 23 | 953 | 953 | 953 | 0.02269 | 362 | 0.008619 | 1088 | 0.025905 | 1.396 | A02 | TEMF0.03005020/AS
Freestanding | Tempo Freestanding | TEMF.03005021/AS | 30 | 50 | 21 | 23 | 974 | 974 | 974 | 0.02319 | 352 | 0.008381 | 1120 | 0.026667 | 1.468 | A02 | TEMF0.03005021/AS
Freestanding | Tempo Freestanding | TEMF.03006010/AS | 30 | 60 | 10 | 13 | 496 | 496 | 496 | 0.01181 | 187 | 0.0044524 | 567 | 0.0135 | 1.403 | A02 | TEMF0.03006010/AS
Freestanding | Tempo Freestanding | TEMF.03006011/AS | 30 | 60 | 11 | 13 | 673 | 673 | 673 | 0.016024 | 248 | 0.0059048 | 772 | 0.018381 | 1.44 | A02 | TEMF0.03006011/AS
Freestanding | Tempo Freestanding | TEMF.03006015/AS | 30 | 60 | 15 | 18 | 815 | 815 | 815 | 0.019405 | 310 | 0.007381 | 931 | 0.022167 | 1.396 | A02 | TEMF0.03006015/AS
Freestanding | Tempo Freestanding | TEMF.03006016/AS | 30 | 60 | 16 | 18 | 888 | 888 | 888 | 0.021143 | 324 | 0.0077143 | 1020 | 0.024286 | 1.456 | A02 | TEMF0.03006016/AS
Freestanding | Tempo Freestanding | TEMF.03006020/AS | 30 | 60 | 20 | 23 | 1144 | 1144 | 1144 | 0.027238 | 435 | 0.010357 | 1306 | 0.031095 | 1.396 | A02 | TEMF0.03006020/AS
Freestanding | Tempo Freestanding | TEMF.03006021/AS | 30 | 60 | 21 | 23 | 1169 | 1169 | 1169 | 0.027833 | 422 | 0.010048 | 1344 | 0.032 | 1.468 | A02 | TEMF0.03006021/AS
Freestanding | Tempo Freestanding | TEMF.03007010/AS | 30 | 70 | 10 | 13 | 578 | 578 | 578 | 0.013762 | 218 | 0.0051905 | 661 | 0.015738 | 1.403 | A02 | TEMF0.03007010/AS
Freestanding | Tempo Freestanding | TEMF.03007011/AS | 30 | 70 | 11 | 13 | 785 | 785 | 785 | 0.01869 | 290 | 0.0069048 | 900 | 0.021429 | 1.44 | A02 | TEMF0.03007011/AS
Freestanding | Tempo Freestanding | TEMF.03007015/AS | 30 | 70 | 15 | 18 | 951 | 951 | 951 | 0.022643 | 361 | 0.0085952 | 1086 | 0.025857 | 1.396 | A02 | TEMF0.03007015/AS
Freestanding | Tempo Freestanding | TEMF.03007016/AS | 30 | 70 | 16 | 18 | 1036 | 1036 | 1036 | 0.024667 | 378 | 0.009 | 1190 | 0.028333 | 1.456 | A02 | TEMF0.03007016/AS
Freestanding | Tempo Freestanding | TEMF.03007020/AS | 30 | 70 | 20 | 23 | 1334 | 1334 | 1334 | 0.031762 | 507 | 0.012071 | 1523 | 0.036262 | 1.396 | A02 | TEMF0.03007020/AS
Freestanding | Tempo Freestanding | TEMF.03007021/AS | 30 | 70 | 21 | 23 | 1364 | 1364 | 1364 | 0.032476 | 492 | 0.011714 | 1569 | 0.037357 | 1.468 | A02 | TEMF0.03007021/AS
Freestanding | Tempo Freestanding | TEMF.03008010/AS | 30 | 80 | 10 | 13 | 661 | 661 | 661 | 0.015738 | 250 | 0.0059524 | 756 | 0.018 | 1.403 | A02 | TEMF0.03008010/AS
Freestanding | Tempo Freestanding | TEMF.03008011/AS | 30 | 80 | 11 | 13 | 897 | 897 | 897 | 0.021357 | 331 | 0.007881 | 1029 | 0.0245 | 1.44 | A02 | TEMF0.03008011/AS
Freestanding | Tempo Freestanding | TEMF.03008015/AS | 30 | 80 | 15 | 18 | 1087 | 1087 | 1087 | 0.025881 | 413 | 0.0098333 | 1241 | 0.029548 | 1.396 | A02 | TEMF0.03008015/AS
Freestanding | Tempo Freestanding | TEMF.03008016/AS | 30 | 80 | 16 | 18 | 1184 | 1184 | 1184 | 0.02819 | 432 | 0.010286 | 1360 | 0.032381 | 1.456 | A02 | TEMF0.03008016/AS
Freestanding | Tempo Freestanding | TEMF.03008020/AS | 30 | 80 | 20 | 23 | 1525 | 1525 | 1525 | 0.03631 | 580 | 0.01381 | 1742 | 0.041476 | 1.396 | A02 | TEMF0.03008020/AS
Freestanding | Tempo Freestanding | TEMF.03008021/AS | 30 | 80 | 21 | 23 | 1558 | 1558 | 1558 | 0.037095 | 562 | 0.013381 | 1792 | 0.042667 | 1.468 | A02 | TEMF0.03008021/AS
Freestanding | Tempo Freestanding | TEMF.03009010/AS | 30 | 90 | 10 | 13 | 743 | 743 | 743 | 0.01769 | 281 | 0.0066905 | 849 | 0.020214 | 1.403 | A02 | TEMF0.03009010/AS
Freestanding | Tempo Freestanding | TEMF.03009011/AS | 30 | 90 | 11 | 13 | 1009 | 1009 | 1009 | 0.024024 | 372 | 0.0088571 | 1157 | 0.027548 | 1.44 | A02 | TEMF0.03009011/AS
Freestanding | Tempo Freestanding | TEMF.03009015/AS | 30 | 90 | 15 | 18 | 1223 | 1223 | 1223 | 0.029119 | 465 | 0.011071 | 1397 | 0.033262 | 1.396 | A02 | TEMF0.03009015/AS
Freestanding | Tempo Freestanding | TEMF.03009016/AS | 30 | 90 | 16 | 18 | 1332 | 1332 | 1332 | 0.031714 | 486 | 0.011571 | 1530 | 0.036429 | 1.456 | A02 | TEMF0.03009016/AS
Freestanding | Tempo Freestanding | TEMF.03009020/AS | 30 | 90 | 20 | 23 | 1715 | 1715 | 1715 | 0.040833 | 652 | 0.015524 | 1959 | 0.046643 | 1.396 | A02 | TEMF0.03009020/AS
Freestanding | Tempo Freestanding | TEMF.03009021/AS | 30 | 90 | 21 | 23 | 1753 | 1753 | 1753 | 0.041738 | 633 | 0.015071 | 2016 | 0.048 | 1.468 | A02 | TEMF0.03009021/AS
Freestanding | Tempo Freestanding | TEMF.03010010/AS | 30 | 100 | 10 | 13 | 826 | 826 | 826 | 0.019667 | 312 | 0.0074286 | 944 | 0.022476 | 1.403 | A02 | TEMF0.03010010/AS
Freestanding | Tempo Freestanding | TEMF.03010011/AS | 30 | 100 | 11 | 13 | 1121 | 1121 | 1121 | 0.02669 | 414 | 0.0098571 | 1286 | 0.030619 | 1.44 | A02 | TEMF0.03010011/AS
Freestanding | Tempo Freestanding | TEMF.03010015/AS | 30 | 100 | 15 | 18 | 1359 | 1359 | 1359 | 0.032357 | 516 | 0.012286 | 1552 | 0.036952 | 1.396 | A02 | TEMF0.03010015/AS
Freestanding | Tempo Freestanding | TEMF.03010016/AS | 30 | 100 | 16 | 18 | 1480 | 1480 | 1480 | 0.035238 | 540 | 0.012857 | 1701 | 0.0405 | 1.456 | A02 | TEMF0.03010016/AS
Freestanding | Tempo Freestanding | TEMF.03010020/AS | 30 | 100 | 20 | 23 | 1906 | 1906 | 1906 | 0.045381 | 724 | 0.017238 | 2177 | 0.051833 | 1.396 | A02 | TEMF0.03010020/AS
Freestanding | Tempo Freestanding | TEMF.03010021/AS | 30 | 100 | 21 | 23 | 1948 | 1948 | 1948 | 0.046381 | 703 | 0.016738 | 2240 | 0.053333 | 1.468 | A02 | TEMF0.03010021/AS
Freestanding | Tempo Freestanding | TEMF.03011010/AS | 30 | 110 | 10 | 13 | 909 | 909 | 909 | 0.021643 | 344 | 0.0081905 | 1039 | 0.024738 | 1.403 | A02 | TEMF0.03011010/AS
Freestanding | Tempo Freestanding | TEMF.03011011/AS | 30 | 110 | 11 | 13 | 1233 | 1233 | 1233 | 0.029357 | 455 | 0.010833 | 1414 | 0.033667 | 1.44 | A02 | TEMF0.03011011/AS
Freestanding | Tempo Freestanding | TEMF.03011015/AS | 30 | 110 | 15 | 18 | 1495 | 1495 | 1495 | 0.035595 | 568 | 0.013524 | 1707 | 0.040643 | 1.396 | A02 | TEMF0.03011015/AS
Freestanding | Tempo Freestanding | TEMF.03011016/AS | 30 | 110 | 16 | 18 | 1628 | 1628 | 1628 | 0.038762 | 594 | 0.014143 | 1871 | 0.044548 | 1.456 | A02 | TEMF0.03011016/AS
Freestanding | Tempo Freestanding | TEMF.03011020/AS | 30 | 110 | 20 | 23 | 2097 | 2097 | 2097 | 0.049929 | 797 | 0.018976 | 2395 | 0.057024 | 1.396 | A02 | TEMF0.03011020/AS
Freestanding | Tempo Freestanding | TEMF.03011021/AS | 30 | 110 | 21 | 23 | 2143 | 2143 | 2143 | 0.051024 | 774 | 0.018429 | 2464 | 0.058667 | 1.468 | A02 | TEMF0.03011021/AS
Freestanding | Tempo Freestanding | TEMF.03012010/AS | 30 | 120 | 10 | 13 | 991 | 991 | 991 | 0.023595 | 375 | 0.0089286 | 1133 | 0.026976 | 1.403 | A02 | TEMF0.03012010/AS
Freestanding | Tempo Freestanding | TEMF.03012011/AS | 30 | 120 | 11 | 13 | 1345 | 1345 | 1345 | 0.032024 | 496 | 0.01181 | 1543 | 0.036738 | 1.44 | A02 | TEMF0.03012011/AS
Freestanding | Tempo Freestanding | TEMF.03012015/AS | 30 | 120 | 15 | 18 | 1631 | 1631 | 1631 | 0.038833 | 620 | 0.014762 | 1863 | 0.044357 | 1.396 | A02 | TEMF0.03012015/AS
Freestanding | Tempo Freestanding | TEMF.03012016/AS | 30 | 120 | 16 | 18 | 1776 | 1776 | 1776 | 0.042286 | 648 | 0.015429 | 2041 | 0.048595 | 1.456 | A02 | TEMF0.03012016/AS
Freestanding | Tempo Freestanding | TEMF.03012020/AS | 30 | 120 | 20 | 23 | 2287 | 2287 | 2287 | 0.054452 | 869 | 0.02069 | 2612 | 0.06219 | 1.396 | A02 | TEMF0.03012020/AS
Freestanding | Tempo Freestanding | TEMF.03012021/AS | 30 | 120 | 21 | 23 | 2338 | 2338 | 2338 | 0.055667 | 844 | 0.020095 | 2689 | 0.064024 | 1.468 | A02 | TEMF0.03012021/AS
Freestanding | Tempo Freestanding | TEMF.03014010/AS | 30 | 140 | 10 | 13 | 1156 | 1156 | 1156 | 0.027524 | 437 | 0.010405 | 1321 | 0.031452 | 1.403 | A02 | TEMF0.03014010/AS
Freestanding | Tempo Freestanding | TEMF.03014011/AS | 30 | 140 | 11 | 13 | 1569 | 1569 | 1569 | 0.037357 | 579 | 0.013786 | 1800 | 0.042857 | 1.44 | A02 | TEMF0.03014011/AS
Freestanding | Tempo Freestanding | TEMF.03014015/AS | 30 | 140 | 15 | 18 | 1903 | 1903 | 1903 | 0.04531 | 723 | 0.017214 | 2173 | 0.051738 | 1.396 | A02 | TEMF0.03014015/AS
Freestanding | Tempo Freestanding | TEMF.03014016/AS | 30 | 140 | 16 | 18 | 2072 | 2072 | 2072 | 0.049333 | 756 | 0.018 | 2381 | 0.05669 | 1.456 | A02 | TEMF0.03014016/AS
Freestanding | Tempo Freestanding | TEMF.03014020/AS | 30 | 140 | 20 | 23 | 2668 | 2668 | 2668 | 0.063524 | 1014 | 0.024143 | 3047 | 0.072548 | 1.396 | A02 | TEMF0.03014020/AS
Freestanding | Tempo Freestanding | TEMF.03014021/AS | 30 | 140 | 21 | 23 | 2727 | 2727 | 2727 | 0.064929 | 984 | 0.023429 | 3136 | 0.074667 | 1.468 | A02 | TEMF0.03014021/AS
Freestanding | Tempo Freestanding | TEMF.03016010/AS | 30 | 160 | 10 | 13 | 1322 | 1322 | 1322 | 0.031476 | 500 | 0.011905 | 1511 | 0.035976 | 1.403 | A02 | TEMF0.03016010/AS
Freestanding | Tempo Freestanding | TEMF.03016011/AS | 30 | 160 | 11 | 13 | 1794 | 1794 | 1794 | 0.042714 | 662 | 0.015762 | 2058 | 0.049 | 1.44 | A02 | TEMF0.03016011/AS
Freestanding | Tempo Freestanding | TEMF.03016015/AS | 30 | 160 | 15 | 18 | 2174 | 2174 | 2174 | 0.051762 | 826 | 0.019667 | 2483 | 0.059119 | 1.396 | A02 | TEMF0.03016015/AS
Freestanding | Tempo Freestanding | TEMF.03016016/AS | 30 | 160 | 16 | 18 | 2368 | 2368 | 2368 | 0.056381 | 864 | 0.020571 | 2721 | 0.064786 | 1.456 | A02 | TEMF0.03016016/AS
Freestanding | Tempo Freestanding | TEMF.03016020/AS | 30 | 160 | 20 | 23 | 3050 | 3050 | 3050 | 0.072619 | 1159 | 0.027595 | 3483 | 0.082929 | 1.396 | A02 | TEMF0.03016020/AS
Freestanding | Tempo Freestanding | TEMF.03016021/AS | 30 | 160 | 21 | 23 | 3117 | 3117 | 3117 | 0.074214 | 1125 | 0.026786 | 3585 | 0.085357 | 1.468 | A02 | TEMF0.03016021/AS
Freestanding | Tempo Freestanding | TEMF.03018010/AS | 30 | 180 | 10 | 13 | 1487 | 1487 | 1487 | 0.035405 | 562 | 0.013381 | 1700 | 0.040476 | 1.403 | A02 | TEMF0.03018010/AS
Freestanding | Tempo Freestanding | TEMF.03018011/AS | 30 | 180 | 11 | 13 | 2018 | 2018 | 2018 | 0.048048 | 745 | 0.017738 | 2315 | 0.055119 | 1.44 | A02 | TEMF0.03018011/AS
Freestanding | Tempo Freestanding | TEMF.03018015/AS | 30 | 180 | 15 | 18 | 2446 | 2446 | 2446 | 0.058238 | 929 | 0.022119 | 2793 | 0.0665 | 1.396 | A02 | TEMF0.03018015/AS
Freestanding | Tempo Freestanding | TEMF.03018016/AS | 30 | 180 | 16 | 18 | 2664 | 2664 | 2664 | 0.063429 | 972 | 0.023143 | 3061 | 0.072881 | 1.456 | A02 | TEMF0.03018016/AS
Freestanding | Tempo Freestanding | TEMF.03018020/AS | 30 | 180 | 20 | 23 | 3431 | 3431 | 3431 | 0.08169 | 1304 | 0.031048 | 3918 | 0.093286 | 1.396 | A02 | TEMF0.03018020/AS
Freestanding | Tempo Freestanding | TEMF.03018021/AS | 30 | 180 | 21 | 23 | 3506 | 3506 | 3506 | 0.083476 | 1266 | 0.030143 | 4032 | 0.096 | 1.468 | A02 | TEMF0.03018021/AS
Freestanding | Tempo Freestanding | TEMF.03020010/AS | 30 | 200 | 10 | 13 | 1652 | 1652 | 1652 | 0.039333 | 624 | 0.014857 | 1888 | 0.044952 | 1.403 | A02 | TEMF0.03020010/AS
Freestanding | Tempo Freestanding | TEMF.03020011/AS | 30 | 200 | 11 | 13 | 2242 | 2242 | 2242 | 0.053381 | 827 | 0.01969 | 2572 | 0.061238 | 1.44 | A02 | TEMF0.03020011/AS
Freestanding | Tempo Freestanding | TEMF.03020015/AS | 30 | 200 | 15 | 18 | 2718 | 2718 | 2718 | 0.064714 | 1033 | 0.024595 | 3104 | 0.073905 | 1.396 | A02 | TEMF0.03020015/AS
Freestanding | Tempo Freestanding | TEMF.03020016/AS | 30 | 200 | 16 | 18 | 2960 | 2960 | 2960 | 0.070476 | 1080 | 0.025714 | 3401 | 0.080976 | 1.456 | A02 | TEMF0.03020016/AS
Freestanding | Tempo Freestanding | TEMF.03020020/AS | 30 | 200 | 20 | 23 | 3812 | 3812 | 3812 | 0.090762 | 1449 | 0.0345 | 4353 | 0.10364 | 1.396 | A02 | TEMF0.03020020/AS
Freestanding | Tempo Freestanding | TEMF.03020021/AS | 30 | 200 | 21 | 23 | 3896 | 3896 | 3896 | 0.092762 | 1406 | 0.033476 | 4480 | 0.10667 | 1.468 | A02 | TEMF0.03020021/AS
Freestanding | Tempo Freestanding | TEMF.03022010/AS | 30 | 220 | 10 | 13 | 1817 | 1817 | 1817 | 0.043262 | 687 | 0.016357 | 2077 | 0.049452 | 1.403 | A02 | TEMF0.03022010/AS
Freestanding | Tempo Freestanding | TEMF.03022011/AS | 30 | 220 | 11 | 13 | 2466 | 2466 | 2466 | 0.058714 | 910 | 0.021667 | 2829 | 0.067357 | 1.44 | A02 | TEMF0.03022011/AS
Freestanding | Tempo Freestanding | TEMF.03022015/AS | 30 | 220 | 15 | 18 | 2990 | 2990 | 2990 | 0.07119 | 1136 | 0.027048 | 3415 | 0.08131 | 1.396 | A02 | TEMF0.03022015/AS
Freestanding | Tempo Freestanding | TEMF.03022016/AS | 30 | 220 | 16 | 18 | 3256 | 3256 | 3256 | 0.077524 | 1188 | 0.028286 | 3741 | 0.089071 | 1.456 | A02 | TEMF0.03022016/AS
Freestanding | Tempo Freestanding | TEMF.03022020/AS | 30 | 220 | 20 | 23 | 4193 | 4193 | 4193 | 0.099833 | 1593 | 0.037929 | 4788 | 0.114 | 1.396 | A02 | TEMF0.03022020/AS
Freestanding | Tempo Freestanding | TEMF.03022021/AS | 30 | 220 | 21 | 23 | 4286 | 4286 | 4286 | 0.10205 | 1547 | 0.036833 | 4929 | 0.11736 | 1.468 | A02 | TEMF0.03022021/AS
Freestanding | Tempo Freestanding | TEMF.03024010/AS | 30 | 240 | 10 | 13 | 1982 | 1982 | 1982 | 0.04719 | 749 | 0.017833 | 2265 | 0.053929 | 1.403 | A02 | TEMF0.03024010/AS
Freestanding | Tempo Freestanding | TEMF.03024011/AS | 30 | 240 | 11 | 13 | 2690 | 2690 | 2690 | 0.064048 | 993 | 0.023643 | 3085 | 0.073452 | 1.44 | A02 | TEMF0.03024011/AS
Freestanding | Tempo Freestanding | TEMF.03024015/AS | 30 | 240 | 15 | 18 | 3262 | 3262 | 3262 | 0.077667 | 1240 | 0.029524 | 3725 | 0.08869 | 1.396 | A02 | TEMF0.03024015/AS
Freestanding | Tempo Freestanding | TEMF.03024016/AS | 30 | 240 | 16 | 18 | 3552 | 3552 | 3552 | 0.084571 | 1296 | 0.030857 | 4081 | 0.097167 | 1.456 | A02 | TEMF0.03024016/AS
Freestanding | Tempo Freestanding | TEMF.03024020/AS | 30 | 240 | 20 | 23 | 4574 | 4574 | 4574 | 0.1089 | 1738 | 0.041381 | 5224 | 0.12438 | 1.396 | A02 | TEMF0.03024020/AS
Freestanding | Tempo Freestanding | TEMF.03024021/AS | 30 | 240 | 21 | 23 | 4675 | 4675 | 4675 | 0.11131 | 1688 | 0.04019 | 5376 | 0.128 | 1.468 | A02 | TEMF0.03024021/AS
Freestanding | Tempo Freestanding | TEMF.03026010/AS | 30 | 260 | 10 | 13 | 2148 | 2148 | 2148 | 0.051143 | 812 | 0.019333 | 2455 | 0.058452 | 1.403 | A02 | TEMF0.03026010/AS
Freestanding | Tempo Freestanding | TEMF.03026011/AS | 30 | 260 | 11 | 13 | 2915 | 2915 | 2915 | 0.069405 | 1076 | 0.025619 | 3344 | 0.079619 | 1.44 | A02 | TEMF0.03026011/AS
Freestanding | Tempo Freestanding | TEMF.03026015/AS | 30 | 260 | 15 | 18 | 3533 | 3533 | 3533 | 0.084119 | 1343 | 0.031976 | 4035 | 0.096071 | 1.396 | A02 | TEMF0.03026015/AS
Freestanding | Tempo Freestanding | TEMF.03026016/AS | 30 | 260 | 16 | 18 | 3848 | 3848 | 3848 | 0.091619 | 1405 | 0.033452 | 4421 | 0.10526 | 1.456 | A02 | TEMF0.03026016/AS
Freestanding | Tempo Freestanding | TEMF.03026020/AS | 30 | 260 | 20 | 23 | 4956 | 4956 | 4956 | 0.118 | 1883 | 0.044833 | 5660 | 0.13476 | 1.396 | A02 | TEMF0.03026020/AS
Freestanding | Tempo Freestanding | TEMF.03026021/AS | 30 | 260 | 21 | 23 | 5065 | 5065 | 5065 | 0.1206 | 1828 | 0.043524 | 5825 | 0.13869 | 1.468 | A02 | TEMF0.03026021/AS
Freestanding | Tempo Freestanding | TEMF.03028010/AS | 30 | 280 | 10 | 13 | 2313 | 2313 | 2313 | 0.055071 | 874 | 0.02081 | 2644 | 0.062952 | 1.403 | A02 | TEMF0.03028010/AS
Freestanding | Tempo Freestanding | TEMF.03028011/AS | 30 | 280 | 11 | 13 | 3139 | 3139 | 3139 | 0.074738 | 1158 | 0.027571 | 3600 | 0.085714 | 1.44 | A02 | TEMF0.03028011/AS
Freestanding | Tempo Freestanding | TEMF.03028015/AS | 30 | 280 | 15 | 18 | 3805 | 3805 | 3805 | 0.090595 | 1446 | 0.034429 | 4345 | 0.10345 | 1.396 | A02 | TEMF0.03028015/AS
Freestanding | Tempo Freestanding | TEMF.03028016/AS | 30 | 280 | 16 | 18 | 4144 | 4144 | 4144 | 0.098667 | 1513 | 0.036024 | 4761 | 0.11336 | 1.456 | A02 | TEMF0.03028016/AS
Freestanding | Tempo Freestanding | TEMF.03028020/AS | 30 | 280 | 20 | 23 | 5337 | 5337 | 5337 | 0.12707 | 2028 | 0.048286 | 6095 | 0.14512 | 1.396 | A02 | TEMF0.03028020/AS
Freestanding | Tempo Freestanding | TEMF.03028021/AS | 30 | 280 | 21 | 23 | 5454 | 5454 | 5454 | 0.12986 | 1969 | 0.046881 | 6272 | 0.14933 | 1.468 | A02 | TEMF0.03028021/AS
Freestanding | Tempo Freestanding | TEMF.03030010/AS | 30 | 300 | 10 | 13 | 2478 | 2478 | 2478 | 0.059 | 937 | 0.02231 | 2832 | 0.067429 | 1.403 | A02 | TEMF0.03030010/AS
Freestanding | Tempo Freestanding | TEMF.03030011/AS | 30 | 300 | 11 | 13 | 3363 | 3363 | 3363 | 0.080071 | 1241 | 0.029548 | 3857 | 0.091833 | 1.44 | A02 | TEMF0.03030011/AS
Freestanding | Tempo Freestanding | TEMF.03030015/AS | 30 | 300 | 15 | 18 | 4077 | 4077 | 4077 | 0.097071 | 1549 | 0.036881 | 4656 | 0.11086 | 1.396 | A02 | TEMF0.03030015/AS
Freestanding | Tempo Freestanding | TEMF.03030016/AS | 30 | 300 | 16 | 18 | 4440 | 4440 | 4440 | 0.10571 | 1621 | 0.038595 | 5102 | 0.12148 | 1.456 | A02 | TEMF0.03030016/AS
Freestanding | Tempo Freestanding | TEMF.03030020/AS | 30 | 300 | 20 | 23 | 5718 | 5718 | 5718 | 0.13614 | 2173 | 0.051738 | 6530 | 0.15548 | 1.396 | A02 | TEMF0.03030020/AS
Freestanding | Tempo Freestanding | TEMF.03030021/AS | 30 | 300 | 21 | 23 | 5844 | 5844 | 5844 | 0.13914 | 2110 | 0.050238 | 6721 | 0.16002 | 1.468 | A02 | TEMF0.03030021/AS
Freestanding | Tempo Freestanding | TEMF.04004010/AS | 40 | 40 | 10 | 13 | 385 | 385 | 385 | 0.0091667 | 147 | 0.0035 | 440 | 0.010476 | 1.394 | A02 | TEMF0.04004010/AS
Freestanding | Tempo Freestanding | TEMF.04004011/AS | 40 | 40 | 11 | 13 | 506 | 506 | 506 | 0.012048 | 187 | 0.0044524 | 580 | 0.01381 | 1.439 | A02 | TEMF0.04004011/AS
Freestanding | Tempo Freestanding | TEMF.04004015/AS | 40 | 40 | 15 | 18 | 627 | 627 | 627 | 0.014929 | 240 | 0.0057143 | 715 | 0.017024 | 1.385 | A02 | TEMF0.04004015/AS
Freestanding | Tempo Freestanding | TEMF.04004016/AS | 40 | 40 | 16 | 18 | 680 | 680 | 680 | 0.01619 | 247 | 0.005881 | 781 | 0.018595 | 1.46 | A02 | TEMF0.04004016/AS
Freestanding | Tempo Freestanding | TEMF.04004020/AS | 40 | 40 | 20 | 23 | 878 | 878 | 878 | 0.020905 | 336 | 0.008 | 1002 | 0.023857 | 1.384 | A02 | TEMF0.04004020/AS
Freestanding | Tempo Freestanding | TEMF.04004021/AS | 40 | 40 | 21 | 23 | 910 | 910 | 910 | 0.021667 | 327 | 0.0077857 | 1047 | 0.024929 | 1.477 | A02 | TEMF0.04004021/AS
Freestanding | Tempo Freestanding | TEMF.04005010/AS | 40 | 50 | 10 | 13 | 482 | 482 | 482 | 0.011476 | 184 | 0.004381 | 550 | 0.013095 | 1.394 | A02 | TEMF0.04005010/AS
Freestanding | Tempo Freestanding | TEMF.04005011/AS | 40 | 50 | 11 | 13 | 632 | 632 | 632 | 0.015048 | 233 | 0.0055476 | 725 | 0.017262 | 1.439 | A02 | TEMF0.04005011/AS
Freestanding | Tempo Freestanding | TEMF.04005015/AS | 40 | 50 | 15 | 18 | 784 | 784 | 784 | 0.018667 | 300 | 0.0071429 | 895 | 0.02131 | 1.385 | A02 | TEMF0.04005015/AS
Freestanding | Tempo Freestanding | TEMF.04005016/AS | 40 | 50 | 16 | 18 | 850 | 850 | 850 | 0.020238 | 309 | 0.0073571 | 977 | 0.023262 | 1.46 | A02 | TEMF0.04005016/AS
Freestanding | Tempo Freestanding | TEMF.04005020/AS | 40 | 50 | 20 | 23 | 1098 | 1098 | 1098 | 0.026143 | 421 | 0.010024 | 1253 | 0.029833 | 1.384 | A02 | TEMF0.04005020/AS
Freestanding | Tempo Freestanding | TEMF.04005021/AS | 40 | 50 | 21 | 23 | 1137 | 1137 | 1137 | 0.027071 | 408 | 0.0097143 | 1309 | 0.031167 | 1.477 | A02 | TEMF0.04005021/AS
Freestanding | Tempo Freestanding | TEMF.04006010/AS | 40 | 60 | 10 | 13 | 578 | 578 | 578 | 0.013762 | 220 | 0.0052381 | 660 | 0.015714 | 1.394 | A02 | TEMF0.04006010/AS
Freestanding | Tempo Freestanding | TEMF.04006011/AS | 40 | 60 | 11 | 13 | 758 | 758 | 758 | 0.018048 | 280 | 0.0066667 | 869 | 0.02069 | 1.439 | A02 | TEMF0.04006011/AS
Freestanding | Tempo Freestanding | TEMF.04006015/AS | 40 | 60 | 15 | 18 | 941 | 941 | 941 | 0.022405 | 360 | 0.0085714 | 1074 | 0.025571 | 1.385 | A02 | TEMF0.04006015/AS
Freestanding | Tempo Freestanding | TEMF.04006016/AS | 40 | 60 | 16 | 18 | 1020 | 1020 | 1020 | 0.024286 | 370 | 0.0088095 | 1172 | 0.027905 | 1.46 | A02 | TEMF0.04006016/AS
Freestanding | Tempo Freestanding | TEMF.04006020/AS | 40 | 60 | 20 | 23 | 1318 | 1318 | 1318 | 0.031381 | 505 | 0.012024 | 1504 | 0.03581 | 1.384 | A02 | TEMF0.04006020/AS
Freestanding | Tempo Freestanding | TEMF.04006021/AS | 40 | 60 | 21 | 23 | 1364 | 1364 | 1364 | 0.032476 | 490 | 0.011667 | 1570 | 0.037381 | 1.477 | A02 | TEMF0.04006021/AS
Freestanding | Tempo Freestanding | TEMF.04007010/AS | 40 | 70 | 10 | 13 | 674 | 674 | 674 | 0.016048 | 257 | 0.006119 | 770 | 0.018333 | 1.394 | A02 | TEMF0.04007010/AS
Freestanding | Tempo Freestanding | TEMF.04007011/AS | 40 | 70 | 11 | 13 | 885 | 885 | 885 | 0.021071 | 327 | 0.0077857 | 1015 | 0.024167 | 1.439 | A02 | TEMF0.04007011/AS
Freestanding | Tempo Freestanding | TEMF.04007015/AS | 40 | 70 | 15 | 18 | 1098 | 1098 | 1098 | 0.026143 | 421 | 0.010024 | 1253 | 0.029833 | 1.385 | A02 | TEMF0.04007015/AS
Freestanding | Tempo Freestanding | TEMF.04007016/AS | 40 | 70 | 16 | 18 | 1190 | 1190 | 1190 | 0.028333 | 432 | 0.010286 | 1367 | 0.032548 | 1.46 | A02 | TEMF0.04007016/AS
Freestanding | Tempo Freestanding | TEMF.04007020/AS | 40 | 70 | 20 | 23 | 1537 | 1537 | 1537 | 0.036595 | 589 | 0.014024 | 1754 | 0.041762 | 1.384 | A02 | TEMF0.04007020/AS
Freestanding | Tempo Freestanding | TEMF.04007021/AS | 40 | 70 | 21 | 23 | 1592 | 1592 | 1592 | 0.037905 | 572 | 0.013619 | 1832 | 0.043619 | 1.477 | A02 | TEMF0.04007021/AS
Freestanding | Tempo Freestanding | TEMF.04008010/AS | 40 | 80 | 10 | 13 | 770 | 770 | 770 | 0.018333 | 293 | 0.0069762 | 879 | 0.020929 | 1.394 | A02 | TEMF0.04008010/AS
Freestanding | Tempo Freestanding | TEMF.04008011/AS | 40 | 80 | 11 | 13 | 1011 | 1011 | 1011 | 0.024071 | 373 | 0.008881 | 1160 | 0.027619 | 1.439 | A02 | TEMF0.04008011/AS
Freestanding | Tempo Freestanding | TEMF.04008015/AS | 40 | 80 | 15 | 18 | 1254 | 1254 | 1254 | 0.029857 | 480 | 0.011429 | 1431 | 0.034071 | 1.385 | A02 | TEMF0.04008015/AS
Freestanding | Tempo Freestanding | TEMF.04008016/AS | 40 | 80 | 16 | 18 | 1360 | 1360 | 1360 | 0.032381 | 494 | 0.011762 | 1563 | 0.037214 | 1.46 | A02 | TEMF0.04008016/AS
Freestanding | Tempo Freestanding | TEMF.04008020/AS | 40 | 80 | 20 | 23 | 1757 | 1757 | 1757 | 0.041833 | 673 | 0.016024 | 2005 | 0.047738 | 1.384 | A02 | TEMF0.04008020/AS
Freestanding | Tempo Freestanding | TEMF.04008021/AS | 40 | 80 | 21 | 23 | 1819 | 1819 | 1819 | 0.04331 | 653 | 0.015548 | 2094 | 0.049857 | 1.477 | A02 | TEMF0.04008021/AS
Freestanding | Tempo Freestanding | TEMF.04009010/AS | 40 | 90 | 10 | 13 | 867 | 867 | 867 | 0.020643 | 330 | 0.0078571 | 990 | 0.023571 | 1.394 | A02 | TEMF0.04009010/AS
Freestanding | Tempo Freestanding | TEMF.04009011/AS | 40 | 90 | 11 | 13 | 1138 | 1138 | 1138 | 0.027095 | 420 | 0.01 | 1305 | 0.031071 | 1.439 | A02 | TEMF0.04009011/AS
Freestanding | Tempo Freestanding | TEMF.04009015/AS | 40 | 90 | 15 | 18 | 1411 | 1411 | 1411 | 0.033595 | 540 | 0.012857 | 1610 | 0.038333 | 1.385 | A02 | TEMF0.04009015/AS
Freestanding | Tempo Freestanding | TEMF.04009016/AS | 40 | 90 | 16 | 18 | 1530 | 1530 | 1530 | 0.036429 | 555 | 0.013214 | 1758 | 0.041857 | 1.46 | A02 | TEMF0.04009016/AS
Freestanding | Tempo Freestanding | TEMF.04009020/AS | 40 | 90 | 20 | 23 | 1976 | 1976 | 1976 | 0.047048 | 757 | 0.018024 | 2255 | 0.05369 | 1.384 | A02 | TEMF0.04009020/AS
Freestanding | Tempo Freestanding | TEMF.04009021/AS | 40 | 90 | 21 | 23 | 2047 | 2047 | 2047 | 0.048738 | 735 | 0.0175 | 2356 | 0.056095 | 1.477 | A02 | TEMF0.04009021/AS
Freestanding | Tempo Freestanding | TEMF.04010010/AS | 40 | 100 | 10 | 13 | 963 | 963 | 963 | 0.022929 | 367 | 0.0087381 | 1100 | 0.02619 | 1.394 | A02 | TEMF0.04010010/AS
Freestanding | Tempo Freestanding | TEMF.04010011/AS | 40 | 100 | 11 | 13 | 1264 | 1264 | 1264 | 0.030095 | 466 | 0.011095 | 1450 | 0.034524 | 1.439 | A02 | TEMF0.04010011/AS
Freestanding | Tempo Freestanding | TEMF.04010015/AS | 40 | 100 | 15 | 18 | 1568 | 1568 | 1568 | 0.037333 | 601 | 0.01431 | 1789 | 0.042595 | 1.385 | A02 | TEMF0.04010015/AS
Freestanding | Tempo Freestanding | TEMF.04010016/AS | 40 | 100 | 16 | 18 | 1700 | 1700 | 1700 | 0.040476 | 617 | 0.01469 | 1953 | 0.0465 | 1.46 | A02 | TEMF0.04010016/AS
Freestanding | Tempo Freestanding | TEMF.04010020/AS | 40 | 100 | 20 | 23 | 2196 | 2196 | 2196 | 0.052286 | 841 | 0.020024 | 2506 | 0.059667 | 1.384 | A02 | TEMF0.04010020/AS
Freestanding | Tempo Freestanding | TEMF.04010021/AS | 40 | 100 | 21 | 23 | 2274 | 2274 | 2274 | 0.054143 | 816 | 0.019429 | 2617 | 0.06231 | 1.477 | A02 | TEMF0.04010021/AS
Freestanding | Tempo Freestanding | TEMF.04011010/AS | 40 | 110 | 10 | 13 | 1059 | 1059 | 1059 | 0.025214 | 403 | 0.0095952 | 1209 | 0.028786 | 1.394 | A02 | TEMF0.04011010/AS
Freestanding | Tempo Freestanding | TEMF.04011011/AS | 40 | 110 | 11 | 13 | 1390 | 1390 | 1390 | 0.033095 | 513 | 0.012214 | 1594 | 0.037952 | 1.439 | A02 | TEMF0.04011011/AS
Freestanding | Tempo Freestanding | TEMF.04011015/AS | 40 | 110 | 15 | 18 | 1725 | 1725 | 1725 | 0.041071 | 661 | 0.015738 | 1968 | 0.046857 | 1.385 | A02 | TEMF0.04011015/AS
Freestanding | Tempo Freestanding | TEMF.04011016/AS | 40 | 110 | 16 | 18 | 1870 | 1870 | 1870 | 0.044524 | 679 | 0.016167 | 2149 | 0.051167 | 1.46 | A02 | TEMF0.04011016/AS
Freestanding | Tempo Freestanding | TEMF.04011020/AS | 40 | 110 | 20 | 23 | 2416 | 2416 | 2416 | 0.057524 | 925 | 0.022024 | 2757 | 0.065643 | 1.384 | A02 | TEMF0.04011020/AS
Freestanding | Tempo Freestanding | TEMF.04011021/AS | 40 | 110 | 21 | 23 | 2501 | 2501 | 2501 | 0.059548 | 898 | 0.021381 | 2879 | 0.068548 | 1.477 | A02 | TEMF0.04011021/AS
Freestanding | Tempo Freestanding | TEMF.04012010/AS | 40 | 120 | 10 | 13 | 1156 | 1156 | 1156 | 0.027524 | 440 | 0.010476 | 1320 | 0.031429 | 1.394 | A02 | TEMF0.04012010/AS
Freestanding | Tempo Freestanding | TEMF.04012011/AS | 40 | 120 | 11 | 13 | 1517 | 1517 | 1517 | 0.036119 | 560 | 0.013333 | 1740 | 0.041429 | 1.439 | A02 | TEMF0.04012011/AS
Freestanding | Tempo Freestanding | TEMF.04012015/AS | 40 | 120 | 15 | 18 | 1882 | 1882 | 1882 | 0.04481 | 721 | 0.017167 | 2147 | 0.051119 | 1.385 | A02 | TEMF0.04012015/AS
Freestanding | Tempo Freestanding | TEMF.04012016/AS | 40 | 120 | 16 | 18 | 2040 | 2040 | 2040 | 0.048571 | 741 | 0.017643 | 2344 | 0.05581 | 1.46 | A02 | TEMF0.04012016/AS
Freestanding | Tempo Freestanding | TEMF.04012020/AS | 40 | 120 | 20 | 23 | 2635 | 2635 | 2635 | 0.062738 | 1009 | 0.024024 | 3007 | 0.071595 | 1.384 | A02 | TEMF0.04012020/AS
Freestanding | Tempo Freestanding | TEMF.04012021/AS | 40 | 120 | 21 | 23 | 2729 | 2729 | 2729 | 0.064976 | 980 | 0.023333 | 3141 | 0.074786 | 1.477 | A02 | TEMF0.04012021/AS
Freestanding | Tempo Freestanding | TEMF.04014010/AS | 40 | 140 | 10 | 13 | 1348 | 1348 | 1348 | 0.032095 | 514 | 0.012238 | 1539 | 0.036643 | 1.394 | A02 | TEMF0.04014010/AS
Freestanding | Tempo Freestanding | TEMF.04014011/AS | 40 | 140 | 11 | 13 | 1770 | 1770 | 1770 | 0.042143 | 653 | 0.015548 | 2030 | 0.048333 | 1.439 | A02 | TEMF0.04014011/AS
Freestanding | Tempo Freestanding | TEMF.04014015/AS | 40 | 140 | 15 | 18 | 2195 | 2195 | 2195 | 0.052262 | 841 | 0.020024 | 2504 | 0.059619 | 1.385 | A02 | TEMF0.04014015/AS
Freestanding | Tempo Freestanding | TEMF.04014016/AS | 40 | 140 | 16 | 18 | 2380 | 2380 | 2380 | 0.056667 | 864 | 0.020571 | 2735 | 0.065119 | 1.46 | A02 | TEMF0.04014016/AS
Freestanding | Tempo Freestanding | TEMF.04014020/AS | 40 | 140 | 20 | 23 | 3074 | 3074 | 3074 | 0.07319 | 1177 | 0.028024 | 3507 | 0.0835 | 1.384 | A02 | TEMF0.04014020/AS
Freestanding | Tempo Freestanding | TEMF.04014021/AS | 40 | 140 | 21 | 23 | 3184 | 3184 | 3184 | 0.07581 | 1143 | 0.027214 | 3665 | 0.087262 | 1.477 | A02 | TEMF0.04014021/AS
Freestanding | Tempo Freestanding | TEMF.04016010/AS | 40 | 160 | 10 | 13 | 1541 | 1541 | 1541 | 0.03669 | 587 | 0.013976 | 1760 | 0.041905 | 1.394 | A02 | TEMF0.04016010/AS
Freestanding | Tempo Freestanding | TEMF.04016011/AS | 40 | 160 | 11 | 13 | 2022 | 2022 | 2022 | 0.048143 | 746 | 0.017762 | 2319 | 0.055214 | 1.439 | A02 | TEMF0.04016011/AS
Freestanding | Tempo Freestanding | TEMF.04016015/AS | 40 | 160 | 15 | 18 | 2509 | 2509 | 2509 | 0.059738 | 961 | 0.022881 | 2863 | 0.068167 | 1.385 | A02 | TEMF0.04016015/AS
Freestanding | Tempo Freestanding | TEMF.04016016/AS | 40 | 160 | 16 | 18 | 2720 | 2720 | 2720 | 0.064762 | 987 | 0.0235 | 3125 | 0.074405 | 1.46 | A02 | TEMF0.04016016/AS
Freestanding | Tempo Freestanding | TEMF.04016020/AS | 40 | 160 | 20 | 23 | 3514 | 3514 | 3514 | 0.083667 | 1346 | 0.032048 | 4009 | 0.095452 | 1.384 | A02 | TEMF0.04016020/AS
Freestanding | Tempo Freestanding | TEMF.04016021/AS | 40 | 160 | 21 | 23 | 3638 | 3638 | 3638 | 0.086619 | 1306 | 0.031095 | 4187 | 0.09969 | 1.477 | A02 | TEMF0.04016021/AS
Freestanding | Tempo Freestanding | TEMF.04018010/AS | 40 | 180 | 10 | 13 | 1733 | 1733 | 1733 | 0.041262 | 660 | 0.015714 | 1979 | 0.047119 | 1.394 | A02 | TEMF0.04018010/AS
Freestanding | Tempo Freestanding | TEMF.04018011/AS | 40 | 180 | 11 | 13 | 2275 | 2275 | 2275 | 0.054167 | 839 | 0.019976 | 2609 | 0.062119 | 1.439 | A02 | TEMF0.04018011/AS
Freestanding | Tempo Freestanding | TEMF.04018015/AS | 40 | 180 | 15 | 18 | 2822 | 2822 | 2822 | 0.06719 | 1081 | 0.025738 | 3220 | 0.076667 | 1.385 | A02 | TEMF0.04018015/AS
Freestanding | Tempo Freestanding | TEMF.04018016/AS | 40 | 180 | 16 | 18 | 3060 | 3060 | 3060 | 0.072857 | 1111 | 0.026452 | 3516 | 0.083714 | 1.46 | A02 | TEMF0.04018016/AS
Freestanding | Tempo Freestanding | TEMF.04018020/AS | 40 | 180 | 20 | 23 | 3953 | 3953 | 3953 | 0.094119 | 1514 | 0.036048 | 4510 | 0.10738 | 1.384 | A02 | TEMF0.04018020/AS
Freestanding | Tempo Freestanding | TEMF.04018021/AS | 40 | 180 | 21 | 23 | 4093 | 4093 | 4093 | 0.097452 | 1469 | 0.034976 | 4711 | 0.11217 | 1.477 | A02 | TEMF0.04018021/AS
Freestanding | Tempo Freestanding | TEMF.04020010/AS | 40 | 200 | 10 | 13 | 1926 | 1926 | 1926 | 0.045857 | 734 | 0.017476 | 2199 | 0.052357 | 1.394 | A02 | TEMF0.04020010/AS
Freestanding | Tempo Freestanding | TEMF.04020011/AS | 40 | 200 | 11 | 13 | 2528 | 2528 | 2528 | 0.06019 | 933 | 0.022214 | 2900 | 0.069048 | 1.439 | A02 | TEMF0.04020011/AS
Freestanding | Tempo Freestanding | TEMF.04020015/AS | 40 | 200 | 15 | 18 | 3136 | 3136 | 3136 | 0.074667 | 1201 | 0.028595 | 3578 | 0.08519 | 1.385 | A02 | TEMF0.04020015/AS
Freestanding | Tempo Freestanding | TEMF.04020016/AS | 40 | 200 | 16 | 18 | 3400 | 3400 | 3400 | 0.080952 | 1234 | 0.029381 | 3907 | 0.093024 | 1.46 | A02 | TEMF0.04020016/AS
Freestanding | Tempo Freestanding | TEMF.04020020/AS | 40 | 200 | 20 | 23 | 4392 | 4392 | 4392 | 0.10457 | 1682 | 0.040048 | 5011 | 0.11931 | 1.384 | A02 | TEMF0.04020020/AS
Freestanding | Tempo Freestanding | TEMF.04020021/AS | 40 | 200 | 21 | 23 | 4548 | 4548 | 4548 | 0.10829 | 1633 | 0.038881 | 5235 | 0.12464 | 1.477 | A02 | TEMF0.04020021/AS
Freestanding | Tempo Freestanding | TEMF.04022010/AS | 40 | 220 | 10 | 13 | 2119 | 2119 | 2119 | 0.050452 | 807 | 0.019214 | 2420 | 0.057619 | 1.394 | A02 | TEMF0.04022010/AS
Freestanding | Tempo Freestanding | TEMF.04022011/AS | 40 | 220 | 11 | 13 | 2781 | 2781 | 2781 | 0.066214 | 1026 | 0.024429 | 3190 | 0.075952 | 1.439 | A02 | TEMF0.04022011/AS
Freestanding | Tempo Freestanding | TEMF.04022015/AS | 40 | 220 | 15 | 18 | 3450 | 3450 | 3450 | 0.082143 | 1321 | 0.031452 | 3936 | 0.093714 | 1.385 | A02 | TEMF0.04022015/AS
Freestanding | Tempo Freestanding | TEMF.04022016/AS | 40 | 220 | 16 | 18 | 3740 | 3740 | 3740 | 0.089048 | 1358 | 0.032333 | 4297 | 0.10231 | 1.46 | A02 | TEMF0.04022016/AS
Freestanding | Tempo Freestanding | TEMF.04022020/AS | 40 | 220 | 20 | 23 | 4831 | 4831 | 4831 | 0.11502 | 1850 | 0.044048 | 5512 | 0.13124 | 1.384 | A02 | TEMF0.04022020/AS
Freestanding | Tempo Freestanding | TEMF.04022021/AS | 40 | 220 | 21 | 23 | 5003 | 5003 | 5003 | 0.11912 | 1796 | 0.042762 | 5758 | 0.1371 | 1.477 | A02 | TEMF0.04022021/AS
Freestanding | Tempo Freestanding | TEMF.04024010/AS | 40 | 240 | 10 | 13 | 2311 | 2311 | 2311 | 0.055024 | 880 | 0.020952 | 2639 | 0.062833 | 1.394 | A02 | TEMF0.04024010/AS
Freestanding | Tempo Freestanding | TEMF.04024011/AS | 40 | 240 | 11 | 13 | 3034 | 3034 | 3034 | 0.072238 | 1120 | 0.026667 | 3480 | 0.082857 | 1.439 | A02 | TEMF0.04024011/AS
Freestanding | Tempo Freestanding | TEMF.04024015/AS | 40 | 240 | 15 | 18 | 3763 | 3763 | 3763 | 0.089595 | 1441 | 0.03431 | 4294 | 0.10224 | 1.385 | A02 | TEMF0.04024015/AS
Freestanding | Tempo Freestanding | TEMF.04024016/AS | 40 | 240 | 16 | 18 | 4080 | 4080 | 4080 | 0.097143 | 1481 | 0.035262 | 4688 | 0.11162 | 1.46 | A02 | TEMF0.04024016/AS
Freestanding | Tempo Freestanding | TEMF.04024020/AS | 40 | 240 | 20 | 23 | 5270 | 5270 | 5270 | 0.12548 | 2018 | 0.048048 | 6013 | 0.14317 | 1.384 | A02 | TEMF0.04024020/AS
Freestanding | Tempo Freestanding | TEMF.04024021/AS | 40 | 240 | 21 | 23 | 5458 | 5458 | 5458 | 0.12995 | 1959 | 0.046643 | 6282 | 0.14957 | 1.477 | A02 | TEMF0.04024021/AS
Freestanding | Tempo Freestanding | TEMF.04026010/AS | 40 | 260 | 10 | 13 | 2504 | 2504 | 2504 | 0.059619 | 954 | 0.022714 | 2860 | 0.068095 | 1.394 | A02 | TEMF0.04026010/AS
Freestanding | Tempo Freestanding | TEMF.04026011/AS | 40 | 260 | 11 | 13 | 3286 | 3286 | 3286 | 0.078238 | 1213 | 0.028881 | 3769 | 0.089738 | 1.439 | A02 | TEMF0.04026011/AS
Freestanding | Tempo Freestanding | TEMF.04026015/AS | 40 | 260 | 15 | 18 | 4077 | 4077 | 4077 | 0.097071 | 1561 | 0.037167 | 4652 | 0.11076 | 1.385 | A02 | TEMF0.04026015/AS
Freestanding | Tempo Freestanding | TEMF.04026016/AS | 40 | 260 | 16 | 18 | 4420 | 4420 | 4420 | 0.10524 | 1604 | 0.03819 | 5079 | 0.12093 | 1.46 | A02 | TEMF0.04026016/AS
Freestanding | Tempo Freestanding | TEMF.04026020/AS | 40 | 260 | 20 | 23 | 5710 | 5710 | 5710 | 0.13595 | 2187 | 0.052071 | 6515 | 0.15512 | 1.384 | A02 | TEMF0.04026020/AS
Freestanding | Tempo Freestanding | TEMF.04026021/AS | 40 | 260 | 21 | 23 | 5912 | 5912 | 5912 | 0.14076 | 2122 | 0.050524 | 6805 | 0.16202 | 1.477 | A02 | TEMF0.04026021/AS
Freestanding | Tempo Freestanding | TEMF.04028010/AS | 40 | 280 | 10 | 13 | 2696 | 2696 | 2696 | 0.06419 | 1027 | 0.024452 | 3079 | 0.07331 | 1.394 | A02 | TEMF0.04028010/AS
Freestanding | Tempo Freestanding | TEMF.04028011/AS | 40 | 280 | 11 | 13 | 3539 | 3539 | 3539 | 0.084262 | 1306 | 0.031095 | 4059 | 0.096643 | 1.439 | A02 | TEMF0.04028011/AS
Freestanding | Tempo Freestanding | TEMF.04028015/AS | 40 | 280 | 15 | 18 | 4390 | 4390 | 4390 | 0.10452 | 1681 | 0.040024 | 5009 | 0.11926 | 1.385 | A02 | TEMF0.04028015/AS
Freestanding | Tempo Freestanding | TEMF.04028016/AS | 40 | 280 | 16 | 18 | 4760 | 4760 | 4760 | 0.11333 | 1728 | 0.041143 | 5469 | 0.13021 | 1.46 | A02 | TEMF0.04028016/AS
Freestanding | Tempo Freestanding | TEMF.04028020/AS | 40 | 280 | 20 | 23 | 6149 | 6149 | 6149 | 0.1464 | 2355 | 0.056071 | 7016 | 0.16705 | 1.384 | A02 | TEMF0.04028020/AS
Freestanding | Tempo Freestanding | TEMF.04028021/AS | 40 | 280 | 21 | 23 | 6367 | 6367 | 6367 | 0.1516 | 2286 | 0.054429 | 7328 | 0.17448 | 1.477 | A02 | TEMF0.04028021/AS
Freestanding | Tempo Freestanding | TEMF.04030010/AS | 40 | 300 | 10 | 13 | 2889 | 2889 | 2889 | 0.068786 | 1101 | 0.026214 | 3299 | 0.078548 | 1.394 | A02 | TEMF0.04030010/AS
Freestanding | Tempo Freestanding | TEMF.04030011/AS | 40 | 300 | 11 | 13 | 3792 | 3792 | 3792 | 0.090286 | 1399 | 0.03331 | 4349 | 0.10355 | 1.439 | A02 | TEMF0.04030011/AS
Freestanding | Tempo Freestanding | TEMF.04030015/AS | 40 | 300 | 15 | 18 | 4704 | 4704 | 4704 | 0.112 | 1802 | 0.042905 | 5367 | 0.12779 | 1.385 | A02 | TEMF0.04030015/AS
Freestanding | Tempo Freestanding | TEMF.04030016/AS | 40 | 300 | 16 | 18 | 5100 | 5100 | 5100 | 0.12143 | 1851 | 0.044071 | 5860 | 0.13952 | 1.46 | A02 | TEMF0.04030016/AS
Freestanding | Tempo Freestanding | TEMF.04030020/AS | 40 | 300 | 20 | 23 | 6588 | 6588 | 6588 | 0.15686 | 2523 | 0.060071 | 7517 | 0.17898 | 1.384 | A02 | TEMF0.04030020/AS
Freestanding | Tempo Freestanding | TEMF.04030021/AS | 40 | 300 | 21 | 23 | 6822 | 6822 | 6822 | 0.16243 | 2449 | 0.05831 | 7852 | 0.18695 | 1.477 | A02 | TEMF0.04030021/AS
Freestanding | Tempo Freestanding | TEMF.05004010/AS | 50 | 40 | 10 | 13 | 430 | 430 | 430 | 0.010238 | 165 | 0.0039286 | 491 | 0.01169 | 1.385 | A02 | TEMF0.05004010/AS
Freestanding | Tempo Freestanding | TEMF.05004011/AS | 50 | 40 | 11 | 13 | 554 | 554 | 554 | 0.01319 | 204 | 0.0048571 | 635 | 0.015119 | 1.438 | A02 | TEMF0.05004011/AS
Freestanding | Tempo Freestanding | TEMF.05004015/AS | 50 | 40 | 15 | 18 | 694 | 694 | 694 | 0.016524 | 268 | 0.006381 | 791 | 0.018833 | 1.373 | A02 | TEMF0.05004015/AS
Freestanding | Tempo Freestanding | TEMF.05004016/AS | 50 | 40 | 16 | 18 | 759 | 759 | 759 | 0.018071 | 275 | 0.0065476 | 873 | 0.020786 | 1.464 | A02 | TEMF0.05004016/AS
Freestanding | Tempo Freestanding | TEMF.05004020/AS | 50 | 40 | 20 | 23 | 970 | 970 | 970 | 0.023095 | 374 | 0.0089048 | 1106 | 0.026333 | 1.373 | A02 | TEMF0.05004020/AS
Freestanding | Tempo Freestanding | TEMF.05004021/AS | 50 | 40 | 21 | 23 | 1033 | 1033 | 1033 | 0.024595 | 369 | 0.0087857 | 1190 | 0.028333 | 1.485 | A02 | TEMF0.05004021/AS
Freestanding | Tempo Freestanding | TEMF.05005010/AS | 50 | 50 | 10 | 13 | 538 | 538 | 538 | 0.01281 | 206 | 0.0049048 | 614 | 0.014619 | 1.385 | A02 | TEMF0.05005010/AS
Freestanding | Tempo Freestanding | TEMF.05005011/AS | 50 | 50 | 11 | 13 | 693 | 693 | 693 | 0.0165 | 256 | 0.0060952 | 795 | 0.018929 | 1.438 | A02 | TEMF0.05005011/AS
Freestanding | Tempo Freestanding | TEMF.05005015/AS | 50 | 50 | 15 | 18 | 867 | 867 | 867 | 0.020643 | 335 | 0.0079762 | 988 | 0.023524 | 1.373 | A02 | TEMF0.05005015/AS
Freestanding | Tempo Freestanding | TEMF.05005016/AS | 50 | 50 | 16 | 18 | 949 | 949 | 949 | 0.022595 | 344 | 0.0081905 | 1091 | 0.025976 | 1.464 | A02 | TEMF0.05005016/AS
Freestanding | Tempo Freestanding | TEMF.05005020/AS | 50 | 50 | 20 | 23 | 1213 | 1213 | 1213 | 0.028881 | 468 | 0.011143 | 1383 | 0.032929 | 1.373 | A02 | TEMF0.05005020/AS
Freestanding | Tempo Freestanding | TEMF.05005021/AS | 50 | 50 | 21 | 23 | 1291 | 1291 | 1291 | 0.030738 | 461 | 0.010976 | 1487 | 0.035405 | 1.485 | A02 | TEMF0.05005021/AS
Freestanding | Tempo Freestanding | TEMF.05006010/AS | 50 | 60 | 10 | 13 | 646 | 646 | 646 | 0.015381 | 247 | 0.005881 | 737 | 0.017548 | 1.385 | A02 | TEMF0.05006010/AS
Freestanding | Tempo Freestanding | TEMF.05006011/AS | 50 | 60 | 11 | 13 | 832 | 832 | 832 | 0.01981 | 307 | 0.0073095 | 954 | 0.022714 | 1.438 | A02 | TEMF0.05006011/AS
Freestanding | Tempo Freestanding | TEMF.05006015/AS | 50 | 60 | 15 | 18 | 1040 | 1040 | 1040 | 0.024762 | 401 | 0.0095476 | 1186 | 0.028238 | 1.373 | A02 | TEMF0.05006015/AS
Freestanding | Tempo Freestanding | TEMF.05006016/AS | 50 | 60 | 16 | 18 | 1139 | 1139 | 1139 | 0.027119 | 412 | 0.0098095 | 1310 | 0.03119 | 1.464 | A02 | TEMF0.05006016/AS
Freestanding | Tempo Freestanding | TEMF.05006020/AS | 50 | 60 | 20 | 23 | 1455 | 1455 | 1455 | 0.034643 | 562 | 0.013381 | 1659 | 0.0395 | 1.373 | A02 | TEMF0.05006020/AS
Freestanding | Tempo Freestanding | TEMF.05006021/AS | 50 | 60 | 21 | 23 | 1549 | 1549 | 1549 | 0.036881 | 553 | 0.013167 | 1784 | 0.042476 | 1.485 | A02 | TEMF0.05006021/AS
Freestanding | Tempo Freestanding | TEMF.05007010/AS | 50 | 70 | 10 | 13 | 753 | 753 | 753 | 0.017929 | 288 | 0.0068571 | 859 | 0.020452 | 1.385 | A02 | TEMF0.05007010/AS
Freestanding | Tempo Freestanding | TEMF.05007011/AS | 50 | 70 | 11 | 13 | 970 | 970 | 970 | 0.023095 | 358 | 0.0085238 | 1113 | 0.0265 | 1.438 | A02 | TEMF0.05007011/AS
Freestanding | Tempo Freestanding | TEMF.05007015/AS | 50 | 70 | 15 | 18 | 1214 | 1214 | 1214 | 0.028905 | 469 | 0.011167 | 1384 | 0.032952 | 1.373 | A02 | TEMF0.05007015/AS
Freestanding | Tempo Freestanding | TEMF.05007016/AS | 50 | 70 | 16 | 18 | 1329 | 1329 | 1329 | 0.031643 | 481 | 0.011452 | 1528 | 0.036381 | 1.464 | A02 | TEMF0.05007016/AS
Freestanding | Tempo Freestanding | TEMF.05007020/AS | 50 | 70 | 20 | 23 | 1698 | 1698 | 1698 | 0.040429 | 655 | 0.015595 | 1936 | 0.046095 | 1.373 | A02 | TEMF0.05007020/AS
Freestanding | Tempo Freestanding | TEMF.05007021/AS | 50 | 70 | 21 | 23 | 1807 | 1807 | 1807 | 0.043024 | 645 | 0.015357 | 2082 | 0.049571 | 1.485 | A02 | TEMF0.05007021/AS
Freestanding | Tempo Freestanding | TEMF.05008010/AS | 50 | 80 | 10 | 13 | 861 | 861 | 861 | 0.0205 | 330 | 0.0078571 | 982 | 0.023381 | 1.385 | A02 | TEMF0.05008010/AS
Freestanding | Tempo Freestanding | TEMF.05008011/AS | 50 | 80 | 11 | 13 | 1109 | 1109 | 1109 | 0.026405 | 409 | 0.0097381 | 1272 | 0.030286 | 1.438 | A02 | TEMF0.05008011/AS
Freestanding | Tempo Freestanding | TEMF.05008015/AS | 50 | 80 | 15 | 18 | 1387 | 1387 | 1387 | 0.033024 | 535 | 0.012738 | 1581 | 0.037643 | 1.373 | A02 | TEMF0.05008015/AS
Freestanding | Tempo Freestanding | TEMF.05008016/AS | 50 | 80 | 16 | 18 | 1518 | 1518 | 1518 | 0.036143 | 550 | 0.013095 | 1746 | 0.041571 | 1.464 | A02 | TEMF0.05008016/AS
Freestanding | Tempo Freestanding | TEMF.05008020/AS | 50 | 80 | 20 | 23 | 1940 | 1940 | 1940 | 0.04619 | 749 | 0.017833 | 2212 | 0.052667 | 1.373 | A02 | TEMF0.05008020/AS
Freestanding | Tempo Freestanding | TEMF.05008021/AS | 50 | 80 | 21 | 23 | 2066 | 2066 | 2066 | 0.04919 | 738 | 0.017571 | 2380 | 0.056667 | 1.485 | A02 | TEMF0.05008021/AS
Freestanding | Tempo Freestanding | TEMF.05009010/AS | 50 | 90 | 10 | 13 | 968 | 968 | 968 | 0.023048 | 371 | 0.0088333 | 1104 | 0.026286 | 1.385 | A02 | TEMF0.05009010/AS
Freestanding | Tempo Freestanding | TEMF.05009011/AS | 50 | 90 | 11 | 13 | 1247 | 1247 | 1247 | 0.02969 | 460 | 0.010952 | 1430 | 0.034048 | 1.438 | A02 | TEMF0.05009011/AS
Freestanding | Tempo Freestanding | TEMF.05009015/AS | 50 | 90 | 15 | 18 | 1561 | 1561 | 1561 | 0.037167 | 603 | 0.014357 | 1780 | 0.042381 | 1.373 | A02 | TEMF0.05009015/AS
Freestanding | Tempo Freestanding | TEMF.05009016/AS | 50 | 90 | 16 | 18 | 1708 | 1708 | 1708 | 0.040667 | 618 | 0.014714 | 1964 | 0.046762 | 1.464 | A02 | TEMF0.05009016/AS
Freestanding | Tempo Freestanding | TEMF.05009020/AS | 50 | 90 | 20 | 23 | 2183 | 2183 | 2183 | 0.051976 | 843 | 0.020071 | 2489 | 0.059262 | 1.373 | A02 | TEMF0.05009020/AS
Freestanding | Tempo Freestanding | TEMF.05009021/AS | 50 | 90 | 21 | 23 | 2324 | 2324 | 2324 | 0.055333 | 830 | 0.019762 | 2677 | 0.063738 | 1.485 | A02 | TEMF0.05009021/AS
Freestanding | Tempo Freestanding | TEMF.05010010/AS | 50 | 100 | 10 | 13 | 1076 | 1076 | 1076 | 0.025619 | 412 | 0.0098095 | 1228 | 0.029238 | 1.385 | A02 | TEMF0.05010010/AS
Freestanding | Tempo Freestanding | TEMF.05010011/AS | 50 | 100 | 11 | 13 | 1386 | 1386 | 1386 | 0.033 | 511 | 0.012167 | 1590 | 0.037857 | 1.438 | A02 | TEMF0.05010011/AS
Freestanding | Tempo Freestanding | TEMF.05010015/AS | 50 | 100 | 15 | 18 | 1734 | 1734 | 1734 | 0.041286 | 669 | 0.015929 | 1977 | 0.047071 | 1.373 | A02 | TEMF0.05010015/AS
Freestanding | Tempo Freestanding | TEMF.05010016/AS | 50 | 100 | 16 | 18 | 1898 | 1898 | 1898 | 0.04519 | 687 | 0.016357 | 2183 | 0.051976 | 1.464 | A02 | TEMF0.05010016/AS
Freestanding | Tempo Freestanding | TEMF.05010020/AS | 50 | 100 | 20 | 23 | 2425 | 2425 | 2425 | 0.057738 | 936 | 0.022286 | 2765 | 0.065833 | 1.373 | A02 | TEMF0.05010020/AS
Freestanding | Tempo Freestanding | TEMF.05010021/AS | 50 | 100 | 21 | 23 | 2582 | 2582 | 2582 | 0.061476 | 922 | 0.021952 | 2974 | 0.07081 | 1.485 | A02 | TEMF0.05010021/AS
Freestanding | Tempo Freestanding | TEMF.05011010/AS | 50 | 110 | 10 | 13 | 1184 | 1184 | 1184 | 0.02819 | 453 | 0.010786 | 1351 | 0.032167 | 1.385 | A02 | TEMF0.05011010/AS
Freestanding | Tempo Freestanding | TEMF.05011011/AS | 50 | 110 | 11 | 13 | 1525 | 1525 | 1525 | 0.03631 | 563 | 0.013405 | 1749 | 0.041643 | 1.438 | A02 | TEMF0.05011011/AS
Freestanding | Tempo Freestanding | TEMF.05011015/AS | 50 | 110 | 15 | 18 | 1907 | 1907 | 1907 | 0.045405 | 736 | 0.017524 | 2174 | 0.051762 | 1.373 | A02 | TEMF0.05011015/AS
Freestanding | Tempo Freestanding | TEMF.05011016/AS | 50 | 110 | 16 | 18 | 2088 | 2088 | 2088 | 0.049714 | 756 | 0.018 | 2401 | 0.057167 | 1.464 | A02 | TEMF0.05011016/AS
Freestanding | Tempo Freestanding | TEMF.05011020/AS | 50 | 110 | 20 | 23 | 2668 | 2668 | 2668 | 0.063524 | 1030 | 0.024524 | 3042 | 0.072429 | 1.373 | A02 | TEMF0.05011020/AS
Freestanding | Tempo Freestanding | TEMF.05011021/AS | 50 | 110 | 21 | 23 | 2840 | 2840 | 2840 | 0.067619 | 1014 | 0.024143 | 3272 | 0.077905 | 1.485 | A02 | TEMF0.05011021/AS
Freestanding | Tempo Freestanding | TEMF.05012010/AS | 50 | 120 | 10 | 13 | 1291 | 1291 | 1291 | 0.030738 | 494 | 0.011762 | 1473 | 0.035071 | 1.385 | A02 | TEMF0.05012010/AS
Freestanding | Tempo Freestanding | TEMF.05012011/AS | 50 | 120 | 11 | 13 | 1663 | 1663 | 1663 | 0.039595 | 614 | 0.014619 | 1907 | 0.045405 | 1.438 | A02 | TEMF0.05012011/AS
Freestanding | Tempo Freestanding | TEMF.05012015/AS | 50 | 120 | 15 | 18 | 2081 | 2081 | 2081 | 0.049548 | 803 | 0.019119 | 2372 | 0.056476 | 1.373 | A02 | TEMF0.05012015/AS
Freestanding | Tempo Freestanding | TEMF.05012016/AS | 50 | 120 | 16 | 18 | 2278 | 2278 | 2278 | 0.054238 | 825 | 0.019643 | 2620 | 0.062381 | 1.464 | A02 | TEMF0.05012016/AS
Freestanding | Tempo Freestanding | TEMF.05012020/AS | 50 | 120 | 20 | 23 | 2910 | 2910 | 2910 | 0.069286 | 1123 | 0.026738 | 3317 | 0.078976 | 1.373 | A02 | TEMF0.05012020/AS
Freestanding | Tempo Freestanding | TEMF.05012021/AS | 50 | 120 | 21 | 23 | 3098 | 3098 | 3098 | 0.073762 | 1106 | 0.026333 | 3569 | 0.084976 | 1.485 | A02 | TEMF0.05012021/AS
Freestanding | Tempo Freestanding | TEMF.05014010/AS | 50 | 140 | 10 | 13 | 1506 | 1506 | 1506 | 0.035857 | 577 | 0.013738 | 1718 | 0.040905 | 1.385 | A02 | TEMF0.05014010/AS
Freestanding | Tempo Freestanding | TEMF.05014011/AS | 50 | 140 | 11 | 13 | 1940 | 1940 | 1940 | 0.04619 | 716 | 0.017048 | 2225 | 0.052976 | 1.438 | A02 | TEMF0.05014011/AS
Freestanding | Tempo Freestanding | TEMF.05014015/AS | 50 | 140 | 15 | 18 | 2428 | 2428 | 2428 | 0.05781 | 937 | 0.02231 | 2768 | 0.065905 | 1.373 | A02 | TEMF0.05014015/AS
Freestanding | Tempo Freestanding | TEMF.05014016/AS | 50 | 140 | 16 | 18 | 2657 | 2657 | 2657 | 0.063262 | 962 | 0.022905 | 3056 | 0.072762 | 1.464 | A02 | TEMF0.05014016/AS
Freestanding | Tempo Freestanding | TEMF.05014020/AS | 50 | 140 | 20 | 23 | 3395 | 3395 | 3395 | 0.080833 | 1310 | 0.03119 | 3870 | 0.092143 | 1.373 | A02 | TEMF0.05014020/AS
Freestanding | Tempo Freestanding | TEMF.05014021/AS | 50 | 140 | 21 | 23 | 3615 | 3615 | 3615 | 0.086071 | 1291 | 0.030738 | 4164 | 0.099143 | 1.485 | A02 | TEMF0.05014021/AS
Freestanding | Tempo Freestanding | TEMF.05016010/AS | 50 | 160 | 10 | 13 | 1722 | 1722 | 1722 | 0.041 | 660 | 0.015714 | 1965 | 0.046786 | 1.385 | A02 | TEMF0.05016010/AS
Freestanding | Tempo Freestanding | TEMF.05016011/AS | 50 | 160 | 11 | 13 | 2218 | 2218 | 2218 | 0.05281 | 818 | 0.019476 | 2544 | 0.060571 | 1.438 | A02 | TEMF0.05016011/AS
Freestanding | Tempo Freestanding | TEMF.05016015/AS | 50 | 160 | 15 | 18 | 2774 | 2774 | 2774 | 0.066048 | 1071 | 0.0255 | 3162 | 0.075286 | 1.373 | A02 | TEMF0.05016015/AS
Freestanding | Tempo Freestanding | TEMF.05016016/AS | 50 | 160 | 16 | 18 | 3037 | 3037 | 3037 | 0.07231 | 1099 | 0.026167 | 3493 | 0.083167 | 1.464 | A02 | TEMF0.05016016/AS
Freestanding | Tempo Freestanding | TEMF.05016020/AS | 50 | 160 | 20 | 23 | 3880 | 3880 | 3880 | 0.092381 | 1498 | 0.035667 | 4423 | 0.10531 | 1.373 | A02 | TEMF0.05016020/AS
Freestanding | Tempo Freestanding | TEMF.05016021/AS | 50 | 160 | 21 | 23 | 4131 | 4131 | 4131 | 0.098357 | 1475 | 0.035119 | 4759 | 0.11331 | 1.485 | A02 | TEMF0.05016021/AS
Freestanding | Tempo Freestanding | TEMF.05018010/AS | 50 | 180 | 10 | 13 | 1937 | 1937 | 1937 | 0.046119 | 742 | 0.017667 | 2210 | 0.052619 | 1.385 | A02 | TEMF0.05018010/AS
Freestanding | Tempo Freestanding | TEMF.05018011/AS | 50 | 180 | 11 | 13 | 2495 | 2495 | 2495 | 0.059405 | 921 | 0.021929 | 2862 | 0.068143 | 1.438 | A02 | TEMF0.05018011/AS
Freestanding | Tempo Freestanding | TEMF.05018015/AS | 50 | 180 | 15 | 18 | 3121 | 3121 | 3121 | 0.07431 | 1205 | 0.02869 | 3558 | 0.084714 | 1.373 | A02 | TEMF0.05018015/AS
Freestanding | Tempo Freestanding | TEMF.05018016/AS | 50 | 180 | 16 | 18 | 3416 | 3416 | 3416 | 0.081333 | 1237 | 0.029452 | 3928 | 0.093524 | 1.464 | A02 | TEMF0.05018016/AS
Freestanding | Tempo Freestanding | TEMF.05018020/AS | 50 | 180 | 20 | 23 | 4365 | 4365 | 4365 | 0.10393 | 1685 | 0.040119 | 4976 | 0.11848 | 1.373 | A02 | TEMF0.05018020/AS
Freestanding | Tempo Freestanding | TEMF.05018021/AS | 50 | 180 | 21 | 23 | 4648 | 4648 | 4648 | 0.11067 | 1659 | 0.0395 | 5354 | 0.12748 | 1.485 | A02 | TEMF0.05018021/AS
Freestanding | Tempo Freestanding | TEMF.05020010/AS | 50 | 200 | 10 | 13 | 2152 | 2152 | 2152 | 0.051238 | 824 | 0.019619 | 2455 | 0.058452 | 1.385 | A02 | TEMF0.05020010/AS
Freestanding | Tempo Freestanding | TEMF.05020011/AS | 50 | 200 | 11 | 13 | 2772 | 2772 | 2772 | 0.066 | 1023 | 0.024357 | 3179 | 0.07569 | 1.438 | A02 | TEMF0.05020011/AS
Freestanding | Tempo Freestanding | TEMF.05020015/AS | 50 | 200 | 15 | 18 | 3468 | 3468 | 3468 | 0.082571 | 1339 | 0.031881 | 3954 | 0.094143 | 1.373 | A02 | TEMF0.05020015/AS
Freestanding | Tempo Freestanding | TEMF.05020016/AS | 50 | 200 | 16 | 18 | 3796 | 3796 | 3796 | 0.090381 | 1374 | 0.032714 | 4365 | 0.10393 | 1.464 | A02 | TEMF0.05020016/AS
Freestanding | Tempo Freestanding | TEMF.05020020/AS | 50 | 200 | 20 | 23 | 4850 | 4850 | 4850 | 0.11548 | 1872 | 0.044571 | 5529 | 0.13164 | 1.373 | A02 | TEMF0.05020020/AS
Freestanding | Tempo Freestanding | TEMF.05020021/AS | 50 | 200 | 21 | 23 | 5164 | 5164 | 5164 | 0.12295 | 1844 | 0.043905 | 5949 | 0.14164 | 1.485 | A02 | TEMF0.05020021/AS
Freestanding | Tempo Freestanding | TEMF.05022010/AS | 50 | 220 | 10 | 13 | 2367 | 2367 | 2367 | 0.056357 | 907 | 0.021595 | 2701 | 0.06431 | 1.385 | A02 | TEMF0.05022010/AS
Freestanding | Tempo Freestanding | TEMF.05022011/AS | 50 | 220 | 11 | 13 | 3049 | 3049 | 3049 | 0.072595 | 1125 | 0.026786 | 3497 | 0.083262 | 1.438 | A02 | TEMF0.05022011/AS
Freestanding | Tempo Freestanding | TEMF.05022015/AS | 50 | 220 | 15 | 18 | 3815 | 3815 | 3815 | 0.090833 | 1473 | 0.035071 | 4349 | 0.10355 | 1.373 | A02 | TEMF0.05022015/AS
Freestanding | Tempo Freestanding | TEMF.05022016/AS | 50 | 220 | 16 | 18 | 4176 | 4176 | 4176 | 0.099429 | 1512 | 0.036 | 4802 | 0.11433 | 1.464 | A02 | TEMF0.05022016/AS
Freestanding | Tempo Freestanding | TEMF.05022020/AS | 50 | 220 | 20 | 23 | 5335 | 5335 | 5335 | 0.12702 | 2059 | 0.049024 | 6082 | 0.14481 | 1.373 | A02 | TEMF0.05022020/AS
Freestanding | Tempo Freestanding | TEMF.05022021/AS | 50 | 220 | 21 | 23 | 5680 | 5680 | 5680 | 0.13524 | 2028 | 0.048286 | 6543 | 0.15579 | 1.485 | A02 | TEMF0.05022021/AS
Freestanding | Tempo Freestanding | TEMF.05024010/AS | 50 | 240 | 10 | 13 | 2582 | 2582 | 2582 | 0.061476 | 989 | 0.023548 | 2946 | 0.070143 | 1.385 | A02 | TEMF0.05024010/AS
Freestanding | Tempo Freestanding | TEMF.05024011/AS | 50 | 240 | 11 | 13 | 3326 | 3326 | 3326 | 0.07919 | 1227 | 0.029214 | 3815 | 0.090833 | 1.438 | A02 | TEMF0.05024011/AS
Freestanding | Tempo Freestanding | TEMF.05024015/AS | 50 | 240 | 15 | 18 | 4162 | 4162 | 4162 | 0.099095 | 1607 | 0.038262 | 4745 | 0.11298 | 1.373 | A02 | TEMF0.05024015/AS
Freestanding | Tempo Freestanding | TEMF.05024016/AS | 50 | 240 | 16 | 18 | 4555 | 4555 | 4555 | 0.10845 | 1649 | 0.039262 | 5238 | 0.12471 | 1.464 | A02 | TEMF0.05024016/AS
Freestanding | Tempo Freestanding | TEMF.05024020/AS | 50 | 240 | 20 | 23 | 5820 | 5820 | 5820 | 0.13857 | 2247 | 0.0535 | 6635 | 0.15798 | 1.373 | A02 | TEMF0.05024020/AS
Freestanding | Tempo Freestanding | TEMF.05024021/AS | 50 | 240 | 21 | 23 | 6197 | 6197 | 6197 | 0.14755 | 2212 | 0.052667 | 7139 | 0.16998 | 1.485 | A02 | TEMF0.05024021/AS
Freestanding | Tempo Freestanding | TEMF.05026010/AS | 50 | 260 | 10 | 13 | 2798 | 2798 | 2798 | 0.066619 | 1072 | 0.025524 | 3193 | 0.076024 | 1.385 | A02 | TEMF0.05026010/AS
Freestanding | Tempo Freestanding | TEMF.05026011/AS | 50 | 260 | 11 | 13 | 3604 | 3604 | 3604 | 0.08581 | 1330 | 0.031667 | 4134 | 0.098429 | 1.438 | A02 | TEMF0.05026011/AS
Freestanding | Tempo Freestanding | TEMF.05026015/AS | 50 | 260 | 15 | 18 | 4508 | 4508 | 4508 | 0.10733 | 1740 | 0.041429 | 5139 | 0.12236 | 1.373 | A02 | TEMF0.05026015/AS
Freestanding | Tempo Freestanding | TEMF.05026016/AS | 50 | 260 | 16 | 18 | 4935 | 4935 | 4935 | 0.1175 | 1786 | 0.042524 | 5675 | 0.13512 | 1.464 | A02 | TEMF0.05026016/AS
Freestanding | Tempo Freestanding | TEMF.05026020/AS | 50 | 260 | 20 | 23 | 6305 | 6305 | 6305 | 0.15012 | 2434 | 0.057952 | 7188 | 0.17114 | 1.373 | A02 | TEMF0.05026020/AS
Freestanding | Tempo Freestanding | TEMF.05026021/AS | 50 | 260 | 21 | 23 | 6713 | 6713 | 6713 | 0.15983 | 2397 | 0.057071 | 7733 | 0.18412 | 1.485 | A02 | TEMF0.05026021/AS
Freestanding | Tempo Freestanding | TEMF.05028010/AS | 50 | 280 | 10 | 13 | 3013 | 3013 | 3013 | 0.071738 | 1154 | 0.027476 | 3438 | 0.081857 | 1.385 | A02 | TEMF0.05028010/AS
Freestanding | Tempo Freestanding | TEMF.05028011/AS | 50 | 280 | 11 | 13 | 3881 | 3881 | 3881 | 0.092405 | 1432 | 0.034095 | 4452 | 0.106 | 1.438 | A02 | TEMF0.05028011/AS
Freestanding | Tempo Freestanding | TEMF.05028015/AS | 50 | 280 | 15 | 18 | 4855 | 4855 | 4855 | 0.1156 | 1874 | 0.044619 | 5535 | 0.13179 | 1.373 | A02 | TEMF0.05028015/AS
Freestanding | Tempo Freestanding | TEMF.05028016/AS | 50 | 280 | 16 | 18 | 5314 | 5314 | 5314 | 0.12652 | 1924 | 0.04581 | 6111 | 0.1455 | 1.464 | A02 | TEMF0.05028016/AS
Freestanding | Tempo Freestanding | TEMF.05028020/AS | 50 | 280 | 20 | 23 | 6790 | 6790 | 6790 | 0.16167 | 2621 | 0.062405 | 7741 | 0.18431 | 1.373 | A02 | TEMF0.05028020/AS
Freestanding | Tempo Freestanding | TEMF.05028021/AS | 50 | 280 | 21 | 23 | 7230 | 7230 | 7230 | 0.17214 | 2581 | 0.061452 | 8329 | 0.19831 | 1.485 | A02 | TEMF0.05028021/AS
Freestanding | Tempo Freestanding | TEMF.05030010/AS | 50 | 300 | 10 | 13 | 3228 | 3228 | 3228 | 0.076857 | 1236 | 0.029429 | 3683 | 0.08769 | 1.385 | A02 | TEMF0.05030010/AS
Freestanding | Tempo Freestanding | TEMF.05030011/AS | 50 | 300 | 11 | 13 | 4158 | 4158 | 4158 | 0.099 | 1534 | 0.036524 | 4769 | 0.11355 | 1.438 | A02 | TEMF0.05030011/AS
Freestanding | Tempo Freestanding | TEMF.05030015/AS | 50 | 300 | 15 | 18 | 5202 | 5202 | 5202 | 0.12386 | 2008 | 0.04781 | 5930 | 0.14119 | 1.373 | A02 | TEMF0.05030015/AS
Freestanding | Tempo Freestanding | TEMF.05030016/AS | 50 | 300 | 16 | 18 | 5694 | 5694 | 5694 | 0.13557 | 2061 | 0.049071 | 6548 | 0.1559 | 1.464 | A02 | TEMF0.05030016/AS
Freestanding | Tempo Freestanding | TEMF.05030020/AS | 50 | 300 | 20 | 23 | 7275 | 7275 | 7275 | 0.17321 | 2808 | 0.066857 | 8294 | 0.19748 | 1.373 | A02 | TEMF0.05030020/AS
Freestanding | Tempo Freestanding | TEMF.05030021/AS | 50 | 300 | 21 | 23 | 7746 | 7746 | 7746 | 0.18443 | 2765 | 0.065833 | 8923 | 0.21245 | 1.485 | A02 | TEMF0.05030021/AS
Horizontal Wall | Tempo Wall | TEMW.02004010 | 20 | 40 | 10 | 12 | 262 | 262 | 262 | 0.0062381 | 99 | 0.0023571 | 300 | 0.0071429 | 1.413 | A02 | TEMW0.02004010
Horizontal Wall | Tempo Wall | TEMW.02004015 | 20 | 40 | 15 | 17 | 436 | 436 | 436 | 0.010381 | 164 | 0.0039048 | 499 | 0.011881 | 1.408 | A02 | TEMW0.02004015
Horizontal Wall | Tempo Wall | TEMW.02004020 | 20 | 40 | 20 | 22 | 613 | 613 | 613 | 0.014595 | 231 | 0.0055 | 701 | 0.01669 | 1.408 | A02 | TEMW0.02004020
Horizontal Wall | Tempo Wall | TEMW.02005010 | 20 | 50 | 10 | 12 | 328 | 328 | 328 | 0.0078095 | 123 | 0.0029286 | 375 | 0.0089286 | 1.413 | A02 | TEMW0.02005010
Horizontal Wall | Tempo Wall | TEMW.02005015 | 20 | 50 | 15 | 17 | 545 | 545 | 545 | 0.012976 | 205 | 0.004881 | 623 | 0.014833 | 1.408 | A02 | TEMW0.02005015
Horizontal Wall | Tempo Wall | TEMW.02005020 | 20 | 50 | 20 | 22 | 766 | 766 | 766 | 0.018238 | 289 | 0.006881 | 876 | 0.020857 | 1.408 | A02 | TEMW0.02005020
Horizontal Wall | Tempo Wall | TEMW.02006010 | 20 | 60 | 10 | 12 | 393 | 393 | 393 | 0.0093571 | 148 | 0.0035238 | 450 | 0.010714 | 1.413 | A02 | TEMW0.02006010
Horizontal Wall | Tempo Wall | TEMW.02006015 | 20 | 60 | 15 | 17 | 654 | 654 | 654 | 0.015571 | 247 | 0.005881 | 748 | 0.01781 | 1.408 | A02 | TEMW0.02006015
Horizontal Wall | Tempo Wall | TEMW.02006020 | 20 | 60 | 20 | 22 | 919 | 919 | 919 | 0.021881 | 346 | 0.0082381 | 1051 | 0.025024 | 1.408 | A02 | TEMW0.02006020
Horizontal Wall | Tempo Wall | TEMW.02007010 | 20 | 70 | 10 | 12 | 459 | 459 | 459 | 0.010929 | 173 | 0.004119 | 525 | 0.0125 | 1.413 | A02 | TEMW0.02007010
Horizontal Wall | Tempo Wall | TEMW.02007015 | 20 | 70 | 15 | 17 | 763 | 763 | 763 | 0.018167 | 288 | 0.0068571 | 873 | 0.020786 | 1.408 | A02 | TEMW0.02007015
Horizontal Wall | Tempo Wall | TEMW.02007020 | 20 | 70 | 20 | 22 | 1072 | 1072 | 1072 | 0.025524 | 404 | 0.009619 | 1226 | 0.02919 | 1.408 | A02 | TEMW0.02007020
Horizontal Wall | Tempo Wall | TEMW.02008010 | 20 | 80 | 10 | 12 | 524 | 524 | 524 | 0.012476 | 197 | 0.0046905 | 599 | 0.014262 | 1.413 | A02 | TEMW0.02008010
Horizontal Wall | Tempo Wall | TEMW.02008015 | 20 | 80 | 15 | 17 | 872 | 872 | 872 | 0.020762 | 329 | 0.0078333 | 998 | 0.023762 | 1.408 | A02 | TEMW0.02008015
Horizontal Wall | Tempo Wall | TEMW.02008020 | 20 | 80 | 20 | 22 | 1226 | 1226 | 1226 | 0.02919 | 462 | 0.011 | 1403 | 0.033405 | 1.408 | A02 | TEMW0.02008020
Horizontal Wall | Tempo Wall | TEMW.02009010 | 20 | 90 | 10 | 12 | 590 | 590 | 590 | 0.014048 | 222 | 0.0052857 | 675 | 0.016071 | 1.413 | A02 | TEMW0.02009010
Horizontal Wall | Tempo Wall | TEMW.02009015 | 20 | 90 | 15 | 17 | 981 | 981 | 981 | 0.023357 | 370 | 0.0088095 | 1122 | 0.026714 | 1.408 | A02 | TEMW0.02009015
Horizontal Wall | Tempo Wall | TEMW.02009020 | 20 | 90 | 20 | 22 | 1379 | 1379 | 1379 | 0.032833 | 520 | 0.012381 | 1578 | 0.037571 | 1.408 | A02 | TEMW0.02009020
Horizontal Wall | Tempo Wall | TEMW.02010010 | 20 | 100 | 10 | 12 | 655 | 655 | 655 | 0.015595 | 246 | 0.0058571 | 749 | 0.017833 | 1.413 | A02 | TEMW0.02010010
Horizontal Wall | Tempo Wall | TEMW.02010015 | 20 | 100 | 15 | 17 | 1090 | 1090 | 1090 | 0.025952 | 411 | 0.0097857 | 1247 | 0.02969 | 1.408 | A02 | TEMW0.02010015
Horizontal Wall | Tempo Wall | TEMW.02010020 | 20 | 100 | 20 | 22 | 1532 | 1532 | 1532 | 0.036476 | 578 | 0.013762 | 1753 | 0.041738 | 1.408 | A02 | TEMW0.02010020
Horizontal Wall | Tempo Wall | TEMW.02011010 | 20 | 110 | 10 | 12 | 721 | 721 | 721 | 0.017167 | 271 | 0.0064524 | 825 | 0.019643 | 1.413 | A02 | TEMW0.02011010
Horizontal Wall | Tempo Wall | TEMW.02011015 | 20 | 110 | 15 | 17 | 1199 | 1199 | 1199 | 0.028548 | 452 | 0.010762 | 1372 | 0.032667 | 1.408 | A02 | TEMW0.02011015
Horizontal Wall | Tempo Wall | TEMW.02011020 | 20 | 110 | 20 | 22 | 1685 | 1685 | 1685 | 0.040119 | 635 | 0.015119 | 1928 | 0.045905 | 1.408 | A02 | TEMW0.02011020
Horizontal Wall | Tempo Wall | TEMW.02012010 | 20 | 120 | 10 | 12 | 786 | 786 | 786 | 0.018714 | 296 | 0.0070476 | 899 | 0.021405 | 1.413 | A02 | TEMW0.02012010
Horizontal Wall | Tempo Wall | TEMW.02012015 | 20 | 120 | 15 | 17 | 1308 | 1308 | 1308 | 0.031143 | 493 | 0.011738 | 1496 | 0.035619 | 1.408 | A02 | TEMW0.02012015
Horizontal Wall | Tempo Wall | TEMW.02012020 | 20 | 120 | 20 | 22 | 1838 | 1838 | 1838 | 0.043762 | 693 | 0.0165 | 2103 | 0.050071 | 1.408 | A02 | TEMW0.02012020
Horizontal Wall | Tempo Wall | TEMW.02014010 | 20 | 140 | 10 | 12 | 917 | 917 | 917 | 0.021833 | 345 | 0.0082143 | 1049 | 0.024976 | 1.413 | A02 | TEMW0.02014010
Horizontal Wall | Tempo Wall | TEMW.02014015 | 20 | 140 | 15 | 17 | 1526 | 1526 | 1526 | 0.036333 | 575 | 0.01369 | 1746 | 0.041571 | 1.408 | A02 | TEMW0.02014015
Horizontal Wall | Tempo Wall | TEMW.02014020 | 20 | 140 | 20 | 22 | 2145 | 2145 | 2145 | 0.051071 | 809 | 0.019262 | 2454 | 0.058429 | 1.408 | A02 | TEMW0.02014020
Horizontal Wall | Tempo Wall | TEMW.02016010 | 20 | 160 | 10 | 12 | 1048 | 1048 | 1048 | 0.024952 | 394 | 0.009381 | 1199 | 0.028548 | 1.413 | A02 | TEMW0.02016010
Horizontal Wall | Tempo Wall | TEMW.02016015 | 20 | 160 | 15 | 17 | 1744 | 1744 | 1744 | 0.041524 | 657 | 0.015643 | 1995 | 0.0475 | 1.408 | A02 | TEMW0.02016015
Horizontal Wall | Tempo Wall | TEMW.02016020 | 20 | 160 | 20 | 22 | 2451 | 2451 | 2451 | 0.058357 | 924 | 0.022 | 2804 | 0.066762 | 1.408 | A02 | TEMW0.02016020
Horizontal Wall | Tempo Wall | TEMW.02018010 | 20 | 180 | 10 | 12 | 1179 | 1179 | 1179 | 0.028071 | 443 | 0.010548 | 1349 | 0.032119 | 1.413 | A02 | TEMW0.02018010
Horizontal Wall | Tempo Wall | TEMW.02018015 | 20 | 180 | 15 | 17 | 1962 | 1962 | 1962 | 0.046714 | 740 | 0.017619 | 2245 | 0.053452 | 1.408 | A02 | TEMW0.02018015
Horizontal Wall | Tempo Wall | TEMW.02018020 | 20 | 180 | 20 | 22 | 2758 | 2758 | 2758 | 0.065667 | 1040 | 0.024762 | 3155 | 0.075119 | 1.408 | A02 | TEMW0.02018020
Horizontal Wall | Tempo Wall | TEMW.02020010 | 20 | 200 | 10 | 12 | 1310 | 1310 | 1310 | 0.03119 | 493 | 0.011738 | 1499 | 0.03569 | 1.413 | A02 | TEMW0.02020010
Horizontal Wall | Tempo Wall | TEMW.02020015 | 20 | 200 | 15 | 17 | 2180 | 2180 | 2180 | 0.051905 | 822 | 0.019571 | 2494 | 0.059381 | 1.408 | A02 | TEMW0.02020015
Horizontal Wall | Tempo Wall | TEMW.02020020 | 20 | 200 | 20 | 22 | 3064 | 3064 | 3064 | 0.072952 | 1155 | 0.0275 | 3505 | 0.083452 | 1.408 | A02 | TEMW0.02020020
Horizontal Wall | Tempo Wall | TEMW.02022010 | 20 | 220 | 10 | 12 | 1441 | 1441 | 1441 | 0.03431 | 542 | 0.012905 | 1649 | 0.039262 | 1.413 | A02 | TEMW0.02022010
Horizontal Wall | Tempo Wall | TEMW.02022015 | 20 | 220 | 15 | 17 | 2398 | 2398 | 2398 | 0.057095 | 904 | 0.021524 | 2743 | 0.06531 | 1.408 | A02 | TEMW0.02022015
Horizontal Wall | Tempo Wall | TEMW.02022020 | 20 | 220 | 20 | 22 | 3370 | 3370 | 3370 | 0.080238 | 1270 | 0.030238 | 3855 | 0.091786 | 1.408 | A02 | TEMW0.02022020
Horizontal Wall | Tempo Wall | TEMW.02024010 | 20 | 240 | 10 | 12 | 1572 | 1572 | 1572 | 0.037429 | 591 | 0.014071 | 1798 | 0.04281 | 1.413 | A02 | TEMW0.02024010
Horizontal Wall | Tempo Wall | TEMW.02024015 | 20 | 240 | 15 | 17 | 2616 | 2616 | 2616 | 0.062286 | 986 | 0.023476 | 2993 | 0.071262 | 1.408 | A02 | TEMW0.02024015
Horizontal Wall | Tempo Wall | TEMW.02024020 | 20 | 240 | 20 | 22 | 3677 | 3677 | 3677 | 0.087548 | 1386 | 0.033 | 4206 | 0.10014 | 1.408 | A02 | TEMW0.02024020
Horizontal Wall | Tempo Wall | TEMW.02026010 | 20 | 260 | 10 | 12 | 1703 | 1703 | 1703 | 0.040548 | 640 | 0.015238 | 1948 | 0.046381 | 1.413 | A02 | TEMW0.02026010
Horizontal Wall | Tempo Wall | TEMW.02026015 | 20 | 260 | 15 | 17 | 2834 | 2834 | 2834 | 0.067476 | 1068 | 0.025429 | 3242 | 0.07719 | 1.408 | A02 | TEMW0.02026015
Horizontal Wall | Tempo Wall | TEMW.02026020 | 20 | 260 | 20 | 22 | 3983 | 3983 | 3983 | 0.094833 | 1502 | 0.035762 | 4557 | 0.1085 | 1.408 | A02 | TEMW0.02026020
Horizontal Wall | Tempo Wall | TEMW.02028010 | 20 | 280 | 10 | 12 | 1834 | 1834 | 1834 | 0.043667 | 690 | 0.016429 | 2098 | 0.049952 | 1.413 | A02 | TEMW0.02028010
Horizontal Wall | Tempo Wall | TEMW.02028015 | 20 | 280 | 15 | 17 | 3052 | 3052 | 3052 | 0.072667 | 1151 | 0.027405 | 3491 | 0.083119 | 1.408 | A02 | TEMW0.02028015
Horizontal Wall | Tempo Wall | TEMW.02028020 | 20 | 280 | 20 | 22 | 4290 | 4290 | 4290 | 0.10214 | 1617 | 0.0385 | 4908 | 0.11686 | 1.408 | A02 | TEMW0.02028020
Horizontal Wall | Tempo Wall | TEMW.02030010 | 20 | 300 | 10 | 12 | 1965 | 1965 | 1965 | 0.046786 | 739 | 0.017595 | 2248 | 0.053524 | 1.413 | A02 | TEMW0.02030010
Horizontal Wall | Tempo Wall | TEMW.02030015 | 20 | 300 | 15 | 17 | 3270 | 3270 | 3270 | 0.077857 | 1233 | 0.029357 | 3741 | 0.089071 | 1.408 | A02 | TEMW0.02030015
Horizontal Wall | Tempo Wall | TEMW.02030020 | 20 | 300 | 20 | 22 | 4596 | 4596 | 4596 | 0.10943 | 1733 | 0.041262 | 5258 | 0.12519 | 1.408 | A02 | TEMW0.02030020
Horizontal Wall | Tempo Wall | TEMW.03004010 | 30 | 40 | 10 | 12 | 330 | 330 | 330 | 0.0078571 | 125 | 0.0029762 | 377 | 0.0089762 | 1.403 | A02 | TEMW0.03004010
Horizontal Wall | Tempo Wall | TEMW.03004011 | 30 | 40 | 11 | 12 | 448 | 448 | 448 | 0.010667 | 165 | 0.0039286 | 514 | 0.012238 | 1.44 | A02 | TEMW0.03004011
Horizontal Wall | Tempo Wall | TEMW.03004015 | 30 | 40 | 15 | 17 | 544 | 544 | 544 | 0.012952 | 207 | 0.0049286 | 621 | 0.014786 | 1.396 | A02 | TEMW0.03004015
Horizontal Wall | Tempo Wall | TEMW.03004016 | 30 | 40 | 16 | 17 | 592 | 592 | 592 | 0.014095 | 216 | 0.0051429 | 680 | 0.01619 | 1.456 | A02 | TEMW0.03004016
Horizontal Wall | Tempo Wall | TEMW.03004020 | 30 | 40 | 20 | 22 | 762 | 762 | 762 | 0.018143 | 290 | 0.0069048 | 870 | 0.020714 | 1.396 | A02 | TEMW0.03004020
Horizontal Wall | Tempo Wall | TEMW.03004021 | 30 | 40 | 21 | 22 | 779 | 779 | 779 | 0.018548 | 281 | 0.0066905 | 896 | 0.021333 | 1.468 | A02 | TEMW0.03004021
Horizontal Wall | Tempo Wall | TEMW.03005010 | 30 | 50 | 10 | 12 | 413 | 413 | 413 | 0.0098333 | 156 | 0.0037143 | 472 | 0.011238 | 1.403 | A02 | TEMW0.03005010
Horizontal Wall | Tempo Wall | TEMW.03005011 | 30 | 50 | 11 | 12 | 561 | 561 | 561 | 0.013357 | 207 | 0.0049286 | 643 | 0.01531 | 1.44 | A02 | TEMW0.03005011
Horizontal Wall | Tempo Wall | TEMW.03005015 | 30 | 50 | 15 | 17 | 680 | 680 | 680 | 0.01619 | 258 | 0.0061429 | 777 | 0.0185 | 1.396 | A02 | TEMW0.03005015
Horizontal Wall | Tempo Wall | TEMW.03005016 | 30 | 50 | 16 | 17 | 740 | 740 | 740 | 0.017619 | 270 | 0.0064286 | 850 | 0.020238 | 1.456 | A02 | TEMW0.03005016
Horizontal Wall | Tempo Wall | TEMW.03005020 | 30 | 50 | 20 | 22 | 953 | 953 | 953 | 0.02269 | 362 | 0.008619 | 1088 | 0.025905 | 1.396 | A02 | TEMW0.03005020
Horizontal Wall | Tempo Wall | TEMW.03005021 | 30 | 50 | 21 | 22 | 974 | 974 | 974 | 0.02319 | 352 | 0.008381 | 1120 | 0.026667 | 1.468 | A02 | TEMW0.03005021
Horizontal Wall | Tempo Wall | TEMW.03006010 | 30 | 60 | 10 | 12 | 496 | 496 | 496 | 0.01181 | 187 | 0.0044524 | 567 | 0.0135 | 1.403 | A02 | TEMW0.03006010
Horizontal Wall | Tempo Wall | TEMW.03006011 | 30 | 60 | 11 | 12 | 673 | 673 | 673 | 0.016024 | 248 | 0.0059048 | 772 | 0.018381 | 1.44 | A02 | TEMW0.03006011
Horizontal Wall | Tempo Wall | TEMW.03006011/DBE | 30 | 60 | 11 | 12 | 973 | 973 | 973 | 0.023167 | 487 | 0.011595 | 1070 | 0.025476 | 1 | A02 | TEMW0.03006011/DBE
Horizontal Wall | Tempo Wall | TEMW.03006015 | 30 | 60 | 15 | 17 | 815 | 815 | 815 | 0.019405 | 310 | 0.007381 | 931 | 0.022167 | 1.396 | A02 | TEMW0.03006015
Horizontal Wall | Tempo Wall | TEMW.03006016 | 30 | 60 | 16 | 17 | 888 | 888 | 888 | 0.021143 | 324 | 0.0077143 | 1020 | 0.024286 | 1.456 | A02 | TEMW0.03006016
Horizontal Wall | Tempo Wall | TEMW.03006016/DBE | 30 | 60 | 16 | 17 | 1368 | 1368 | 1368 | 0.032571 | 684 | 0.016286 | 1505 | 0.035833 | 1 | A02 | TEMW0.03006016/DBE
Horizontal Wall | Tempo Wall | TEMW.03006020 | 30 | 60 | 20 | 22 | 1144 | 1144 | 1144 | 0.027238 | 435 | 0.010357 | 1306 | 0.031095 | 1.396 | A02 | TEMW0.03006020
Horizontal Wall | Tempo Wall | TEMW.03006021 | 30 | 60 | 21 | 22 | 1169 | 1169 | 1169 | 0.027833 | 422 | 0.010048 | 1344 | 0.032 | 1.468 | A02 | TEMW0.03006021
Horizontal Wall | Tempo Wall | TEMW.03006021/DBE | 30 | 60 | 21 | 22 | 1649 | 1649 | 1649 | 0.039262 | 825 | 0.019643 | 1814 | 0.04319 | 1 | A02 | TEMW0.03006021/DBE
Horizontal Wall | Tempo Wall | TEMW.03007010 | 30 | 70 | 10 | 12 | 578 | 578 | 578 | 0.013762 | 218 | 0.0051905 | 661 | 0.015738 | 1.403 | A02 | TEMW0.03007010
Horizontal Wall | Tempo Wall | TEMW.03007011 | 30 | 70 | 11 | 12 | 785 | 785 | 785 | 0.01869 | 290 | 0.0069048 | 900 | 0.021429 | 1.44 | A02 | TEMW0.03007011
Horizontal Wall | Tempo Wall | TEMW.03007011/DBE | 30 | 70 | 11 | 12 | 1085 | 1085 | 1085 | 0.025833 | 543 | 0.012929 | 1194 | 0.028429 | 1 | A02 | TEMW0.03007011/DBE
Horizontal Wall | Tempo Wall | TEMW.03007015 | 30 | 70 | 15 | 17 | 951 | 951 | 951 | 0.022643 | 361 | 0.0085952 | 1086 | 0.025857 | 1.396 | A02 | TEMW0.03007015
Horizontal Wall | Tempo Wall | TEMW.03007016 | 30 | 70 | 16 | 17 | 1036 | 1036 | 1036 | 0.024667 | 378 | 0.009 | 1190 | 0.028333 | 1.456 | A02 | TEMW0.03007016
Horizontal Wall | Tempo Wall | TEMW.03007016/DBE | 30 | 70 | 16 | 17 | 1516 | 1516 | 1516 | 0.036095 | 758 | 0.018048 | 1668 | 0.039714 | 1 | A02 | TEMW0.03007016/DBE
Horizontal Wall | Tempo Wall | TEMW.03007020 | 30 | 70 | 20 | 22 | 1334 | 1334 | 1334 | 0.031762 | 507 | 0.012071 | 1523 | 0.036262 | 1.396 | A02 | TEMW0.03007020
Horizontal Wall | Tempo Wall | TEMW.03007021 | 30 | 70 | 21 | 22 | 1364 | 1364 | 1364 | 0.032476 | 492 | 0.011714 | 1569 | 0.037357 | 1.468 | A02 | TEMW0.03007021
Horizontal Wall | Tempo Wall | TEMW.03007021/DBE | 30 | 70 | 21 | 22 | 1844 | 1844 | 1844 | 0.043905 | 922 | 0.021952 | 2028 | 0.048286 | 1 | A02 | TEMW0.03007021/DBE
Horizontal Wall | Tempo Wall | TEMW.03008010 | 30 | 80 | 10 | 12 | 661 | 661 | 661 | 0.015738 | 250 | 0.0059524 | 756 | 0.018 | 1.403 | A02 | TEMW0.03008010
Horizontal Wall | Tempo Wall | TEMW.03008011 | 30 | 80 | 11 | 12 | 897 | 897 | 897 | 0.021357 | 331 | 0.007881 | 1029 | 0.0245 | 1.44 | A02 | TEMW0.03008011
Horizontal Wall | Tempo Wall | TEMW.03008011/DBE | 30 | 80 | 11 | 12 | 1197 | 1197 | 1197 | 0.0285 | 599 | 0.014262 | 1317 | 0.031357 | 1 | A02 | TEMW0.03008011/DBE
Horizontal Wall | Tempo Wall | TEMW.03008015 | 30 | 80 | 15 | 17 | 1087 | 1087 | 1087 | 0.025881 | 413 | 0.0098333 | 1241 | 0.029548 | 1.396 | A02 | TEMW0.03008015
Horizontal Wall | Tempo Wall | TEMW.03008016 | 30 | 80 | 16 | 17 | 1184 | 1184 | 1184 | 0.02819 | 432 | 0.010286 | 1360 | 0.032381 | 1.456 | A02 | TEMW0.03008016
Horizontal Wall | Tempo Wall | TEMW.03008016/DBE | 30 | 80 | 16 | 17 | 1664 | 1664 | 1664 | 0.039619 | 832 | 0.01981 | 1830 | 0.043571 | 1 | A02 | TEMW0.03008016/DBE
Horizontal Wall | Tempo Wall | TEMW.03008020 | 30 | 80 | 20 | 22 | 1525 | 1525 | 1525 | 0.03631 | 580 | 0.01381 | 1742 | 0.041476 | 1.396 | A02 | TEMW0.03008020
Horizontal Wall | Tempo Wall | TEMW.03008021 | 30 | 80 | 21 | 22 | 1558 | 1558 | 1558 | 0.037095 | 562 | 0.013381 | 1792 | 0.042667 | 1.468 | A02 | TEMW0.03008021
Horizontal Wall | Tempo Wall | TEMW.03008021/DBE | 30 | 80 | 21 | 22 | 2038 | 2038 | 2038 | 0.048524 | 1019 | 0.024262 | 2242 | 0.053381 | 1 | A02 | TEMW0.03008021/DBE
Horizontal Wall | Tempo Wall | TEMW.03009010 | 30 | 90 | 10 | 12 | 743 | 743 | 743 | 0.01769 | 281 | 0.0066905 | 849 | 0.020214 | 1.403 | A02 | TEMW0.03009010
Horizontal Wall | Tempo Wall | TEMW.03009011 | 30 | 90 | 11 | 12 | 1009 | 1009 | 1009 | 0.024024 | 372 | 0.0088571 | 1157 | 0.027548 | 1.44 | A02 | TEMW0.03009011
Horizontal Wall | Tempo Wall | TEMW.03009011/DBE | 30 | 90 | 11 | 12 | 1609 | 1609 | 1609 | 0.03831 | 805 | 0.019167 | 1770 | 0.042143 | 1 | A02 | TEMW0.03009011/DBE
Horizontal Wall | Tempo Wall | TEMW.03009015 | 30 | 90 | 15 | 17 | 1223 | 1223 | 1223 | 0.029119 | 465 | 0.011071 | 1397 | 0.033262 | 1.396 | A02 | TEMW0.03009015
Horizontal Wall | Tempo Wall | TEMW.03009016 | 30 | 90 | 16 | 17 | 1332 | 1332 | 1332 | 0.031714 | 486 | 0.011571 | 1530 | 0.036429 | 1.456 | A02 | TEMW0.03009016
Horizontal Wall | Tempo Wall | TEMW.03009016/DBE | 30 | 90 | 16 | 17 | 2292 | 2292 | 2292 | 0.054571 | 1146 | 0.027286 | 2521 | 0.060024 | 1 | A02 | TEMW0.03009016/DBE
Horizontal Wall | Tempo Wall | TEMW.03009020 | 30 | 90 | 20 | 22 | 1715 | 1715 | 1715 | 0.040833 | 652 | 0.015524 | 1959 | 0.046643 | 1.396 | A02 | TEMW0.03009020
Horizontal Wall | Tempo Wall | TEMW.03009021 | 30 | 90 | 21 | 22 | 1753 | 1753 | 1753 | 0.041738 | 633 | 0.015071 | 2016 | 0.048 | 1.468 | A02 | TEMW0.03009021
Horizontal Wall | Tempo Wall | TEMW.03009021/DBE | 30 | 90 | 21 | 22 | 2713 | 2713 | 2713 | 0.064595 | 1357 | 0.03231 | 2984 | 0.071048 | 1 | A02 | TEMW0.03009021/DBE
Horizontal Wall | Tempo Wall | TEMW.03010010 | 30 | 100 | 10 | 12 | 826 | 826 | 826 | 0.019667 | 312 | 0.0074286 | 944 | 0.022476 | 1.403 | A02 | TEMW0.03010010
Horizontal Wall | Tempo Wall | TEMW.03010011 | 30 | 100 | 11 | 12 | 1121 | 1121 | 1121 | 0.02669 | 414 | 0.0098571 | 1286 | 0.030619 | 1.44 | A02 | TEMW0.03010011
Horizontal Wall | Tempo Wall | TEMW.03010011/DBE | 30 | 100 | 11 | 12 | 1721 | 1721 | 1721 | 0.040976 | 861 | 0.0205 | 1893 | 0.045071 | 1 | A02 | TEMW0.03010011/DBE
Horizontal Wall | Tempo Wall | TEMW.03010015 | 30 | 100 | 15 | 17 | 1359 | 1359 | 1359 | 0.032357 | 516 | 0.012286 | 1552 | 0.036952 | 1.396 | A02 | TEMW0.03010015
Horizontal Wall | Tempo Wall | TEMW.03010016 | 30 | 100 | 16 | 17 | 1480 | 1480 | 1480 | 0.035238 | 540 | 0.012857 | 1701 | 0.0405 | 1.456 | A02 | TEMW0.03010016
Horizontal Wall | Tempo Wall | TEMW.03010016/DBE | 30 | 100 | 16 | 17 | 2440 | 2440 | 2440 | 0.058095 | 1220 | 0.029048 | 2684 | 0.063905 | 1 | A02 | TEMW0.03010016/DBE
Horizontal Wall | Tempo Wall | TEMW.03010020 | 30 | 100 | 20 | 22 | 1906 | 1906 | 1906 | 0.045381 | 724 | 0.017238 | 2177 | 0.051833 | 1.396 | A02 | TEMW0.03010020
Horizontal Wall | Tempo Wall | TEMW.03010021 | 30 | 100 | 21 | 22 | 1948 | 1948 | 1948 | 0.046381 | 703 | 0.016738 | 2240 | 0.053333 | 1.468 | A02 | TEMW0.03010021
Horizontal Wall | Tempo Wall | TEMW.03010021/DBE | 30 | 100 | 21 | 22 | 2908 | 2908 | 2908 | 0.069238 | 1454 | 0.034619 | 3199 | 0.076167 | 1 | A02 | TEMW0.03010021/DBE
Horizontal Wall | Tempo Wall | TEMW.03011010 | 30 | 110 | 10 | 12 | 909 | 909 | 909 | 0.021643 | 344 | 0.0081905 | 1039 | 0.024738 | 1.403 | A02 | TEMW0.03011010
Horizontal Wall | Tempo Wall | TEMW.03011011 | 30 | 110 | 11 | 12 | 1233 | 1233 | 1233 | 0.029357 | 455 | 0.010833 | 1414 | 0.033667 | 1.44 | A02 | TEMW0.03011011
Horizontal Wall | Tempo Wall | TEMW.03011011/DBE | 30 | 110 | 11 | 12 | 1833 | 1833 | 1833 | 0.043643 | 917 | 0.021833 | 2016 | 0.048 | 1 | A02 | TEMW0.03011011/DBE
Horizontal Wall | Tempo Wall | TEMW.03011015 | 30 | 110 | 15 | 17 | 1495 | 1495 | 1495 | 0.035595 | 568 | 0.013524 | 1707 | 0.040643 | 1.396 | A02 | TEMW0.03011015
Horizontal Wall | Tempo Wall | TEMW.03011016 | 30 | 110 | 16 | 17 | 1628 | 1628 | 1628 | 0.038762 | 594 | 0.014143 | 1871 | 0.044548 | 1.456 | A02 | TEMW0.03011016
Horizontal Wall | Tempo Wall | TEMW.03011016/DBE | 30 | 110 | 16 | 17 | 2588 | 2588 | 2588 | 0.061619 | 1294 | 0.03081 | 2847 | 0.067786 | 1 | A02 | TEMW0.03011016/DBE
Horizontal Wall | Tempo Wall | TEMW.03011020 | 30 | 110 | 20 | 22 | 2097 | 2097 | 2097 | 0.049929 | 797 | 0.018976 | 2395 | 0.057024 | 1.396 | A02 | TEMW0.03011020
Horizontal Wall | Tempo Wall | TEMW.03011021 | 30 | 110 | 21 | 22 | 2143 | 2143 | 2143 | 0.051024 | 774 | 0.018429 | 2464 | 0.058667 | 1.468 | A02 | TEMW0.03011021
Horizontal Wall | Tempo Wall | TEMW.03011021/DBE | 30 | 110 | 21 | 22 | 3103 | 3103 | 3103 | 0.073881 | 1552 | 0.036952 | 3413 | 0.081262 | 1 | A02 | TEMW0.03011021/DBE
Horizontal Wall | Tempo Wall | TEMW.03012010 | 30 | 120 | 10 | 12 | 991 | 991 | 991 | 0.023595 | 375 | 0.0089286 | 1133 | 0.026976 | 1.403 | A02 | TEMW0.03012010
Horizontal Wall | Tempo Wall | TEMW.03012011 | 30 | 120 | 11 | 12 | 1345 | 1345 | 1345 | 0.032024 | 496 | 0.01181 | 1543 | 0.036738 | 1.44 | A02 | TEMW0.03012011
Horizontal Wall | Tempo Wall | TEMW.03012011/DBE | 30 | 120 | 11 | 12 | 1945 | 1945 | 1945 | 0.04631 | 973 | 0.023167 | 2140 | 0.050952 | 1 | A02 | TEMW0.03012011/DBE
Horizontal Wall | Tempo Wall | TEMW.03012015 | 30 | 120 | 15 | 17 | 1631 | 1631 | 1631 | 0.038833 | 620 | 0.014762 | 1863 | 0.044357 | 1.396 | A02 | TEMW0.03012015
Horizontal Wall | Tempo Wall | TEMW.03012016 | 30 | 120 | 16 | 17 | 1776 | 1776 | 1776 | 0.042286 | 648 | 0.015429 | 2041 | 0.048595 | 1.456 | A02 | TEMW0.03012016
Horizontal Wall | Tempo Wall | TEMW.03012016/DBE | 30 | 120 | 16 | 17 | 2736 | 2736 | 2736 | 0.065143 | 1368 | 0.032571 | 3010 | 0.071667 | 1 | A02 | TEMW0.03012016/DBE
Horizontal Wall | Tempo Wall | TEMW.03012020 | 30 | 120 | 20 | 22 | 2287 | 2287 | 2287 | 0.054452 | 869 | 0.02069 | 2612 | 0.06219 | 1.396 | A02 | TEMW0.03012020
Horizontal Wall | Tempo Wall | TEMW.03012021 | 30 | 120 | 21 | 22 | 2338 | 2338 | 2338 | 0.055667 | 844 | 0.020095 | 2689 | 0.064024 | 1.468 | A02 | TEMW0.03012021
Horizontal Wall | Tempo Wall | TEMW.03012021/DBE | 30 | 120 | 21 | 22 | 3298 | 3298 | 3298 | 0.078524 | 1649 | 0.039262 | 3628 | 0.086381 | 1 | A02 | TEMW0.03012021/DBE
Horizontal Wall | Tempo Wall | TEMW.03014010 | 30 | 140 | 10 | 12 | 1156 | 1156 | 1156 | 0.027524 | 437 | 0.010405 | 1321 | 0.031452 | 1.403 | A02 | TEMW0.03014010
Horizontal Wall | Tempo Wall | TEMW.03014011 | 30 | 140 | 11 | 12 | 1569 | 1569 | 1569 | 0.037357 | 579 | 0.013786 | 1800 | 0.042857 | 1.44 | A02 | TEMW0.03014011
Horizontal Wall | Tempo Wall | TEMW.03014011/DBE | 30 | 140 | 11 | 12 | 2169 | 2169 | 2169 | 0.051643 | 1085 | 0.025833 | 2386 | 0.05681 | 1 | A02 | TEMW0.03014011/DBE
Horizontal Wall | Tempo Wall | TEMW.03014015 | 30 | 140 | 15 | 17 | 1903 | 1903 | 1903 | 0.04531 | 723 | 0.017214 | 2173 | 0.051738 | 1.396 | A02 | TEMW0.03014015
Horizontal Wall | Tempo Wall | TEMW.03014016 | 30 | 140 | 16 | 17 | 2072 | 2072 | 2072 | 0.049333 | 756 | 0.018 | 2381 | 0.05669 | 1.456 | A02 | TEMW0.03014016
Horizontal Wall | Tempo Wall | TEMW.03014016/DBE | 30 | 140 | 16 | 17 | 3032 | 3032 | 3032 | 0.07219 | 1516 | 0.036095 | 3335 | 0.079405 | 1 | A02 | TEMW0.03014016/DBE
Horizontal Wall | Tempo Wall | TEMW.03014020 | 30 | 140 | 20 | 22 | 2668 | 2668 | 2668 | 0.063524 | 1014 | 0.024143 | 3047 | 0.072548 | 1.396 | A02 | TEMW0.03014020
Horizontal Wall | Tempo Wall | TEMW.03014021 | 30 | 140 | 21 | 22 | 2727 | 2727 | 2727 | 0.064929 | 984 | 0.023429 | 3136 | 0.074667 | 1.468 | A02 | TEMW0.03014021
Horizontal Wall | Tempo Wall | TEMW.03014021/DBE | 30 | 140 | 21 | 22 | 3687 | 3687 | 3687 | 0.087786 | 1844 | 0.043905 | 4056 | 0.096571 | 1 | A02 | TEMW0.03014021/DBE
Horizontal Wall | Tempo Wall | TEMW.03016010 | 30 | 160 | 10 | 12 | 1322 | 1322 | 1322 | 0.031476 | 500 | 0.011905 | 1511 | 0.035976 | 1.403 | A02 | TEMW0.03016010
Horizontal Wall | Tempo Wall | TEMW.03016011 | 30 | 160 | 11 | 12 | 1794 | 1794 | 1794 | 0.042714 | 662 | 0.015762 | 2058 | 0.049 | 1.44 | A02 | TEMW0.03016011
Horizontal Wall | Tempo Wall | TEMW.03016011/DBE | 30 | 160 | 11 | 12 | 2994 | 2994 | 2994 | 0.071286 | 1497 | 0.035643 | 3293 | 0.078405 | 1 | A02 | TEMW0.03016011/DBE
Horizontal Wall | Tempo Wall | TEMW.03016015 | 30 | 160 | 15 | 17 | 2174 | 2174 | 2174 | 0.051762 | 826 | 0.019667 | 2483 | 0.059119 | 1.396 | A02 | TEMW0.03016015
Horizontal Wall | Tempo Wall | TEMW.03016016 | 30 | 160 | 16 | 17 | 2368 | 2368 | 2368 | 0.056381 | 864 | 0.020571 | 2721 | 0.064786 | 1.456 | A02 | TEMW0.03016016
Horizontal Wall | Tempo Wall | TEMW.03016016/DBE | 30 | 160 | 16 | 17 | 4288 | 4288 | 4288 | 0.1021 | 2144 | 0.051048 | 4717 | 0.11231 | 1 | A02 | TEMW0.03016016/DBE
Horizontal Wall | Tempo Wall | TEMW.03016020 | 30 | 160 | 20 | 22 | 3050 | 3050 | 3050 | 0.072619 | 1159 | 0.027595 | 3483 | 0.082929 | 1.396 | A02 | TEMW0.03016020
Horizontal Wall | Tempo Wall | TEMW.03016021 | 30 | 160 | 21 | 22 | 3117 | 3117 | 3117 | 0.074214 | 1125 | 0.026786 | 3585 | 0.085357 | 1.468 | A02 | TEMW0.03016021
Horizontal Wall | Tempo Wall | TEMW.03016021/DBE | 30 | 160 | 21 | 22 | 5037 | 5037 | 5037 | 0.11993 | 2519 | 0.059976 | 5541 | 0.13193 | 1 | A02 | TEMW0.03016021/DBE
Horizontal Wall | Tempo Wall | TEMW.03018010 | 30 | 180 | 10 | 12 | 1487 | 1487 | 1487 | 0.035405 | 562 | 0.013381 | 1700 | 0.040476 | 1.403 | A02 | TEMW0.03018010
Horizontal Wall | Tempo Wall | TEMW.03018011 | 30 | 180 | 11 | 12 | 2018 | 2018 | 2018 | 0.048048 | 745 | 0.017738 | 2315 | 0.055119 | 1.44 | A02 | TEMW0.03018011
Horizontal Wall | Tempo Wall | TEMW.03018011/DBE | 30 | 180 | 11 | 12 | 3218 | 3218 | 3218 | 0.076619 | 1609 | 0.03831 | 3540 | 0.084286 | 1 | A02 | TEMW0.03018011/DBE
Horizontal Wall | Tempo Wall | TEMW.03018015 | 30 | 180 | 15 | 17 | 2446 | 2446 | 2446 | 0.058238 | 929 | 0.022119 | 2793 | 0.0665 | 1.396 | A02 | TEMW0.03018015
Horizontal Wall | Tempo Wall | TEMW.03018016 | 30 | 180 | 16 | 17 | 2664 | 2664 | 2664 | 0.063429 | 972 | 0.023143 | 3061 | 0.072881 | 1.456 | A02 | TEMW0.03018016
Horizontal Wall | Tempo Wall | TEMW.03018016/DBE | 30 | 180 | 16 | 17 | 4584 | 4584 | 4584 | 0.10914 | 2292 | 0.054571 | 5042 | 0.12005 | 1 | A02 | TEMW0.03018016/DBE
Horizontal Wall | Tempo Wall | TEMW.03018020 | 30 | 180 | 20 | 22 | 3431 | 3431 | 3431 | 0.08169 | 1304 | 0.031048 | 3918 | 0.093286 | 1.396 | A02 | TEMW0.03018020
Horizontal Wall | Tempo Wall | TEMW.03018021 | 30 | 180 | 21 | 22 | 3506 | 3506 | 3506 | 0.083476 | 1266 | 0.030143 | 4032 | 0.096 | 1.468 | A02 | TEMW0.03018021
Horizontal Wall | Tempo Wall | TEMW.03018021/DBE | 30 | 180 | 21 | 22 | 5426 | 5426 | 5426 | 0.12919 | 2713 | 0.064595 | 5969 | 0.14212 | 1 | A02 | TEMW0.03018021/DBE
Horizontal Wall | Tempo Wall | TEMW.03020010 | 30 | 200 | 10 | 12 | 1652 | 1652 | 1652 | 0.039333 | 624 | 0.014857 | 1888 | 0.044952 | 1.403 | A02 | TEMW0.03020010
Horizontal Wall | Tempo Wall | TEMW.03020011 | 30 | 200 | 11 | 12 | 2242 | 2242 | 2242 | 0.053381 | 827 | 0.01969 | 2572 | 0.061238 | 1.44 | A02 | TEMW0.03020011
Horizontal Wall | Tempo Wall | TEMW.03020011/DBE | 30 | 200 | 11 | 12 | 3442 | 3442 | 3442 | 0.081952 | 1721 | 0.040976 | 3786 | 0.090143 | 1 | A02 | TEMW0.03020011/DBE
Horizontal Wall | Tempo Wall | TEMW.03020015 | 30 | 200 | 15 | 17 | 2718 | 2718 | 2718 | 0.064714 | 1033 | 0.024595 | 3104 | 0.073905 | 1.396 | A02 | TEMW0.03020015
Horizontal Wall | Tempo Wall | TEMW.03020016 | 30 | 200 | 16 | 17 | 2960 | 2960 | 2960 | 0.070476 | 1080 | 0.025714 | 3401 | 0.080976 | 1.456 | A02 | TEMW0.03020016
Horizontal Wall | Tempo Wall | TEMW.03020016/DBE | 30 | 200 | 16 | 17 | 4880 | 4880 | 4880 | 0.11619 | 2440 | 0.058095 | 5368 | 0.12781 | 1 | A02 | TEMW0.03020016/DBE
Horizontal Wall | Tempo Wall | TEMW.03020020 | 30 | 200 | 20 | 22 | 3812 | 3812 | 3812 | 0.090762 | 1449 | 0.0345 | 4353 | 0.10364 | 1.396 | A02 | TEMW0.03020020
Horizontal Wall | Tempo Wall | TEMW.03020021 | 30 | 200 | 21 | 22 | 3896 | 3896 | 3896 | 0.092762 | 1406 | 0.033476 | 4480 | 0.10667 | 1.468 | A02 | TEMW0.03020021
Horizontal Wall | Tempo Wall | TEMW.03020021/DBE | 30 | 200 | 21 | 22 | 5816 | 5816 | 5816 | 0.13848 | 2908 | 0.069238 | 6398 | 0.15233 | 1 | A02 | TEMW0.03020021/DBE
Horizontal Wall | Tempo Wall | TEMW.03022010 | 30 | 220 | 10 | 12 | 1817 | 1817 | 1817 | 0.043262 | 687 | 0.016357 | 2077 | 0.049452 | 1.403 | A02 | TEMW0.03022010
Horizontal Wall | Tempo Wall | TEMW.03022011 | 30 | 220 | 11 | 12 | 2466 | 2466 | 2466 | 0.058714 | 910 | 0.021667 | 2829 | 0.067357 | 1.44 | A02 | TEMW0.03022011
Horizontal Wall | Tempo Wall | TEMW.03022011/DBE | 30 | 220 | 11 | 12 | 3666 | 3666 | 3666 | 0.087286 | 1833 | 0.043643 | 4033 | 0.096024 | 1 | A02 | TEMW0.03022011/DBE
Horizontal Wall | Tempo Wall | TEMW.03022015 | 30 | 220 | 15 | 17 | 2990 | 2990 | 2990 | 0.07119 | 1136 | 0.027048 | 3415 | 0.08131 | 1.396 | A02 | TEMW0.03022015
Horizontal Wall | Tempo Wall | TEMW.03022016 | 30 | 220 | 16 | 17 | 3256 | 3256 | 3256 | 0.077524 | 1188 | 0.028286 | 3741 | 0.089071 | 1.456 | A02 | TEMW0.03022016
Horizontal Wall | Tempo Wall | TEMW.03022016/DBE | 30 | 220 | 16 | 17 | 5176 | 5176 | 5176 | 0.12324 | 2588 | 0.061619 | 5694 | 0.13557 | 1 | A02 | TEMW0.03022016/DBE
Horizontal Wall | Tempo Wall | TEMW.03022020 | 30 | 220 | 20 | 22 | 4193 | 4193 | 4193 | 0.099833 | 1593 | 0.037929 | 4788 | 0.114 | 1.396 | A02 | TEMW0.03022020
Horizontal Wall | Tempo Wall | TEMW.03022021 | 30 | 220 | 21 | 22 | 4286 | 4286 | 4286 | 0.10205 | 1547 | 0.036833 | 4929 | 0.11736 | 1.468 | A02 | TEMW0.03022021
Horizontal Wall | Tempo Wall | TEMW.03022021/DBE | 30 | 220 | 21 | 22 | 6206 | 6206 | 6206 | 0.14776 | 3103 | 0.073881 | 6827 | 0.16255 | 1 | A02 | TEMW0.03022021/DBE
Horizontal Wall | Tempo Wall | TEMW.03024010 | 30 | 240 | 10 | 12 | 1982 | 1982 | 1982 | 0.04719 | 749 | 0.017833 | 2265 | 0.053929 | 1.403 | A02 | TEMW0.03024010
Horizontal Wall | Tempo Wall | TEMW.03024011 | 30 | 240 | 11 | 12 | 2690 | 2690 | 2690 | 0.064048 | 993 | 0.023643 | 3085 | 0.073452 | 1.44 | A02 | TEMW0.03024011
Horizontal Wall | Tempo Wall | TEMW.03024011/DBE | 30 | 240 | 11 | 12 | 4490 | 4490 | 4490 | 0.1069 | 2245 | 0.053452 | 4939 | 0.1176 | 1 | A02 | TEMW0.03024011/DBE
Horizontal Wall | Tempo Wall | TEMW.03024015 | 30 | 240 | 15 | 17 | 3262 | 3262 | 3262 | 0.077667 | 1240 | 0.029524 | 3725 | 0.08869 | 1.396 | A02 | TEMW0.03024015
Horizontal Wall | Tempo Wall | TEMW.03024016 | 30 | 240 | 16 | 17 | 3552 | 3552 | 3552 | 0.084571 | 1296 | 0.030857 | 4081 | 0.097167 | 1.456 | A02 | TEMW0.03024016
Horizontal Wall | Tempo Wall | TEMW.03024016/DBE | 30 | 240 | 16 | 17 | 6432 | 6432 | 6432 | 0.15314 | 3216 | 0.076571 | 7075 | 0.16845 | 1 | A02 | TEMW0.03024016/DBE
Horizontal Wall | Tempo Wall | TEMW.03024020 | 30 | 240 | 20 | 22 | 4574 | 4574 | 4574 | 0.1089 | 1738 | 0.041381 | 5224 | 0.12438 | 1.396 | A02 | TEMW0.03024020
Horizontal Wall | Tempo Wall | TEMW.03024021 | 30 | 240 | 21 | 22 | 4675 | 4675 | 4675 | 0.11131 | 1688 | 0.04019 | 5376 | 0.128 | 1.468 | A02 | TEMW0.03024021
Horizontal Wall | Tempo Wall | TEMW.03024021/DBE | 30 | 240 | 21 | 22 | 7555 | 7555 | 7555 | 0.17988 | 3778 | 0.089952 | 8311 | 0.19788 | 1 | A02 | TEMW0.03024021/DBE
Horizontal Wall | Tempo Wall | TEMW.03026010 | 30 | 260 | 10 | 12 | 2148 | 2148 | 2148 | 0.051143 | 812 | 0.019333 | 2455 | 0.058452 | 1.403 | A02 | TEMW0.03026010
Horizontal Wall | Tempo Wall | TEMW.03026011 | 30 | 260 | 11 | 12 | 2915 | 2915 | 2915 | 0.069405 | 1076 | 0.025619 | 3344 | 0.079619 | 1.44 | A02 | TEMW0.03026011
Horizontal Wall | Tempo Wall | TEMW.03026011/DBE | 30 | 260 | 11 | 12 | 4715 | 4715 | 4715 | 0.11226 | 2358 | 0.056143 | 5187 | 0.1235 | 1 | A02 | TEMW0.03026011/DBE
Horizontal Wall | Tempo Wall | TEMW.03026015 | 30 | 260 | 15 | 17 | 3533 | 3533 | 3533 | 0.084119 | 1343 | 0.031976 | 4035 | 0.096071 | 1.396 | A02 | TEMW0.03026015
Horizontal Wall | Tempo Wall | TEMW.03026016 | 30 | 260 | 16 | 17 | 3848 | 3848 | 3848 | 0.091619 | 1405 | 0.033452 | 4421 | 0.10526 | 1.456 | A02 | TEMW0.03026016
Horizontal Wall | Tempo Wall | TEMW.03026016/DBE | 30 | 260 | 16 | 17 | 6728 | 6728 | 6728 | 0.16019 | 3364 | 0.080095 | 7401 | 0.17621 | 1 | A02 | TEMW0.03026016/DBE
Horizontal Wall | Tempo Wall | TEMW.03026020 | 30 | 260 | 20 | 22 | 4956 | 4956 | 4956 | 0.118 | 1883 | 0.044833 | 5660 | 0.13476 | 1.396 | A02 | TEMW0.03026020
Horizontal Wall | Tempo Wall | TEMW.03026021 | 30 | 260 | 21 | 22 | 5065 | 5065 | 5065 | 0.1206 | 1828 | 0.043524 | 5825 | 0.13869 | 1.468 | A02 | TEMW0.03026021
Horizontal Wall | Tempo Wall | TEMW.03026021/DBE | 30 | 260 | 21 | 22 | 7945 | 7945 | 7945 | 0.18917 | 3973 | 0.094595 | 8740 | 0.2081 | 1 | A02 | TEMW0.03026021/DBE
Horizontal Wall | Tempo Wall | TEMW.03028010 | 30 | 280 | 10 | 12 | 2313 | 2313 | 2313 | 0.055071 | 874 | 0.02081 | 2644 | 0.062952 | 1.403 | A02 | TEMW0.03028010
Horizontal Wall | Tempo Wall | TEMW.03028011 | 30 | 280 | 11 | 12 | 3139 | 3139 | 3139 | 0.074738 | 1158 | 0.027571 | 3600 | 0.085714 | 1.44 | A02 | TEMW0.03028011
Horizontal Wall | Tempo Wall | TEMW.03028011/DBE | 30 | 280 | 11 | 12 | 4939 | 4939 | 4939 | 0.1176 | 2470 | 0.05881 | 5433 | 0.12936 | 1 | A02 | TEMW0.03028011/DBE
Horizontal Wall | Tempo Wall | TEMW.03028015 | 30 | 280 | 15 | 17 | 3805 | 3805 | 3805 | 0.090595 | 1446 | 0.034429 | 4345 | 0.10345 | 1.396 | A02 | TEMW0.03028015
Horizontal Wall | Tempo Wall | TEMW.03028016 | 30 | 280 | 16 | 17 | 4144 | 4144 | 4144 | 0.098667 | 1513 | 0.036024 | 4761 | 0.11336 | 1.456 | A02 | TEMW0.03028016
Horizontal Wall | Tempo Wall | TEMW.03028016/DBE | 30 | 280 | 16 | 17 | 7024 | 7024 | 7024 | 0.16724 | 3512 | 0.083619 | 7726 | 0.18395 | 1 | A02 | TEMW0.03028016/DBE
Horizontal Wall | Tempo Wall | TEMW.03028020 | 30 | 280 | 20 | 22 | 5337 | 5337 | 5337 | 0.12707 | 2028 | 0.048286 | 6095 | 0.14512 | 1.396 | A02 | TEMW0.03028020
Horizontal Wall | Tempo Wall | TEMW.03028021 | 30 | 280 | 21 | 22 | 5454 | 5454 | 5454 | 0.12986 | 1969 | 0.046881 | 6272 | 0.14933 | 1.468 | A02 | TEMW0.03028021
Horizontal Wall | Tempo Wall | TEMW.03028021/DBE | 30 | 280 | 21 | 22 | 8334 | 8334 | 8334 | 0.19843 | 4167 | 0.099214 | 9167 | 0.21826 | 1 | A02 | TEMW0.03028021/DBE
Horizontal Wall | Tempo Wall | TEMW.03030010 | 30 | 300 | 10 | 12 | 2478 | 2478 | 2478 | 0.059 | 937 | 0.02231 | 2832 | 0.067429 | 1.403 | A02 | TEMW0.03030010
Horizontal Wall | Tempo Wall | TEMW.03030011 | 30 | 300 | 11 | 12 | 3363 | 3363 | 3363 | 0.080071 | 1241 | 0.029548 | 3857 | 0.091833 | 1.44 | A02 | TEMW0.03030011
Horizontal Wall | Tempo Wall | TEMW.03030011/DBE | 30 | 300 | 11 | 12 | 5163 | 5163 | 5163 | 0.12293 | 2582 | 0.061476 | 5679 | 0.13521 | 1 | A02 | TEMW0.03030011/DBE
Horizontal Wall | Tempo Wall | TEMW.03030015 | 30 | 300 | 15 | 17 | 4077 | 4077 | 4077 | 0.097071 | 1549 | 0.036881 | 4656 | 0.11086 | 1.396 | A02 | TEMW0.03030015
Horizontal Wall | Tempo Wall | TEMW.03030016 | 30 | 300 | 16 | 17 | 4440 | 4440 | 4440 | 0.10571 | 1621 | 0.038595 | 5102 | 0.12148 | 1.456 | A02 | TEMW0.03030016
Horizontal Wall | Tempo Wall | TEMW.03030016/DBE | 30 | 300 | 16 | 17 | 7320 | 7320 | 7320 | 0.17429 | 3660 | 0.087143 | 8052 | 0.19171 | 1 | A02 | TEMW0.03030016/DBE
Horizontal Wall | Tempo Wall | TEMW.03030020 | 30 | 300 | 20 | 22 | 5718 | 5718 | 5718 | 0.13614 | 2173 | 0.051738 | 6530 | 0.15548 | 1.396 | A02 | TEMW0.03030020
Horizontal Wall | Tempo Wall | TEMW.03030021 | 30 | 300 | 21 | 22 | 5844 | 5844 | 5844 | 0.13914 | 2110 | 0.050238 | 6721 | 0.16002 | 1.468 | A02 | TEMW0.03030021
Horizontal Wall | Tempo Wall | TEMW.03030021/DBE | 30 | 300 | 21 | 22 | 8724 | 8724 | 8724 | 0.20771 | 4362 | 0.10386 | 9596 | 0.22848 | 1 | A02 | TEMW0.03030021/DBE
Horizontal Wall | Tempo Wall | TEMW.04004010 | 40 | 40 | 10 | 12 | 385 | 385 | 385 | 0.0091667 | 147 | 0.0035 | 440 | 0.010476 | 1.394 | A02 | TEMW0.04004010
Horizontal Wall | Tempo Wall | TEMW.04004011 | 40 | 40 | 11 | 12 | 506 | 506 | 506 | 0.012048 | 187 | 0.0044524 | 580 | 0.01381 | 1.439 | A02 | TEMW0.04004011
Horizontal Wall | Tempo Wall | TEMW.04004015 | 40 | 40 | 15 | 17 | 627 | 627 | 627 | 0.014929 | 240 | 0.0057143 | 715 | 0.017024 | 1.385 | A02 | TEMW0.04004015
Horizontal Wall | Tempo Wall | TEMW.04004016 | 40 | 40 | 16 | 17 | 680 | 680 | 680 | 0.01619 | 247 | 0.005881 | 781 | 0.018595 | 1.46 | A02 | TEMW0.04004016
Horizontal Wall | Tempo Wall | TEMW.04004020 | 40 | 40 | 20 | 22 | 878 | 878 | 878 | 0.020905 | 336 | 0.008 | 1002 | 0.023857 | 1.384 | A02 | TEMW0.04004020
Horizontal Wall | Tempo Wall | TEMW.04004021 | 40 | 40 | 21 | 22 | 910 | 910 | 910 | 0.021667 | 327 | 0.0077857 | 1047 | 0.024929 | 1.477 | A02 | TEMW0.04004021
Horizontal Wall | Tempo Wall | TEMW.04005010 | 40 | 50 | 10 | 12 | 482 | 482 | 482 | 0.011476 | 184 | 0.004381 | 550 | 0.013095 | 1.394 | A02 | TEMW0.04005010
Horizontal Wall | Tempo Wall | TEMW.04005011 | 40 | 50 | 11 | 12 | 632 | 632 | 632 | 0.015048 | 233 | 0.0055476 | 725 | 0.017262 | 1.439 | A02 | TEMW0.04005011
Horizontal Wall | Tempo Wall | TEMW.04005015 | 40 | 50 | 15 | 17 | 784 | 784 | 784 | 0.018667 | 300 | 0.0071429 | 895 | 0.02131 | 1.385 | A02 | TEMW0.04005015
Horizontal Wall | Tempo Wall | TEMW.04005016 | 40 | 50 | 16 | 17 | 850 | 850 | 850 | 0.020238 | 309 | 0.0073571 | 977 | 0.023262 | 1.46 | A02 | TEMW0.04005016
Horizontal Wall | Tempo Wall | TEMW.04005020 | 40 | 50 | 20 | 22 | 1098 | 1098 | 1098 | 0.026143 | 421 | 0.010024 | 1253 | 0.029833 | 1.384 | A02 | TEMW0.04005020
Horizontal Wall | Tempo Wall | TEMW.04005021 | 40 | 50 | 21 | 22 | 1137 | 1137 | 1137 | 0.027071 | 408 | 0.0097143 | 1309 | 0.031167 | 1.477 | A02 | TEMW0.04005021
Horizontal Wall | Tempo Wall | TEMW.04006010 | 40 | 60 | 10 | 12 | 578 | 578 | 578 | 0.013762 | 220 | 0.0052381 | 660 | 0.015714 | 1.394 | A02 | TEMW0.04006010
Horizontal Wall | Tempo Wall | TEMW.04006011 | 40 | 60 | 11 | 12 | 758 | 758 | 758 | 0.018048 | 280 | 0.0066667 | 869 | 0.02069 | 1.439 | A02 | TEMW0.04006011
Horizontal Wall | Tempo Wall | TEMW.04006011/DBE | 40 | 60 | 11 | 12 | 1058 | 1058 | 1058 | 0.02519 | 529 | 0.012595 | 1164 | 0.027714 | 1 | A02 | TEMW0.04006011/DBE
Horizontal Wall | Tempo Wall | TEMW.04006015 | 40 | 60 | 15 | 17 | 941 | 941 | 941 | 0.022405 | 360 | 0.0085714 | 1074 | 0.025571 | 1.385 | A02 | TEMW0.04006015
Horizontal Wall | Tempo Wall | TEMW.04006016 | 40 | 60 | 16 | 17 | 1020 | 1020 | 1020 | 0.024286 | 370 | 0.0088095 | 1172 | 0.027905 | 1.46 | A02 | TEMW0.04006016
Horizontal Wall | Tempo Wall | TEMW.04006016/DBE | 40 | 60 | 16 | 17 | 1500 | 1500 | 1500 | 0.035714 | 750 | 0.017857 | 1650 | 0.039286 | 1 | A02 | TEMW0.04006016/DBE
Horizontal Wall | Tempo Wall | TEMW.04006020 | 40 | 60 | 20 | 22 | 1318 | 1318 | 1318 | 0.031381 | 505 | 0.012024 | 1504 | 0.03581 | 1.384 | A02 | TEMW0.04006020
Horizontal Wall | Tempo Wall | TEMW.04006021 | 40 | 60 | 21 | 22 | 1364 | 1364 | 1364 | 0.032476 | 490 | 0.011667 | 1570 | 0.037381 | 1.477 | A02 | TEMW0.04006021
Horizontal Wall | Tempo Wall | TEMW.04006021/DBE | 40 | 60 | 21 | 22 | 1844 | 1844 | 1844 | 0.043905 | 922 | 0.021952 | 2028 | 0.048286 | 1 | A02 | TEMW0.04006021/DBE
Horizontal Wall | Tempo Wall | TEMW.04007010 | 40 | 70 | 10 | 12 | 674 | 674 | 674 | 0.016048 | 257 | 0.006119 | 770 | 0.018333 | 1.394 | A02 | TEMW0.04007010
Horizontal Wall | Tempo Wall | TEMW.04007011 | 40 | 70 | 11 | 12 | 885 | 885 | 885 | 0.021071 | 327 | 0.0077857 | 1015 | 0.024167 | 1.439 | A02 | TEMW0.04007011
Horizontal Wall | Tempo Wall | TEMW.04007011/DBE | 40 | 70 | 11 | 12 | 1185 | 1185 | 1185 | 0.028214 | 593 | 0.014119 | 1304 | 0.031048 | 1 | A02 | TEMW0.04007011/DBE
Horizontal Wall | Tempo Wall | TEMW.04007015 | 40 | 70 | 15 | 17 | 1098 | 1098 | 1098 | 0.026143 | 421 | 0.010024 | 1253 | 0.029833 | 1.385 | A02 | TEMW0.04007015
Horizontal Wall | Tempo Wall | TEMW.04007016 | 40 | 70 | 16 | 17 | 1190 | 1190 | 1190 | 0.028333 | 432 | 0.010286 | 1367 | 0.032548 | 1.46 | A02 | TEMW0.04007016
Horizontal Wall | Tempo Wall | TEMW.04007016/DBE | 40 | 70 | 16 | 17 | 1670 | 1670 | 1670 | 0.039762 | 835 | 0.019881 | 1837 | 0.043738 | 1 | A02 | TEMW0.04007016/DBE
Horizontal Wall | Tempo Wall | TEMW.04007020 | 40 | 70 | 20 | 22 | 1537 | 1537 | 1537 | 0.036595 | 589 | 0.014024 | 1754 | 0.041762 | 1.384 | A02 | TEMW0.04007020
Horizontal Wall | Tempo Wall | TEMW.04007021 | 40 | 70 | 21 | 22 | 1592 | 1592 | 1592 | 0.037905 | 572 | 0.013619 | 1832 | 0.043619 | 1.477 | A02 | TEMW0.04007021
Horizontal Wall | Tempo Wall | TEMW.04007021/DBE | 40 | 70 | 21 | 22 | 2072 | 2072 | 2072 | 0.049333 | 1036 | 0.024667 | 2279 | 0.054262 | 1 | A02 | TEMW0.04007021/DBE
Horizontal Wall | Tempo Wall | TEMW.04008010 | 40 | 80 | 10 | 12 | 770 | 770 | 770 | 0.018333 | 293 | 0.0069762 | 879 | 0.020929 | 1.394 | A02 | TEMW0.04008010
Horizontal Wall | Tempo Wall | TEMW.04008011 | 40 | 80 | 11 | 12 | 1011 | 1011 | 1011 | 0.024071 | 373 | 0.008881 | 1160 | 0.027619 | 1.439 | A02 | TEMW0.04008011
Horizontal Wall | Tempo Wall | TEMW.04008011/DBE | 40 | 80 | 11 | 12 | 1311 | 1311 | 1311 | 0.031214 | 656 | 0.015619 | 1442 | 0.034333 | 1 | A02 | TEMW0.04008011/DBE
Horizontal Wall | Tempo Wall | TEMW.04008015 | 40 | 80 | 15 | 17 | 1254 | 1254 | 1254 | 0.029857 | 480 | 0.011429 | 1431 | 0.034071 | 1.385 | A02 | TEMW0.04008015
Horizontal Wall | Tempo Wall | TEMW.04008016 | 40 | 80 | 16 | 17 | 1360 | 1360 | 1360 | 0.032381 | 494 | 0.011762 | 1563 | 0.037214 | 1.46 | A02 | TEMW0.04008016
Horizontal Wall | Tempo Wall | TEMW.04008016/DBE | 40 | 80 | 16 | 17 | 1840 | 1840 | 1840 | 0.04381 | 920 | 0.021905 | 2024 | 0.04819 | 1 | A02 | TEMW0.04008016/DBE
Horizontal Wall | Tempo Wall | TEMW.04008020 | 40 | 80 | 20 | 22 | 1757 | 1757 | 1757 | 0.041833 | 673 | 0.016024 | 2005 | 0.047738 | 1.384 | A02 | TEMW0.04008020
Horizontal Wall | Tempo Wall | TEMW.04008021 | 40 | 80 | 21 | 22 | 1819 | 1819 | 1819 | 0.04331 | 653 | 0.015548 | 2094 | 0.049857 | 1.477 | A02 | TEMW0.04008021
Horizontal Wall | Tempo Wall | TEMW.04008021/DBE | 40 | 80 | 21 | 22 | 2299 | 2299 | 2299 | 0.054738 | 1150 | 0.027381 | 2529 | 0.060214 | 1 | A02 | TEMW0.04008021/DBE
Horizontal Wall | Tempo Wall | TEMW.04009010 | 40 | 90 | 10 | 12 | 867 | 867 | 867 | 0.020643 | 330 | 0.0078571 | 990 | 0.023571 | 1.394 | A02 | TEMW0.04009010
Horizontal Wall | Tempo Wall | TEMW.04009011 | 40 | 90 | 11 | 12 | 1138 | 1138 | 1138 | 0.027095 | 420 | 0.01 | 1305 | 0.031071 | 1.439 | A02 | TEMW0.04009011
Horizontal Wall | Tempo Wall | TEMW.04009011/DBE | 40 | 90 | 11 | 12 | 1738 | 1738 | 1738 | 0.041381 | 869 | 0.02069 | 1912 | 0.045524 | 1 | A02 | TEMW0.04009011/DBE
Horizontal Wall | Tempo Wall | TEMW.04009015 | 40 | 90 | 15 | 17 | 1411 | 1411 | 1411 | 0.033595 | 540 | 0.012857 | 1610 | 0.038333 | 1.385 | A02 | TEMW0.04009015
Horizontal Wall | Tempo Wall | TEMW.04009016 | 40 | 90 | 16 | 17 | 1530 | 1530 | 1530 | 0.036429 | 555 | 0.013214 | 1758 | 0.041857 | 1.46 | A02 | TEMW0.04009016
Horizontal Wall | Tempo Wall | TEMW.04009016/DBE | 40 | 90 | 16 | 17 | 2490 | 2490 | 2490 | 0.059286 | 1245 | 0.029643 | 2739 | 0.065214 | 1 | A02 | TEMW0.04009016/DBE
Horizontal Wall | Tempo Wall | TEMW.04009020 | 40 | 90 | 20 | 22 | 1976 | 1976 | 1976 | 0.047048 | 757 | 0.018024 | 2255 | 0.05369 | 1.384 | A02 | TEMW0.04009020
Horizontal Wall | Tempo Wall | TEMW.04009021 | 40 | 90 | 21 | 22 | 2047 | 2047 | 2047 | 0.048738 | 735 | 0.0175 | 2356 | 0.056095 | 1.477 | A02 | TEMW0.04009021
Horizontal Wall | Tempo Wall | TEMW.04009021/DBE | 40 | 90 | 21 | 22 | 3007 | 3007 | 3007 | 0.071595 | 1504 | 0.03581 | 3308 | 0.078762 | 1 | A02 | TEMW0.04009021/DBE
Horizontal Wall | Tempo Wall | TEMW.04010010 | 40 | 100 | 10 | 12 | 963 | 963 | 963 | 0.022929 | 367 | 0.0087381 | 1100 | 0.02619 | 1.394 | A02 | TEMW0.04010010
Horizontal Wall | Tempo Wall | TEMW.04010011 | 40 | 100 | 11 | 12 | 1264 | 1264 | 1264 | 0.030095 | 466 | 0.011095 | 1450 | 0.034524 | 1.439 | A02 | TEMW0.04010011
Horizontal Wall | Tempo Wall | TEMW.04010011/DBE | 40 | 100 | 11 | 12 | 1864 | 1864 | 1864 | 0.044381 | 932 | 0.02219 | 2050 | 0.04881 | 1 | A02 | TEMW0.04010011/DBE
Horizontal Wall | Tempo Wall | TEMW.04010015 | 40 | 100 | 15 | 17 | 1568 | 1568 | 1568 | 0.037333 | 601 | 0.01431 | 1789 | 0.042595 | 1.385 | A02 | TEMW0.04010015
Horizontal Wall | Tempo Wall | TEMW.04010016 | 40 | 100 | 16 | 17 | 1700 | 1700 | 1700 | 0.040476 | 617 | 0.01469 | 1953 | 0.0465 | 1.46 | A02 | TEMW0.04010016
Horizontal Wall | Tempo Wall | TEMW.04010016/DBE | 40 | 100 | 16 | 17 | 2660 | 2660 | 2660 | 0.063333 | 1330 | 0.031667 | 2926 | 0.069667 | 1 | A02 | TEMW0.04010016/DBE
Horizontal Wall | Tempo Wall | TEMW.04010020 | 40 | 100 | 20 | 22 | 2196 | 2196 | 2196 | 0.052286 | 841 | 0.020024 | 2506 | 0.059667 | 1.384 | A02 | TEMW0.04010020
Horizontal Wall | Tempo Wall | TEMW.04010021 | 40 | 100 | 21 | 22 | 2274 | 2274 | 2274 | 0.054143 | 816 | 0.019429 | 2617 | 0.06231 | 1.477 | A02 | TEMW0.04010021
Horizontal Wall | Tempo Wall | TEMW.04010021/DBE | 40 | 100 | 21 | 22 | 3234 | 3234 | 3234 | 0.077 | 1617 | 0.0385 | 3557 | 0.08469 | 1 | A02 | TEMW0.04010021/DBE
Horizontal Wall | Tempo Wall | TEMW.04011010 | 40 | 110 | 10 | 12 | 1059 | 1059 | 1059 | 0.025214 | 403 | 0.0095952 | 1209 | 0.028786 | 1.394 | A02 | TEMW0.04011010
Horizontal Wall | Tempo Wall | TEMW.04011011 | 40 | 110 | 11 | 12 | 1390 | 1390 | 1390 | 0.033095 | 513 | 0.012214 | 1594 | 0.037952 | 1.439 | A02 | TEMW0.04011011
Horizontal Wall | Tempo Wall | TEMW.04011011/DBE | 40 | 110 | 11 | 12 | 1990 | 1990 | 1990 | 0.047381 | 995 | 0.02369 | 2189 | 0.052119 | 1 | A02 | TEMW0.04011011/DBE
Horizontal Wall | Tempo Wall | TEMW.04011015 | 40 | 110 | 15 | 17 | 1725 | 1725 | 1725 | 0.041071 | 661 | 0.015738 | 1968 | 0.046857 | 1.385 | A02 | TEMW0.04011015
Horizontal Wall | Tempo Wall | TEMW.04011016 | 40 | 110 | 16 | 17 | 1870 | 1870 | 1870 | 0.044524 | 679 | 0.016167 | 2149 | 0.051167 | 1.46 | A02 | TEMW0.04011016
Horizontal Wall | Tempo Wall | TEMW.04011016/DBE | 40 | 110 | 16 | 17 | 2830 | 2830 | 2830 | 0.067381 | 1415 | 0.03369 | 3113 | 0.074119 | 1 | A02 | TEMW0.04011016/DBE
Horizontal Wall | Tempo Wall | TEMW.04011020 | 40 | 110 | 20 | 22 | 2416 | 2416 | 2416 | 0.057524 | 925 | 0.022024 | 2757 | 0.065643 | 1.384 | A02 | TEMW0.04011020
Horizontal Wall | Tempo Wall | TEMW.04011021 | 40 | 110 | 21 | 22 | 2501 | 2501 | 2501 | 0.059548 | 898 | 0.021381 | 2879 | 0.068548 | 1.477 | A02 | TEMW0.04011021
Horizontal Wall | Tempo Wall | TEMW.04011021/DBE | 40 | 110 | 21 | 22 | 3461 | 3461 | 3461 | 0.082405 | 1731 | 0.041214 | 3807 | 0.090643 | 1 | A02 | TEMW0.04011021/DBE
Horizontal Wall | Tempo Wall | TEMW.04012010 | 40 | 120 | 10 | 12 | 1156 | 1156 | 1156 | 0.027524 | 440 | 0.010476 | 1320 | 0.031429 | 1.394 | A02 | TEMW0.04012010
Horizontal Wall | Tempo Wall | TEMW.04012011 | 40 | 120 | 11 | 12 | 1517 | 1517 | 1517 | 0.036119 | 560 | 0.013333 | 1740 | 0.041429 | 1.439 | A02 | TEMW0.04012011
Horizontal Wall | Tempo Wall | TEMW.04012011/DBE | 40 | 120 | 11 | 12 | 2117 | 2117 | 2117 | 0.050405 | 1059 | 0.025214 | 2329 | 0.055452 | 1 | A02 | TEMW0.04012011/DBE
Horizontal Wall | Tempo Wall | TEMW.04012015 | 40 | 120 | 15 | 17 | 1882 | 1882 | 1882 | 0.04481 | 721 | 0.017167 | 2147 | 0.051119 | 1.385 | A02 | TEMW0.04012015
Horizontal Wall | Tempo Wall | TEMW.04012016 | 40 | 120 | 16 | 17 | 2040 | 2040 | 2040 | 0.048571 | 741 | 0.017643 | 2344 | 0.05581 | 1.46 | A02 | TEMW0.04012016
Horizontal Wall | Tempo Wall | TEMW.04012016/DBE | 40 | 120 | 16 | 17 | 3000 | 3000 | 3000 | 0.071429 | 1500 | 0.035714 | 3300 | 0.078571 | 1 | A02 | TEMW0.04012016/DBE
Horizontal Wall | Tempo Wall | TEMW.04012020 | 40 | 120 | 20 | 22 | 2635 | 2635 | 2635 | 0.062738 | 1009 | 0.024024 | 3007 | 0.071595 | 1.384 | A02 | TEMW0.04012020
Horizontal Wall | Tempo Wall | TEMW.04012021 | 40 | 120 | 21 | 22 | 2729 | 2729 | 2729 | 0.064976 | 980 | 0.023333 | 3141 | 0.074786 | 1.477 | A02 | TEMW0.04012021
Horizontal Wall | Tempo Wall | TEMW.04012021/DBE | 40 | 120 | 21 | 22 | 3689 | 3689 | 3689 | 0.087833 | 1845 | 0.043929 | 4058 | 0.096619 | 1 | A02 | TEMW0.04012021/DBE
Horizontal Wall | Tempo Wall | TEMW.04014010 | 40 | 140 | 10 | 12 | 1348 | 1348 | 1348 | 0.032095 | 514 | 0.012238 | 1539 | 0.036643 | 1.394 | A02 | TEMW0.04014010
Horizontal Wall | Tempo Wall | TEMW.04014011 | 40 | 140 | 11 | 12 | 1770 | 1770 | 1770 | 0.042143 | 653 | 0.015548 | 2030 | 0.048333 | 1.439 | A02 | TEMW0.04014011
Horizontal Wall | Tempo Wall | TEMW.04014011/DBE | 40 | 140 | 11 | 12 | 2370 | 2370 | 2370 | 0.056429 | 1185 | 0.028214 | 2607 | 0.062071 | 1 | A02 | TEMW0.04014011/DBE
Horizontal Wall | Tempo Wall | TEMW.04014015 | 40 | 140 | 15 | 17 | 2195 | 2195 | 2195 | 0.052262 | 841 | 0.020024 | 2504 | 0.059619 | 1.385 | A02 | TEMW0.04014015
Horizontal Wall | Tempo Wall | TEMW.04014016 | 40 | 140 | 16 | 17 | 2380 | 2380 | 2380 | 0.056667 | 864 | 0.020571 | 2735 | 0.065119 | 1.46 | A02 | TEMW0.04014016
Horizontal Wall | Tempo Wall | TEMW.04014016/DBE | 40 | 140 | 16 | 17 | 3340 | 3340 | 3340 | 0.079524 | 1670 | 0.039762 | 3674 | 0.087476 | 1 | A02 | TEMW0.04014016/DBE
Horizontal Wall | Tempo Wall | TEMW.04014020 | 40 | 140 | 20 | 22 | 3074 | 3074 | 3074 | 0.07319 | 1177 | 0.028024 | 3507 | 0.0835 | 1.384 | A02 | TEMW0.04014020
Horizontal Wall | Tempo Wall | TEMW.04014021 | 40 | 140 | 21 | 22 | 3184 | 3184 | 3184 | 0.07581 | 1143 | 0.027214 | 3665 | 0.087262 | 1.477 | A02 | TEMW0.04014021
Horizontal Wall | Tempo Wall | TEMW.04014021/DBE | 40 | 140 | 21 | 22 | 4144 | 4144 | 4144 | 0.098667 | 2072 | 0.049333 | 4558 | 0.10852 | 1 | A02 | TEMW0.04014021/DBE
Horizontal Wall | Tempo Wall | TEMW.04016010 | 40 | 160 | 10 | 12 | 1541 | 1541 | 1541 | 0.03669 | 587 | 0.013976 | 1760 | 0.041905 | 1.394 | A02 | TEMW0.04016010
Horizontal Wall | Tempo Wall | TEMW.04016011 | 40 | 160 | 11 | 12 | 2022 | 2022 | 2022 | 0.048143 | 746 | 0.017762 | 2319 | 0.055214 | 1.439 | A02 | TEMW0.04016011
Horizontal Wall | Tempo Wall | TEMW.04016011/DBE | 40 | 160 | 11 | 12 | 3222 | 3222 | 3222 | 0.076714 | 1611 | 0.038357 | 3544 | 0.084381 | 1 | A02 | TEMW0.04016011/DBE
Horizontal Wall | Tempo Wall | TEMW.04016015 | 40 | 160 | 15 | 17 | 2509 | 2509 | 2509 | 0.059738 | 961 | 0.022881 | 2863 | 0.068167 | 1.385 | A02 | TEMW0.04016015
Horizontal Wall | Tempo Wall | TEMW.04016016 | 40 | 160 | 16 | 17 | 2720 | 2720 | 2720 | 0.064762 | 987 | 0.0235 | 3125 | 0.074405 | 1.46 | A02 | TEMW0.04016016
Horizontal Wall | Tempo Wall | TEMW.04016016/DBE | 40 | 160 | 16 | 17 | 4640 | 4640 | 4640 | 0.11048 | 2320 | 0.055238 | 5104 | 0.12152 | 1 | A02 | TEMW0.04016016/DBE
Horizontal Wall | Tempo Wall | TEMW.04016020 | 40 | 160 | 20 | 22 | 3514 | 3514 | 3514 | 0.083667 | 1346 | 0.032048 | 4009 | 0.095452 | 1.384 | A02 | TEMW0.04016020
Horizontal Wall | Tempo Wall | TEMW.04016021 | 40 | 160 | 21 | 22 | 3638 | 3638 | 3638 | 0.086619 | 1306 | 0.031095 | 4187 | 0.09969 | 1.477 | A02 | TEMW0.04016021
Horizontal Wall | Tempo Wall | TEMW.04016021/DBE | 40 | 160 | 21 | 22 | 5558 | 5558 | 5558 | 0.13233 | 2779 | 0.066167 | 6114 | 0.14557 | 1 | A02 | TEMW0.04016021/DBE
Horizontal Wall | Tempo Wall | TEMW.04018010 | 40 | 180 | 10 | 12 | 1733 | 1733 | 1733 | 0.041262 | 660 | 0.015714 | 1979 | 0.047119 | 1.394 | A02 | TEMW0.04018010
Horizontal Wall | Tempo Wall | TEMW.04018011 | 40 | 180 | 11 | 12 | 2275 | 2275 | 2275 | 0.054167 | 839 | 0.019976 | 2609 | 0.062119 | 1.439 | A02 | TEMW0.04018011
Horizontal Wall | Tempo Wall | TEMW.04018011/DBE | 40 | 180 | 11 | 12 | 3475 | 3475 | 3475 | 0.082738 | 1738 | 0.041381 | 3823 | 0.091024 | 1 | A02 | TEMW0.04018011/DBE
Horizontal Wall | Tempo Wall | TEMW.04018015 | 40 | 180 | 15 | 17 | 2822 | 2822 | 2822 | 0.06719 | 1081 | 0.025738 | 3220 | 0.076667 | 1.385 | A02 | TEMW0.04018015
Horizontal Wall | Tempo Wall | TEMW.04018016 | 40 | 180 | 16 | 17 | 3060 | 3060 | 3060 | 0.072857 | 1111 | 0.026452 | 3516 | 0.083714 | 1.46 | A02 | TEMW0.04018016
Horizontal Wall | Tempo Wall | TEMW.04018016/DBE | 40 | 180 | 16 | 17 | 4980 | 4980 | 4980 | 0.11857 | 2490 | 0.059286 | 5478 | 0.13043 | 1 | A02 | TEMW0.04018016/DBE
Horizontal Wall | Tempo Wall | TEMW.04018020 | 40 | 180 | 20 | 22 | 3953 | 3953 | 3953 | 0.094119 | 1514 | 0.036048 | 4510 | 0.10738 | 1.384 | A02 | TEMW0.04018020
Horizontal Wall | Tempo Wall | TEMW.04018021 | 40 | 180 | 21 | 22 | 4093 | 4093 | 4093 | 0.097452 | 1469 | 0.034976 | 4711 | 0.11217 | 1.477 | A02 | TEMW0.04018021
Horizontal Wall | Tempo Wall | TEMW.04018021/DBE | 40 | 180 | 21 | 22 | 6013 | 6013 | 6013 | 0.14317 | 3007 | 0.071595 | 6614 | 0.15748 | 1 | A02 | TEMW0.04018021/DBE
Horizontal Wall | Tempo Wall | TEMW.04020010 | 40 | 200 | 10 | 12 | 1926 | 1926 | 1926 | 0.045857 | 734 | 0.017476 | 2199 | 0.052357 | 1.394 | A02 | TEMW0.04020010
Horizontal Wall | Tempo Wall | TEMW.04020011 | 40 | 200 | 11 | 12 | 2528 | 2528 | 2528 | 0.06019 | 933 | 0.022214 | 2900 | 0.069048 | 1.439 | A02 | TEMW0.04020011
Horizontal Wall | Tempo Wall | TEMW.04020011/DBE | 40 | 200 | 11 | 12 | 3728 | 3728 | 3728 | 0.088762 | 1864 | 0.044381 | 4101 | 0.097643 | 1 | A02 | TEMW0.04020011/DBE
Horizontal Wall | Tempo Wall | TEMW.04020015 | 40 | 200 | 15 | 17 | 3136 | 3136 | 3136 | 0.074667 | 1201 | 0.028595 | 3578 | 0.08519 | 1.385 | A02 | TEMW0.04020015
Horizontal Wall | Tempo Wall | TEMW.04020016 | 40 | 200 | 16 | 17 | 3400 | 3400 | 3400 | 0.080952 | 1234 | 0.029381 | 3907 | 0.093024 | 1.46 | A02 | TEMW0.04020016
Horizontal Wall | Tempo Wall | TEMW.04020016/DBE | 40 | 200 | 16 | 17 | 5320 | 5320 | 5320 | 0.12667 | 2660 | 0.063333 | 5852 | 0.13933 | 1 | A02 | TEMW0.04020016/DBE
Horizontal Wall | Tempo Wall | TEMW.04020020 | 40 | 200 | 20 | 22 | 4392 | 4392 | 4392 | 0.10457 | 1682 | 0.040048 | 5011 | 0.11931 | 1.384 | A02 | TEMW0.04020020
Horizontal Wall | Tempo Wall | TEMW.04020021 | 40 | 200 | 21 | 22 | 4548 | 4548 | 4548 | 0.10829 | 1633 | 0.038881 | 5235 | 0.12464 | 1.477 | A02 | TEMW0.04020021
Horizontal Wall | Tempo Wall | TEMW.04020021/DBE | 40 | 200 | 21 | 22 | 6468 | 6468 | 6468 | 0.154 | 3234 | 0.077 | 7115 | 0.1694 | 1 | A02 | TEMW0.04020021/DBE
Horizontal Wall | Tempo Wall | TEMW.04022010 | 40 | 220 | 10 | 12 | 2119 | 2119 | 2119 | 0.050452 | 807 | 0.019214 | 2420 | 0.057619 | 1.394 | A02 | TEMW0.04022010
Horizontal Wall | Tempo Wall | TEMW.04022011 | 40 | 220 | 11 | 12 | 2781 | 2781 | 2781 | 0.066214 | 1026 | 0.024429 | 3190 | 0.075952 | 1.439 | A02 | TEMW0.04022011
Horizontal Wall | Tempo Wall | TEMW.04022011/DBE | 40 | 220 | 11 | 12 | 3981 | 3981 | 3981 | 0.094786 | 1991 | 0.047405 | 4379 | 0.10426 | 1 | A02 | TEMW0.04022011/DBE
Horizontal Wall | Tempo Wall | TEMW.04022015 | 40 | 220 | 15 | 17 | 3450 | 3450 | 3450 | 0.082143 | 1321 | 0.031452 | 3936 | 0.093714 | 1.385 | A02 | TEMW0.04022015
Horizontal Wall | Tempo Wall | TEMW.04022016 | 40 | 220 | 16 | 17 | 3740 | 3740 | 3740 | 0.089048 | 1358 | 0.032333 | 4297 | 0.10231 | 1.46 | A02 | TEMW0.04022016
Horizontal Wall | Tempo Wall | TEMW.04022016/DBE | 40 | 220 | 16 | 17 | 5660 | 5660 | 5660 | 0.13476 | 2830 | 0.067381 | 6226 | 0.14824 | 1 | A02 | TEMW0.04022016/DBE
Horizontal Wall | Tempo Wall | TEMW.04022020 | 40 | 220 | 20 | 22 | 4831 | 4831 | 4831 | 0.11502 | 1850 | 0.044048 | 5512 | 0.13124 | 1.384 | A02 | TEMW0.04022020
Horizontal Wall | Tempo Wall | TEMW.04022021 | 40 | 220 | 21 | 22 | 5003 | 5003 | 5003 | 0.11912 | 1796 | 0.042762 | 5758 | 0.1371 | 1.477 | A02 | TEMW0.04022021
Horizontal Wall | Tempo Wall | TEMW.04022021/DBE | 40 | 220 | 21 | 22 | 6923 | 6923 | 6923 | 0.16483 | 3462 | 0.082429 | 7615 | 0.18131 | 1 | A02 | TEMW0.04022021/DBE
Horizontal Wall | Tempo Wall | TEMW.04024010 | 40 | 240 | 10 | 12 | 2311 | 2311 | 2311 | 0.055024 | 880 | 0.020952 | 2639 | 0.062833 | 1.394 | A02 | TEMW0.04024010
Horizontal Wall | Tempo Wall | TEMW.04024011 | 40 | 240 | 11 | 12 | 3034 | 3034 | 3034 | 0.072238 | 1120 | 0.026667 | 3480 | 0.082857 | 1.439 | A02 | TEMW0.04024011
Horizontal Wall | Tempo Wall | TEMW.04024011/DBE | 40 | 240 | 11 | 12 | 4834 | 4834 | 4834 | 0.1151 | 2417 | 0.057548 | 5317 | 0.1266 | 1 | A02 | TEMW0.04024011/DBE
Horizontal Wall | Tempo Wall | TEMW.04024015 | 40 | 240 | 15 | 17 | 3763 | 3763 | 3763 | 0.089595 | 1441 | 0.03431 | 4294 | 0.10224 | 1.385 | A02 | TEMW0.04024015
Horizontal Wall | Tempo Wall | TEMW.04024016 | 40 | 240 | 16 | 17 | 4080 | 4080 | 4080 | 0.097143 | 1481 | 0.035262 | 4688 | 0.11162 | 1.46 | A02 | TEMW0.04024016
Horizontal Wall | Tempo Wall | TEMW.04024016/DBE | 40 | 240 | 16 | 17 | 6960 | 6960 | 6960 | 0.16571 | 3480 | 0.082857 | 7656 | 0.18229 | 1 | A02 | TEMW0.04024016/DBE
Horizontal Wall | Tempo Wall | TEMW.04024020 | 40 | 240 | 20 | 22 | 5270 | 5270 | 5270 | 0.12548 | 2018 | 0.048048 | 6013 | 0.14317 | 1.384 | A02 | TEMW0.04024020
Horizontal Wall | Tempo Wall | TEMW.04024021 | 40 | 240 | 21 | 22 | 5458 | 5458 | 5458 | 0.12995 | 1959 | 0.046643 | 6282 | 0.14957 | 1.477 | A02 | TEMW0.04024021
Horizontal Wall | Tempo Wall | TEMW.04024021/DBE | 40 | 240 | 21 | 22 | 8338 | 8338 | 8338 | 0.19852 | 4169 | 0.099262 | 9172 | 0.21838 | 1 | A02 | TEMW0.04024021/DBE
Horizontal Wall | Tempo Wall | TEMW.04026010 | 40 | 260 | 10 | 12 | 2504 | 2504 | 2504 | 0.059619 | 954 | 0.022714 | 2860 | 0.068095 | 1.394 | A02 | TEMW0.04026010
Horizontal Wall | Tempo Wall | TEMW.04026011 | 40 | 260 | 11 | 12 | 3286 | 3286 | 3286 | 0.078238 | 1213 | 0.028881 | 3769 | 0.089738 | 1.439 | A02 | TEMW0.04026011
Horizontal Wall | Tempo Wall | TEMW.04026011/DBE | 40 | 260 | 11 | 12 | 5086 | 5086 | 5086 | 0.1211 | 2543 | 0.060548 | 5595 | 0.13321 | 1 | A02 | TEMW0.04026011/DBE
Horizontal Wall | Tempo Wall | TEMW.04026015 | 40 | 260 | 15 | 17 | 4077 | 4077 | 4077 | 0.097071 | 1561 | 0.037167 | 4652 | 0.11076 | 1.385 | A02 | TEMW0.04026015
Horizontal Wall | Tempo Wall | TEMW.04026016 | 40 | 260 | 16 | 17 | 4420 | 4420 | 4420 | 0.10524 | 1604 | 0.03819 | 5079 | 0.12093 | 1.46 | A02 | TEMW0.04026016
Horizontal Wall | Tempo Wall | TEMW.04026016/DBE | 40 | 260 | 16 | 17 | 7300 | 7300 | 7300 | 0.17381 | 3650 | 0.086905 | 8030 | 0.19119 | 1 | A02 | TEMW0.04026016/DBE
Horizontal Wall | Tempo Wall | TEMW.04026020 | 40 | 260 | 20 | 22 | 5710 | 5710 | 5710 | 0.13595 | 2187 | 0.052071 | 6515 | 0.15512 | 1.384 | A02 | TEMW0.04026020
Horizontal Wall | Tempo Wall | TEMW.04026021 | 40 | 260 | 21 | 22 | 5912 | 5912 | 5912 | 0.14076 | 2122 | 0.050524 | 6805 | 0.16202 | 1.477 | A02 | TEMW0.04026021
Horizontal Wall | Tempo Wall | TEMW.04026021/DBE | 40 | 260 | 21 | 22 | 8792 | 8792 | 8792 | 0.20933 | 4396 | 0.10467 | 9671 | 0.23026 | 1 | A02 | TEMW0.04026021/DBE
Horizontal Wall | Tempo Wall | TEMW.04028010 | 40 | 280 | 10 | 12 | 2696 | 2696 | 2696 | 0.06419 | 1027 | 0.024452 | 3079 | 0.07331 | 1.394 | A02 | TEMW0.04028010
Horizontal Wall | Tempo Wall | TEMW.04028011 | 40 | 280 | 11 | 12 | 3539 | 3539 | 3539 | 0.084262 | 1306 | 0.031095 | 4059 | 0.096643 | 1.439 | A02 | TEMW0.04028011
Horizontal Wall | Tempo Wall | TEMW.04028011/DBE | 40 | 280 | 11 | 12 | 5339 | 5339 | 5339 | 0.12712 | 2670 | 0.063571 | 5873 | 0.13983 | 1 | A02 | TEMW0.04028011/DBE
Horizontal Wall | Tempo Wall | TEMW.04028015 | 40 | 280 | 15 | 17 | 4390 | 4390 | 4390 | 0.10452 | 1681 | 0.040024 | 5009 | 0.11926 | 1.385 | A02 | TEMW0.04028015
Horizontal Wall | Tempo Wall | TEMW.04028016 | 40 | 280 | 16 | 17 | 4760 | 4760 | 4760 | 0.11333 | 1728 | 0.041143 | 5469 | 0.13021 | 1.46 | A02 | TEMW0.04028016
Horizontal Wall | Tempo Wall | TEMW.04028016/DBE | 40 | 280 | 16 | 17 | 7640 | 7640 | 7640 | 0.1819 | 3820 | 0.090952 | 8404 | 0.2001 | 1 | A02 | TEMW0.04028016/DBE
Horizontal Wall | Tempo Wall | TEMW.04028020 | 40 | 280 | 20 | 22 | 6149 | 6149 | 6149 | 0.1464 | 2355 | 0.056071 | 7016 | 0.16705 | 1.384 | A02 | TEMW0.04028020
Horizontal Wall | Tempo Wall | TEMW.04028021 | 40 | 280 | 21 | 22 | 6367 | 6367 | 6367 | 0.1516 | 2286 | 0.054429 | 7328 | 0.17448 | 1.477 | A02 | TEMW0.04028021
Horizontal Wall | Tempo Wall | TEMW.04028021/DBE | 40 | 280 | 21 | 22 | 9247 | 9247 | 9247 | 0.22017 | 4624 | 0.1101 | 10172 | 0.24219 | 1 | A02 | TEMW0.04028021/DBE
Horizontal Wall | Tempo Wall | TEMW.04030010 | 40 | 300 | 10 | 12 | 2889 | 2889 | 2889 | 0.068786 | 1101 | 0.026214 | 3299 | 0.078548 | 1.394 | A02 | TEMW0.04030010
Horizontal Wall | Tempo Wall | TEMW.04030011 | 40 | 300 | 11 | 12 | 3792 | 3792 | 3792 | 0.090286 | 1399 | 0.03331 | 4349 | 0.10355 | 1.439 | A02 | TEMW0.04030011
Horizontal Wall | Tempo Wall | TEMW.04030011/DBE | 40 | 300 | 11 | 12 | 5592 | 5592 | 5592 | 0.13314 | 2796 | 0.066571 | 6151 | 0.14645 | 1 | A02 | TEMW0.04030011/DBE
Horizontal Wall | Tempo Wall | TEMW.04030015 | 40 | 300 | 15 | 17 | 4704 | 4704 | 4704 | 0.112 | 1802 | 0.042905 | 5367 | 0.12779 | 1.385 | A02 | TEMW0.04030015
Horizontal Wall | Tempo Wall | TEMW.04030016 | 40 | 300 | 16 | 17 | 5100 | 5100 | 5100 | 0.12143 | 1851 | 0.044071 | 5860 | 0.13952 | 1.46 | A02 | TEMW0.04030016
Horizontal Wall | Tempo Wall | TEMW.04030016/DBE | 40 | 300 | 16 | 17 | 7980 | 7980 | 7980 | 0.19 | 3990 | 0.095 | 8778 | 0.209 | 1 | A02 | TEMW0.04030016/DBE
Horizontal Wall | Tempo Wall | TEMW.04030020 | 40 | 300 | 20 | 22 | 6588 | 6588 | 6588 | 0.15686 | 2523 | 0.060071 | 7517 | 0.17898 | 1.384 | A02 | TEMW0.04030020
Horizontal Wall | Tempo Wall | TEMW.04030021 | 40 | 300 | 21 | 22 | 6822 | 6822 | 6822 | 0.16243 | 2449 | 0.05831 | 7852 | 0.18695 | 1.477 | A02 | TEMW0.04030021
Horizontal Wall | Tempo Wall | TEMW.04030021/DBE | 40 | 300 | 21 | 22 | 9702 | 9702 | 9702 | 0.231 | 4851 | 0.1155 | 10672 | 0.2541 | 1 | A02 | TEMW0.04030021/DBE
Horizontal Wall | Tempo Wall | TEMW.05004010 | 50 | 40 | 10 | 12 | 430 | 430 | 430 | 0.010238 | 165 | 0.0039286 | 491 | 0.01169 | 1.385 | A02 | TEMW0.05004010
Horizontal Wall | Tempo Wall | TEMW.05004011 | 50 | 40 | 11 | 12 | 554 | 554 | 554 | 0.01319 | 204 | 0.0048571 | 635 | 0.015119 | 1.438 | A02 | TEMW0.05004011
Horizontal Wall | Tempo Wall | TEMW.05004015 | 50 | 40 | 15 | 17 | 694 | 694 | 694 | 0.016524 | 268 | 0.006381 | 791 | 0.018833 | 1.373 | A02 | TEMW0.05004015
Horizontal Wall | Tempo Wall | TEMW.05004016 | 50 | 40 | 16 | 17 | 759 | 759 | 759 | 0.018071 | 275 | 0.0065476 | 873 | 0.020786 | 1.464 | A02 | TEMW0.05004016
Horizontal Wall | Tempo Wall | TEMW.05004020 | 50 | 40 | 20 | 22 | 970 | 970 | 970 | 0.023095 | 374 | 0.0089048 | 1106 | 0.026333 | 1.373 | A02 | TEMW0.05004020
Horizontal Wall | Tempo Wall | TEMW.05004021 | 50 | 40 | 21 | 22 | 1033 | 1033 | 1033 | 0.024595 | 369 | 0.0087857 | 1190 | 0.028333 | 1.485 | A02 | TEMW0.05004021
Horizontal Wall | Tempo Wall | TEMW.05005010 | 50 | 50 | 10 | 12 | 538 | 538 | 538 | 0.01281 | 206 | 0.0049048 | 614 | 0.014619 | 1.385 | A02 | TEMW0.05005010
Horizontal Wall | Tempo Wall | TEMW.05005011 | 50 | 50 | 11 | 12 | 693 | 693 | 693 | 0.0165 | 256 | 0.0060952 | 795 | 0.018929 | 1.438 | A02 | TEMW0.05005011
Horizontal Wall | Tempo Wall | TEMW.05005015 | 50 | 50 | 15 | 17 | 867 | 867 | 867 | 0.020643 | 335 | 0.0079762 | 988 | 0.023524 | 1.373 | A02 | TEMW0.05005015
Horizontal Wall | Tempo Wall | TEMW.05005016 | 50 | 50 | 16 | 17 | 949 | 949 | 949 | 0.022595 | 344 | 0.0081905 | 1091 | 0.025976 | 1.464 | A02 | TEMW0.05005016
Horizontal Wall | Tempo Wall | TEMW.05005020 | 50 | 50 | 20 | 22 | 1213 | 1213 | 1213 | 0.028881 | 468 | 0.011143 | 1383 | 0.032929 | 1.373 | A02 | TEMW0.05005020
Horizontal Wall | Tempo Wall | TEMW.05005021 | 50 | 50 | 21 | 22 | 1291 | 1291 | 1291 | 0.030738 | 461 | 0.010976 | 1487 | 0.035405 | 1.485 | A02 | TEMW0.05005021
Horizontal Wall | Tempo Wall | TEMW.05006010 | 50 | 60 | 10 | 12 | 646 | 646 | 646 | 0.015381 | 247 | 0.005881 | 737 | 0.017548 | 1.385 | A02 | TEMW0.05006010
Horizontal Wall | Tempo Wall | TEMW.05006011 | 50 | 60 | 11 | 12 | 832 | 832 | 832 | 0.01981 | 307 | 0.0073095 | 954 | 0.022714 | 1.438 | A02 | TEMW0.05006011
Horizontal Wall | Tempo Wall | TEMW.05006011/DBE | 50 | 60 | 11 | 12 | 1132 | 1132 | 1132 | 0.026952 | 566 | 0.013476 | 1245 | 0.029643 | 1 | A02 | TEMW0.05006011/DBE
Horizontal Wall | Tempo Wall | TEMW.05006015 | 50 | 60 | 15 | 17 | 1040 | 1040 | 1040 | 0.024762 | 401 | 0.0095476 | 1186 | 0.028238 | 1.373 | A02 | TEMW0.05006015
Horizontal Wall | Tempo Wall | TEMW.05006016 | 50 | 60 | 16 | 17 | 1139 | 1139 | 1139 | 0.027119 | 412 | 0.0098095 | 1310 | 0.03119 | 1.464 | A02 | TEMW0.05006016
Horizontal Wall | Tempo Wall | TEMW.05006016/DBE | 50 | 60 | 16 | 17 | 1619 | 1619 | 1619 | 0.038548 | 810 | 0.019286 | 1781 | 0.042405 | 1 | A02 | TEMW0.05006016/DBE
Horizontal Wall | Tempo Wall | TEMW.05006020 | 50 | 60 | 20 | 22 | 1455 | 1455 | 1455 | 0.034643 | 562 | 0.013381 | 1659 | 0.0395 | 1.373 | A02 | TEMW0.05006020
Horizontal Wall | Tempo Wall | TEMW.05006021 | 50 | 60 | 21 | 22 | 1549 | 1549 | 1549 | 0.036881 | 553 | 0.013167 | 1784 | 0.042476 | 1.485 | A02 | TEMW0.05006021
Horizontal Wall | Tempo Wall | TEMW.05006021/DBE | 50 | 60 | 21 | 22 | 2029 | 2029 | 2029 | 0.04831 | 1015 | 0.024167 | 2232 | 0.053143 | 1 | A02 | TEMW0.05006021/DBE
Horizontal Wall | Tempo Wall | TEMW.05007010 | 50 | 70 | 10 | 12 | 753 | 753 | 753 | 0.017929 | 288 | 0.0068571 | 859 | 0.020452 | 1.385 | A02 | TEMW0.05007010
Horizontal Wall | Tempo Wall | TEMW.05007011 | 50 | 70 | 11 | 12 | 970 | 970 | 970 | 0.023095 | 358 | 0.0085238 | 1113 | 0.0265 | 1.438 | A02 | TEMW0.05007011
Horizontal Wall | Tempo Wall | TEMW.05007011/DBE | 50 | 70 | 11 | 12 | 1270 | 1270 | 1270 | 0.030238 | 635 | 0.015119 | 1397 | 0.033262 | 1 | A02 | TEMW0.05007011/DBE
Horizontal Wall | Tempo Wall | TEMW.05007015 | 50 | 70 | 15 | 17 | 1214 | 1214 | 1214 | 0.028905 | 469 | 0.011167 | 1384 | 0.032952 | 1.373 | A02 | TEMW0.05007015
Horizontal Wall | Tempo Wall | TEMW.05007016 | 50 | 70 | 16 | 17 | 1329 | 1329 | 1329 | 0.031643 | 481 | 0.011452 | 1528 | 0.036381 | 1.464 | A02 | TEMW0.05007016
Horizontal Wall | Tempo Wall | TEMW.05007016/DBE | 50 | 70 | 16 | 17 | 1809 | 1809 | 1809 | 0.043071 | 905 | 0.021548 | 1990 | 0.047381 | 1 | A02 | TEMW0.05007016/DBE
Horizontal Wall | Tempo Wall | TEMW.05007020 | 50 | 70 | 20 | 22 | 1698 | 1698 | 1698 | 0.040429 | 655 | 0.015595 | 1936 | 0.046095 | 1.373 | A02 | TEMW0.05007020
Horizontal Wall | Tempo Wall | TEMW.05007021 | 50 | 70 | 21 | 22 | 1807 | 1807 | 1807 | 0.043024 | 645 | 0.015357 | 2082 | 0.049571 | 1.485 | A02 | TEMW0.05007021
Horizontal Wall | Tempo Wall | TEMW.05007021/DBE | 50 | 70 | 21 | 22 | 2287 | 2287 | 2287 | 0.054452 | 1144 | 0.027238 | 2516 | 0.059905 | 1 | A02 | TEMW0.05007021/DBE
Horizontal Wall | Tempo Wall | TEMW.05008010 | 50 | 80 | 10 | 12 | 861 | 861 | 861 | 0.0205 | 330 | 0.0078571 | 982 | 0.023381 | 1.385 | A02 | TEMW0.05008010
Horizontal Wall | Tempo Wall | TEMW.05008011 | 50 | 80 | 11 | 12 | 1109 | 1109 | 1109 | 0.026405 | 409 | 0.0097381 | 1272 | 0.030286 | 1.438 | A02 | TEMW0.05008011
Horizontal Wall | Tempo Wall | TEMW.05008011/DBE | 50 | 80 | 11 | 12 | 1409 | 1409 | 1409 | 0.033548 | 705 | 0.016786 | 1550 | 0.036905 | 1 | A02 | TEMW0.05008011/DBE
Horizontal Wall | Tempo Wall | TEMW.05008015 | 50 | 80 | 15 | 17 | 1387 | 1387 | 1387 | 0.033024 | 535 | 0.012738 | 1581 | 0.037643 | 1.373 | A02 | TEMW0.05008015
Horizontal Wall | Tempo Wall | TEMW.05008016 | 50 | 80 | 16 | 17 | 1518 | 1518 | 1518 | 0.036143 | 550 | 0.013095 | 1746 | 0.041571 | 1.464 | A02 | TEMW0.05008016
Horizontal Wall | Tempo Wall | TEMW.05008016/DBE | 50 | 80 | 16 | 17 | 1998 | 1998 | 1998 | 0.047571 | 999 | 0.023786 | 2198 | 0.052333 | 1 | A02 | TEMW0.05008016/DBE
Horizontal Wall | Tempo Wall | TEMW.05008020 | 50 | 80 | 20 | 22 | 1940 | 1940 | 1940 | 0.04619 | 749 | 0.017833 | 2212 | 0.052667 | 1.373 | A02 | TEMW0.05008020
Horizontal Wall | Tempo Wall | TEMW.05008021 | 50 | 80 | 21 | 22 | 2066 | 2066 | 2066 | 0.04919 | 738 | 0.017571 | 2380 | 0.056667 | 1.485 | A02 | TEMW0.05008021
Horizontal Wall | Tempo Wall | TEMW.05008021/DBE | 50 | 80 | 21 | 22 | 2546 | 2546 | 2546 | 0.060619 | 1273 | 0.03031 | 2801 | 0.06669 | 1 | A02 | TEMW0.05008021/DBE
Horizontal Wall | Tempo Wall | TEMW.05009010 | 50 | 90 | 10 | 12 | 968 | 968 | 968 | 0.023048 | 371 | 0.0088333 | 1104 | 0.026286 | 1.385 | A02 | TEMW0.05009010
Horizontal Wall | Tempo Wall | TEMW.05009011 | 50 | 90 | 11 | 12 | 1247 | 1247 | 1247 | 0.02969 | 460 | 0.010952 | 1430 | 0.034048 | 1.438 | A02 | TEMW0.05009011
Horizontal Wall | Tempo Wall | TEMW.05009011/DBE | 50 | 90 | 11 | 12 | 1847 | 1847 | 1847 | 0.043976 | 924 | 0.022 | 2032 | 0.048381 | 1 | A02 | TEMW0.05009011/DBE
Horizontal Wall | Tempo Wall | TEMW.05009015 | 50 | 90 | 15 | 17 | 1561 | 1561 | 1561 | 0.037167 | 603 | 0.014357 | 1780 | 0.042381 | 1.373 | A02 | TEMW0.05009015
Horizontal Wall | Tempo Wall | TEMW.05009016 | 50 | 90 | 16 | 17 | 1708 | 1708 | 1708 | 0.040667 | 618 | 0.014714 | 1964 | 0.046762 | 1.464 | A02 | TEMW0.05009016
Horizontal Wall | Tempo Wall | TEMW.05009016/DBE | 50 | 90 | 16 | 17 | 2668 | 2668 | 2668 | 0.063524 | 1334 | 0.031762 | 2935 | 0.069881 | 1 | A02 | TEMW0.05009016/DBE
Horizontal Wall | Tempo Wall | TEMW.05009020 | 50 | 90 | 20 | 22 | 2183 | 2183 | 2183 | 0.051976 | 843 | 0.020071 | 2489 | 0.059262 | 1.373 | A02 | TEMW0.05009020
Horizontal Wall | Tempo Wall | TEMW.05009021 | 50 | 90 | 21 | 22 | 2324 | 2324 | 2324 | 0.055333 | 830 | 0.019762 | 2677 | 0.063738 | 1.485 | A02 | TEMW0.05009021
Horizontal Wall | Tempo Wall | TEMW.05009021/DBE | 50 | 90 | 21 | 22 | 3284 | 3284 | 3284 | 0.07819 | 1642 | 0.039095 | 3612 | 0.086 | 1 | A02 | TEMW0.05009021/DBE
Horizontal Wall | Tempo Wall | TEMW.05010010 | 50 | 100 | 10 | 12 | 1076 | 1076 | 1076 | 0.025619 | 412 | 0.0098095 | 1228 | 0.029238 | 1.385 | A02 | TEMW0.05010010
Horizontal Wall | Tempo Wall | TEMW.05010011 | 50 | 100 | 11 | 12 | 1386 | 1386 | 1386 | 0.033 | 511 | 0.012167 | 1590 | 0.037857 | 1.438 | A02 | TEMW0.05010011
Horizontal Wall | Tempo Wall | TEMW.05010011/DBE | 50 | 100 | 11 | 12 | 1986 | 1986 | 1986 | 0.047286 | 993 | 0.023643 | 2185 | 0.052024 | 1 | A02 | TEMW0.05010011/DBE
Horizontal Wall | Tempo Wall | TEMW.05010015 | 50 | 100 | 15 | 17 | 1734 | 1734 | 1734 | 0.041286 | 669 | 0.015929 | 1977 | 0.047071 | 1.373 | A02 | TEMW0.05010015
Horizontal Wall | Tempo Wall | TEMW.05010016 | 50 | 100 | 16 | 17 | 1898 | 1898 | 1898 | 0.04519 | 687 | 0.016357 | 2183 | 0.051976 | 1.464 | A02 | TEMW0.05010016
Horizontal Wall | Tempo Wall | TEMW.05010016/DBE | 50 | 100 | 16 | 17 | 2858 | 2858 | 2858 | 0.068048 | 1429 | 0.034024 | 3144 | 0.074857 | 1 | A02 | TEMW0.05010016/DBE
Horizontal Wall | Tempo Wall | TEMW.05010020 | 50 | 100 | 20 | 22 | 2425 | 2425 | 2425 | 0.057738 | 936 | 0.022286 | 2765 | 0.065833 | 1.373 | A02 | TEMW0.05010020
Horizontal Wall | Tempo Wall | TEMW.05010021 | 50 | 100 | 21 | 22 | 2582 | 2582 | 2582 | 0.061476 | 922 | 0.021952 | 2974 | 0.07081 | 1.485 | A02 | TEMW0.05010021
Horizontal Wall | Tempo Wall | TEMW.05010021/DBE | 50 | 100 | 21 | 22 | 3542 | 3542 | 3542 | 0.084333 | 1771 | 0.042167 | 3896 | 0.092762 | 1 | A02 | TEMW0.05010021/DBE
Horizontal Wall | Tempo Wall | TEMW.05011010 | 50 | 110 | 10 | 12 | 1184 | 1184 | 1184 | 0.02819 | 453 | 0.010786 | 1351 | 0.032167 | 1.385 | A02 | TEMW0.05011010
Horizontal Wall | Tempo Wall | TEMW.05011011 | 50 | 110 | 11 | 12 | 1525 | 1525 | 1525 | 0.03631 | 563 | 0.013405 | 1749 | 0.041643 | 1.438 | A02 | TEMW0.05011011
Horizontal Wall | Tempo Wall | TEMW.05011011/DBE | 50 | 110 | 11 | 12 | 2125 | 2125 | 2125 | 0.050595 | 1063 | 0.02531 | 2338 | 0.055667 | 1 | A02 | TEMW0.05011011/DBE
Horizontal Wall | Tempo Wall | TEMW.05011015 | 50 | 110 | 15 | 17 | 1907 | 1907 | 1907 | 0.045405 | 736 | 0.017524 | 2174 | 0.051762 | 1.373 | A02 | TEMW0.05011015
Horizontal Wall | Tempo Wall | TEMW.05011016 | 50 | 110 | 16 | 17 | 2088 | 2088 | 2088 | 0.049714 | 756 | 0.018 | 2401 | 0.057167 | 1.464 | A02 | TEMW0.05011016
Horizontal Wall | Tempo Wall | TEMW.05011016/DBE | 50 | 110 | 16 | 17 | 3048 | 3048 | 3048 | 0.072571 | 1524 | 0.036286 | 3353 | 0.079833 | 1 | A02 | TEMW0.05011016/DBE
Horizontal Wall | Tempo Wall | TEMW.05011020 | 50 | 110 | 20 | 22 | 2668 | 2668 | 2668 | 0.063524 | 1030 | 0.024524 | 3042 | 0.072429 | 1.373 | A02 | TEMW0.05011020
Horizontal Wall | Tempo Wall | TEMW.05011021 | 50 | 110 | 21 | 22 | 2840 | 2840 | 2840 | 0.067619 | 1014 | 0.024143 | 3272 | 0.077905 | 1.485 | A02 | TEMW0.05011021
Horizontal Wall | Tempo Wall | TEMW.05011021/DBE | 50 | 110 | 21 | 22 | 3800 | 3800 | 3800 | 0.090476 | 1900 | 0.045238 | 4180 | 0.099524 | 1 | A02 | TEMW0.05011021/DBE
Horizontal Wall | Tempo Wall | TEMW.05012010 | 50 | 120 | 10 | 12 | 1291 | 1291 | 1291 | 0.030738 | 494 | 0.011762 | 1473 | 0.035071 | 1.385 | A02 | TEMW0.05012010
Horizontal Wall | Tempo Wall | TEMW.05012011 | 50 | 120 | 11 | 12 | 1663 | 1663 | 1663 | 0.039595 | 614 | 0.014619 | 1907 | 0.045405 | 1.438 | A02 | TEMW0.05012011
Horizontal Wall | Tempo Wall | TEMW.05012011/DBE | 50 | 120 | 11 | 12 | 2263 | 2263 | 2263 | 0.053881 | 1132 | 0.026952 | 2489 | 0.059262 | 1 | A02 | TEMW0.05012011/DBE
Horizontal Wall | Tempo Wall | TEMW.05012015 | 50 | 120 | 15 | 17 | 2081 | 2081 | 2081 | 0.049548 | 803 | 0.019119 | 2372 | 0.056476 | 1.373 | A02 | TEMW0.05012015
Horizontal Wall | Tempo Wall | TEMW.05012016 | 50 | 120 | 16 | 17 | 2278 | 2278 | 2278 | 0.054238 | 825 | 0.019643 | 2620 | 0.062381 | 1.464 | A02 | TEMW0.05012016
Horizontal Wall | Tempo Wall | TEMW.05012016/DBE | 50 | 120 | 16 | 17 | 3238 | 3238 | 3238 | 0.077095 | 1619 | 0.038548 | 3562 | 0.08481 | 1 | A02 | TEMW0.05012016/DBE
Horizontal Wall | Tempo Wall | TEMW.05012020 | 50 | 120 | 20 | 22 | 2910 | 2910 | 2910 | 0.069286 | 1123 | 0.026738 | 3317 | 0.078976 | 1.373 | A02 | TEMW0.05012020
Horizontal Wall | Tempo Wall | TEMW.05012021 | 50 | 120 | 21 | 22 | 3098 | 3098 | 3098 | 0.073762 | 1106 | 0.026333 | 3569 | 0.084976 | 1.485 | A02 | TEMW0.05012021
Horizontal Wall | Tempo Wall | TEMW.05012021/DBE | 50 | 120 | 21 | 22 | 4058 | 4058 | 4058 | 0.096619 | 2029 | 0.04831 | 4464 | 0.10629 | 1 | A02 | TEMW0.05012021/DBE
Horizontal Wall | Tempo Wall | TEMW.05014010 | 50 | 140 | 10 | 12 | 1506 | 1506 | 1506 | 0.035857 | 577 | 0.013738 | 1718 | 0.040905 | 1.385 | A02 | TEMW0.05014010
Horizontal Wall | Tempo Wall | TEMW.05014011 | 50 | 140 | 11 | 12 | 1940 | 1940 | 1940 | 0.04619 | 716 | 0.017048 | 2225 | 0.052976 | 1.438 | A02 | TEMW0.05014011
Horizontal Wall | Tempo Wall | TEMW.05014011/DBE | 50 | 140 | 11 | 12 | 2540 | 2540 | 2540 | 0.060476 | 1270 | 0.030238 | 2794 | 0.066524 | 1 | A02 | TEMW0.05014011/DBE
Horizontal Wall | Tempo Wall | TEMW.05014015 | 50 | 140 | 15 | 17 | 2428 | 2428 | 2428 | 0.05781 | 937 | 0.02231 | 2768 | 0.065905 | 1.373 | A02 | TEMW0.05014015
Horizontal Wall | Tempo Wall | TEMW.05014016 | 50 | 140 | 16 | 17 | 2657 | 2657 | 2657 | 0.063262 | 962 | 0.022905 | 3056 | 0.072762 | 1.464 | A02 | TEMW0.05014016
Horizontal Wall | Tempo Wall | TEMW.05014016/DBE | 50 | 140 | 16 | 17 | 3617 | 3617 | 3617 | 0.086119 | 1809 | 0.043071 | 3979 | 0.094738 | 1 | A02 | TEMW0.05014016/DBE
Horizontal Wall | Tempo Wall | TEMW.05014020 | 50 | 140 | 20 | 22 | 3395 | 3395 | 3395 | 0.080833 | 1310 | 0.03119 | 3870 | 0.092143 | 1.373 | A02 | TEMW0.05014020
Horizontal Wall | Tempo Wall | TEMW.05014021 | 50 | 140 | 21 | 22 | 3615 | 3615 | 3615 | 0.086071 | 1291 | 0.030738 | 4164 | 0.099143 | 1.485 | A02 | TEMW0.05014021
Horizontal Wall | Tempo Wall | TEMW.05014021/DBE | 50 | 140 | 21 | 22 | 4575 | 4575 | 4575 | 0.10893 | 2288 | 0.054476 | 5033 | 0.11983 | 1 | A02 | TEMW0.05014021/DBE
Horizontal Wall | Tempo Wall | TEMW.05016010 | 50 | 160 | 10 | 12 | 1722 | 1722 | 1722 | 0.041 | 660 | 0.015714 | 1965 | 0.046786 | 1.385 | A02 | TEMW0.05016010
Horizontal Wall | Tempo Wall | TEMW.05016011 | 50 | 160 | 11 | 12 | 2218 | 2218 | 2218 | 0.05281 | 818 | 0.019476 | 2544 | 0.060571 | 1.438 | A02 | TEMW0.05016011
Horizontal Wall | Tempo Wall | TEMW.05016011/DBE | 50 | 160 | 11 | 12 | 3418 | 3418 | 3418 | 0.081381 | 1709 | 0.04069 | 3760 | 0.089524 | 1 | A02 | TEMW0.05016011/DBE
Horizontal Wall | Tempo Wall | TEMW.05016015 | 50 | 160 | 15 | 17 | 2774 | 2774 | 2774 | 0.066048 | 1071 | 0.0255 | 3162 | 0.075286 | 1.373 | A02 | TEMW0.05016015
Horizontal Wall | Tempo Wall | TEMW.05016016 | 50 | 160 | 16 | 17 | 3037 | 3037 | 3037 | 0.07231 | 1099 | 0.026167 | 3493 | 0.083167 | 1.464 | A02 | TEMW0.05016016
Horizontal Wall | Tempo Wall | TEMW.05016016/DBE | 50 | 160 | 16 | 17 | 4957 | 4957 | 4957 | 0.11802 | 2479 | 0.059024 | 5453 | 0.12983 | 1 | A02 | TEMW0.05016016/DBE
Horizontal Wall | Tempo Wall | TEMW.05016020 | 50 | 160 | 20 | 22 | 3880 | 3880 | 3880 | 0.092381 | 1498 | 0.035667 | 4423 | 0.10531 | 1.373 | A02 | TEMW0.05016020
Horizontal Wall | Tempo Wall | TEMW.05016021 | 50 | 160 | 21 | 22 | 4131 | 4131 | 4131 | 0.098357 | 1475 | 0.035119 | 4759 | 0.11331 | 1.485 | A02 | TEMW0.05016021
Horizontal Wall | Tempo Wall | TEMW.05016021/DBE | 50 | 160 | 21 | 22 | 6051 | 6051 | 6051 | 0.14407 | 3026 | 0.072048 | 6656 | 0.15848 | 1 | A02 | TEMW0.05016021/DBE
Horizontal Wall | Tempo Wall | TEMW.05018010 | 50 | 180 | 10 | 12 | 1937 | 1937 | 1937 | 0.046119 | 742 | 0.017667 | 2210 | 0.052619 | 1.385 | A02 | TEMW0.05018010
Horizontal Wall | Tempo Wall | TEMW.05018011 | 50 | 180 | 11 | 12 | 2495 | 2495 | 2495 | 0.059405 | 921 | 0.021929 | 2862 | 0.068143 | 1.438 | A02 | TEMW0.05018011
Horizontal Wall | Tempo Wall | TEMW.05018011/DBE | 50 | 180 | 11 | 12 | 3695 | 3695 | 3695 | 0.087976 | 1848 | 0.044 | 4065 | 0.096786 | 1 | A02 | TEMW0.05018011/DBE
Horizontal Wall | Tempo Wall | TEMW.05018015 | 50 | 180 | 15 | 17 | 3121 | 3121 | 3121 | 0.07431 | 1205 | 0.02869 | 3558 | 0.084714 | 1.373 | A02 | TEMW0.05018015
Horizontal Wall | Tempo Wall | TEMW.05018016 | 50 | 180 | 16 | 17 | 3416 | 3416 | 3416 | 0.081333 | 1237 | 0.029452 | 3928 | 0.093524 | 1.464 | A02 | TEMW0.05018016
Horizontal Wall | Tempo Wall | TEMW.05018016/DBE | 50 | 180 | 16 | 17 | 5336 | 5336 | 5336 | 0.12705 | 2668 | 0.063524 | 5870 | 0.13976 | 1 | A02 | TEMW0.05018016/DBE
Horizontal Wall | Tempo Wall | TEMW.05018020 | 50 | 180 | 20 | 22 | 4365 | 4365 | 4365 | 0.10393 | 1685 | 0.040119 | 4976 | 0.11848 | 1.373 | A02 | TEMW0.05018020
Horizontal Wall | Tempo Wall | TEMW.05018021 | 50 | 180 | 21 | 22 | 4648 | 4648 | 4648 | 0.11067 | 1659 | 0.0395 | 5354 | 0.12748 | 1.485 | A02 | TEMW0.05018021
Horizontal Wall | Tempo Wall | TEMW.05018021/DBE | 50 | 180 | 21 | 22 | 6568 | 6568 | 6568 | 0.15638 | 3284 | 0.07819 | 7225 | 0.17202 | 1 | A02 | TEMW0.05018021/DBE
Horizontal Wall | Tempo Wall | TEMW.05020010 | 50 | 200 | 10 | 12 | 2152 | 2152 | 2152 | 0.051238 | 824 | 0.019619 | 2455 | 0.058452 | 1.385 | A02 | TEMW0.05020010
Horizontal Wall | Tempo Wall | TEMW.05020011 | 50 | 200 | 11 | 12 | 2772 | 2772 | 2772 | 0.066 | 1023 | 0.024357 | 3179 | 0.07569 | 1.438 | A02 | TEMW0.05020011
Horizontal Wall | Tempo Wall | TEMW.05020011/DBE | 50 | 200 | 11 | 12 | 3972 | 3972 | 3972 | 0.094571 | 1986 | 0.047286 | 4369 | 0.10402 | 1 | A02 | TEMW0.05020011/DBE
Horizontal Wall | Tempo Wall | TEMW.05020015 | 50 | 200 | 15 | 17 | 3468 | 3468 | 3468 | 0.082571 | 1339 | 0.031881 | 3954 | 0.094143 | 1.373 | A02 | TEMW0.05020015
Horizontal Wall | Tempo Wall | TEMW.05020016 | 50 | 200 | 16 | 17 | 3796 | 3796 | 3796 | 0.090381 | 1374 | 0.032714 | 4365 | 0.10393 | 1.464 | A02 | TEMW0.05020016
Horizontal Wall | Tempo Wall | TEMW.05020016/DBE | 50 | 200 | 16 | 17 | 5716 | 5716 | 5716 | 0.1361 | 2858 | 0.068048 | 6288 | 0.14971 | 1 | A02 | TEMW0.05020016/DBE
Horizontal Wall | Tempo Wall | TEMW.05020020 | 50 | 200 | 20 | 22 | 4850 | 4850 | 4850 | 0.11548 | 1872 | 0.044571 | 5529 | 0.13164 | 1.373 | A02 | TEMW0.05020020
Horizontal Wall | Tempo Wall | TEMW.05020021 | 50 | 200 | 21 | 22 | 5164 | 5164 | 5164 | 0.12295 | 1844 | 0.043905 | 5949 | 0.14164 | 1.485 | A02 | TEMW0.05020021
Horizontal Wall | Tempo Wall | TEMW.05020021/DBE | 50 | 200 | 21 | 22 | 7084 | 7084 | 7084 | 0.16867 | 3542 | 0.084333 | 7792 | 0.18552 | 1 | A02 | TEMW0.05020021/DBE
Horizontal Wall | Tempo Wall | TEMW.05022010 | 50 | 220 | 10 | 12 | 2367 | 2367 | 2367 | 0.056357 | 907 | 0.021595 | 2701 | 0.06431 | 1.385 | A02 | TEMW0.05022010
Horizontal Wall | Tempo Wall | TEMW.05022011 | 50 | 220 | 11 | 12 | 3049 | 3049 | 3049 | 0.072595 | 1125 | 0.026786 | 3497 | 0.083262 | 1.438 | A02 | TEMW0.05022011
Horizontal Wall | Tempo Wall | TEMW.05022011/DBE | 50 | 220 | 11 | 12 | 4249 | 4249 | 4249 | 0.10117 | 2125 | 0.050595 | 4674 | 0.11129 | 1 | A02 | TEMW0.05022011/DBE
Horizontal Wall | Tempo Wall | TEMW.05022015 | 50 | 220 | 15 | 17 | 3815 | 3815 | 3815 | 0.090833 | 1473 | 0.035071 | 4349 | 0.10355 | 1.373 | A02 | TEMW0.05022015
Horizontal Wall | Tempo Wall | TEMW.05022016 | 50 | 220 | 16 | 17 | 4176 | 4176 | 4176 | 0.099429 | 1512 | 0.036 | 4802 | 0.11433 | 1.464 | A02 | TEMW0.05022016
Horizontal Wall | Tempo Wall | TEMW.05022016/DBE | 50 | 220 | 16 | 17 | 6096 | 6096 | 6096 | 0.14514 | 3048 | 0.072571 | 6706 | 0.15967 | 1 | A02 | TEMW0.05022016/DBE
Horizontal Wall | Tempo Wall | TEMW.05022020 | 50 | 220 | 20 | 22 | 5335 | 5335 | 5335 | 0.12702 | 2059 | 0.049024 | 6082 | 0.14481 | 1.373 | A02 | TEMW0.05022020
Horizontal Wall | Tempo Wall | TEMW.05022021 | 50 | 220 | 21 | 22 | 5680 | 5680 | 5680 | 0.13524 | 2028 | 0.048286 | 6543 | 0.15579 | 1.485 | A02 | TEMW0.05022021
Horizontal Wall | Tempo Wall | TEMW.05022021/DBE | 50 | 220 | 21 | 22 | 7600 | 7600 | 7600 | 0.18095 | 3800 | 0.090476 | 8360 | 0.19905 | 1 | A02 | TEMW0.05022021/DBE
Horizontal Wall | Tempo Wall | TEMW.05024010 | 50 | 240 | 10 | 12 | 2582 | 2582 | 2582 | 0.061476 | 989 | 0.023548 | 2946 | 0.070143 | 1.385 | A02 | TEMW0.05024010
Horizontal Wall | Tempo Wall | TEMW.05024011 | 50 | 240 | 11 | 12 | 3326 | 3326 | 3326 | 0.07919 | 1227 | 0.029214 | 3815 | 0.090833 | 1.438 | A02 | TEMW0.05024011
Horizontal Wall | Tempo Wall | TEMW.05024011/DBE | 50 | 240 | 11 | 12 | 5126 | 5126 | 5126 | 0.12205 | 2563 | 0.061024 | 5639 | 0.13426 | 1 | A02 | TEMW0.05024011/DBE
Horizontal Wall | Tempo Wall | TEMW.05024015 | 50 | 240 | 15 | 17 | 4162 | 4162 | 4162 | 0.099095 | 1607 | 0.038262 | 4745 | 0.11298 | 1.373 | A02 | TEMW0.05024015
Horizontal Wall | Tempo Wall | TEMW.05024016 | 50 | 240 | 16 | 17 | 4555 | 4555 | 4555 | 0.10845 | 1649 | 0.039262 | 5238 | 0.12471 | 1.464 | A02 | TEMW0.05024016
Horizontal Wall | Tempo Wall | TEMW.05024016/DBE | 50 | 240 | 16 | 17 | 7435 | 7435 | 7435 | 0.17702 | 3718 | 0.088524 | 8179 | 0.19474 | 1 | A02 | TEMW0.05024016/DBE
Horizontal Wall | Tempo Wall | TEMW.05024020 | 50 | 240 | 20 | 22 | 5820 | 5820 | 5820 | 0.13857 | 2247 | 0.0535 | 6635 | 0.15798 | 1.373 | A02 | TEMW0.05024020
Horizontal Wall | Tempo Wall | TEMW.05024021 | 50 | 240 | 21 | 22 | 6197 | 6197 | 6197 | 0.14755 | 2212 | 0.052667 | 7139 | 0.16998 | 1.485 | A02 | TEMW0.05024021
Horizontal Wall | Tempo Wall | TEMW.05024021/DBE | 50 | 240 | 21 | 22 | 9077 | 9077 | 9077 | 0.21612 | 4539 | 0.10807 | 9985 | 0.23774 | 1 | A02 | TEMW0.05024021/DBE
Horizontal Wall | Tempo Wall | TEMW.05026010 | 50 | 260 | 10 | 12 | 2798 | 2798 | 2798 | 0.066619 | 1072 | 0.025524 | 3193 | 0.076024 | 1.385 | A02 | TEMW0.05026010
Horizontal Wall | Tempo Wall | TEMW.05026011 | 50 | 260 | 11 | 12 | 3604 | 3604 | 3604 | 0.08581 | 1330 | 0.031667 | 4134 | 0.098429 | 1.438 | A02 | TEMW0.05026011
Horizontal Wall | Tempo Wall | TEMW.05026011/DBE | 50 | 260 | 11 | 12 | 5404 | 5404 | 5404 | 0.12867 | 2702 | 0.064333 | 5944 | 0.14152 | 1 | A02 | TEMW0.05026011/DBE
Horizontal Wall | Tempo Wall | TEMW.05026015 | 50 | 260 | 15 | 17 | 4508 | 4508 | 4508 | 0.10733 | 1740 | 0.041429 | 5139 | 0.12236 | 1.373 | A02 | TEMW0.05026015
Horizontal Wall | Tempo Wall | TEMW.05026016 | 50 | 260 | 16 | 17 | 4935 | 4935 | 4935 | 0.1175 | 1786 | 0.042524 | 5675 | 0.13512 | 1.464 | A02 | TEMW0.05026016
Horizontal Wall | Tempo Wall | TEMW.05026016/DBE | 50 | 260 | 16 | 17 | 7815 | 7815 | 7815 | 0.18607 | 3908 | 0.093048 | 8597 | 0.20469 | 1 | A02 | TEMW0.05026016/DBE
Horizontal Wall | Tempo Wall | TEMW.05026020 | 50 | 260 | 20 | 22 | 6305 | 6305 | 6305 | 0.15012 | 2434 | 0.057952 | 7188 | 0.17114 | 1.373 | A02 | TEMW0.05026020
Horizontal Wall | Tempo Wall | TEMW.05026021 | 50 | 260 | 21 | 22 | 6713 | 6713 | 6713 | 0.15983 | 2397 | 0.057071 | 7733 | 0.18412 | 1.485 | A02 | TEMW0.05026021
Horizontal Wall | Tempo Wall | TEMW.05026021/DBE | 50 | 260 | 21 | 22 | 9593 | 9593 | 9593 | 0.2284 | 4797 | 0.11421 | 10552 | 0.25124 | 1 | A02 | TEMW0.05026021/DBE
Horizontal Wall | Tempo Wall | TEMW.05028010 | 50 | 280 | 10 | 12 | 3013 | 3013 | 3013 | 0.071738 | 1154 | 0.027476 | 3438 | 0.081857 | 1.385 | A02 | TEMW0.05028010
Horizontal Wall | Tempo Wall | TEMW.05028011 | 50 | 280 | 11 | 12 | 3881 | 3881 | 3881 | 0.092405 | 1432 | 0.034095 | 4452 | 0.106 | 1.438 | A02 | TEMW0.05028011
Horizontal Wall | Tempo Wall | TEMW.05028011/DBE | 50 | 280 | 11 | 12 | 5681 | 5681 | 5681 | 0.13526 | 2841 | 0.067643 | 6249 | 0.14879 | 1 | A02 | TEMW0.05028011/DBE
Horizontal Wall | Tempo Wall | TEMW.05028015 | 50 | 280 | 15 | 17 | 4855 | 4855 | 4855 | 0.1156 | 1874 | 0.044619 | 5535 | 0.13179 | 1.373 | A02 | TEMW0.05028015
Horizontal Wall | Tempo Wall | TEMW.05028016 | 50 | 280 | 16 | 17 | 5314 | 5314 | 5314 | 0.12652 | 1924 | 0.04581 | 6111 | 0.1455 | 1.464 | A02 | TEMW0.05028016
Horizontal Wall | Tempo Wall | TEMW.05028016/DBE | 50 | 280 | 16 | 17 | 8194 | 8194 | 8194 | 0.1951 | 4097 | 0.097548 | 9013 | 0.2146 | 1 | A02 | TEMW0.05028016/DBE
Horizontal Wall | Tempo Wall | TEMW.05028020 | 50 | 280 | 20 | 22 | 6790 | 6790 | 6790 | 0.16167 | 2621 | 0.062405 | 7741 | 0.18431 | 1.373 | A02 | TEMW0.05028020
Horizontal Wall | Tempo Wall | TEMW.05028021 | 50 | 280 | 21 | 22 | 7230 | 7230 | 7230 | 0.17214 | 2581 | 0.061452 | 8329 | 0.19831 | 1.485 | A02 | TEMW0.05028021
Horizontal Wall | Tempo Wall | TEMW.05028021/DBE | 50 | 280 | 21 | 22 | 10110 | 10110 | 10110 | 0.24071 | 5055 | 0.12036 | 11121 | 0.26479 | 1 | A02 | TEMW0.05028021/DBE
Horizontal Wall | Tempo Wall | TEMW.05030010 | 50 | 300 | 10 | 12 | 3228 | 3228 | 3228 | 0.076857 | 1236 | 0.029429 | 3683 | 0.08769 | 1.385 | A02 | TEMW0.05030010
Horizontal Wall | Tempo Wall | TEMW.05030011 | 50 | 300 | 11 | 12 | 4158 | 4158 | 4158 | 0.099 | 1534 | 0.036524 | 4769 | 0.11355 | 1.438 | A02 | TEMW0.05030011
Horizontal Wall | Tempo Wall | TEMW.05030011/DBE | 50 | 300 | 11 | 12 | 5958 | 5958 | 5958 | 0.14186 | 2979 | 0.070929 | 6554 | 0.15605 | 1 | A02 | TEMW0.05030011/DBE
Horizontal Wall | Tempo Wall | TEMW.05030015 | 50 | 300 | 15 | 17 | 5202 | 5202 | 5202 | 0.12386 | 2008 | 0.04781 | 5930 | 0.14119 | 1.373 | A02 | TEMW0.05030015
Horizontal Wall | Tempo Wall | TEMW.05030016 | 50 | 300 | 16 | 17 | 5694 | 5694 | 5694 | 0.13557 | 2061 | 0.049071 | 6548 | 0.1559 | 1.464 | A02 | TEMW0.05030016
Horizontal Wall | Tempo Wall | TEMW.05030016/DBE | 50 | 300 | 16 | 17 | 8574 | 8574 | 8574 | 0.20414 | 4287 | 0.10207 | 9431 | 0.22455 | 1 | A02 | TEMW0.05030016/DBE
Horizontal Wall | Tempo Wall | TEMW.05030020 | 50 | 300 | 20 | 22 | 7275 | 7275 | 7275 | 0.17321 | 2808 | 0.066857 | 8294 | 0.19748 | 1.373 | A02 | TEMW0.05030020
Horizontal Wall | Tempo Wall | TEMW.05030021 | 50 | 300 | 21 | 22 | 7746 | 7746 | 7746 | 0.18443 | 2765 | 0.065833 | 8923 | 0.21245 | 1.485 | A02 | TEMW0.05030021
Horizontal Wall | Tempo Wall | TEMW.05030021/DBE | 50 | 300 | 21 | 22 | 10626 | 10626 | 10626 | 0.253 | 5313 | 0.1265 | 11689 | 0.27831 | 1 | A02 | TEMW0.05030021/DBE
Horizontal Wall | Tempo Wall | TEMW.06004010 | 60 | 40 | 10 | 12 | 468 | 468 | 468 | 0.011143 | 180 | 0.0042857 | 534 | 0.012714 | 1.376 | A02 | TEMW0.06004010
Horizontal Wall | Tempo Wall | TEMW.06004011 | 60 | 40 | 11 | 12 | 598 | 598 | 598 | 0.014238 | 221 | 0.0052619 | 686 | 0.016333 | 1.437 | A02 | TEMW0.06004011
Horizontal Wall | Tempo Wall | TEMW.06004015 | 60 | 40 | 15 | 17 | 746 | 746 | 746 | 0.017762 | 290 | 0.0069048 | 850 | 0.020238 | 1.361 | A02 | TEMW0.06004015
Horizontal Wall | Tempo Wall | TEMW.06004016 | 60 | 40 | 16 | 17 | 834 | 834 | 834 | 0.019857 | 301 | 0.0071667 | 959 | 0.022833 | 1.468 | A02 | TEMW0.06004016
Horizontal Wall | Tempo Wall | TEMW.06004020 | 60 | 40 | 20 | 22 | 1043 | 1043 | 1043 | 0.024833 | 406 | 0.0096667 | 1188 | 0.028286 | 1.361 | A02 | TEMW0.06004020
Horizontal Wall | Tempo Wall | TEMW.06004021 | 60 | 40 | 21 | 22 | 1153 | 1153 | 1153 | 0.027452 | 409 | 0.0097381 | 1329 | 0.031643 | 1.493 | A02 | TEMW0.06004021
Horizontal Wall | Tempo Wall | TEMW.06005010 | 60 | 50 | 10 | 12 | 585 | 585 | 585 | 0.013929 | 225 | 0.0053571 | 667 | 0.015881 | 1.376 | A02 | TEMW0.06005010
Horizontal Wall | Tempo Wall | TEMW.06005011 | 60 | 50 | 11 | 12 | 747 | 747 | 747 | 0.017786 | 276 | 0.0065714 | 857 | 0.020405 | 1.437 | A02 | TEMW0.06005011
Horizontal Wall | Tempo Wall | TEMW.06005015 | 60 | 50 | 15 | 17 | 933 | 933 | 933 | 0.022214 | 363 | 0.0086429 | 1063 | 0.02531 | 1.361 | A02 | TEMW0.06005015
Horizontal Wall | Tempo Wall | TEMW.06005016 | 60 | 50 | 16 | 17 | 1042 | 1042 | 1042 | 0.02481 | 376 | 0.0089524 | 1198 | 0.028524 | 1.468 | A02 | TEMW0.06005016
Horizontal Wall | Tempo Wall | TEMW.06005020 | 60 | 50 | 20 | 22 | 1304 | 1304 | 1304 | 0.031048 | 507 | 0.012071 | 1485 | 0.035357 | 1.361 | A02 | TEMW0.06005020
Horizontal Wall | Tempo Wall | TEMW.06005021 | 60 | 50 | 21 | 22 | 1441 | 1441 | 1441 | 0.03431 | 512 | 0.01219 | 1661 | 0.039548 | 1.493 | A02 | TEMW0.06005021
Horizontal Wall | Tempo Wall | TEMW.06006010 | 60 | 60 | 10 | 12 | 702 | 702 | 702 | 0.016714 | 270 | 0.0064286 | 800 | 0.019048 | 1.376 | A02 | TEMW0.06006010
Horizontal Wall | Tempo Wall | TEMW.06006011 | 60 | 60 | 11 | 12 | 896 | 896 | 896 | 0.021333 | 331 | 0.007881 | 1028 | 0.024476 | 1.437 | A02 | TEMW0.06006011
Horizontal Wall | Tempo Wall | TEMW.06006011/DBE | 60 | 60 | 11 | 12 | 1196 | 1196 | 1196 | 0.028476 | 598 | 0.014238 | 1316 | 0.031333 | 1 | A02 | TEMW0.06006011/DBE
Horizontal Wall | Tempo Wall | TEMW.06006015 | 60 | 60 | 15 | 17 | 1120 | 1120 | 1120 | 0.026667 | 436 | 0.010381 | 1276 | 0.030381 | 1.361 | A02 | TEMW0.06006015
Horizontal Wall | Tempo Wall | TEMW.06006016 | 60 | 60 | 16 | 17 | 1250 | 1250 | 1250 | 0.029762 | 451 | 0.010738 | 1438 | 0.034238 | 1.468 | A02 | TEMW0.06006016
Horizontal Wall | Tempo Wall | TEMW.06006016/DBE | 60 | 60 | 16 | 17 | 1730 | 1730 | 1730 | 0.04119 | 865 | 0.020595 | 1903 | 0.04531 | 1 | A02 | TEMW0.06006016/DBE
Horizontal Wall | Tempo Wall | TEMW.06006020 | 60 | 60 | 20 | 22 | 1565 | 1565 | 1565 | 0.037262 | 609 | 0.0145 | 1783 | 0.042452 | 1.361 | A02 | TEMW0.06006020
Horizontal Wall | Tempo Wall | TEMW.06006021 | 60 | 60 | 21 | 22 | 1729 | 1729 | 1729 | 0.041167 | 614 | 0.014619 | 1994 | 0.047476 | 1.493 | A02 | TEMW0.06006021
Horizontal Wall | Tempo Wall | TEMW.06006021/DBE | 60 | 60 | 21 | 22 | 2209 | 2209 | 2209 | 0.052595 | 1105 | 0.02631 | 2430 | 0.057857 | 1 | A02 | TEMW0.06006021/DBE
Horizontal Wall | Tempo Wall | TEMW.06007010 | 60 | 70 | 10 | 12 | 819 | 819 | 819 | 0.0195 | 315 | 0.0075 | 934 | 0.022238 | 1.376 | A02 | TEMW0.06007010
Horizontal Wall | Tempo Wall | TEMW.06007011 | 60 | 70 | 11 | 12 | 1046 | 1046 | 1046 | 0.024905 | 386 | 0.0091905 | 1200 | 0.028571 | 1.437 | A02 | TEMW0.06007011
Horizontal Wall | Tempo Wall | TEMW.06007011/DBE | 60 | 70 | 11 | 12 | 1346 | 1346 | 1346 | 0.032048 | 673 | 0.016024 | 1481 | 0.035262 | 1 | A02 | TEMW0.06007011/DBE
Horizontal Wall | Tempo Wall | TEMW.06007015 | 60 | 70 | 15 | 17 | 1306 | 1306 | 1306 | 0.031095 | 508 | 0.012095 | 1488 | 0.035429 | 1.361 | A02 | TEMW0.06007015
Horizontal Wall | Tempo Wall | TEMW.06007016 | 60 | 70 | 16 | 17 | 1459 | 1459 | 1459 | 0.034738 | 527 | 0.012548 | 1678 | 0.039952 | 1.468 | A02 | TEMW0.06007016
Horizontal Wall | Tempo Wall | TEMW.06007016/DBE | 60 | 70 | 16 | 17 | 1939 | 1939 | 1939 | 0.046167 | 970 | 0.023095 | 2133 | 0.050786 | 1 | A02 | TEMW0.06007016/DBE
Horizontal Wall | Tempo Wall | TEMW.06007020 | 60 | 70 | 20 | 22 | 1826 | 1826 | 1826 | 0.043476 | 710 | 0.016905 | 2080 | 0.049524 | 1.361 | A02 | TEMW0.06007020
Horizontal Wall | Tempo Wall | TEMW.06007021 | 60 | 70 | 21 | 22 | 2017 | 2017 | 2017 | 0.048024 | 716 | 0.017048 | 2326 | 0.055381 | 1.493 | A02 | TEMW0.06007021
Horizontal Wall | Tempo Wall | TEMW.06007021/DBE | 60 | 70 | 21 | 22 | 2497 | 2497 | 2497 | 0.059452 | 1249 | 0.029738 | 2747 | 0.065405 | 1 | A02 | TEMW0.06007021/DBE
Horizontal Wall | Tempo Wall | TEMW.06008010 | 60 | 80 | 10 | 12 | 936 | 936 | 936 | 0.022286 | 360 | 0.0085714 | 1067 | 0.025405 | 1.376 | A02 | TEMW0.06008010
Horizontal Wall | Tempo Wall | TEMW.06008011 | 60 | 80 | 11 | 12 | 1195 | 1195 | 1195 | 0.028452 | 441 | 0.0105 | 1371 | 0.032643 | 1.437 | A02 | TEMW0.06008011
Horizontal Wall | Tempo Wall | TEMW.06008011/DBE | 60 | 80 | 11 | 12 | 1495 | 1495 | 1495 | 0.035595 | 748 | 0.01781 | 1645 | 0.039167 | 1 | A02 | TEMW0.06008011/DBE
Horizontal Wall | Tempo Wall | TEMW.06008015 | 60 | 80 | 15 | 17 | 1493 | 1493 | 1493 | 0.035548 | 581 | 0.013833 | 1701 | 0.0405 | 1.361 | A02 | TEMW0.06008015
Horizontal Wall | Tempo Wall | TEMW.06008016 | 60 | 80 | 16 | 17 | 1667 | 1667 | 1667 | 0.03969 | 602 | 0.014333 | 1917 | 0.045643 | 1.468 | A02 | TEMW0.06008016
Horizontal Wall | Tempo Wall | TEMW.06008016/DBE | 60 | 80 | 16 | 17 | 2147 | 2147 | 2147 | 0.051119 | 1074 | 0.025571 | 2362 | 0.056238 | 1 | A02 | TEMW0.06008016/DBE
Horizontal Wall | Tempo Wall | TEMW.06008020 | 60 | 80 | 20 | 22 | 2086 | 2086 | 2086 | 0.049667 | 811 | 0.01931 | 2376 | 0.056571 | 1.361 | A02 | TEMW0.06008020
Horizontal Wall | Tempo Wall | TEMW.06008021 | 60 | 80 | 21 | 22 | 2306 | 2306 | 2306 | 0.054905 | 819 | 0.0195 | 2659 | 0.06331 | 1.493 | A02 | TEMW0.06008021
Horizontal Wall | Tempo Wall | TEMW.06008021/DBE | 60 | 80 | 21 | 22 | 2786 | 2786 | 2786 | 0.066333 | 1393 | 0.033167 | 3065 | 0.072976 | 1 | A02 | TEMW0.06008021/DBE
Horizontal Wall | Tempo Wall | TEMW.06009010 | 60 | 90 | 10 | 12 | 1053 | 1053 | 1053 | 0.025071 | 405 | 0.0096429 | 1200 | 0.028571 | 1.376 | A02 | TEMW0.06009010
Horizontal Wall | Tempo Wall | TEMW.06009011 | 60 | 90 | 11 | 12 | 1345 | 1345 | 1345 | 0.032024 | 496 | 0.01181 | 1543 | 0.036738 | 1.437 | A02 | TEMW0.06009011
Horizontal Wall | Tempo Wall | TEMW.06009011/DBE | 60 | 90 | 11 | 12 | 1945 | 1945 | 1945 | 0.04631 | 973 | 0.023167 | 2140 | 0.050952 | 1 | A02 | TEMW0.06009011/DBE
Horizontal Wall | Tempo Wall | TEMW.06009015 | 60 | 90 | 15 | 17 | 1679 | 1679 | 1679 | 0.039976 | 653 | 0.015548 | 1912 | 0.045524 | 1.361 | A02 | TEMW0.06009015
Horizontal Wall | Tempo Wall | TEMW.06009016 | 60 | 90 | 16 | 17 | 1876 | 1876 | 1876 | 0.044667 | 677 | 0.016119 | 2157 | 0.051357 | 1.468 | A02 | TEMW0.06009016
Horizontal Wall | Tempo Wall | TEMW.06009016/DBE | 60 | 90 | 16 | 17 | 2836 | 2836 | 2836 | 0.067524 | 1418 | 0.033762 | 3120 | 0.074286 | 1 | A02 | TEMW0.06009016/DBE
Horizontal Wall | Tempo Wall | TEMW.06009020 | 60 | 90 | 20 | 22 | 2347 | 2347 | 2347 | 0.055881 | 913 | 0.021738 | 2673 | 0.063643 | 1.361 | A02 | TEMW0.06009020
Horizontal Wall | Tempo Wall | TEMW.06009021 | 60 | 90 | 21 | 22 | 2594 | 2594 | 2594 | 0.061762 | 921 | 0.021929 | 2991 | 0.071214 | 1.493 | A02 | TEMW0.06009021
Horizontal Wall | Tempo Wall | TEMW.06009021/DBE | 60 | 90 | 21 | 22 | 3554 | 3554 | 3554 | 0.084619 | 1777 | 0.04231 | 3909 | 0.093071 | 1 | A02 | TEMW0.06009021/DBE
Horizontal Wall | Tempo Wall | TEMW.06010010 | 60 | 100 | 10 | 12 | 1170 | 1170 | 1170 | 0.027857 | 450 | 0.010714 | 1334 | 0.031762 | 1.376 | A02 | TEMW0.06010010
Horizontal Wall | Tempo Wall | TEMW.06010011 | 60 | 100 | 11 | 12 | 1494 | 1494 | 1494 | 0.035571 | 551 | 0.013119 | 1714 | 0.04081 | 1.437 | A02 | TEMW0.06010011
Horizontal Wall | Tempo Wall | TEMW.06010011/DBE | 60 | 100 | 11 | 12 | 2094 | 2094 | 2094 | 0.049857 | 1047 | 0.024929 | 2303 | 0.054833 | 1 | A02 | TEMW0.06010011/DBE
Horizontal Wall | Tempo Wall | TEMW.06010015 | 60 | 100 | 15 | 17 | 1866 | 1866 | 1866 | 0.044429 | 726 | 0.017286 | 2125 | 0.050595 | 1.361 | A02 | TEMW0.06010015
Horizontal Wall | Tempo Wall | TEMW.06010016 | 60 | 100 | 16 | 17 | 2084 | 2084 | 2084 | 0.049619 | 752 | 0.017905 | 2397 | 0.057071 | 1.468 | A02 | TEMW0.06010016
Horizontal Wall | Tempo Wall | TEMW.06010016/DBE | 60 | 100 | 16 | 17 | 3044 | 3044 | 3044 | 0.072476 | 1522 | 0.036238 | 3348 | 0.079714 | 1 | A02 | TEMW0.06010016/DBE
Horizontal Wall | Tempo Wall | TEMW.06010020 | 60 | 100 | 20 | 22 | 2608 | 2608 | 2608 | 0.062095 | 1015 | 0.024167 | 2971 | 0.070738 | 1.361 | A02 | TEMW0.06010020
Horizontal Wall | Tempo Wall | TEMW.06010021 | 60 | 100 | 21 | 22 | 2882 | 2882 | 2882 | 0.068619 | 1023 | 0.024357 | 3323 | 0.079119 | 1.493 | A02 | TEMW0.06010021
Horizontal Wall | Tempo Wall | TEMW.06010021/DBE | 60 | 100 | 21 | 22 | 3842 | 3842 | 3842 | 0.091476 | 1921 | 0.045738 | 4226 | 0.10062 | 1 | A02 | TEMW0.06010021/DBE
Horizontal Wall | Tempo Wall | TEMW.06011010 | 60 | 110 | 10 | 12 | 1287 | 1287 | 1287 | 0.030643 | 495 | 0.011786 | 1467 | 0.034929 | 1.376 | A02 | TEMW0.06011010
Horizontal Wall | Tempo Wall | TEMW.06011011 | 60 | 110 | 11 | 12 | 1643 | 1643 | 1643 | 0.039119 | 606 | 0.014429 | 1885 | 0.044881 | 1.437 | A02 | TEMW0.06011011
Horizontal Wall | Tempo Wall | TEMW.06011011/DBE | 60 | 110 | 11 | 12 | 2243 | 2243 | 2243 | 0.053405 | 1122 | 0.026714 | 2467 | 0.058738 | 1 | A02 | TEMW0.06011011/DBE
Horizontal Wall | Tempo Wall | TEMW.06011015 | 60 | 110 | 15 | 17 | 2053 | 2053 | 2053 | 0.048881 | 799 | 0.019024 | 2338 | 0.055667 | 1.361 | A02 | TEMW0.06011015
Horizontal Wall | Tempo Wall | TEMW.06011016 | 60 | 110 | 16 | 17 | 2292 | 2292 | 2292 | 0.054571 | 827 | 0.01969 | 2636 | 0.062762 | 1.468 | A02 | TEMW0.06011016
Horizontal Wall | Tempo Wall | TEMW.06011016/DBE | 60 | 110 | 16 | 17 | 3252 | 3252 | 3252 | 0.077429 | 1626 | 0.038714 | 3577 | 0.085167 | 1 | A02 | TEMW0.06011016/DBE
Horizontal Wall | Tempo Wall | TEMW.06011020 | 60 | 110 | 20 | 22 | 2869 | 2869 | 2869 | 0.06831 | 1116 | 0.026571 | 3268 | 0.07781 | 1.361 | A02 | TEMW0.06011020
Horizontal Wall | Tempo Wall | TEMW.06011021 | 60 | 110 | 21 | 22 | 3170 | 3170 | 3170 | 0.075476 | 1125 | 0.026786 | 3655 | 0.087024 | 1.493 | A02 | TEMW0.06011021
Horizontal Wall | Tempo Wall | TEMW.06011021/DBE | 60 | 110 | 21 | 22 | 4130 | 4130 | 4130 | 0.098333 | 2065 | 0.049167 | 4543 | 0.10817 | 1 | A02 | TEMW0.06011021/DBE
Horizontal Wall | Tempo Wall | TEMW.06012010 | 60 | 120 | 10 | 12 | 1404 | 1404 | 1404 | 0.033429 | 541 | 0.012881 | 1601 | 0.038119 | 1.376 | A02 | TEMW0.06012010
Horizontal Wall | Tempo Wall | TEMW.06012011 | 60 | 120 | 11 | 12 | 1793 | 1793 | 1793 | 0.04269 | 662 | 0.015762 | 2057 | 0.048976 | 1.437 | A02 | TEMW0.06012011
Horizontal Wall | Tempo Wall | TEMW.06012011/DBE | 60 | 120 | 11 | 12 | 2393 | 2393 | 2393 | 0.056976 | 1197 | 0.0285 | 2632 | 0.062667 | 1 | A02 | TEMW0.06012011/DBE
Horizontal Wall | Tempo Wall | TEMW.06012015 | 60 | 120 | 15 | 17 | 2239 | 2239 | 2239 | 0.05331 | 871 | 0.020738 | 2550 | 0.060714 | 1.361 | A02 | TEMW0.06012015
Horizontal Wall | Tempo Wall | TEMW.06012016 | 60 | 120 | 16 | 17 | 2501 | 2501 | 2501 | 0.059548 | 903 | 0.0215 | 2876 | 0.068476 | 1.468 | A02 | TEMW0.06012016
Horizontal Wall | Tempo Wall | TEMW.06012016/DBE | 60 | 120 | 16 | 17 | 3461 | 3461 | 3461 | 0.082405 | 1731 | 0.041214 | 3807 | 0.090643 | 1 | A02 | TEMW0.06012016/DBE
Horizontal Wall | Tempo Wall | TEMW.06012020 | 60 | 120 | 20 | 22 | 3130 | 3130 | 3130 | 0.074524 | 1218 | 0.029 | 3565 | 0.084881 | 1.361 | A02 | TEMW0.06012020
Horizontal Wall | Tempo Wall | TEMW.06012021 | 60 | 120 | 21 | 22 | 3458 | 3458 | 3458 | 0.082333 | 1228 | 0.029238 | 3987 | 0.094929 | 1.493 | A02 | TEMW0.06012021
Horizontal Wall | Tempo Wall | TEMW.06012021/DBE | 60 | 120 | 21 | 22 | 4418 | 4418 | 4418 | 0.10519 | 2209 | 0.052595 | 4860 | 0.11571 | 1 | A02 | TEMW0.06012021/DBE
Horizontal Wall | Tempo Wall | TEMW.06014010 | 60 | 140 | 10 | 12 | 1638 | 1638 | 1638 | 0.039 | 631 | 0.015024 | 1867 | 0.044452 | 1.376 | A02 | TEMW0.06014010
Horizontal Wall | Tempo Wall | TEMW.06014011 | 60 | 140 | 11 | 12 | 2092 | 2092 | 2092 | 0.04981 | 772 | 0.018381 | 2400 | 0.057143 | 1.437 | A02 | TEMW0.06014011
Horizontal Wall | Tempo Wall | TEMW.06014011/DBE | 60 | 140 | 11 | 12 | 2692 | 2692 | 2692 | 0.064095 | 1346 | 0.032048 | 2961 | 0.0705 | 1 | A02 | TEMW0.06014011/DBE
Horizontal Wall | Tempo Wall | TEMW.06014015 | 60 | 140 | 15 | 17 | 2612 | 2612 | 2612 | 0.06219 | 1016 | 0.02419 | 2975 | 0.070833 | 1.361 | A02 | TEMW0.06014015
Horizontal Wall | Tempo Wall | TEMW.06014016 | 60 | 140 | 16 | 17 | 2918 | 2918 | 2918 | 0.069476 | 1053 | 0.025071 | 3356 | 0.079905 | 1.468 | A02 | TEMW0.06014016
Horizontal Wall | Tempo Wall | TEMW.06014016/DBE | 60 | 140 | 16 | 17 | 3878 | 3878 | 3878 | 0.092333 | 1939 | 0.046167 | 4266 | 0.10157 | 1 | A02 | TEMW0.06014016/DBE
Horizontal Wall | Tempo Wall | TEMW.06014020 | 60 | 140 | 20 | 22 | 3651 | 3651 | 3651 | 0.086929 | 1420 | 0.03381 | 4158 | 0.099 | 1.361 | A02 | TEMW0.06014020
Horizontal Wall | Tempo Wall | TEMW.06014021 | 60 | 140 | 21 | 22 | 4035 | 4035 | 4035 | 0.096071 | 1432 | 0.034095 | 4652 | 0.11076 | 1.493 | A02 | TEMW0.06014021
Horizontal Wall | Tempo Wall | TEMW.06014021/DBE | 60 | 140 | 21 | 22 | 4995 | 4995 | 4995 | 0.11893 | 2498 | 0.059476 | 5495 | 0.13083 | 1 | A02 | TEMW0.06014021/DBE
Horizontal Wall | Tempo Wall | TEMW.06016010 | 60 | 160 | 10 | 12 | 1872 | 1872 | 1872 | 0.044571 | 721 | 0.017167 | 2134 | 0.05081 | 1.376 | A02 | TEMW0.06016010
Horizontal Wall | Tempo Wall | TEMW.06016011 | 60 | 160 | 11 | 12 | 2390 | 2390 | 2390 | 0.056905 | 882 | 0.021 | 2741 | 0.065262 | 1.437 | A02 | TEMW0.06016011
Horizontal Wall | Tempo Wall | TEMW.06016011/DBE | 60 | 160 | 11 | 12 | 3590 | 3590 | 3590 | 0.085476 | 1795 | 0.042738 | 3949 | 0.094024 | 1 | A02 | TEMW0.06016011/DBE
Horizontal Wall | Tempo Wall | TEMW.06016015 | 60 | 160 | 15 | 17 | 2986 | 2986 | 2986 | 0.071095 | 1162 | 0.027667 | 3401 | 0.080976 | 1.361 | A02 | TEMW0.06016015
Horizontal Wall | Tempo Wall | TEMW.06016016 | 60 | 160 | 16 | 17 | 3334 | 3334 | 3334 | 0.079381 | 1204 | 0.028667 | 3834 | 0.091286 | 1.468 | A02 | TEMW0.06016016
Horizontal Wall | Tempo Wall | TEMW.06016016/DBE | 60 | 160 | 16 | 17 | 5254 | 5254 | 5254 | 0.1251 | 2627 | 0.062548 | 5779 | 0.1376 | 1 | A02 | TEMW0.06016016/DBE
Horizontal Wall | Tempo Wall | TEMW.06016020 | 60 | 160 | 20 | 22 | 4173 | 4173 | 4173 | 0.099357 | 1623 | 0.038643 | 4753 | 0.11317 | 1.361 | A02 | TEMW0.06016020
Horizontal Wall | Tempo Wall | TEMW.06016021 | 60 | 160 | 21 | 22 | 4611 | 4611 | 4611 | 0.10979 | 1637 | 0.038976 | 5316 | 0.12657 | 1.493 | A02 | TEMW0.06016021
Horizontal Wall | Tempo Wall | TEMW.06016021/DBE | 60 | 160 | 21 | 22 | 6531 | 6531 | 6531 | 0.1555 | 3266 | 0.077762 | 7184 | 0.17105 | 1 | A02 | TEMW0.06016021/DBE
Horizontal Wall | Tempo Wall | TEMW.06018010 | 60 | 180 | 10 | 12 | 2106 | 2106 | 2106 | 0.050143 | 811 | 0.01931 | 2401 | 0.057167 | 1.376 | A02 | TEMW0.06018010
Horizontal Wall | Tempo Wall | TEMW.06018011 | 60 | 180 | 11 | 12 | 2689 | 2689 | 2689 | 0.064024 | 992 | 0.023619 | 3084 | 0.073429 | 1.437 | A02 | TEMW0.06018011
Horizontal Wall | Tempo Wall | TEMW.06018011/DBE | 60 | 180 | 11 | 12 | 3889 | 3889 | 3889 | 0.092595 | 1945 | 0.04631 | 4278 | 0.10186 | 1 | A02 | TEMW0.06018011/DBE
Horizontal Wall | Tempo Wall | TEMW.06018015 | 60 | 180 | 15 | 17 | 3359 | 3359 | 3359 | 0.079976 | 1307 | 0.031119 | 3826 | 0.091095 | 1.361 | A02 | TEMW0.06018015
Horizontal Wall | Tempo Wall | TEMW.06018016 | 60 | 180 | 16 | 17 | 3751 | 3751 | 3751 | 0.08931 | 1354 | 0.032238 | 4314 | 0.10271 | 1.468 | A02 | TEMW0.06018016
Horizontal Wall | Tempo Wall | TEMW.06018016/DBE | 60 | 180 | 16 | 17 | 5671 | 5671 | 5671 | 0.13502 | 2836 | 0.067524 | 6238 | 0.14852 | 1 | A02 | TEMW0.06018016/DBE
Horizontal Wall | Tempo Wall | TEMW.06018020 | 60 | 180 | 20 | 22 | 4694 | 4694 | 4694 | 0.11176 | 1826 | 0.043476 | 5346 | 0.12729 | 1.361 | A02 | TEMW0.06018020
Horizontal Wall | Tempo Wall | TEMW.06018021 | 60 | 180 | 21 | 22 | 5188 | 5188 | 5188 | 0.12352 | 1842 | 0.043857 | 5982 | 0.14243 | 1.493 | A02 | TEMW0.06018021
Horizontal Wall | Tempo Wall | TEMW.06018021/DBE | 60 | 180 | 21 | 22 | 7108 | 7108 | 7108 | 0.16924 | 3554 | 0.084619 | 7819 | 0.18617 | 1 | A02 | TEMW0.06018021/DBE
Horizontal Wall | Tempo Wall | TEMW.06020010 | 60 | 200 | 10 | 12 | 2340 | 2340 | 2340 | 0.055714 | 901 | 0.021452 | 2668 | 0.063524 | 1.376 | A02 | TEMW0.06020010
Horizontal Wall | Tempo Wall | TEMW.06020011 | 60 | 200 | 11 | 12 | 2988 | 2988 | 2988 | 0.071143 | 1103 | 0.026262 | 3427 | 0.081595 | 1.437 | A02 | TEMW0.06020011
Horizontal Wall | Tempo Wall | TEMW.06020011/DBE | 60 | 200 | 11 | 12 | 4188 | 4188 | 4188 | 0.099714 | 2094 | 0.049857 | 4607 | 0.10969 | 1 | A02 | TEMW0.06020011/DBE
Horizontal Wall | Tempo Wall | TEMW.06020015 | 60 | 200 | 15 | 17 | 3732 | 3732 | 3732 | 0.088857 | 1452 | 0.034571 | 4251 | 0.10121 | 1.361 | A02 | TEMW0.06020015
Horizontal Wall | Tempo Wall | TEMW.06020016 | 60 | 200 | 16 | 17 | 4168 | 4168 | 4168 | 0.099238 | 1505 | 0.035833 | 4793 | 0.11412 | 1.468 | A02 | TEMW0.06020016
Horizontal Wall | Tempo Wall | TEMW.06020016/DBE | 60 | 200 | 16 | 17 | 6088 | 6088 | 6088 | 0.14495 | 3044 | 0.072476 | 6697 | 0.15945 | 1 | A02 | TEMW0.06020016/DBE
Horizontal Wall | Tempo Wall | TEMW.06020020 | 60 | 200 | 20 | 22 | 5216 | 5216 | 5216 | 0.12419 | 2029 | 0.04831 | 5941 | 0.14145 | 1.361 | A02 | TEMW0.06020020
Horizontal Wall | Tempo Wall | TEMW.06020021 | 60 | 200 | 21 | 22 | 5764 | 5764 | 5764 | 0.13724 | 2046 | 0.048714 | 6646 | 0.15824 | 1.493 | A02 | TEMW0.06020021
Horizontal Wall | Tempo Wall | TEMW.06020021/DBE | 60 | 200 | 21 | 22 | 7684 | 7684 | 7684 | 0.18295 | 3842 | 0.091476 | 8452 | 0.20124 | 1 | A02 | TEMW0.06020021/DBE
Horizontal Wall | Tempo Wall | TEMW.06022010 | 60 | 220 | 10 | 12 | 2574 | 2574 | 2574 | 0.061286 | 991 | 0.023595 | 2934 | 0.069857 | 1.376 | A02 | TEMW0.06022010
Horizontal Wall | Tempo Wall | TEMW.06022011 | 60 | 220 | 11 | 12 | 3287 | 3287 | 3287 | 0.078262 | 1213 | 0.028881 | 3770 | 0.089762 | 1.437 | A02 | TEMW0.06022011
Horizontal Wall | Tempo Wall | TEMW.06022011/DBE | 60 | 220 | 11 | 12 | 4487 | 4487 | 4487 | 0.10683 | 2244 | 0.053429 | 4936 | 0.11752 | 1 | A02 | TEMW0.06022011/DBE
Horizontal Wall | Tempo Wall | TEMW.06022015 | 60 | 220 | 15 | 17 | 4105 | 4105 | 4105 | 0.097738 | 1597 | 0.038024 | 4676 | 0.11133 | 1.361 | A02 | TEMW0.06022015
Horizontal Wall | Tempo Wall | TEMW.06022016 | 60 | 220 | 16 | 17 | 4585 | 4585 | 4585 | 0.10917 | 1655 | 0.039405 | 5273 | 0.12555 | 1.468 | A02 | TEMW0.06022016
Horizontal Wall | Tempo Wall | TEMW.06022016/DBE | 60 | 220 | 16 | 17 | 6505 | 6505 | 6505 | 0.15488 | 3253 | 0.077452 | 7156 | 0.17038 | 1 | A02 | TEMW0.06022016/DBE
Horizontal Wall | Tempo Wall | TEMW.06022020 | 60 | 220 | 20 | 22 | 5738 | 5738 | 5738 | 0.13662 | 2232 | 0.053143 | 6536 | 0.15562 | 1.361 | A02 | TEMW0.06022020
Horizontal Wall | Tempo Wall | TEMW.06022021 | 60 | 220 | 21 | 22 | 6340 | 6340 | 6340 | 0.15095 | 2251 | 0.053595 | 7310 | 0.17405 | 1.493 | A02 | TEMW0.06022021
Horizontal Wall | Tempo Wall | TEMW.06022021/DBE | 60 | 220 | 21 | 22 | 8260 | 8260 | 8260 | 0.19667 | 4130 | 0.098333 | 9086 | 0.21633 | 1 | A02 | TEMW0.06022021/DBE
Horizontal Wall | Tempo Wall | TEMW.06024010 | 60 | 240 | 10 | 12 | 2808 | 2808 | 2808 | 0.066857 | 1081 | 0.025738 | 3201 | 0.076214 | 1.376 | A02 | TEMW0.06024010
Horizontal Wall | Tempo Wall | TEMW.06024011 | 60 | 240 | 11 | 12 | 3586 | 3586 | 3586 | 0.085381 | 1323 | 0.0315 | 4113 | 0.097929 | 1.437 | A02 | TEMW0.06024011
Horizontal Wall | Tempo Wall | TEMW.06024011/DBE | 60 | 240 | 11 | 12 | 5386 | 5386 | 5386 | 0.12824 | 2693 | 0.064119 | 5925 | 0.14107 | 1 | A02 | TEMW0.06024011/DBE
Horizontal Wall | Tempo Wall | TEMW.06024015 | 60 | 240 | 15 | 17 | 4478 | 4478 | 4478 | 0.10662 | 1742 | 0.041476 | 5100 | 0.12143 | 1.361 | A02 | TEMW0.06024015
Horizontal Wall | Tempo Wall | TEMW.06024016 | 60 | 240 | 16 | 17 | 5002 | 5002 | 5002 | 0.1191 | 1806 | 0.043 | 5752 | 0.13695 | 1.468 | A02 | TEMW0.06024016
Horizontal Wall | Tempo Wall | TEMW.06024016/DBE | 60 | 240 | 16 | 17 | 7882 | 7882 | 7882 | 0.18767 | 3941 | 0.093833 | 8670 | 0.20643 | 1 | A02 | TEMW0.06024016/DBE
Horizontal Wall | Tempo Wall | TEMW.06024020 | 60 | 240 | 20 | 22 | 6259 | 6259 | 6259 | 0.14902 | 2435 | 0.057976 | 7129 | 0.16974 | 1.361 | A02 | TEMW0.06024020
Horizontal Wall | Tempo Wall | TEMW.06024021 | 60 | 240 | 21 | 22 | 6917 | 6917 | 6917 | 0.16469 | 2456 | 0.058476 | 7975 | 0.18988 | 1.493 | A02 | TEMW0.06024021
Horizontal Wall | Tempo Wall | TEMW.06024021/DBE | 60 | 240 | 21 | 22 | 9797 | 9797 | 9797 | 0.23326 | 4899 | 0.11664 | 10777 | 0.2566 | 1 | A02 | TEMW0.06024021/DBE
Horizontal Wall | Tempo Wall | TEMW.06026010 | 60 | 260 | 10 | 12 | 3042 | 3042 | 3042 | 0.072429 | 1171 | 0.027881 | 3468 | 0.082571 | 1.376 | A02 | TEMW0.06026010
Horizontal Wall | Tempo Wall | TEMW.06026011 | 60 | 260 | 11 | 12 | 3884 | 3884 | 3884 | 0.092476 | 1433 | 0.034119 | 4455 | 0.10607 | 1.437 | A02 | TEMW0.06026011
Horizontal Wall | Tempo Wall | TEMW.06026011/DBE | 60 | 260 | 11 | 12 | 5684 | 5684 | 5684 | 0.13533 | 2842 | 0.067667 | 6252 | 0.14886 | 1 | A02 | TEMW0.06026011/DBE
Horizontal Wall | Tempo Wall | TEMW.06026015 | 60 | 260 | 15 | 17 | 4852 | 4852 | 4852 | 0.11552 | 1887 | 0.044929 | 5526 | 0.13157 | 1.361 | A02 | TEMW0.06026015
Horizontal Wall | Tempo Wall | TEMW.06026016 | 60 | 260 | 16 | 17 | 5418 | 5418 | 5418 | 0.129 | 1956 | 0.046571 | 6231 | 0.14836 | 1.468 | A02 | TEMW0.06026016
Horizontal Wall | Tempo Wall | TEMW.06026016/DBE | 60 | 260 | 16 | 17 | 8298 | 8298 | 8298 | 0.19757 | 4149 | 0.098786 | 9128 | 0.21733 | 1 | A02 | TEMW0.06026016/DBE
Horizontal Wall | Tempo Wall | TEMW.06026020 | 60 | 260 | 20 | 22 | 6781 | 6781 | 6781 | 0.16145 | 2638 | 0.06281 | 7724 | 0.1839 | 1.361 | A02 | TEMW0.06026020
Horizontal Wall | Tempo Wall | TEMW.06026021 | 60 | 260 | 21 | 22 | 7493 | 7493 | 7493 | 0.1784 | 2660 | 0.063333 | 8639 | 0.20569 | 1.493 | A02 | TEMW0.06026021
Horizontal Wall | Tempo Wall | TEMW.06026021/DBE | 60 | 260 | 21 | 22 | 10373 | 10373 | 10373 | 0.24698 | 5187 | 0.1235 | 11410 | 0.27167 | 1 | A02 | TEMW0.06026021/DBE
Horizontal Wall | Tempo Wall | TEMW.06028010 | 60 | 280 | 10 | 12 | 3276 | 3276 | 3276 | 0.078 | 1261 | 0.030024 | 3735 | 0.088929 | 1.376 | A02 | TEMW0.06028010
Horizontal Wall | Tempo Wall | TEMW.06028011 | 60 | 280 | 11 | 12 | 4183 | 4183 | 4183 | 0.099595 | 1544 | 0.036762 | 4798 | 0.11424 | 1.437 | A02 | TEMW0.06028011
Horizontal Wall | Tempo Wall | TEMW.06028011/DBE | 60 | 280 | 11 | 12 | 5983 | 5983 | 5983 | 0.14245 | 2992 | 0.071238 | 6581 | 0.15669 | 1 | A02 | TEMW0.06028011/DBE
Horizontal Wall | Tempo Wall | TEMW.06028015 | 60 | 280 | 15 | 17 | 5225 | 5225 | 5225 | 0.1244 | 2033 | 0.048405 | 5951 | 0.14169 | 1.361 | A02 | TEMW0.06028015
Horizontal Wall | Tempo Wall | TEMW.06028016 | 60 | 280 | 16 | 17 | 5835 | 5835 | 5835 | 0.13893 | 2106 | 0.050143 | 6710 | 0.15976 | 1.468 | A02 | TEMW0.06028016
Horizontal Wall | Tempo Wall | TEMW.06028016/DBE | 60 | 280 | 16 | 17 | 8715 | 8715 | 8715 | 0.2075 | 4358 | 0.10376 | 9587 | 0.22826 | 1 | A02 | TEMW0.06028016/DBE
Horizontal Wall | Tempo Wall | TEMW.06028020 | 60 | 280 | 20 | 22 | 7302 | 7302 | 7302 | 0.17386 | 2840 | 0.067619 | 8317 | 0.19802 | 1.361 | A02 | TEMW0.06028020
Horizontal Wall | Tempo Wall | TEMW.06028021 | 60 | 280 | 21 | 22 | 8070 | 8070 | 8070 | 0.19214 | 2865 | 0.068214 | 9305 | 0.22155 | 1.493 | A02 | TEMW0.06028021
Horizontal Wall | Tempo Wall | TEMW.06028021/DBE | 60 | 280 | 21 | 22 | 10950 | 10950 | 10950 | 0.26071 | 5475 | 0.13036 | 12045 | 0.28679 | 1 | A02 | TEMW0.06028021/DBE
Horizontal Wall | Tempo Wall | TEMW.06030010 | 60 | 300 | 10 | 12 | 3510 | 3510 | 3510 | 0.083571 | 1351 | 0.032167 | 4001 | 0.095262 | 1.376 | A02 | TEMW0.06030010
Horizontal Wall | Tempo Wall | TEMW.06030011 | 60 | 300 | 11 | 12 | 4482 | 4482 | 4482 | 0.10671 | 1654 | 0.039381 | 5141 | 0.1224 | 1.437 | A02 | TEMW0.06030011
Horizontal Wall | Tempo Wall | TEMW.06030011/DBE | 60 | 300 | 11 | 12 | 6282 | 6282 | 6282 | 0.14957 | 3141 | 0.074786 | 6910 | 0.16452 | 1 | A02 | TEMW0.06030011/DBE
Horizontal Wall | Tempo Wall | TEMW.06030015 | 60 | 300 | 15 | 17 | 5598 | 5598 | 5598 | 0.13329 | 2178 | 0.051857 | 6376 | 0.15181 | 1.361 | A02 | TEMW0.06030015
Horizontal Wall | Tempo Wall | TEMW.06030016 | 60 | 300 | 16 | 17 | 6252 | 6252 | 6252 | 0.14886 | 2257 | 0.053738 | 7190 | 0.17119 | 1.468 | A02 | TEMW0.06030016
Horizontal Wall | Tempo Wall | TEMW.06030016/DBE | 60 | 300 | 16 | 17 | 9132 | 9132 | 9132 | 0.21743 | 4566 | 0.10871 | 10045 | 0.23917 | 1 | A02 | TEMW0.06030016/DBE
Horizontal Wall | Tempo Wall | TEMW.06030020 | 60 | 300 | 20 | 22 | 7824 | 7824 | 7824 | 0.18629 | 3044 | 0.072476 | 8912 | 0.21219 | 1.361 | A02 | TEMW0.06030020
Horizontal Wall | Tempo Wall | TEMW.06030021 | 60 | 300 | 21 | 22 | 8646 | 8646 | 8646 | 0.20586 | 3069 | 0.073071 | 9969 | 0.23736 | 1.493 | A02 | TEMW0.06030021
Horizontal Wall | Tempo Wall | TEMW.06030021/DBE | 60 | 300 | 21 | 22 | 11526 | 11526 | 11526 | 0.27443 | 5763 | 0.13721 | 12679 | 0.30188 | 1 | A02 | TEMW0.06030021/DBE
Horizontal Wall | Tempo Wall | TEMW.07004010 | 70 | 40 | 10 | 12 | 499 | 499 | 499 | 0.011881 | 194 | 0.004619 | 568 | 0.013524 | 1.366 | A02 | TEMW0.07004010
Horizontal Wall | Tempo Wall | TEMW.07004011 | 70 | 40 | 11 | 12 | 636 | 636 | 636 | 0.015143 | 235 | 0.0055952 | 729 | 0.017357 | 1.436 | A02 | TEMW0.07004011
Horizontal Wall | Tempo Wall | TEMW.07004015 | 70 | 40 | 15 | 17 | 789 | 789 | 789 | 0.018786 | 309 | 0.0073571 | 897 | 0.021357 | 1.35 | A02 | TEMW0.07004015
Horizontal Wall | Tempo Wall | TEMW.07004016 | 70 | 40 | 16 | 17 | 904 | 904 | 904 | 0.021524 | 325 | 0.0077381 | 1041 | 0.024786 | 1.472 | A02 | TEMW0.07004016
Horizontal Wall | Tempo Wall | TEMW.07004020 | 70 | 40 | 20 | 22 | 1101 | 1101 | 1101 | 0.026214 | 433 | 0.01031 | 1252 | 0.02981 | 1.349 | A02 | TEMW0.07004020
Horizontal Wall | Tempo Wall | TEMW.07004021 | 70 | 40 | 21 | 22 | 1271 | 1271 | 1271 | 0.030262 | 449 | 0.01069 | 1467 | 0.034929 | 1.501 | A02 | TEMW0.07004021
Horizontal Wall | Tempo Wall | TEMW.07005010 | 70 | 50 | 10 | 12 | 624 | 624 | 624 | 0.014857 | 242 | 0.0057619 | 711 | 0.016929 | 1.366 | A02 | TEMW0.07005010
Horizontal Wall | Tempo Wall | TEMW.07005011 | 70 | 50 | 11 | 12 | 795 | 795 | 795 | 0.018929 | 294 | 0.007 | 912 | 0.021714 | 1.436 | A02 | TEMW0.07005011
Horizontal Wall | Tempo Wall | TEMW.07005015 | 70 | 50 | 15 | 17 | 986 | 986 | 986 | 0.023476 | 387 | 0.0092143 | 1121 | 0.02669 | 1.35 | A02 | TEMW0.07005015
Horizontal Wall | Tempo Wall | TEMW.07005016 | 70 | 50 | 16 | 17 | 1130 | 1130 | 1130 | 0.026905 | 407 | 0.0096905 | 1301 | 0.030976 | 1.472 | A02 | TEMW0.07005016
Horizontal Wall | Tempo Wall | TEMW.07005020 | 70 | 50 | 20 | 22 | 1377 | 1377 | 1377 | 0.032786 | 541 | 0.012881 | 1566 | 0.037286 | 1.349 | A02 | TEMW0.07005020
Horizontal Wall | Tempo Wall | TEMW.07005021 | 70 | 50 | 21 | 22 | 1589 | 1589 | 1589 | 0.037833 | 561 | 0.013357 | 1834 | 0.043667 | 1.501 | A02 | TEMW0.07005021
Horizontal Wall | Tempo Wall | TEMW.07006010 | 70 | 60 | 10 | 12 | 749 | 749 | 749 | 0.017833 | 291 | 0.0069286 | 853 | 0.02031 | 1.366 | A02 | TEMW0.07006010
Horizontal Wall | Tempo Wall | TEMW.07006011 | 70 | 60 | 11 | 12 | 954 | 954 | 954 | 0.022714 | 353 | 0.0084048 | 1094 | 0.026048 | 1.436 | A02 | TEMW0.07006011
Horizontal Wall | Tempo Wall | TEMW.07006011/DBE | 70 | 60 | 11 | 12 | 1254 | 1254 | 1254 | 0.029857 | 627 | 0.014929 | 1379 | 0.032833 | 1 | A02 | TEMW0.07006011/DBE
Horizontal Wall | Tempo Wall | TEMW.07006015 | 70 | 60 | 15 | 17 | 1183 | 1183 | 1183 | 0.028167 | 464 | 0.011048 | 1345 | 0.032024 | 1.35 | A02 | TEMW0.07006015
Horizontal Wall | Tempo Wall | TEMW.07006016 | 70 | 60 | 16 | 17 | 1356 | 1356 | 1356 | 0.032286 | 488 | 0.011619 | 1561 | 0.037167 | 1.472 | A02 | TEMW0.07006016
Horizontal Wall | Tempo Wall | TEMW.07006016/DBE | 70 | 60 | 16 | 17 | 1836 | 1836 | 1836 | 0.043714 | 918 | 0.021857 | 2020 | 0.048095 | 1 | A02 | TEMW0.07006016/DBE
Horizontal Wall | Tempo Wall | TEMW.07006020 | 70 | 60 | 20 | 22 | 1652 | 1652 | 1652 | 0.039333 | 649 | 0.015452 | 1878 | 0.044714 | 1.349 | A02 | TEMW0.07006020
Horizontal Wall | Tempo Wall | TEMW.07006021 | 70 | 60 | 21 | 22 | 1906 | 1906 | 1906 | 0.045381 | 673 | 0.016024 | 2200 | 0.052381 | 1.501 | A02 | TEMW0.07006021
Horizontal Wall | Tempo Wall | TEMW.07006021/DBE | 70 | 60 | 21 | 22 | 2386 | 2386 | 2386 | 0.05681 | 1193 | 0.028405 | 2625 | 0.0625 | 1 | A02 | TEMW0.07006021/DBE
Horizontal Wall | Tempo Wall | TEMW.07007010 | 70 | 70 | 10 | 12 | 874 | 874 | 874 | 0.02081 | 339 | 0.0080714 | 995 | 0.02369 | 1.366 | A02 | TEMW0.07007010
Horizontal Wall | Tempo Wall | TEMW.07007011 | 70 | 70 | 11 | 12 | 1113 | 1113 | 1113 | 0.0265 | 412 | 0.0098095 | 1277 | 0.030405 | 1.436 | A02 | TEMW0.07007011
Horizontal Wall | Tempo Wall | TEMW.07007011/DBE | 70 | 70 | 11 | 12 | 1413 | 1413 | 1413 | 0.033643 | 707 | 0.016833 | 1554 | 0.037 | 1 | A02 | TEMW0.07007011/DBE
Horizontal Wall | Tempo Wall | TEMW.07007015 | 70 | 70 | 15 | 17 | 1380 | 1380 | 1380 | 0.032857 | 541 | 0.012881 | 1569 | 0.037357 | 1.35 | A02 | TEMW0.07007015
Horizontal Wall | Tempo Wall | TEMW.07007016 | 70 | 70 | 16 | 17 | 1582 | 1582 | 1582 | 0.037667 | 570 | 0.013571 | 1821 | 0.043357 | 1.472 | A02 | TEMW0.07007016
Horizontal Wall | Tempo Wall | TEMW.07007016/DBE | 70 | 70 | 16 | 17 | 2062 | 2062 | 2062 | 0.049095 | 1031 | 0.024548 | 2268 | 0.054 | 1 | A02 | TEMW0.07007016/DBE
Horizontal Wall | Tempo Wall | TEMW.07007020 | 70 | 70 | 20 | 22 | 1927 | 1927 | 1927 | 0.045881 | 757 | 0.018024 | 2191 | 0.052167 | 1.349 | A02 | TEMW0.07007020
Horizontal Wall | Tempo Wall | TEMW.07007021 | 70 | 70 | 21 | 22 | 2224 | 2224 | 2224 | 0.052952 | 785 | 0.01869 | 2566 | 0.061095 | 1.501 | A02 | TEMW0.07007021
Horizontal Wall | Tempo Wall | TEMW.07007021/DBE | 70 | 70 | 21 | 22 | 2704 | 2704 | 2704 | 0.064381 | 1352 | 0.03219 | 2974 | 0.07081 | 1 | A02 | TEMW0.07007021/DBE
Horizontal Wall | Tempo Wall | TEMW.07008010 | 70 | 80 | 10 | 12 | 998 | 998 | 998 | 0.023762 | 387 | 0.0092143 | 1137 | 0.027071 | 1.366 | A02 | TEMW0.07008010
Horizontal Wall | Tempo Wall | TEMW.07008011 | 70 | 80 | 11 | 12 | 1272 | 1272 | 1272 | 0.030286 | 471 | 0.011214 | 1459 | 0.034738 | 1.436 | A02 | TEMW0.07008011
Horizontal Wall | Tempo Wall | TEMW.07008011/DBE | 70 | 80 | 11 | 12 | 1572 | 1572 | 1572 | 0.037429 | 786 | 0.018714 | 1729 | 0.041167 | 1 | A02 | TEMW0.07008011/DBE
Horizontal Wall | Tempo Wall | TEMW.07008015 | 70 | 80 | 15 | 17 | 1578 | 1578 | 1578 | 0.037571 | 619 | 0.014738 | 1794 | 0.042714 | 1.35 | A02 | TEMW0.07008015
Horizontal Wall | Tempo Wall | TEMW.07008016 | 70 | 80 | 16 | 17 | 1808 | 1808 | 1808 | 0.043048 | 651 | 0.0155 | 2081 | 0.049548 | 1.472 | A02 | TEMW0.07008016
Horizontal Wall | Tempo Wall | TEMW.07008016/DBE | 70 | 80 | 16 | 17 | 2288 | 2288 | 2288 | 0.054476 | 1144 | 0.027238 | 2517 | 0.059929 | 1 | A02 | TEMW0.07008016/DBE
Horizontal Wall | Tempo Wall | TEMW.07008020 | 70 | 80 | 20 | 22 | 2202 | 2202 | 2202 | 0.052429 | 865 | 0.020595 | 2504 | 0.059619 | 1.349 | A02 | TEMW0.07008020
Horizontal Wall | Tempo Wall | TEMW.07008021 | 70 | 80 | 21 | 22 | 2542 | 2542 | 2542 | 0.060524 | 897 | 0.021357 | 2933 | 0.069833 | 1.501 | A02 | TEMW0.07008021
Horizontal Wall | Tempo Wall | TEMW.07008021/DBE | 70 | 80 | 21 | 22 | 3022 | 3022 | 3022 | 0.071952 | 1511 | 0.035976 | 3324 | 0.079143 | 1 | A02 | TEMW0.07008021/DBE
Horizontal Wall | Tempo Wall | TEMW.07009010 | 70 | 90 | 10 | 12 | 1123 | 1123 | 1123 | 0.026738 | 436 | 0.010381 | 1279 | 0.030452 | 1.366 | A02 | TEMW0.07009010
Horizontal Wall | Tempo Wall | TEMW.07009011 | 70 | 90 | 11 | 12 | 1431 | 1431 | 1431 | 0.034071 | 529 | 0.012595 | 1641 | 0.039071 | 1.436 | A02 | TEMW0.07009011
Horizontal Wall | Tempo Wall | TEMW.07009011/DBE | 70 | 90 | 11 | 12 | 2031 | 2031 | 2031 | 0.048357 | 1016 | 0.02419 | 2234 | 0.05319 | 1 | A02 | TEMW0.07009011/DBE
Horizontal Wall | Tempo Wall | TEMW.07009015 | 70 | 90 | 15 | 17 | 1775 | 1775 | 1775 | 0.042262 | 696 | 0.016571 | 2018 | 0.048048 | 1.35 | A02 | TEMW0.07009015
Horizontal Wall | Tempo Wall | TEMW.07009016 | 70 | 90 | 16 | 17 | 2034 | 2034 | 2034 | 0.048429 | 732 | 0.017429 | 2341 | 0.055738 | 1.472 | A02 | TEMW0.07009016
Horizontal Wall | Tempo Wall | TEMW.07009016/DBE | 70 | 90 | 16 | 17 | 2994 | 2994 | 2994 | 0.071286 | 1497 | 0.035643 | 3293 | 0.078405 | 1 | A02 | TEMW0.07009016/DBE
Horizontal Wall | Tempo Wall | TEMW.07009020 | 70 | 90 | 20 | 22 | 2478 | 2478 | 2478 | 0.059 | 974 | 0.02319 | 2817 | 0.067071 | 1.349 | A02 | TEMW0.07009020
Horizontal Wall | Tempo Wall | TEMW.07009021 | 70 | 90 | 21 | 22 | 2859 | 2859 | 2859 | 0.068071 | 1009 | 0.024024 | 3299 | 0.078548 | 1.501 | A02 | TEMW0.07009021
Horizontal Wall | Tempo Wall | TEMW.07009021/DBE | 70 | 90 | 21 | 22 | 3819 | 3819 | 3819 | 0.090929 | 1910 | 0.045476 | 4201 | 0.10002 | 1 | A02 | TEMW0.07009021/DBE
Horizontal Wall | Tempo Wall | TEMW.07010010 | 70 | 100 | 10 | 12 | 1248 | 1248 | 1248 | 0.029714 | 484 | 0.011524 | 1421 | 0.033833 | 1.366 | A02 | TEMW0.07010010
Horizontal Wall | Tempo Wall | TEMW.07010011 | 70 | 100 | 11 | 12 | 1590 | 1590 | 1590 | 0.037857 | 588 | 0.014 | 1824 | 0.043429 | 1.436 | A02 | TEMW0.07010011
Horizontal Wall | Tempo Wall | TEMW.07010011/DBE | 70 | 100 | 11 | 12 | 2190 | 2190 | 2190 | 0.052143 | 1095 | 0.026071 | 2409 | 0.057357 | 1 | A02 | TEMW0.07010011/DBE
Horizontal Wall | Tempo Wall | TEMW.07010015 | 70 | 100 | 15 | 17 | 1972 | 1972 | 1972 | 0.046952 | 773 | 0.018405 | 2242 | 0.053381 | 1.35 | A02 | TEMW0.07010015
Horizontal Wall | Tempo Wall | TEMW.07010016 | 70 | 100 | 16 | 17 | 2260 | 2260 | 2260 | 0.05381 | 814 | 0.019381 | 2601 | 0.061929 | 1.472 | A02 | TEMW0.07010016
Horizontal Wall | Tempo Wall | TEMW.07010016/DBE | 70 | 100 | 16 | 17 | 3220 | 3220 | 3220 | 0.076667 | 1610 | 0.038333 | 3542 | 0.084333 | 1 | A02 | TEMW0.07010016/DBE
Horizontal Wall | Tempo Wall | TEMW.07010020 | 70 | 100 | 20 | 22 | 2753 | 2753 | 2753 | 0.065548 | 1082 | 0.025762 | 3130 | 0.074524 | 1.349 | A02 | TEMW0.07010020
Horizontal Wall | Tempo Wall | TEMW.07010021 | 70 | 100 | 21 | 22 | 3177 | 3177 | 3177 | 0.075643 | 1121 | 0.02669 | 3666 | 0.087286 | 1.501 | A02 | TEMW0.07010021
Horizontal Wall | Tempo Wall | TEMW.07010021/DBE | 70 | 100 | 21 | 22 | 4137 | 4137 | 4137 | 0.0985 | 2069 | 0.049262 | 4551 | 0.10836 | 1 | A02 | TEMW0.07010021/DBE
Horizontal Wall | Tempo Wall | TEMW.07011010 | 70 | 110 | 10 | 12 | 1373 | 1373 | 1373 | 0.03269 | 533 | 0.01269 | 1564 | 0.037238 | 1.366 | A02 | TEMW0.07011010
Horizontal Wall | Tempo Wall | TEMW.07011011 | 70 | 110 | 11 | 12 | 1749 | 1749 | 1749 | 0.041643 | 647 | 0.015405 | 2006 | 0.047762 | 1.436 | A02 | TEMW0.07011011
Horizontal Wall | Tempo Wall | TEMW.07011011/DBE | 70 | 110 | 11 | 12 | 2349 | 2349 | 2349 | 0.055929 | 1175 | 0.027976 | 2584 | 0.061524 | 1 | A02 | TEMW0.07011011/DBE
Horizontal Wall | Tempo Wall | TEMW.07011015 | 70 | 110 | 15 | 17 | 2169 | 2169 | 2169 | 0.051643 | 850 | 0.020238 | 2466 | 0.058714 | 1.35 | A02 | TEMW0.07011015
Horizontal Wall | Tempo Wall | TEMW.07011016 | 70 | 110 | 16 | 17 | 2486 | 2486 | 2486 | 0.05919 | 895 | 0.02131 | 2861 | 0.068119 | 1.472 | A02 | TEMW0.07011016
Horizontal Wall | Tempo Wall | TEMW.07011016/DBE | 70 | 110 | 16 | 17 | 3446 | 3446 | 3446 | 0.082048 | 1723 | 0.041024 | 3791 | 0.090262 | 1 | A02 | TEMW0.07011016/DBE
Horizontal Wall | Tempo Wall | TEMW.07011020 | 70 | 110 | 20 | 22 | 3028 | 3028 | 3028 | 0.072095 | 1190 | 0.028333 | 3443 | 0.081976 | 1.349 | A02 | TEMW0.07011020
Horizontal Wall | Tempo Wall | TEMW.07011021 | 70 | 110 | 21 | 22 | 3495 | 3495 | 3495 | 0.083214 | 1234 | 0.029381 | 4033 | 0.096024 | 1.501 | A02 | TEMW0.07011021
Horizontal Wall | Tempo Wall | TEMW.07011021/DBE | 70 | 110 | 21 | 22 | 4455 | 4455 | 4455 | 0.10607 | 2228 | 0.053048 | 4901 | 0.11669 | 1 | A02 | TEMW0.07011021/DBE
Horizontal Wall | Tempo Wall | TEMW.07012010 | 70 | 120 | 10 | 12 | 1498 | 1498 | 1498 | 0.035667 | 581 | 0.013833 | 1706 | 0.040619 | 1.366 | A02 | TEMW0.07012010
Horizontal Wall | Tempo Wall | TEMW.07012011 | 70 | 120 | 11 | 12 | 1908 | 1908 | 1908 | 0.045429 | 706 | 0.01681 | 2188 | 0.052095 | 1.436 | A02 | TEMW0.07012011
Horizontal Wall | Tempo Wall | TEMW.07012011/DBE | 70 | 120 | 11 | 12 | 2508 | 2508 | 2508 | 0.059714 | 1254 | 0.029857 | 2759 | 0.06569 | 1 | A02 | TEMW0.07012011/DBE
Horizontal Wall | Tempo Wall | TEMW.07012015 | 70 | 120 | 15 | 17 | 2366 | 2366 | 2366 | 0.056333 | 927 | 0.022071 | 2690 | 0.064048 | 1.35 | A02 | TEMW0.07012015
Horizontal Wall | Tempo Wall | TEMW.07012016 | 70 | 120 | 16 | 17 | 2712 | 2712 | 2712 | 0.064571 | 976 | 0.023238 | 3122 | 0.074333 | 1.472 | A02 | TEMW0.07012016
Horizontal Wall | Tempo Wall | TEMW.07012016/DBE | 70 | 120 | 16 | 17 | 3672 | 3672 | 3672 | 0.087429 | 1836 | 0.043714 | 4039 | 0.096167 | 1 | A02 | TEMW0.07012016/DBE
Horizontal Wall | Tempo Wall | TEMW.07012020 | 70 | 120 | 20 | 22 | 3304 | 3304 | 3304 | 0.078667 | 1298 | 0.030905 | 3757 | 0.089452 | 1.349 | A02 | TEMW0.07012020
Horizontal Wall | Tempo Wall | TEMW.07012021 | 70 | 120 | 21 | 22 | 3812 | 3812 | 3812 | 0.090762 | 1346 | 0.032048 | 4399 | 0.10474 | 1.501 | A02 | TEMW0.07012021
Horizontal Wall | Tempo Wall | TEMW.07012021/DBE | 70 | 120 | 21 | 22 | 4772 | 4772 | 4772 | 0.11362 | 2386 | 0.05681 | 5249 | 0.12498 | 1 | A02 | TEMW0.07012021/DBE
Horizontal Wall | Tempo Wall | TEMW.07014010 | 70 | 140 | 10 | 12 | 1747 | 1747 | 1747 | 0.041595 | 678 | 0.016143 | 1990 | 0.047381 | 1.366 | A02 | TEMW0.07014010
Horizontal Wall | Tempo Wall | TEMW.07014011 | 70 | 140 | 11 | 12 | 2226 | 2226 | 2226 | 0.053 | 824 | 0.019619 | 2553 | 0.060786 | 1.436 | A02 | TEMW0.07014011
Horizontal Wall | Tempo Wall | TEMW.07014011/DBE | 70 | 140 | 11 | 12 | 2826 | 2826 | 2826 | 0.067286 | 1413 | 0.033643 | 3109 | 0.074024 | 1 | A02 | TEMW0.07014011/DBE
Horizontal Wall | Tempo Wall | TEMW.07014015 | 70 | 140 | 15 | 17 | 2761 | 2761 | 2761 | 0.065738 | 1082 | 0.025762 | 3139 | 0.074738 | 1.35 | A02 | TEMW0.07014015
Horizontal Wall | Tempo Wall | TEMW.07014016 | 70 | 140 | 16 | 17 | 3164 | 3164 | 3164 | 0.075333 | 1139 | 0.027119 | 3642 | 0.086714 | 1.472 | A02 | TEMW0.07014016
Horizontal Wall | Tempo Wall | TEMW.07014016/DBE | 70 | 140 | 16 | 17 | 4124 | 4124 | 4124 | 0.09819 | 2062 | 0.049095 | 4536 | 0.108 | 1 | A02 | TEMW0.07014016/DBE
Horizontal Wall | Tempo Wall | TEMW.07014020 | 70 | 140 | 20 | 22 | 3854 | 3854 | 3854 | 0.091762 | 1515 | 0.036071 | 4382 | 0.10433 | 1.349 | A02 | TEMW0.07014020
Horizontal Wall | Tempo Wall | TEMW.07014021 | 70 | 140 | 21 | 22 | 4448 | 4448 | 4448 | 0.1059 | 1570 | 0.037381 | 5133 | 0.12221 | 1.501 | A02 | TEMW0.07014021
Horizontal Wall | Tempo Wall | TEMW.07014021/DBE | 70 | 140 | 21 | 22 | 5408 | 5408 | 5408 | 0.12876 | 2704 | 0.064381 | 5949 | 0.14164 | 1 | A02 | TEMW0.07014021/DBE
Horizontal Wall | Tempo Wall | TEMW.07016010 | 70 | 160 | 10 | 12 | 1997 | 1997 | 1997 | 0.047548 | 775 | 0.018452 | 2275 | 0.054167 | 1.366 | A02 | TEMW0.07016010
Horizontal Wall | Tempo Wall | TEMW.07016011 | 70 | 160 | 11 | 12 | 2544 | 2544 | 2544 | 0.060571 | 941 | 0.022405 | 2918 | 0.069476 | 1.436 | A02 | TEMW0.07016011
Horizontal Wall | Tempo Wall | TEMW.07016011/DBE | 70 | 160 | 11 | 12 | 3744 | 3744 | 3744 | 0.089143 | 1872 | 0.044571 | 4118 | 0.098048 | 1 | A02 | TEMW0.07016011/DBE
Horizontal Wall | Tempo Wall | TEMW.07016015 | 70 | 160 | 15 | 17 | 3155 | 3155 | 3155 | 0.075119 | 1237 | 0.029452 | 3587 | 0.085405 | 1.35 | A02 | TEMW0.07016015
Horizontal Wall | Tempo Wall | TEMW.07016016 | 70 | 160 | 16 | 17 | 3616 | 3616 | 3616 | 0.086095 | 1302 | 0.031 | 4162 | 0.099095 | 1.472 | A02 | TEMW0.07016016
Horizontal Wall | Tempo Wall | TEMW.07016016/DBE | 70 | 160 | 16 | 17 | 5536 | 5536 | 5536 | 0.13181 | 2768 | 0.065905 | 6090 | 0.145 | 1 | A02 | TEMW0.07016016/DBE
Horizontal Wall | Tempo Wall | TEMW.07016020 | 70 | 160 | 20 | 22 | 4405 | 4405 | 4405 | 0.10488 | 1731 | 0.041214 | 5008 | 0.11924 | 1.349 | A02 | TEMW0.07016020
Horizontal Wall | Tempo Wall | TEMW.07016021 | 70 | 160 | 21 | 22 | 5083 | 5083 | 5083 | 0.12102 | 1794 | 0.042714 | 5866 | 0.13967 | 1.501 | A02 | TEMW0.07016021
Horizontal Wall | Tempo Wall | TEMW.07016021/DBE | 70 | 160 | 21 | 22 | 7003 | 7003 | 7003 | 0.16674 | 3502 | 0.083381 | 7703 | 0.1834 | 1 | A02 | TEMW0.07016021/DBE
Horizontal Wall | Tempo Wall | TEMW.07018010 | 70 | 180 | 10 | 12 | 2246 | 2246 | 2246 | 0.053476 | 871 | 0.020738 | 2558 | 0.060905 | 1.366 | A02 | TEMW0.07018010
Horizontal Wall | Tempo Wall | TEMW.07018011 | 70 | 180 | 11 | 12 | 2862 | 2862 | 2862 | 0.068143 | 1059 | 0.025214 | 3283 | 0.078167 | 1.436 | A02 | TEMW0.07018011
Horizontal Wall | Tempo Wall | TEMW.07018011/DBE | 70 | 180 | 11 | 12 | 4062 | 4062 | 4062 | 0.096714 | 2031 | 0.048357 | 4468 | 0.10638 | 1 | A02 | TEMW0.07018011/DBE
Horizontal Wall | Tempo Wall | TEMW.07018015 | 70 | 180 | 15 | 17 | 3550 | 3550 | 3550 | 0.084524 | 1392 | 0.033143 | 4036 | 0.096095 | 1.35 | A02 | TEMW0.07018015
Horizontal Wall | Tempo Wall | TEMW.07018016 | 70 | 180 | 16 | 17 | 4068 | 4068 | 4068 | 0.096857 | 1464 | 0.034857 | 4682 | 0.11148 | 1.472 | A02 | TEMW0.07018016
Horizontal Wall | Tempo Wall | TEMW.07018016/DBE | 70 | 180 | 16 | 17 | 5988 | 5988 | 5988 | 0.14257 | 2994 | 0.071286 | 6587 | 0.15683 | 1 | A02 | TEMW0.07018016/DBE
Horizontal Wall | Tempo Wall | TEMW.07018020 | 70 | 180 | 20 | 22 | 4955 | 4955 | 4955 | 0.11798 | 1947 | 0.046357 | 5634 | 0.13414 | 1.349 | A02 | TEMW0.07018020
Horizontal Wall | Tempo Wall | TEMW.07018021 | 70 | 180 | 21 | 22 | 5719 | 5719 | 5719 | 0.13617 | 2019 | 0.048071 | 6600 | 0.15714 | 1.501 | A02 | TEMW0.07018021
Horizontal Wall | Tempo Wall | TEMW.07018021/DBE | 70 | 180 | 21 | 22 | 7639 | 7639 | 7639 | 0.18188 | 3820 | 0.090952 | 8403 | 0.20007 | 1 | A02 | TEMW0.07018021/DBE
Horizontal Wall | Tempo Wall | TEMW.07020010 | 70 | 200 | 10 | 12 | 2496 | 2496 | 2496 | 0.059429 | 968 | 0.023048 | 2843 | 0.06769 | 1.366 | A02 | TEMW0.07020010
Horizontal Wall | Tempo Wall | TEMW.07020011 | 70 | 200 | 11 | 12 | 3180 | 3180 | 3180 | 0.075714 | 1177 | 0.028024 | 3647 | 0.086833 | 1.436 | A02 | TEMW0.07020011
Horizontal Wall | Tempo Wall | TEMW.07020011/DBE | 70 | 200 | 11 | 12 | 4380 | 4380 | 4380 | 0.10429 | 2190 | 0.052143 | 4818 | 0.11471 | 1 | A02 | TEMW0.07020011/DBE
Horizontal Wall | Tempo Wall | TEMW.07020015 | 70 | 200 | 15 | 17 | 3944 | 3944 | 3944 | 0.093905 | 1546 | 0.03681 | 4484 | 0.10676 | 1.35 | A02 | TEMW0.07020015
Horizontal Wall | Tempo Wall | TEMW.07020016 | 70 | 200 | 16 | 17 | 4520 | 4520 | 4520 | 0.10762 | 1627 | 0.038738 | 5203 | 0.12388 | 1.472 | A02 | TEMW0.07020016
Horizontal Wall | Tempo Wall | TEMW.07020016/DBE | 70 | 200 | 16 | 17 | 6440 | 6440 | 6440 | 0.15333 | 3220 | 0.076667 | 7084 | 0.16867 | 1 | A02 | TEMW0.07020016/DBE
Horizontal Wall | Tempo Wall | TEMW.07020020 | 70 | 200 | 20 | 22 | 5506 | 5506 | 5506 | 0.1311 | 2164 | 0.051524 | 6260 | 0.14905 | 1.349 | A02 | TEMW0.07020020
Horizontal Wall | Tempo Wall | TEMW.07020021 | 70 | 200 | 21 | 22 | 6354 | 6354 | 6354 | 0.15129 | 2243 | 0.053405 | 7333 | 0.1746 | 1.501 | A02 | TEMW0.07020021
Horizontal Wall | Tempo Wall | TEMW.07020021/DBE | 70 | 200 | 21 | 22 | 8274 | 8274 | 8274 | 0.197 | 4137 | 0.0985 | 9101 | 0.21669 | 1 | A02 | TEMW0.07020021/DBE
Horizontal Wall | Tempo Wall | TEMW.07022010 | 70 | 220 | 10 | 12 | 2746 | 2746 | 2746 | 0.065381 | 1065 | 0.025357 | 3128 | 0.074476 | 1.366 | A02 | TEMW0.07022010
Horizontal Wall | Tempo Wall | TEMW.07022011 | 70 | 220 | 11 | 12 | 3498 | 3498 | 3498 | 0.083286 | 1294 | 0.03081 | 4012 | 0.095524 | 1.436 | A02 | TEMW0.07022011
Horizontal Wall | Tempo Wall | TEMW.07022011/DBE | 70 | 220 | 11 | 12 | 4698 | 4698 | 4698 | 0.11186 | 2349 | 0.055929 | 5168 | 0.12305 | 1 | A02 | TEMW0.07022011/DBE
Horizontal Wall | Tempo Wall | TEMW.07022015 | 70 | 220 | 15 | 17 | 4338 | 4338 | 4338 | 0.10329 | 1700 | 0.040476 | 4932 | 0.11743 | 1.35 | A02 | TEMW0.07022015
Horizontal Wall | Tempo Wall | TEMW.07022016 | 70 | 220 | 16 | 17 | 4972 | 4972 | 4972 | 0.11838 | 1790 | 0.042619 | 5723 | 0.13626 | 1.472 | A02 | TEMW0.07022016
Horizontal Wall | Tempo Wall | TEMW.07022016/DBE | 70 | 220 | 16 | 17 | 6892 | 6892 | 6892 | 0.1641 | 3446 | 0.082048 | 7581 | 0.1805 | 1 | A02 | TEMW0.07022016/DBE
Horizontal Wall | Tempo Wall | TEMW.07022020 | 70 | 220 | 20 | 22 | 6057 | 6057 | 6057 | 0.14421 | 2380 | 0.056667 | 6887 | 0.16398 | 1.349 | A02 | TEMW0.07022020
Horizontal Wall | Tempo Wall | TEMW.07022021 | 70 | 220 | 21 | 22 | 6989 | 6989 | 6989 | 0.1664 | 2467 | 0.058738 | 8065 | 0.19202 | 1.501 | A02 | TEMW0.07022021
Horizontal Wall | Tempo Wall | TEMW.07022021/DBE | 70 | 220 | 21 | 22 | 8909 | 8909 | 8909 | 0.21212 | 4455 | 0.10607 | 9800 | 0.23333 | 1 | A02 | TEMW0.07022021/DBE
Horizontal Wall | Tempo Wall | TEMW.07024010 | 70 | 240 | 10 | 12 | 2995 | 2995 | 2995 | 0.07131 | 1162 | 0.027667 | 3411 | 0.081214 | 1.366 | A02 | TEMW0.07024010
Horizontal Wall | Tempo Wall | TEMW.07024011 | 70 | 240 | 11 | 12 | 3816 | 3816 | 3816 | 0.090857 | 1412 | 0.033619 | 4377 | 0.10421 | 1.436 | A02 | TEMW0.07024011
Horizontal Wall | Tempo Wall | TEMW.07024011/DBE | 70 | 240 | 11 | 12 | 5616 | 5616 | 5616 | 0.13371 | 2808 | 0.066857 | 6178 | 0.1471 | 1 | A02 | TEMW0.07024011/DBE
Horizontal Wall | Tempo Wall | TEMW.07024015 | 70 | 240 | 15 | 17 | 4733 | 4733 | 4733 | 0.11269 | 1855 | 0.044167 | 5381 | 0.12812 | 1.35 | A02 | TEMW0.07024015
Horizontal Wall | Tempo Wall | TEMW.07024016 | 70 | 240 | 16 | 17 | 5424 | 5424 | 5424 | 0.12914 | 1953 | 0.0465 | 6243 | 0.14864 | 1.472 | A02 | TEMW0.07024016
Horizontal Wall | Tempo Wall | TEMW.07024016/DBE | 70 | 240 | 16 | 17 | 8304 | 8304 | 8304 | 0.19771 | 4152 | 0.098857 | 9134 | 0.21748 | 1 | A02 | TEMW0.07024016/DBE
Horizontal Wall | Tempo Wall | TEMW.07024020 | 70 | 240 | 20 | 22 | 6607 | 6607 | 6607 | 0.15731 | 2597 | 0.061833 | 7512 | 0.17886 | 1.349 | A02 | TEMW0.07024020
Horizontal Wall | Tempo Wall | TEMW.07024021 | 70 | 240 | 21 | 22 | 7625 | 7625 | 7625 | 0.18155 | 2692 | 0.064095 | 8799 | 0.2095 | 1.501 | A02 | TEMW0.07024021
Horizontal Wall | Tempo Wall | TEMW.07024021/DBE | 70 | 240 | 21 | 22 | 10505 | 10505 | 10505 | 0.25012 | 5253 | 0.12507 | 11556 | 0.27514 | 1 | A02 | TEMW0.07024021/DBE
Horizontal Wall | Tempo Wall | TEMW.07026010 | 70 | 260 | 10 | 12 | 3245 | 3245 | 3245 | 0.077262 | 1259 | 0.029976 | 3696 | 0.088 | 1.366 | A02 | TEMW0.07026010
Horizontal Wall | Tempo Wall | TEMW.07026011 | 70 | 260 | 11 | 12 | 4134 | 4134 | 4134 | 0.098429 | 1530 | 0.036429 | 4742 | 0.1129 | 1.436 | A02 | TEMW0.07026011
Horizontal Wall | Tempo Wall | TEMW.07026011/DBE | 70 | 260 | 11 | 12 | 5934 | 5934 | 5934 | 0.14129 | 2967 | 0.070643 | 6527 | 0.1554 | 1 | A02 | TEMW0.07026011/DBE
Horizontal Wall | Tempo Wall | TEMW.07026015 | 70 | 260 | 15 | 17 | 5127 | 5127 | 5127 | 0.12207 | 2010 | 0.047857 | 5829 | 0.13879 | 1.35 | A02 | TEMW0.07026015
Horizontal Wall | Tempo Wall | TEMW.07026016 | 70 | 260 | 16 | 17 | 5876 | 5876 | 5876 | 0.1399 | 2115 | 0.050357 | 6763 | 0.16102 | 1.472 | A02 | TEMW0.07026016
Horizontal Wall | Tempo Wall | TEMW.07026016/DBE | 70 | 260 | 16 | 17 | 8756 | 8756 | 8756 | 0.20848 | 4378 | 0.10424 | 9632 | 0.22933 | 1 | A02 | TEMW0.07026016/DBE
Horizontal Wall | Tempo Wall | TEMW.07026020 | 70 | 260 | 20 | 22 | 7158 | 7158 | 7158 | 0.17043 | 2813 | 0.066976 | 8139 | 0.19379 | 1.349 | A02 | TEMW0.07026020
Horizontal Wall | Tempo Wall | TEMW.07026021 | 70 | 260 | 21 | 22 | 8260 | 8260 | 8260 | 0.19667 | 2916 | 0.069429 | 9532 | 0.22695 | 1.501 | A02 | TEMW0.07026021
Horizontal Wall | Tempo Wall | TEMW.07026021/DBE | 70 | 260 | 21 | 22 | 11140 | 11140 | 11140 | 0.26524 | 5570 | 0.13262 | 12254 | 0.29176 | 1 | A02 | TEMW0.07026021/DBE
Horizontal Wall | Tempo Wall | TEMW.07028010 | 70 | 280 | 10 | 12 | 3494 | 3494 | 3494 | 0.08319 | 1356 | 0.032286 | 3980 | 0.094762 | 1.366 | A02 | TEMW0.07028010
Horizontal Wall | Tempo Wall | TEMW.07028011 | 70 | 280 | 11 | 12 | 4452 | 4452 | 4452 | 0.106 | 1647 | 0.039214 | 5106 | 0.12157 | 1.436 | A02 | TEMW0.07028011
Horizontal Wall | Tempo Wall | TEMW.07028011/DBE | 70 | 280 | 11 | 12 | 6252 | 6252 | 6252 | 0.14886 | 3126 | 0.074429 | 6877 | 0.16374 | 1 | A02 | TEMW0.07028011/DBE
Horizontal Wall | Tempo Wall | TEMW.07028015 | 70 | 280 | 15 | 17 | 5522 | 5522 | 5522 | 0.13148 | 2165 | 0.051548 | 6279 | 0.1495 | 1.35 | A02 | TEMW0.07028015
Horizontal Wall | Tempo Wall | TEMW.07028016 | 70 | 280 | 16 | 17 | 6328 | 6328 | 6328 | 0.15067 | 2278 | 0.054238 | 7284 | 0.17343 | 1.472 | A02 | TEMW0.07028016
Horizontal Wall | Tempo Wall | TEMW.07028016/DBE | 70 | 280 | 16 | 17 | 9208 | 9208 | 9208 | 0.21924 | 4604 | 0.10962 | 10129 | 0.24117 | 1 | A02 | TEMW0.07028016/DBE
Horizontal Wall | Tempo Wall | TEMW.07028020 | 70 | 280 | 20 | 22 | 7708 | 7708 | 7708 | 0.18352 | 3029 | 0.072119 | 8764 | 0.20867 | 1.349 | A02 | TEMW0.07028020
Horizontal Wall | Tempo Wall | TEMW.07028021 | 70 | 280 | 21 | 22 | 8896 | 8896 | 8896 | 0.21181 | 3140 | 0.074762 | 10266 | 0.24443 | 1.501 | A02 | TEMW0.07028021
Horizontal Wall | Tempo Wall | TEMW.07028021/DBE | 70 | 280 | 21 | 22 | 11776 | 11776 | 11776 | 0.28038 | 5888 | 0.14019 | 12954 | 0.30843 | 1 | A02 | TEMW0.07028021/DBE
Horizontal Wall | Tempo Wall | TEMW.07030010 | 70 | 300 | 10 | 12 | 3744 | 3744 | 3744 | 0.089143 | 1453 | 0.034595 | 4264 | 0.10152 | 1.366 | A02 | TEMW0.07030010
Horizontal Wall | Tempo Wall | TEMW.07030011 | 70 | 300 | 11 | 12 | 4770 | 4770 | 4770 | 0.11357 | 1765 | 0.042024 | 5471 | 0.13026 | 1.436 | A02 | TEMW0.07030011
Horizontal Wall | Tempo Wall | TEMW.07030011/DBE | 70 | 300 | 11 | 12 | 6570 | 6570 | 6570 | 0.15643 | 3285 | 0.078214 | 7227 | 0.17207 | 1 | A02 | TEMW0.07030011/DBE
Horizontal Wall | Tempo Wall | TEMW.07030015 | 70 | 300 | 15 | 17 | 5916 | 5916 | 5916 | 0.14086 | 2319 | 0.055214 | 6726 | 0.16014 | 1.35 | A02 | TEMW0.07030015
Horizontal Wall | Tempo Wall | TEMW.07030016 | 70 | 300 | 16 | 17 | 6780 | 6780 | 6780 | 0.16143 | 2441 | 0.058119 | 7804 | 0.18581 | 1.472 | A02 | TEMW0.07030016
Horizontal Wall | Tempo Wall | TEMW.07030016/DBE | 70 | 300 | 16 | 17 | 9660 | 9660 | 9660 | 0.23 | 4830 | 0.115 | 10626 | 0.253 | 1 | A02 | TEMW0.07030016/DBE
Horizontal Wall | Tempo Wall | TEMW.07030020 | 70 | 300 | 20 | 22 | 8259 | 8259 | 8259 | 0.19664 | 3246 | 0.077286 | 9390 | 0.22357 | 1.349 | A02 | TEMW0.07030020
Horizontal Wall | Tempo Wall | TEMW.07030021 | 70 | 300 | 21 | 22 | 9531 | 9531 | 9531 | 0.22693 | 3364 | 0.080095 | 10999 | 0.26188 | 1.501 | A02 | TEMW0.07030021
Horizontal Wall | Tempo Wall | TEMW.07030021/DBE | 70 | 300 | 21 | 22 | 12411 | 12411 | 12411 | 0.2955 | 6206 | 0.14776 | 13652 | 0.32505 | 1 | A02 | TEMW0.07030021/DBE
Horizontal Wall | Tempo Wall | TEMW.09004010 | 90 | 40 | 10 | 12 | 548 | 548 | 548 | 0.013048 | 215 | 0.005119 | 623 | 0.014833 | 1.348 | A02 | TEMW0.09004010
Horizontal Wall | Tempo Wall | TEMW.09004011 | 90 | 40 | 11 | 12 | 703 | 703 | 703 | 0.016738 | 260 | 0.0061905 | 806 | 0.01919 | 1.434 | A02 | TEMW0.09004011
Horizontal Wall | Tempo Wall | TEMW.09004015 | 90 | 40 | 15 | 17 | 848 | 848 | 848 | 0.02019 | 338 | 0.0080476 | 962 | 0.022905 | 1.326 | A02 | TEMW0.09004015
Horizontal Wall | Tempo Wall | TEMW.09004016 | 90 | 40 | 16 | 17 | 1038 | 1038 | 1038 | 0.024714 | 372 | 0.0088571 | 1195 | 0.028452 | 1.48 | A02 | TEMW0.09004016
Horizontal Wall | Tempo Wall | TEMW.09004020 | 90 | 40 | 20 | 22 | 1183 | 1183 | 1183 | 0.028167 | 472 | 0.011238 | 1343 | 0.031976 | 1.326 | A02 | TEMW0.09004020
Horizontal Wall | Tempo Wall | TEMW.09004021 | 90 | 40 | 21 | 22 | 1508 | 1508 | 1508 | 0.035905 | 526 | 0.012524 | 1743 | 0.0415 | 1.518 | A02 | TEMW0.09004021
Horizontal Wall | Tempo Wall | TEMW.09005010 | 90 | 50 | 10 | 12 | 685 | 685 | 685 | 0.01631 | 269 | 0.0064048 | 779 | 0.018548 | 1.348 | A02 | TEMW0.09005010
Horizontal Wall | Tempo Wall | TEMW.09005011 | 90 | 50 | 11 | 12 | 879 | 879 | 879 | 0.020929 | 325 | 0.0077381 | 1007 | 0.023976 | 1.434 | A02 | TEMW0.09005011
Horizontal Wall | Tempo Wall | TEMW.09005015 | 90 | 50 | 15 | 17 | 1060 | 1060 | 1060 | 0.025238 | 423 | 0.010071 | 1203 | 0.028643 | 1.326 | A02 | TEMW0.09005015
Horizontal Wall | Tempo Wall | TEMW.09005016 | 90 | 50 | 16 | 17 | 1298 | 1298 | 1298 | 0.030905 | 465 | 0.011071 | 1494 | 0.035571 | 1.48 | A02 | TEMW0.09005016
Horizontal Wall | Tempo Wall | TEMW.09005020 | 90 | 50 | 20 | 22 | 1479 | 1479 | 1479 | 0.035214 | 590 | 0.014048 | 1679 | 0.039976 | 1.326 | A02 | TEMW0.09005020
Horizontal Wall | Tempo Wall | TEMW.09005021 | 90 | 50 | 21 | 22 | 1885 | 1885 | 1885 | 0.044881 | 658 | 0.015667 | 2179 | 0.051881 | 1.518 | A02 | TEMW0.09005021
Horizontal Wall | Tempo Wall | TEMW.09006010 | 90 | 60 | 10 | 12 | 821 | 821 | 821 | 0.019548 | 323 | 0.0076905 | 933 | 0.022214 | 1.348 | A02 | TEMW0.09006010
Horizontal Wall | Tempo Wall | TEMW.09006011 | 90 | 60 | 11 | 12 | 1055 | 1055 | 1055 | 0.025119 | 390 | 0.0092857 | 1209 | 0.028786 | 1.434 | A02 | TEMW0.09006011
Horizontal Wall | Tempo Wall | TEMW.09006011/DBE | 90 | 60 | 11 | 12 | 1355 | 1355 | 1355 | 0.032262 | 678 | 0.016143 | 1491 | 0.0355 | 1 | A02 | TEMW0.09006011/DBE
Horizontal Wall | Tempo Wall | TEMW.09006015 | 90 | 60 | 15 | 17 | 1272 | 1272 | 1272 | 0.030286 | 508 | 0.012095 | 1444 | 0.034381 | 1.326 | A02 | TEMW0.09006015
Horizontal Wall | Tempo Wall | TEMW.09006016 | 90 | 60 | 16 | 17 | 1558 | 1558 | 1558 | 0.037095 | 558 | 0.013286 | 1793 | 0.04269 | 1.48 | A02 | TEMW0.09006016
Horizontal Wall | Tempo Wall | TEMW.09006016/DBE | 90 | 60 | 16 | 17 | 2038 | 2038 | 2038 | 0.048524 | 1019 | 0.024262 | 2242 | 0.053381 | 1 | A02 | TEMW0.09006016/DBE
Horizontal Wall | Tempo Wall | TEMW.09006020 | 90 | 60 | 20 | 22 | 1774 | 1774 | 1774 | 0.042238 | 708 | 0.016857 | 2013 | 0.047929 | 1.326 | A02 | TEMW0.09006020
Horizontal Wall | Tempo Wall | TEMW.09006021 | 90 | 60 | 21 | 22 | 2262 | 2262 | 2262 | 0.053857 | 789 | 0.018786 | 2615 | 0.062262 | 1.518 | A02 | TEMW0.09006021
Horizontal Wall | Tempo Wall | TEMW.09006021/DBE | 90 | 60 | 21 | 22 | 2742 | 2742 | 2742 | 0.065286 | 1371 | 0.032643 | 3016 | 0.07181 | 1 | A02 | TEMW0.09006021/DBE
Horizontal Wall | Tempo Wall | TEMW.09007010 | 90 | 70 | 10 | 12 | 958 | 958 | 958 | 0.02281 | 376 | 0.0089524 | 1089 | 0.025929 | 1.348 | A02 | TEMW0.09007010
Horizontal Wall | Tempo Wall | TEMW.09007011 | 90 | 70 | 11 | 12 | 1231 | 1231 | 1231 | 0.02931 | 455 | 0.010833 | 1411 | 0.033595 | 1.434 | A02 | TEMW0.09007011
Horizontal Wall | Tempo Wall | TEMW.09007011/DBE | 90 | 70 | 11 | 12 | 1531 | 1531 | 1531 | 0.036452 | 766 | 0.018238 | 1684 | 0.040095 | 1 | A02 | TEMW0.09007011/DBE
Horizontal Wall | Tempo Wall | TEMW.09007015 | 90 | 70 | 15 | 17 | 1484 | 1484 | 1484 | 0.035333 | 592 | 0.014095 | 1684 | 0.040095 | 1.326 | A02 | TEMW0.09007015
Horizontal Wall | Tempo Wall | TEMW.09007016 | 90 | 70 | 16 | 17 | 1817 | 1817 | 1817 | 0.043262 | 650 | 0.015476 | 2091 | 0.049786 | 1.48 | A02 | TEMW0.09007016
Horizontal Wall | Tempo Wall | TEMW.09007016/DBE | 90 | 70 | 16 | 17 | 2297 | 2297 | 2297 | 0.05469 | 1149 | 0.027357 | 2527 | 0.060167 | 1 | A02 | TEMW0.09007016/DBE
Horizontal Wall | Tempo Wall | TEMW.09007020 | 90 | 70 | 20 | 22 | 2070 | 2070 | 2070 | 0.049286 | 826 | 0.019667 | 2349 | 0.055929 | 1.326 | A02 | TEMW0.09007020
Horizontal Wall | Tempo Wall | TEMW.09007021 | 90 | 70 | 21 | 22 | 2639 | 2639 | 2639 | 0.062833 | 921 | 0.021929 | 3051 | 0.072643 | 1.518 | A02 | TEMW0.09007021
Horizontal Wall | Tempo Wall | TEMW.09007021/DBE | 90 | 70 | 21 | 22 | 3119 | 3119 | 3119 | 0.074262 | 1560 | 0.037143 | 3431 | 0.08169 | 1 | A02 | TEMW0.09007021/DBE
Horizontal Wall | Tempo Wall | TEMW.09008010 | 90 | 80 | 10 | 12 | 1095 | 1095 | 1095 | 0.026071 | 430 | 0.010238 | 1245 | 0.029643 | 1.348 | A02 | TEMW0.09008010
Horizontal Wall | Tempo Wall | TEMW.09008011 | 90 | 80 | 11 | 12 | 1406 | 1406 | 1406 | 0.033476 | 520 | 0.012381 | 1611 | 0.038357 | 1.434 | A02 | TEMW0.09008011
Horizontal Wall | Tempo Wall | TEMW.09008011/DBE | 90 | 80 | 11 | 12 | 1706 | 1706 | 1706 | 0.040619 | 853 | 0.02031 | 1877 | 0.04469 | 1 | A02 | TEMW0.09008011/DBE
Horizontal Wall | Tempo Wall | TEMW.09008015 | 90 | 80 | 15 | 17 | 1696 | 1696 | 1696 | 0.040381 | 677 | 0.016119 | 1925 | 0.045833 | 1.326 | A02 | TEMW0.09008015
Horizontal Wall | Tempo Wall | TEMW.09008016 | 90 | 80 | 16 | 17 | 2077 | 2077 | 2077 | 0.049452 | 744 | 0.017714 | 2391 | 0.056929 | 1.48 | A02 | TEMW0.09008016
Horizontal Wall | Tempo Wall | TEMW.09008016/DBE | 90 | 80 | 16 | 17 | 2557 | 2557 | 2557 | 0.060881 | 1279 | 0.030452 | 2813 | 0.066976 | 1 | A02 | TEMW0.09008016/DBE
Horizontal Wall | Tempo Wall | TEMW.09008020 | 90 | 80 | 20 | 22 | 2366 | 2366 | 2366 | 0.056333 | 944 | 0.022476 | 2685 | 0.063929 | 1.326 | A02 | TEMW0.09008020
Horizontal Wall | Tempo Wall | TEMW.09008021 | 90 | 80 | 21 | 22 | 3016 | 3016 | 3016 | 0.07181 | 1053 | 0.025071 | 3486 | 0.083 | 1.518 | A02 | TEMW0.09008021
Horizontal Wall | Tempo Wall | TEMW.09008021/DBE | 90 | 80 | 21 | 22 | 3496 | 3496 | 3496 | 0.083238 | 1748 | 0.041619 | 3846 | 0.091571 | 1 | A02 | TEMW0.09008021/DBE
Horizontal Wall | Tempo Wall | TEMW.09009010 | 90 | 90 | 10 | 12 | 1232 | 1232 | 1232 | 0.029333 | 484 | 0.011524 | 1401 | 0.033357 | 1.348 | A02 | TEMW0.09009010
Horizontal Wall | Tempo Wall | TEMW.09009011 | 90 | 90 | 11 | 12 | 1582 | 1582 | 1582 | 0.037667 | 585 | 0.013929 | 1813 | 0.043167 | 1.434 | A02 | TEMW0.09009011
Horizontal Wall | Tempo Wall | TEMW.09009011/DBE | 90 | 90 | 11 | 12 | 2182 | 2182 | 2182 | 0.051952 | 1091 | 0.025976 | 2400 | 0.057143 | 1 | A02 | TEMW0.09009011/DBE
Horizontal Wall | Tempo Wall | TEMW.09009015 | 90 | 90 | 15 | 17 | 1908 | 1908 | 1908 | 0.045429 | 761 | 0.018119 | 2166 | 0.051571 | 1.326 | A02 | TEMW0.09009015
Horizontal Wall | Tempo Wall | TEMW.09009016 | 90 | 90 | 16 | 17 | 2336 | 2336 | 2336 | 0.055619 | 836 | 0.019905 | 2689 | 0.064024 | 1.48 | A02 | TEMW0.09009016
Horizontal Wall | Tempo Wall | TEMW.09009016/DBE | 90 | 90 | 16 | 17 | 3296 | 3296 | 3296 | 0.078476 | 1648 | 0.039238 | 3626 | 0.086333 | 1 | A02 | TEMW0.09009016/DBE
Horizontal Wall | Tempo Wall | TEMW.09009020 | 90 | 90 | 20 | 22 | 2661 | 2661 | 2661 | 0.063357 | 1062 | 0.025286 | 3020 | 0.071905 | 1.326 | A02 | TEMW0.09009020
Horizontal Wall | Tempo Wall | TEMW.09009021 | 90 | 90 | 21 | 22 | 3393 | 3393 | 3393 | 0.080786 | 1184 | 0.02819 | 3922 | 0.093381 | 1.518 | A02 | TEMW0.09009021
Horizontal Wall | Tempo Wall | TEMW.09009021/DBE | 90 | 90 | 21 | 22 | 4353 | 4353 | 4353 | 0.10364 | 2177 | 0.051833 | 4788 | 0.114 | 1 | A02 | TEMW0.09009021/DBE
Horizontal Wall | Tempo Wall | TEMW.09010010 | 90 | 100 | 10 | 12 | 1369 | 1369 | 1369 | 0.032595 | 538 | 0.01281 | 1557 | 0.037071 | 1.348 | A02 | TEMW0.09010010
Horizontal Wall | Tempo Wall | TEMW.09010011 | 90 | 100 | 11 | 12 | 1758 | 1758 | 1758 | 0.041857 | 650 | 0.015476 | 2015 | 0.047976 | 1.434 | A02 | TEMW0.09010011
Horizontal Wall | Tempo Wall | TEMW.09010011/DBE | 90 | 100 | 11 | 12 | 2358 | 2358 | 2358 | 0.056143 | 1179 | 0.028071 | 2594 | 0.061762 | 1 | A02 | TEMW0.09010011/DBE
Horizontal Wall | Tempo Wall | TEMW.09010015 | 90 | 100 | 15 | 17 | 2120 | 2120 | 2120 | 0.050476 | 846 | 0.020143 | 2406 | 0.057286 | 1.326 | A02 | TEMW0.09010015
Horizontal Wall | Tempo Wall | TEMW.09010016 | 90 | 100 | 16 | 17 | 2596 | 2596 | 2596 | 0.06181 | 929 | 0.022119 | 2988 | 0.071143 | 1.48 | A02 | TEMW0.09010016
Horizontal Wall | Tempo Wall | TEMW.09010016/DBE | 90 | 100 | 16 | 17 | 3556 | 3556 | 3556 | 0.084667 | 1778 | 0.042333 | 3912 | 0.093143 | 1 | A02 | TEMW0.09010016/DBE
Horizontal Wall | Tempo Wall | TEMW.09010020 | 90 | 100 | 20 | 22 | 2957 | 2957 | 2957 | 0.070405 | 1180 | 0.028095 | 3356 | 0.079905 | 1.326 | A02 | TEMW0.09010020
Horizontal Wall | Tempo Wall | TEMW.09010021 | 90 | 100 | 21 | 22 | 3770 | 3770 | 3770 | 0.089762 | 1316 | 0.031333 | 4358 | 0.10376 | 1.518 | A02 | TEMW0.09010021
Horizontal Wall | Tempo Wall | TEMW.09010021/DBE | 90 | 100 | 21 | 22 | 4730 | 4730 | 4730 | 0.11262 | 2365 | 0.05631 | 5203 | 0.12388 | 1 | A02 | TEMW0.09010021/DBE
Horizontal Wall | Tempo Wall | TEMW.09011010 | 90 | 110 | 10 | 12 | 1506 | 1506 | 1506 | 0.035857 | 592 | 0.014095 | 1712 | 0.040762 | 1.348 | A02 | TEMW0.09011010
Horizontal Wall | Tempo Wall | TEMW.09011011 | 90 | 110 | 11 | 12 | 1934 | 1934 | 1934 | 0.046048 | 716 | 0.017048 | 2216 | 0.052762 | 1.434 | A02 | TEMW0.09011011
Horizontal Wall | Tempo Wall | TEMW.09011011/DBE | 90 | 110 | 11 | 12 | 2534 | 2534 | 2534 | 0.060333 | 1267 | 0.030167 | 2787 | 0.066357 | 1 | A02 | TEMW0.09011011/DBE
Horizontal Wall | Tempo Wall | TEMW.09011015 | 90 | 110 | 15 | 17 | 2332 | 2332 | 2332 | 0.055524 | 930 | 0.022143 | 2647 | 0.063024 | 1.326 | A02 | TEMW0.09011015
Horizontal Wall | Tempo Wall | TEMW.09011016 | 90 | 110 | 16 | 17 | 2856 | 2856 | 2856 | 0.068 | 1022 | 0.024333 | 3287 | 0.078262 | 1.48 | A02 | TEMW0.09011016
Horizontal Wall | Tempo Wall | TEMW.09011016/DBE | 90 | 110 | 16 | 17 | 3816 | 3816 | 3816 | 0.090857 | 1908 | 0.045429 | 4198 | 0.099952 | 1 | A02 | TEMW0.09011016/DBE
Horizontal Wall | Tempo Wall | TEMW.09011020 | 90 | 110 | 20 | 22 | 3253 | 3253 | 3253 | 0.077452 | 1298 | 0.030905 | 3692 | 0.087905 | 1.326 | A02 | TEMW0.09011020
Horizontal Wall | Tempo Wall | TEMW.09011021 | 90 | 110 | 21 | 22 | 4147 | 4147 | 4147 | 0.098738 | 1447 | 0.034452 | 4794 | 0.11414 | 1.518 | A02 | TEMW0.09011021
Horizontal Wall | Tempo Wall | TEMW.09011021/DBE | 90 | 110 | 21 | 22 | 5107 | 5107 | 5107 | 0.1216 | 2554 | 0.06081 | 5618 | 0.13376 | 1 | A02 | TEMW0.09011021/DBE
Horizontal Wall | Tempo Wall | TEMW.09012010 | 90 | 120 | 10 | 12 | 1643 | 1643 | 1643 | 0.039119 | 646 | 0.015381 | 1868 | 0.044476 | 1.348 | A02 | TEMW0.09012010
Horizontal Wall | Tempo Wall | TEMW.09012011 | 90 | 120 | 11 | 12 | 2110 | 2110 | 2110 | 0.050238 | 781 | 0.018595 | 2418 | 0.057571 | 1.434 | A02 | TEMW0.09012011
Horizontal Wall | Tempo Wall | TEMW.09012011/DBE | 90 | 120 | 11 | 12 | 2710 | 2710 | 2710 | 0.064524 | 1355 | 0.032262 | 2981 | 0.070976 | 1 | A02 | TEMW0.09012011/DBE
Horizontal Wall | Tempo Wall | TEMW.09012015 | 90 | 120 | 15 | 17 | 2544 | 2544 | 2544 | 0.060571 | 1015 | 0.024167 | 2887 | 0.068738 | 1.326 | A02 | TEMW0.09012015
Horizontal Wall | Tempo Wall | TEMW.09012016 | 90 | 120 | 16 | 17 | 3115 | 3115 | 3115 | 0.074167 | 1115 | 0.026548 | 3585 | 0.085357 | 1.48 | A02 | TEMW0.09012016
Horizontal Wall | Tempo Wall | TEMW.09012016/DBE | 90 | 120 | 16 | 17 | 4075 | 4075 | 4075 | 0.097024 | 2038 | 0.048524 | 4483 | 0.10674 | 1 | A02 | TEMW0.09012016/DBE
Horizontal Wall | Tempo Wall | TEMW.09012020 | 90 | 120 | 20 | 22 | 3548 | 3548 | 3548 | 0.084476 | 1416 | 0.033714 | 4027 | 0.095881 | 1.326 | A02 | TEMW0.09012020
Horizontal Wall | Tempo Wall | TEMW.09012021 | 90 | 120 | 21 | 22 | 4524 | 4524 | 4524 | 0.10771 | 1579 | 0.037595 | 5230 | 0.12452 | 1.518 | A02 | TEMW0.09012021
Horizontal Wall | Tempo Wall | TEMW.09012021/DBE | 90 | 120 | 21 | 22 | 5484 | 5484 | 5484 | 0.13057 | 2742 | 0.065286 | 6032 | 0.14362 | 1 | A02 | TEMW0.09012021/DBE
Horizontal Wall | Tempo Wall | TEMW.09014010 | 90 | 140 | 10 | 12 | 1917 | 1917 | 1917 | 0.045643 | 753 | 0.017929 | 2180 | 0.051905 | 1.348 | A02 | TEMW0.09014010
Horizontal Wall | Tempo Wall | TEMW.09014011 | 90 | 140 | 11 | 12 | 2461 | 2461 | 2461 | 0.058595 | 911 | 0.02169 | 2820 | 0.067143 | 1.434 | A02 | TEMW0.09014011
Horizontal Wall | Tempo Wall | TEMW.09014011/DBE | 90 | 140 | 11 | 12 | 3061 | 3061 | 3061 | 0.072881 | 1531 | 0.036452 | 3367 | 0.080167 | 1 | A02 | TEMW0.09014011/DBE
Horizontal Wall | Tempo Wall | TEMW.09014015 | 90 | 140 | 15 | 17 | 2968 | 2968 | 2968 | 0.070667 | 1184 | 0.02819 | 3369 | 0.080214 | 1.326 | A02 | TEMW0.09014015
Horizontal Wall | Tempo Wall | TEMW.09014016 | 90 | 140 | 16 | 17 | 3634 | 3634 | 3634 | 0.086524 | 1301 | 0.030976 | 4183 | 0.099595 | 1.48 | A02 | TEMW0.09014016
Horizontal Wall | Tempo Wall | TEMW.09014016/DBE | 90 | 140 | 16 | 17 | 4594 | 4594 | 4594 | 0.10938 | 2297 | 0.05469 | 5053 | 0.12031 | 1 | A02 | TEMW0.09014016/DBE
Horizontal Wall | Tempo Wall | TEMW.09014020 | 90 | 140 | 20 | 22 | 4140 | 4140 | 4140 | 0.098571 | 1652 | 0.039333 | 4699 | 0.11188 | 1.326 | A02 | TEMW0.09014020
Horizontal Wall | Tempo Wall | TEMW.09014021 | 90 | 140 | 21 | 22 | 5278 | 5278 | 5278 | 0.12567 | 1842 | 0.043857 | 6101 | 0.14526 | 1.518 | A02 | TEMW0.09014021
Horizontal Wall | Tempo Wall | TEMW.09014021/DBE | 90 | 140 | 21 | 22 | 6238 | 6238 | 6238 | 0.14852 | 3119 | 0.074262 | 6862 | 0.16338 | 1 | A02 | TEMW0.09014021/DBE
Horizontal Wall | Tempo Wall | TEMW.09016010 | 90 | 160 | 10 | 12 | 2190 | 2190 | 2190 | 0.052143 | 861 | 0.0205 | 2490 | 0.059286 | 1.348 | A02 | TEMW0.09016010
Horizontal Wall | Tempo Wall | TEMW.09016011 | 90 | 160 | 11 | 12 | 2813 | 2813 | 2813 | 0.066976 | 1041 | 0.024786 | 3224 | 0.076762 | 1.434 | A02 | TEMW0.09016011
Horizontal Wall | Tempo Wall | TEMW.09016011/DBE | 90 | 160 | 11 | 12 | 4013 | 4013 | 4013 | 0.095548 | 2007 | 0.047786 | 4414 | 0.1051 | 1 | A02 | TEMW0.09016011/DBE
Horizontal Wall | Tempo Wall | TEMW.09016015 | 90 | 160 | 15 | 17 | 3392 | 3392 | 3392 | 0.080762 | 1353 | 0.032214 | 3850 | 0.091667 | 1.326 | A02 | TEMW0.09016015
Horizontal Wall | Tempo Wall | TEMW.09016016 | 90 | 160 | 16 | 17 | 4154 | 4154 | 4154 | 0.098905 | 1487 | 0.035405 | 4781 | 0.11383 | 1.48 | A02 | TEMW0.09016016
Horizontal Wall | Tempo Wall | TEMW.09016016/DBE | 90 | 160 | 16 | 17 | 6074 | 6074 | 6074 | 0.14462 | 3037 | 0.07231 | 6681 | 0.15907 | 1 | A02 | TEMW0.09016016/DBE
Horizontal Wall | Tempo Wall | TEMW.09016020 | 90 | 160 | 20 | 22 | 4731 | 4731 | 4731 | 0.11264 | 1888 | 0.044952 | 5370 | 0.12786 | 1.326 | A02 | TEMW0.09016020
Horizontal Wall | Tempo Wall | TEMW.09016021 | 90 | 160 | 21 | 22 | 6032 | 6032 | 6032 | 0.14362 | 2105 | 0.050119 | 6973 | 0.16602 | 1.518 | A02 | TEMW0.09016021
Horizontal Wall | Tempo Wall | TEMW.09016021/DBE | 90 | 160 | 21 | 22 | 7952 | 7952 | 7952 | 0.18933 | 3976 | 0.094667 | 8747 | 0.20826 | 1 | A02 | TEMW0.09016021/DBE
Horizontal Wall | Tempo Wall | TEMW.09018010 | 90 | 180 | 10 | 12 | 2464 | 2464 | 2464 | 0.058667 | 968 | 0.023048 | 2802 | 0.066714 | 1.348 | A02 | TEMW0.09018010
Horizontal Wall | Tempo Wall | TEMW.09018011 | 90 | 180 | 11 | 12 | 3164 | 3164 | 3164 | 0.075333 | 1171 | 0.027881 | 3626 | 0.086333 | 1.434 | A02 | TEMW0.09018011
Horizontal Wall | Tempo Wall | TEMW.09018011/DBE | 90 | 180 | 11 | 12 | 4364 | 4364 | 4364 | 0.1039 | 2182 | 0.051952 | 4800 | 0.11429 | 1 | A02 | TEMW0.09018011/DBE
Horizontal Wall | Tempo Wall | TEMW.09018015 | 90 | 180 | 15 | 17 | 3816 | 3816 | 3816 | 0.090857 | 1523 | 0.036262 | 4331 | 0.10312 | 1.326 | A02 | TEMW0.09018015
Horizontal Wall | Tempo Wall | TEMW.09018016 | 90 | 180 | 16 | 17 | 4673 | 4673 | 4673 | 0.11126 | 1673 | 0.039833 | 5379 | 0.12807 | 1.48 | A02 | TEMW0.09018016
Horizontal Wall | Tempo Wall | TEMW.09018016/DBE | 90 | 180 | 16 | 17 | 6593 | 6593 | 6593 | 0.15698 | 3297 | 0.0785 | 7252 | 0.17267 | 1 | A02 | TEMW0.09018016/DBE
Horizontal Wall | Tempo Wall | TEMW.09018020 | 90 | 180 | 20 | 22 | 5323 | 5323 | 5323 | 0.12674 | 2124 | 0.050571 | 6042 | 0.14386 | 1.326 | A02 | TEMW0.09018020
Horizontal Wall | Tempo Wall | TEMW.09018021 | 90 | 180 | 21 | 22 | 6786 | 6786 | 6786 | 0.16157 | 2368 | 0.056381 | 7845 | 0.18679 | 1.518 | A02 | TEMW0.09018021
Horizontal Wall | Tempo Wall | TEMW.09018021/DBE | 90 | 180 | 21 | 22 | 8706 | 8706 | 8706 | 0.20729 | 4353 | 0.10364 | 9577 | 0.22802 | 1 | A02 | TEMW0.09018021/DBE
Horizontal Wall | Tempo Wall | TEMW.09020010 | 90 | 200 | 10 | 12 | 2738 | 2738 | 2738 | 0.06519 | 1076 | 0.025619 | 3113 | 0.074119 | 1.348 | A02 | TEMW0.09020010
Horizontal Wall | Tempo Wall | TEMW.09020011 | 90 | 200 | 11 | 12 | 3516 | 3516 | 3516 | 0.083714 | 1301 | 0.030976 | 4029 | 0.095929 | 1.434 | A02 | TEMW0.09020011
Horizontal Wall | Tempo Wall | TEMW.09020011/DBE | 90 | 200 | 11 | 12 | 4716 | 4716 | 4716 | 0.11229 | 2358 | 0.056143 | 5188 | 0.12352 | 1 | A02 | TEMW0.09020011/DBE
Horizontal Wall | Tempo Wall | TEMW.09020015 | 90 | 200 | 15 | 17 | 4240 | 4240 | 4240 | 0.10095 | 1692 | 0.040286 | 4812 | 0.11457 | 1.326 | A02 | TEMW0.09020015
Horizontal Wall | Tempo Wall | TEMW.09020016 | 90 | 200 | 16 | 17 | 5192 | 5192 | 5192 | 0.12362 | 1859 | 0.044262 | 5976 | 0.14229 | 1.48 | A02 | TEMW0.09020016
Horizontal Wall | Tempo Wall | TEMW.09020016/DBE | 90 | 200 | 16 | 17 | 7112 | 7112 | 7112 | 0.16933 | 3556 | 0.084667 | 7823 | 0.18626 | 1 | A02 | TEMW0.09020016/DBE
Horizontal Wall | Tempo Wall | TEMW.09020020 | 90 | 200 | 20 | 22 | 5914 | 5914 | 5914 | 0.14081 | 2360 | 0.05619 | 6712 | 0.15981 | 1.326 | A02 | TEMW0.09020020
Horizontal Wall | Tempo Wall | TEMW.09020021 | 90 | 200 | 21 | 22 | 7540 | 7540 | 7540 | 0.17952 | 2631 | 0.062643 | 8716 | 0.20752 | 1.518 | A02 | TEMW0.09020021
Horizontal Wall | Tempo Wall | TEMW.09020021/DBE | 90 | 200 | 21 | 22 | 9460 | 9460 | 9460 | 0.22524 | 4730 | 0.11262 | 10406 | 0.24776 | 1 | A02 | TEMW0.09020021/DBE
Horizontal Wall | Tempo Wall | TEMW.09022010 | 90 | 220 | 10 | 12 | 3012 | 3012 | 3012 | 0.071714 | 1184 | 0.02819 | 3425 | 0.081548 | 1.348 | A02 | TEMW0.09022010
Horizontal Wall | Tempo Wall | TEMW.09022011 | 90 | 220 | 11 | 12 | 3868 | 3868 | 3868 | 0.092095 | 1431 | 0.034071 | 4433 | 0.10555 | 1.434 | A02 | TEMW0.09022011
Horizontal Wall | Tempo Wall | TEMW.09022011/DBE | 90 | 220 | 11 | 12 | 5068 | 5068 | 5068 | 0.12067 | 2534 | 0.060333 | 5575 | 0.13274 | 1 | A02 | TEMW0.09022011/DBE
Horizontal Wall | Tempo Wall | TEMW.09022015 | 90 | 220 | 15 | 17 | 4664 | 4664 | 4664 | 0.11105 | 1861 | 0.04431 | 5294 | 0.12605 | 1.326 | A02 | TEMW0.09022015
Horizontal Wall | Tempo Wall | TEMW.09022016 | 90 | 220 | 16 | 17 | 5711 | 5711 | 5711 | 0.13598 | 2045 | 0.04869 | 6573 | 0.1565 | 1.48 | A02 | TEMW0.09022016
Horizontal Wall | Tempo Wall | TEMW.09022016/DBE | 90 | 220 | 16 | 17 | 7631 | 7631 | 7631 | 0.18169 | 3816 | 0.090857 | 8394 | 0.19986 | 1 | A02 | TEMW0.09022016/DBE
Horizontal Wall | Tempo Wall | TEMW.09022020 | 90 | 220 | 20 | 22 | 6505 | 6505 | 6505 | 0.15488 | 2595 | 0.061786 | 7383 | 0.17579 | 1.326 | A02 | TEMW0.09022020
Horizontal Wall | Tempo Wall | TEMW.09022021 | 90 | 220 | 21 | 22 | 8294 | 8294 | 8294 | 0.19748 | 2895 | 0.068929 | 9588 | 0.22829 | 1.518 | A02 | TEMW0.09022021
Horizontal Wall | Tempo Wall | TEMW.09022021/DBE | 90 | 220 | 21 | 22 | 10214 | 10214 | 10214 | 0.24319 | 5107 | 0.1216 | 11235 | 0.2675 | 1 | A02 | TEMW0.09022021/DBE
Horizontal Wall | Tempo Wall | TEMW.09024010 | 90 | 240 | 10 | 12 | 3286 | 3286 | 3286 | 0.078238 | 1291 | 0.030738 | 3736 | 0.088952 | 1.348 | A02 | TEMW0.09024010
Horizontal Wall | Tempo Wall | TEMW.09024011 | 90 | 240 | 11 | 12 | 4219 | 4219 | 4219 | 0.10045 | 1561 | 0.037167 | 4835 | 0.11512 | 1.434 | A02 | TEMW0.09024011
Horizontal Wall | Tempo Wall | TEMW.09024011/DBE | 90 | 240 | 11 | 12 | 6019 | 6019 | 6019 | 0.14331 | 3010 | 0.071667 | 6621 | 0.15764 | 1 | A02 | TEMW0.09024011/DBE
Horizontal Wall | Tempo Wall | TEMW.09024015 | 90 | 240 | 15 | 17 | 5088 | 5088 | 5088 | 0.12114 | 2030 | 0.048333 | 5775 | 0.1375 | 1.326 | A02 | TEMW0.09024015
Horizontal Wall | Tempo Wall | TEMW.09024016 | 90 | 240 | 16 | 17 | 6230 | 6230 | 6230 | 0.14833 | 2230 | 0.053095 | 7171 | 0.17074 | 1.48 | A02 | TEMW0.09024016
Horizontal Wall | Tempo Wall | TEMW.09024016/DBE | 90 | 240 | 16 | 17 | 9110 | 9110 | 9110 | 0.2169 | 4555 | 0.10845 | 10021 | 0.2386 | 1 | A02 | TEMW0.09024016/DBE
Horizontal Wall | Tempo Wall | TEMW.09024020 | 90 | 240 | 20 | 22 | 7097 | 7097 | 7097 | 0.16898 | 2832 | 0.067429 | 8055 | 0.19179 | 1.326 | A02 | TEMW0.09024020
Horizontal Wall | Tempo Wall | TEMW.09024021 | 90 | 240 | 21 | 22 | 9048 | 9048 | 9048 | 0.21543 | 3158 | 0.07519 | 10459 | 0.24902 | 1.518 | A02 | TEMW0.09024021
Horizontal Wall | Tempo Wall | TEMW.09024021/DBE | 90 | 240 | 21 | 22 | 11928 | 11928 | 11928 | 0.284 | 5964 | 0.142 | 13121 | 0.3124 | 1 | A02 | TEMW0.09024021/DBE
Horizontal Wall | Tempo Wall | TEMW.09026010 | 90 | 260 | 10 | 12 | 3559 | 3559 | 3559 | 0.084738 | 1399 | 0.03331 | 4047 | 0.096357 | 1.348 | A02 | TEMW0.09026010
Horizontal Wall | Tempo Wall | TEMW.09026011 | 90 | 260 | 11 | 12 | 4571 | 4571 | 4571 | 0.10883 | 1691 | 0.040262 | 5238 | 0.12471 | 1.434 | A02 | TEMW0.09026011
Horizontal Wall | Tempo Wall | TEMW.09026011/DBE | 90 | 260 | 11 | 12 | 6371 | 6371 | 6371 | 0.15169 | 3186 | 0.075857 | 7008 | 0.16686 | 1 | A02 | TEMW0.09026011/DBE
Horizontal Wall | Tempo Wall | TEMW.09026015 | 90 | 260 | 15 | 17 | 5512 | 5512 | 5512 | 0.13124 | 2199 | 0.052357 | 6256 | 0.14895 | 1.326 | A02 | TEMW0.09026015
Horizontal Wall | Tempo Wall | TEMW.09026016 | 90 | 260 | 16 | 17 | 6750 | 6750 | 6750 | 0.16071 | 2417 | 0.057548 | 7769 | 0.18498 | 1.48 | A02 | TEMW0.09026016
Horizontal Wall | Tempo Wall | TEMW.09026016/DBE | 90 | 260 | 16 | 17 | 9630 | 9630 | 9630 | 0.22929 | 4815 | 0.11464 | 10593 | 0.25221 | 1 | A02 | TEMW0.09026016/DBE
Horizontal Wall | Tempo Wall | TEMW.09026020 | 90 | 260 | 20 | 22 | 7688 | 7688 | 7688 | 0.18305 | 3068 | 0.073048 | 8726 | 0.20776 | 1.326 | A02 | TEMW0.09026020
Horizontal Wall | Tempo Wall | TEMW.09026021 | 90 | 260 | 21 | 22 | 9802 | 9802 | 9802 | 0.23338 | 3421 | 0.081452 | 11331 | 0.26979 | 1.518 | A02 | TEMW0.09026021
Horizontal Wall | Tempo Wall | TEMW.09026021/DBE | 90 | 260 | 21 | 22 | 12682 | 12682 | 12682 | 0.30195 | 6341 | 0.15098 | 13950 | 0.33214 | 1 | A02 | TEMW0.09026021/DBE
Horizontal Wall | Tempo Wall | TEMW.09028010 | 90 | 280 | 10 | 12 | 3833 | 3833 | 3833 | 0.091262 | 1506 | 0.035857 | 4358 | 0.10376 | 1.348 | A02 | TEMW0.09028010
Horizontal Wall | Tempo Wall | TEMW.09028011 | 90 | 280 | 11 | 12 | 4922 | 4922 | 4922 | 0.11719 | 1821 | 0.043357 | 5641 | 0.13431 | 1.434 | A02 | TEMW0.09028011
Horizontal Wall | Tempo Wall | TEMW.09028011/DBE | 90 | 280 | 11 | 12 | 6722 | 6722 | 6722 | 0.16005 | 3361 | 0.080024 | 7394 | 0.17605 | 1 | A02 | TEMW0.09028011/DBE
Horizontal Wall | Tempo Wall | TEMW.09028015 | 90 | 280 | 15 | 17 | 5936 | 5936 | 5936 | 0.14133 | 2368 | 0.056381 | 6737 | 0.1604 | 1.326 | A02 | TEMW0.09028015
Horizontal Wall | Tempo Wall | TEMW.09028016 | 90 | 280 | 16 | 17 | 7269 | 7269 | 7269 | 0.17307 | 2602 | 0.061952 | 8367 | 0.19921 | 1.48 | A02 | TEMW0.09028016
Horizontal Wall | Tempo Wall | TEMW.09028016/DBE | 90 | 280 | 16 | 17 | 10149 | 10149 | 10149 | 0.24164 | 5075 | 0.12083 | 11164 | 0.26581 | 1 | A02 | TEMW0.09028016/DBE
Horizontal Wall | Tempo Wall | TEMW.09028020 | 90 | 280 | 20 | 22 | 8280 | 8280 | 8280 | 0.19714 | 3304 | 0.078667 | 9398 | 0.22376 | 1.326 | A02 | TEMW0.09028020
Horizontal Wall | Tempo Wall | TEMW.09028021 | 90 | 280 | 21 | 22 | 10556 | 10556 | 10556 | 0.25133 | 3684 | 0.087714 | 12203 | 0.29055 | 1.518 | A02 | TEMW0.09028021
Horizontal Wall | Tempo Wall | TEMW.09028021/DBE | 90 | 280 | 21 | 22 | 13436 | 13436 | 13436 | 0.3199 | 6718 | 0.15995 | 14780 | 0.3519 | 1 | A02 | TEMW0.09028021/DBE
Horizontal Wall | Tempo Wall | TEMW.09030010 | 90 | 300 | 10 | 12 | 4107 | 4107 | 4107 | 0.097786 | 1614 | 0.038429 | 4670 | 0.11119 | 1.348 | A02 | TEMW0.09030010
Horizontal Wall | Tempo Wall | TEMW.09030011 | 90 | 300 | 11 | 12 | 5274 | 5274 | 5274 | 0.12557 | 1951 | 0.046452 | 6044 | 0.1439 | 1.434 | A02 | TEMW0.09030011
Horizontal Wall | Tempo Wall | TEMW.09030011/DBE | 90 | 300 | 11 | 12 | 7074 | 7074 | 7074 | 0.16843 | 3537 | 0.084214 | 7781 | 0.18526 | 1 | A02 | TEMW0.09030011/DBE
Horizontal Wall | Tempo Wall | TEMW.09030015 | 90 | 300 | 15 | 17 | 6360 | 6360 | 6360 | 0.15143 | 2538 | 0.060429 | 7219 | 0.17188 | 1.326 | A02 | TEMW0.09030015
Horizontal Wall | Tempo Wall | TEMW.09030016 | 90 | 300 | 16 | 17 | 7788 | 7788 | 7788 | 0.18543 | 2788 | 0.066381 | 8964 | 0.21343 | 1.48 | A02 | TEMW0.09030016
Horizontal Wall | Tempo Wall | TEMW.09030016/DBE | 90 | 300 | 16 | 17 | 10668 | 10668 | 10668 | 0.254 | 5334 | 0.127 | 11735 | 0.2794 | 1 | A02 | TEMW0.09030016/DBE
Horizontal Wall | Tempo Wall | TEMW.09030020 | 90 | 300 | 20 | 22 | 8871 | 8871 | 8871 | 0.21121 | 3540 | 0.084286 | 10069 | 0.23974 | 1.326 | A02 | TEMW0.09030020
Horizontal Wall | Tempo Wall | TEMW.09030021 | 90 | 300 | 21 | 22 | 11310 | 11310 | 11310 | 0.26929 | 3947 | 0.093976 | 13074 | 0.31129 | 1.518 | A02 | TEMW0.09030021
Horizontal Wall | Tempo Wall | TEMW.09030021/DBE | 90 | 300 | 21 | 22 | 14190 | 14190 | 14190 | 0.33786 | 7095 | 0.16893 | 15609 | 0.37164 | 1 | A02 | TEMW0.09030021/DBE
Vertical Wall | Vertiga | VERW.20004108/GLO/01 | 200 | 41 | 08 | 9 | 1448 | 1448 | 1448 | 0.034476 | 720 | 0.017143 | 1583 | 0.03769 | 1 | B12 | VERW0.20004108/GLO/01
Vertical Wall | Vertiga | VERW.20004108/PRI/01 | 200 | 41 | 08 | 9 | 1448 | 1448 | 1448 | 0.034476 | 720 | 0.017143 | 1583 | 0.03769 | 1 | B12 | VERW0.20004108/PRI/01
Vertical Wall | Vertiga | VERW.20005208/GLO/01 | 200 | 52 | 08 | 9 | 1632 | 1632 | 1632 | 0.038857 | 826 | 0.019667 | 1817 | 0.043262 | 1 | B12 | VERW0.20005208/GLO/01
Vertical Wall | Vertiga | VERW.20005208/PRI/01 | 200 | 52 | 08 | 9 | 1632 | 1632 | 1632 | 0.038857 | 826 | 0.019667 | 1817 | 0.043262 | 1 | B12 | VERW0.20005208/PRI/01
Vertical Wall | Vertiga | VERW.20005312/GLO/01 | 200 | 53 | 12 | 13 | 2868 | 2868 | 2868 | 0.068286 | 1395 | 0.033214 | 3069 | 0.073071 | 1 | B12 | VERW0.20005312/GLO/01
Vertical Wall | Vertiga | VERW.20005312/PRI/01 | 200 | 53 | 12 | 13 | 2868 | 2868 | 2868 | 0.068286 | 1395 | 0.033214 | 3069 | 0.073071 | 1 | B12 | VERW0.20005312/PRI/01
Vertical Wall | Vertiga | VERW.20006508/GLO/01 | 200 | 65 | 08 | 9 | 1870 | 1870 | 1870 | 0.044524 | 956 | 0.022762 | 2102 | 0.050048 | 1 | B12 | VERW0.20006508/GLO/01
Vertical Wall | Vertiga | VERW.20006508/PRI/01 | 200 | 65 | 08 | 9 | 1870 | 1870 | 1870 | 0.044524 | 956 | 0.022762 | 2102 | 0.050048 | 1 | B12 | VERW0.20006508/PRI/01
Vertical Wall | Vertiga | VERW.20007012/GLO/01 | 200 | 70 | 12 | 13 | 4170 | 4170 | 4170 | 0.099286 | 2023 | 0.048167 | 4450 | 0.10595 | 1 | B12 | VERW0.20007012/GLO/01
Vertical Wall | Vertiga | VERW.20007012/PRI/01 | 200 | 70 | 12 | 13 | 4170 | 4170 | 4170 | 0.099286 | 2023 | 0.048167 | 4450 | 0.10595 | 1 | B12 | VERW0.20007012/PRI/01
Vertical Wall | Vertiga | VERW.20009012/GLO/01 | 200 | 90 | 12 | 13 | 4761 | 4761 | 4761 | 0.11336 | 2381 | 0.05669 | 5237 | 0.12469 | 1 | B12 | VERW0.20009012/GLO/01
Vertical Wall | Vertiga | VERW.20009012/PRI/01 | 200 | 90 | 12 | 13 | 4761 | 4761 | 4761 | 0.11336 | 2381 | 0.05669 | 5237 | 0.12469 | 1 | B12 | VERW0.20009012/PRI/01
Selectionmodel 2015-07
Metric

## Towel Rails & Architectural Rad
[5 empty] | Entering T | ºC |  |  | 75
[5 empty] | Return T | ºC |  |  | 65
[5 empty] | Air T | ºC |  |  | 20
[5 empty] | Mean T | ºC |  |  | 70
HEATING (with DBE: fans in comfort speed)
LA/220615 | [8 empty] | 75/65/20º |  | 50/40/20º |  | 80/70/20º
Group | Model | Productcode | H in cm | L in cm | Type | D in cm | 75/65/20ºC | 167/149/68ºF | Watt | Flow in l/s | Watt | Flow in l/s | Watt | Flow in l/s | N-Waarde (EN442) | SalesGroup | JagaSourceCode Stnd
Towel rail | Accolade Deco | ACDW.089050 | 89 | 50 |  | 11 | 565 | 565 | 565 | 0.013452 | 231 | 0.0055 | 639 | 0.015214 | 1.292 | B05 | ACDW0.089050
Towel rail | Accolade Deco | ACDW.089065 | 89 | 65 |  | 11 | 715 | 715 | 715 | 0.017024 | 292 | 0.0069524 | 809 | 0.019262 | 1.289 | B05 | ACDW0.089065
Towel rail | Accolade Deco | ACDW.089080 | 89 | 80 |  | 11 | 864 | 864 | 864 | 0.020571 | 354 | 0.0084286 | 977 | 0.023262 | 1.287 | B05 | ACDW0.089080
Towel rail | Accolade Deco | ACDW.089095 | 89 | 95 |  | 11 | 1014 | 1014 | 1014 | 0.024143 | 416 | 0.0099048 | 1146 | 0.027286 | 1.286 | B05 | ACDW0.089095
Towel rail | Accolade Deco | ACDW.122050 | 122 | 50 |  | 11 | 750 | 750 | 750 | 0.017857 | 305 | 0.0072619 | 849 | 0.020214 | 1.3 | B05 | ACDW0.122050
Towel rail | Accolade Deco | ACDW.122065 | 122 | 65 |  | 11 | 964 | 964 | 964 | 0.022952 | 395 | 0.0094048 | 1089 | 0.025929 | 1.286 | B05 | ACDW0.122065
Towel rail | Accolade Deco | ACDW.122080 | 122 | 80 |  | 11 | 1178 | 1178 | 1178 | 0.028048 | 485 | 0.011548 | 1331 | 0.03169 | 1.278 | B05 | ACDW0.122080
Towel rail | Accolade Deco | ACDW.122095 | 122 | 95 |  | 11 | 1392 | 1392 | 1392 | 0.033143 | 576 | 0.013714 | 1572 | 0.037429 | 1.272 | B05 | ACDW0.122095
Towel rail | Accolade Deco | ACDW.153050 | 153 | 50 |  | 11 | 920 | 920 | 920 | 0.021905 | 372 | 0.0088571 | 1042 | 0.02481 | 1.307 | B05 | ACDW0.153050
Towel rail | Accolade Deco | ACDW.153065 | 153 | 65 |  | 11 | 1185 | 1185 | 1185 | 0.028214 | 487 | 0.011595 | 1339 | 0.031881 | 1.284 | B05 | ACDW0.153065
Towel rail | Accolade Deco | ACDW.153080 | 153 | 80 |  | 11 | 1450 | 1450 | 1450 | 0.034524 | 602 | 0.014333 | 1637 | 0.038976 | 1.269 | B05 | ACDW0.153080
Towel rail | Accolade Deco | ACDW.153095 | 153 | 95 |  | 11 | 1715 | 1715 | 1715 | 0.040833 | 717 | 0.017071 | 1933 | 0.046024 | 1.259 | B05 | ACDW0.153095
Towel rail | Accolade Deco | ACDW.181050 | 181 | 50 |  | 11 | 1076 | 1076 | 1076 | 0.025619 | 433 | 0.01031 | 1219 | 0.029024 | 1.313 | B05 | ACDW0.181050
Towel rail | Accolade Deco | ACDW.181065 | 181 | 65 |  | 11 | 1380 | 1380 | 1380 | 0.032857 | 567 | 0.0135 | 1559 | 0.037119 | 1.282 | B05 | ACDW0.181065
Towel rail | Accolade Deco | ACDW.181080 | 181 | 80 |  | 11 | 1683 | 1683 | 1683 | 0.040071 | 702 | 0.016714 | 1898 | 0.04519 | 1.262 | B05 | ACDW0.181080
Towel rail | Accolade Deco | ACDW.181095 | 181 | 95 |  | 11 | 1987 | 1987 | 1987 | 0.04731 | 837 | 0.019929 | 2237 | 0.053262 | 1.248 | B05 | ACDW0.181095
Towel rail | Accolade Deco | ACDW.215050 | 215 | 50 |  | 11 | 1267 | 1267 | 1267 | 0.030167 | 507 | 0.012071 | 1437 | 0.034214 | 1.321 | B05 | ACDW0.215050
Towel rail | Accolade Deco | ACDW.215065 | 215 | 65 |  | 11 | 1607 | 1607 | 1607 | 0.038262 | 662 | 0.015762 | 1816 | 0.043238 | 1.279 | B05 | ACDW0.215065
Towel rail | Accolade Deco | ACDW.215080 | 215 | 80 |  | 11 | 1947 | 1947 | 1947 | 0.046357 | 818 | 0.019476 | 2194 | 0.052238 | 1.253 | B05 | ACDW0.215080
Towel rail | Accolade Deco | ACDW.215095 | 215 | 95 |  | 11 | 2287 | 2287 | 2287 | 0.054452 | 972 | 0.023143 | 2573 | 0.061262 | 1.234 | B05 | ACDW0.215095
Towel rail | Accolade Sani | ACSW.089050 | 89 | 50 |  | 11 | 502 | 502 | 502 | 0.011952 | 205 | 0.004881 | 568 | 0.013524 | 1.289 | B05 | ACSW0.089050
Towel rail | Accolade Sani | ACSW.089065 | 89 | 65 |  | 11 | 629 | 629 | 629 | 0.014976 | 257 | 0.006119 | 711 | 0.016929 | 1.29 | B05 | ACSW0.089065
Towel rail | Accolade Sani | ACSW.089080 | 89 | 80 |  | 11 | 756 | 756 | 756 | 0.018 | 309 | 0.0073571 | 855 | 0.020357 | 1.29 | B05 | ACSW0.089080
Towel rail | Accolade Sani | ACSW.089095 | 89 | 95 |  | 11 | 883 | 883 | 883 | 0.021024 | 361 | 0.0085952 | 999 | 0.023786 | 1.291 | B05 | ACSW0.089095
Towel rail | Accolade Sani | ACSW.122050 | 122 | 50 |  | 11 | 688 | 688 | 688 | 0.016381 | 280 | 0.0066667 | 779 | 0.018548 | 1.297 | B05 | ACSW0.122050
Towel rail | Accolade Sani | ACSW.122065 | 122 | 65 |  | 11 | 882 | 882 | 882 | 0.021 | 362 | 0.008619 | 998 | 0.023762 | 1.287 | B05 | ACSW0.122065
Towel rail | Accolade Sani | ACSW.122080 | 122 | 80 |  | 11 | 1075 | 1075 | 1075 | 0.025595 | 443 | 0.010548 | 1215 | 0.028929 | 1.281 | B05 | ACSW0.122080
Towel rail | Accolade Sani | ACSW.122095 | 122 | 95 |  | 11 | 1269 | 1269 | 1269 | 0.030214 | 524 | 0.012476 | 1433 | 0.034119 | 1.277 | B05 | ACSW0.122095
Towel rail | Accolade Sani | ACSW.153050 | 153 | 50 |  | 11 | 827 | 827 | 827 | 0.01969 | 335 | 0.0079762 | 936 | 0.022286 | 1.303 | B05 | ACSW0.153050
Towel rail | Accolade Sani | ACSW.153065 | 153 | 65 |  | 11 | 1065 | 1065 | 1065 | 0.025357 | 437 | 0.010405 | 1203 | 0.028643 | 1.285 | B05 | ACSW0.153065
Towel rail | Accolade Sani | ACSW.153080 | 153 | 80 |  | 11 | 1303 | 1303 | 1303 | 0.031024 | 539 | 0.012833 | 1471 | 0.035024 | 1.274 | B05 | ACSW0.153080
Towel rail | Accolade Sani | ACSW.153095 | 153 | 95 |  | 11 | 1542 | 1542 | 1542 | 0.036714 | 641 | 0.015262 | 1739 | 0.041405 | 1.266 | B05 | ACSW0.153095
Towel rail | Accolade Sani | ACSW.181050 | 181 | 50 |  | 11 | 982 | 982 | 982 | 0.023381 | 397 | 0.0094524 | 1113 | 0.0265 | 1.309 | B05 | ACSW0.181050
Towel rail | Accolade Sani | ACSW.181065 | 181 | 65 |  | 11 | 1263 | 1263 | 1263 | 0.030071 | 519 | 0.012357 | 1427 | 0.033976 | 1.283 | B05 | ACSW0.181065
Towel rail | Accolade Sani | ACSW.181080 | 181 | 80 |  | 11 | 1545 | 1545 | 1545 | 0.036786 | 643 | 0.01531 | 1743 | 0.0415 | 1.266 | B05 | ACSW0.181080
Towel rail | Accolade Sani | ACSW.181095 | 181 | 95 |  | 11 | 1826 | 1826 | 1826 | 0.043476 | 765 | 0.018214 | 2058 | 0.049 | 1.255 | B05 | ACSW0.181095
Towel rail | Accolade Sani | ACSW.215050 | 215 | 50 |  | 11 | 1171 | 1171 | 1171 | 0.027881 | 470 | 0.01119 | 1328 | 0.031619 | 1.317 | B05 | ACSW0.215050
Towel rail | Accolade Sani | ACSW.215065 | 215 | 65 |  | 11 | 1494 | 1494 | 1494 | 0.035571 | 616 | 0.014667 | 1688 | 0.04019 | 1.281 | B05 | ACSW0.215065
Towel rail | Accolade Sani | ACSW.215080 | 215 | 80 |  | 11 | 1818 | 1818 | 1818 | 0.043286 | 760 | 0.018095 | 2049 | 0.048786 | 1.257 | B05 | ACSW0.215080
Towel rail | Accolade Sani | ACSW.215095 | 215 | 95 |  | 11 | 2141 | 2141 | 2141 | 0.050976 | 906 | 0.021571 | 2411 | 0.057405 | 1.241 | B05 | ACSW0.215095
Vertical Wall | Iguana Angula PLUS | ANPW.180040/CL | 180 | 40 |  | 12 | 1745 | 1745 | 1745 | 0.041548 | 682 | 0.016238 | 1986 | 0.047286 | 1.355 | B01 | ANPW0.180040/CL
Vertical Wall | Iguana Angula PLUS | ANPW.180040/CR | 180 | 40 |  | 12 | 1745 | 1745 | 1745 | 0.041548 | 682 | 0.016238 | 1986 | 0.047286 | 1.355 | B01 | ANPW0.180040/CR
Vertical Wall | Iguana Angula PLUS | ANPW.180046/CL | 180 | 46 |  | 12 | 2078 | 2078 | 2078 | 0.049476 | 812 | 0.019333 | 2365 | 0.05631 | 1.355 | B01 | ANPW0.180046/CL
Vertical Wall | Iguana Angula PLUS | ANPW.180046/CR | 180 | 46 |  | 12 | 2078 | 2078 | 2078 | 0.049476 | 812 | 0.019333 | 2365 | 0.05631 | 1.355 | B01 | ANPW0.180046/CR
Vertical Wall | Iguana Angula PLUS | ANPW.180051/CL | 180 | 51 |  | 12 | 2410 | 2410 | 2410 | 0.057381 | 942 | 0.022429 | 2743 | 0.06531 | 1.355 | B01 | ANPW0.180051/CL
Vertical Wall | Iguana Angula PLUS | ANPW.180051/CR | 180 | 51 |  | 12 | 2410 | 2410 | 2410 | 0.057381 | 942 | 0.022429 | 2743 | 0.06531 | 1.355 | B01 | ANPW0.180051/CR
Vertical Wall | Iguana Angula PLUS | ANPW.192040/CL | 192 | 40 |  | 12 | 1823 | 1823 | 1823 | 0.043405 | 718 | 0.017095 | 2073 | 0.049357 | 1.343 | B01 | ANPW0.192040/CL
Vertical Wall | Iguana Angula PLUS | ANPW.192040/CR | 192 | 40 |  | 12 | 1823 | 1823 | 1823 | 0.043405 | 718 | 0.017095 | 2073 | 0.049357 | 1.343 | B01 | ANPW0.192040/CR
Vertical Wall | Iguana Angula PLUS | ANPW.192046/CL | 192 | 46 |  | 12 | 2170 | 2170 | 2170 | 0.051667 | 855 | 0.020357 | 2467 | 0.058738 | 1.343 | B01 | ANPW0.192046/CL
Vertical Wall | Iguana Angula PLUS | ANPW.192046/CR | 192 | 46 |  | 12 | 2170 | 2170 | 2170 | 0.051667 | 855 | 0.020357 | 2467 | 0.058738 | 1.343 | B01 | ANPW0.192046/CR
Vertical Wall | Iguana Angula PLUS | ANPW.192051/CL | 192 | 51 |  | 12 | 2517 | 2517 | 2517 | 0.059929 | 992 | 0.023619 | 2862 | 0.068143 | 1.343 | B01 | ANPW0.192051/CL
Vertical Wall | Iguana Angula PLUS | ANPW.192051/CR | 192 | 51 |  | 12 | 2517 | 2517 | 2517 | 0.059929 | 992 | 0.023619 | 2862 | 0.068143 | 1.343 | B01 | ANPW0.192051/CR
Vertical Wall | Iguana Angula PLUS | ANPW.200040/CL | 200 | 40 |  | 12 | 1871 | 1871 | 1871 | 0.044548 | 741 | 0.017643 | 2125 | 0.050595 | 1.335 | B01 | ANPW0.200040/CL
Vertical Wall | Iguana Angula PLUS | ANPW.200040/CR | 200 | 40 |  | 12 | 1871 | 1871 | 1871 | 0.044548 | 741 | 0.017643 | 2125 | 0.050595 | 1.335 | B01 | ANPW0.200040/CR
Vertical Wall | Iguana Angula PLUS | ANPW.200046/CL | 200 | 46 |  | 12 | 2228 | 2228 | 2228 | 0.053048 | 882 | 0.021 | 2531 | 0.060262 | 1.335 | B01 | ANPW0.200046/CL
Vertical Wall | Iguana Angula PLUS | ANPW.200046/CR | 200 | 46 |  | 12 | 2228 | 2228 | 2228 | 0.053048 | 882 | 0.021 | 2531 | 0.060262 | 1.335 | B01 | ANPW0.200046/CR
Vertical Wall | Iguana Angula PLUS | ANPW.200051/CL | 200 | 51 |  | 12 | 2584 | 2584 | 2584 | 0.061524 | 1023 | 0.024357 | 2935 | 0.069881 | 1.335 | B01 | ANPW0.200051/CL
Vertical Wall | Iguana Angula PLUS | ANPW.200051/CR | 200 | 51 |  | 12 | 2584 | 2584 | 2584 | 0.061524 | 1023 | 0.024357 | 2935 | 0.069881 | 1.335 | B01 | ANPW0.200051/CR
Vertical Wall | Iguana Angula PLUS | ANPW.220040/CL | 220 | 40 |  | 12 | 1978 | 1978 | 1978 | 0.047095 | 795 | 0.018929 | 2243 | 0.053405 | 1.315 | B01 | ANPW0.220040/CL
Vertical Wall | Iguana Angula PLUS | ANPW.220040/CR | 220 | 40 |  | 12 | 1978 | 1978 | 1978 | 0.047095 | 795 | 0.018929 | 2243 | 0.053405 | 1.315 | B01 | ANPW0.220040/CR
Vertical Wall | Iguana Angula PLUS | ANPW.220046/CL | 220 | 46 |  | 12 | 2355 | 2355 | 2355 | 0.056071 | 947 | 0.022548 | 2671 | 0.063595 | 1.315 | B01 | ANPW0.220046/CL
Vertical Wall | Iguana Angula PLUS | ANPW.220046/CR | 220 | 46 |  | 12 | 2355 | 2355 | 2355 | 0.056071 | 947 | 0.022548 | 2671 | 0.063595 | 1.315 | B01 | ANPW0.220046/CR
Vertical Wall | Iguana Angula PLUS | ANPW.220051/CL | 220 | 51 |  | 12 | 2732 | 2732 | 2732 | 0.065048 | 1098 | 0.026143 | 3098 | 0.073762 | 1.315 | B01 | ANPW0.220051/CL
Vertical Wall | Iguana Angula PLUS | ANPW.220051/CR | 220 | 51 |  | 12 | 2732 | 2732 | 2732 | 0.065048 | 1098 | 0.026143 | 3098 | 0.073762 | 1.315 | B01 | ANPW0.220051/CR
Vertical Wall | Iguana Angula PLUS | ANPW.240040/CL | 240 | 40 |  | 12 | 2066 | 2066 | 2066 | 0.04919 | 843 | 0.020071 | 2337 | 0.055643 | 1.295 | B01 | ANPW0.240040/CL
Vertical Wall | Iguana Angula PLUS | ANPW.240040/CR | 240 | 40 |  | 12 | 2066 | 2066 | 2066 | 0.04919 | 843 | 0.020071 | 2337 | 0.055643 | 1.295 | B01 | ANPW0.240040/CR
Vertical Wall | Iguana Angula PLUS | ANPW.240046/CL | 240 | 46 |  | 12 | 2460 | 2460 | 2460 | 0.058571 | 1004 | 0.023905 | 2782 | 0.066238 | 1.295 | B01 | ANPW0.240046/CL
Vertical Wall | Iguana Angula PLUS | ANPW.240046/CR | 240 | 46 |  | 12 | 2460 | 2460 | 2460 | 0.058571 | 1004 | 0.023905 | 2782 | 0.066238 | 1.295 | B01 | ANPW0.240046/CR
Vertical Wall | Iguana Angula PLUS | ANPW.240051/CL | 240 | 51 |  | 12 | 2854 | 2854 | 2854 | 0.067952 | 1164 | 0.027714 | 3228 | 0.076857 | 1.295 | B01 | ANPW0.240051/CL
Vertical Wall | Iguana Angula PLUS | ANPW.240051/CR | 240 | 51 |  | 12 | 2854 | 2854 | 2854 | 0.067952 | 1164 | 0.027714 | 3228 | 0.076857 | 1.295 | B01 | ANPW0.240051/CR
Vertical Wall | Iguana Aplano PLUS | APPW.180030 | 180 | 30 |  | 12 | 964 | 964 | 964 | 0.022952 | 359 | 0.0085476 | 1105 | 0.02631 | 1.428 | B01 | APPW0.180030
Vertical Wall | Iguana Aplano PLUS | APPW.180041 | 180 | 41 |  | 12 | 1314 | 1314 | 1314 | 0.031286 | 489 | 0.011643 | 1506 | 0.035857 | 1.428 | B01 | APPW0.180041
Vertical Wall | Iguana Aplano PLUS | APPW.180052 | 180 | 52 |  | 12 | 1664 | 1664 | 1664 | 0.039619 | 619 | 0.014738 | 1907 | 0.045405 | 1.428 | B01 | APPW0.180052
Vertical Wall | Iguana Aplano PLUS | APPW.180063 | 180 | 63 |  | 12 | 2015 | 2015 | 2015 | 0.047976 | 750 | 0.017857 | 2309 | 0.054976 | 1.428 | B01 | APPW0.180063
Vertical Wall | Iguana Aplano PLUS | APPW.180074 | 180 | 74 |  | 12 | 2365 | 2365 | 2365 | 0.05631 | 880 | 0.020952 | 2710 | 0.064524 | 1.428 | B01 | APPW0.180074
Vertical Wall | Iguana Aplano PLUS | APPW.180085 | 180 | 85 |  | 12 | 2716 | 2716 | 2716 | 0.064667 | 1010 | 0.024048 | 3113 | 0.074119 | 1.428 | B01 | APPW0.180085
Vertical Wall | Iguana Aplano PLUS | APPW.192030 | 192 | 30 |  | 12 | 997 | 997 | 997 | 0.023738 | 370 | 0.0088095 | 1143 | 0.027214 | 1.429 | B01 | APPW0.192030
Vertical Wall | Iguana Aplano PLUS | APPW.192041 | 192 | 41 |  | 12 | 1359 | 1359 | 1359 | 0.032357 | 504 | 0.012 | 1557 | 0.037071 | 1.429 | B01 | APPW0.192041
Vertical Wall | Iguana Aplano PLUS | APPW.192052 | 192 | 52 |  | 12 | 1721 | 1721 | 1721 | 0.040976 | 638 | 0.01519 | 1972 | 0.046952 | 1.429 | B01 | APPW0.192052
Vertical Wall | Iguana Aplano PLUS | APPW.192063 | 192 | 63 |  | 12 | 2084 | 2084 | 2084 | 0.049619 | 773 | 0.018405 | 2388 | 0.056857 | 1.429 | B01 | APPW0.192063
Vertical Wall | Iguana Aplano PLUS | APPW.192074 | 192 | 74 |  | 12 | 2446 | 2446 | 2446 | 0.058238 | 907 | 0.021595 | 2803 | 0.066738 | 1.429 | B01 | APPW0.192074
Vertical Wall | Iguana Aplano PLUS | APPW.192085 | 192 | 85 |  | 12 | 2809 | 2809 | 2809 | 0.066881 | 1042 | 0.02481 | 3219 | 0.076643 | 1.429 | B01 | APPW0.192085
Vertical Wall | Iguana Aplano PLUS | APPW.200030 | 200 | 30 |  | 12 | 1018 | 1018 | 1018 | 0.024238 | 378 | 0.009 | 1167 | 0.027786 | 1.429 | B01 | APPW0.200030
Vertical Wall | Iguana Aplano PLUS | APPW.200041 | 200 | 41 |  | 12 | 1388 | 1388 | 1388 | 0.033048 | 515 | 0.012262 | 1591 | 0.037881 | 1.429 | B01 | APPW0.200041
Vertical Wall | Iguana Aplano PLUS | APPW.200052 | 200 | 52 |  | 12 | 1758 | 1758 | 1758 | 0.041857 | 652 | 0.015524 | 2015 | 0.047976 | 1.429 | B01 | APPW0.200052
Vertical Wall | Iguana Aplano PLUS | APPW.200063 | 200 | 63 |  | 12 | 2128 | 2128 | 2128 | 0.050667 | 789 | 0.018786 | 2439 | 0.058071 | 1.429 | B01 | APPW0.200063
Vertical Wall | Iguana Aplano PLUS | APPW.200074 | 200 | 74 |  | 12 | 2498 | 2498 | 2498 | 0.059476 | 927 | 0.022071 | 2863 | 0.068167 | 1.429 | B01 | APPW0.200074
Vertical Wall | Iguana Aplano PLUS | APPW.200085 | 200 | 85 |  | 12 | 2868 | 2868 | 2868 | 0.068286 | 1064 | 0.025333 | 3287 | 0.078262 | 1.429 | B01 | APPW0.200085
Vertical Wall | Iguana Aplano PLUS | APPW.220030 | 220 | 30 |  | 12 | 1070 | 1070 | 1070 | 0.025476 | 397 | 0.0094524 | 1226 | 0.02919 | 1.43 | B01 | APPW0.220030
Vertical Wall | Iguana Aplano PLUS | APPW.220041 | 220 | 41 |  | 12 | 1460 | 1460 | 1460 | 0.034762 | 542 | 0.012905 | 1673 | 0.039833 | 1.43 | B01 | APPW0.220041
Vertical Wall | Iguana Aplano PLUS | APPW.220052 | 220 | 52 |  | 12 | 1849 | 1849 | 1849 | 0.044024 | 686 | 0.016333 | 2119 | 0.050452 | 1.43 | B01 | APPW0.220052
Vertical Wall | Iguana Aplano PLUS | APPW.220063 | 220 | 63 |  | 12 | 2238 | 2238 | 2238 | 0.053286 | 830 | 0.019762 | 2565 | 0.061071 | 1.43 | B01 | APPW0.220063
Vertical Wall | Iguana Aplano PLUS | APPW.220074 | 220 | 74 |  | 12 | 2627 | 2627 | 2627 | 0.062548 | 975 | 0.023214 | 3011 | 0.07169 | 1.43 | B01 | APPW0.220074
Vertical Wall | Iguana Aplano PLUS | APPW.220085 | 220 | 85 |  | 12 | 3016 | 3016 | 3016 | 0.07181 | 1119 | 0.026643 | 3456 | 0.082286 | 1.43 | B01 | APPW0.220085
Vertical Wall | Iguana Aplano PLUS | APPW.240030 | 240 | 30 |  | 12 | 1121 | 1121 | 1121 | 0.02669 | 416 | 0.0099048 | 1285 | 0.030595 | 1.432 | B01 | APPW0.240030
Vertical Wall | Iguana Aplano PLUS | APPW.240041 | 240 | 41 |  | 12 | 1529 | 1529 | 1529 | 0.036405 | 567 | 0.0135 | 1752 | 0.041714 | 1.432 | B01 | APPW0.240041
Vertical Wall | Iguana Aplano PLUS | APPW.240052 | 240 | 52 |  | 12 | 1936 | 1936 | 1936 | 0.046095 | 718 | 0.017095 | 2219 | 0.052833 | 1.432 | B01 | APPW0.240052
Vertical Wall | Iguana Aplano PLUS | APPW.240063 | 240 | 63 |  | 12 | 2344 | 2344 | 2344 | 0.05581 | 870 | 0.020714 | 2686 | 0.063952 | 1.432 | B01 | APPW0.240063
Vertical Wall | Iguana Aplano PLUS | APPW.240074 | 240 | 74 |  | 12 | 2751 | 2751 | 2751 | 0.0655 | 1021 | 0.02431 | 3153 | 0.075071 | 1.432 | B01 | APPW0.240074
Vertical Wall | Iguana Aplano PLUS | APPW.240085 | 240 | 85 |  | 12 | 3159 | 3159 | 3159 | 0.075214 | 1172 | 0.027905 | 3620 | 0.08619 | 1.432 | B01 | APPW0.240085
Vertical Wall | Iguana Arco PLUS | ARPW.180029 | 180 | 29 |  | 14 | 999 | 999 | 999 | 0.023786 | 386 | 0.0091905 | 1139 | 0.027119 | 1.372 | B01 | ARPW0.180029
Vertical Wall | Iguana Arco PLUS | ARPW.180041 | 180 | 41 |  | 16 | 1362 | 1362 | 1362 | 0.032429 | 526 | 0.012524 | 1553 | 0.036976 | 1.372 | B01 | ARPW0.180041
Vertical Wall | Iguana Arco PLUS | ARPW.180051 | 180 | 51 |  | 18 | 1725 | 1725 | 1725 | 0.041071 | 666 | 0.015857 | 1967 | 0.046833 | 1.372 | B01 | ARPW0.180051
Vertical Wall | Iguana Arco PLUS | ARPW.180062 | 180 | 62 |  | 17 | 2088 | 2088 | 2088 | 0.049714 | 806 | 0.01919 | 2380 | 0.056667 | 1.372 | B01 | ARPW0.180062
Vertical Wall | Iguana Arco PLUS | ARPW.180073 | 180 | 73 |  | 19 | 2452 | 2452 | 2452 | 0.058381 | 946 | 0.022524 | 2795 | 0.066548 | 1.372 | B01 | ARPW0.180073
Vertical Wall | Iguana Arco PLUS | ARPW.180083 | 180 | 83 |  | 21 | 2815 | 2815 | 2815 | 0.067024 | 1087 | 0.025881 | 3209 | 0.076405 | 1.372 | B01 | ARPW0.180083
Vertical Wall | Iguana Arco PLUS | ARPW.192029 | 192 | 29 |  | 14 | 1046 | 1046 | 1046 | 0.024905 | 406 | 0.0096667 | 1191 | 0.028357 | 1.366 | B01 | ARPW0.192029
Vertical Wall | Iguana Arco PLUS | ARPW.192041 | 192 | 41 |  | 16 | 1427 | 1427 | 1427 | 0.033976 | 554 | 0.01319 | 1625 | 0.03869 | 1.366 | B01 | ARPW0.192041
Vertical Wall | Iguana Arco PLUS | ARPW.192051 | 192 | 51 |  | 18 | 1807 | 1807 | 1807 | 0.043024 | 701 | 0.01669 | 2058 | 0.049 | 1.366 | B01 | ARPW0.192051
Vertical Wall | Iguana Arco PLUS | ARPW.192062 | 192 | 62 |  | 17 | 2187 | 2187 | 2187 | 0.052071 | 849 | 0.020214 | 2491 | 0.05931 | 1.366 | B01 | ARPW0.192062
Vertical Wall | Iguana Arco PLUS | ARPW.192073 | 192 | 73 |  | 19 | 2568 | 2568 | 2568 | 0.061143 | 996 | 0.023714 | 2925 | 0.069643 | 1.366 | B01 | ARPW0.192073
Vertical Wall | Iguana Arco PLUS | ARPW.192083 | 192 | 83 |  | 21 | 2948 | 2948 | 2948 | 0.07019 | 1144 | 0.027238 | 3358 | 0.079952 | 1.366 | B01 | ARPW0.192083
Vertical Wall | Iguana Arco PLUS | ARPW.200029 | 200 | 29 |  | 14 | 1076 | 1076 | 1076 | 0.025619 | 419 | 0.0099762 | 1226 | 0.02919 | 1.362 | B01 | ARPW0.200029
Vertical Wall | Iguana Arco PLUS | ARPW.200041 | 200 | 41 |  | 16 | 1467 | 1467 | 1467 | 0.034929 | 571 | 0.013595 | 1671 | 0.039786 | 1.362 | B01 | ARPW0.200041
Vertical Wall | Iguana Arco PLUS | ARPW.200051 | 200 | 51 |  | 18 | 1858 | 1858 | 1858 | 0.044238 | 723 | 0.017214 | 2116 | 0.050381 | 1.362 | B01 | ARPW0.200051
Vertical Wall | Iguana Arco PLUS | ARPW.200062 | 200 | 62 |  | 17 | 2249 | 2249 | 2249 | 0.053548 | 875 | 0.020833 | 2562 | 0.061 | 1.362 | B01 | ARPW0.200062
Vertical Wall | Iguana Arco PLUS | ARPW.200073 | 200 | 73 |  | 19 | 2641 | 2641 | 2641 | 0.062881 | 1027 | 0.024452 | 3008 | 0.071619 | 1.362 | B01 | ARPW0.200073
Vertical Wall | Iguana Arco PLUS | ARPW.200083 | 200 | 83 |  | 21 | 3032 | 3032 | 3032 | 0.07219 | 1179 | 0.028071 | 3453 | 0.082214 | 1.362 | B01 | ARPW0.200083
Vertical Wall | Iguana Arco PLUS | ARPW.220029 | 220 | 29 |  | 14 | 1146 | 1146 | 1146 | 0.027286 | 448 | 0.010667 | 1304 | 0.031048 | 1.353 | B01 | ARPW0.220029
Vertical Wall | Iguana Arco PLUS | ARPW.220041 | 220 | 41 |  | 16 | 1563 | 1563 | 1563 | 0.037214 | 611 | 0.014548 | 1779 | 0.042357 | 1.353 | B01 | ARPW0.220041
Vertical Wall | Iguana Arco PLUS | ARPW.220051 | 220 | 51 |  | 18 | 1980 | 1980 | 1980 | 0.047143 | 774 | 0.018429 | 2253 | 0.053643 | 1.353 | B01 | ARPW0.220051
Vertical Wall | Iguana Arco PLUS | ARPW.220062 | 220 | 62 |  | 17 | 2397 | 2397 | 2397 | 0.057071 | 937 | 0.02231 | 2728 | 0.064952 | 1.353 | B01 | ARPW0.220062
Vertical Wall | Iguana Arco PLUS | ARPW.220073 | 220 | 73 |  | 19 | 2813 | 2813 | 2813 | 0.066976 | 1100 | 0.02619 | 3201 | 0.076214 | 1.353 | B01 | ARPW0.220073
Vertical Wall | Iguana Arco PLUS | ARPW.220083 | 220 | 83 |  | 21 | 3230 | 3230 | 3230 | 0.076905 | 1263 | 0.030071 | 3676 | 0.087524 | 1.353 | B01 | ARPW0.220083
Vertical Wall | Iguana Arco PLUS | ARPW.240029 | 240 | 29 |  | 14 | 1210 | 1210 | 1210 | 0.02881 | 477 | 0.011357 | 1376 | 0.032762 | 1.344 | B01 | ARPW0.240029
Vertical Wall | Iguana Arco PLUS | ARPW.240041 | 240 | 41 |  | 16 | 1650 | 1650 | 1650 | 0.039286 | 650 | 0.015476 | 1876 | 0.044667 | 1.344 | B01 | ARPW0.240041
Vertical Wall | Iguana Arco PLUS | ARPW.240051 | 240 | 51 |  | 18 | 2090 | 2090 | 2090 | 0.049762 | 823 | 0.019595 | 2376 | 0.056571 | 1.344 | B01 | ARPW0.240051
Vertical Wall | Iguana Arco PLUS | ARPW.240062 | 240 | 62 |  | 17 | 2530 | 2530 | 2530 | 0.060238 | 997 | 0.023738 | 2877 | 0.0685 | 1.344 | B01 | ARPW0.240062
Vertical Wall | Iguana Arco PLUS | ARPW.240073 | 240 | 73 |  | 19 | 2970 | 2970 | 2970 | 0.070714 | 1170 | 0.027857 | 3377 | 0.080405 | 1.344 | B01 | ARPW0.240073
Vertical Wall | Iguana Arco PLUS | ARPW.240083 | 240 | 83 |  | 21 | 3410 | 3410 | 3410 | 0.08119 | 1344 | 0.032 | 3877 | 0.09231 | 1.344 | B01 | ARPW0.240083
Freestanding | Iguana Circo Freestanding | CIRF.180027 | 180 | 27 |  | 27 | 1602 | 1602 | 1602 | 0.038143 | 593 | 0.014119 | 1837 | 0.043738 | 1.436 | B01 | CIRF0.180027
Freestanding | Iguana Circo Freestanding | CIRF.180031 | 180 | 31 |  | 31 | 1893 | 1893 | 1893 | 0.045071 | 700 | 0.016667 | 2171 | 0.05169 | 1.436 | B01 | CIRF0.180031
Freestanding | Iguana Circo Freestanding | CIRF.180034 | 180 | 34 |  | 34 | 2184 | 2184 | 2184 | 0.052 | 808 | 0.019238 | 2505 | 0.059643 | 1.436 | B01 | CIRF0.180034
Freestanding | Iguana Circo Freestanding | CIRF.192027 | 192 | 27 |  | 27 | 1707 | 1707 | 1707 | 0.040643 | 638 | 0.01519 | 1955 | 0.046548 | 1.418 | B01 | CIRF0.192027
Freestanding | Iguana Circo Freestanding | CIRF.192031 | 192 | 31 |  | 31 | 2018 | 2018 | 2018 | 0.048048 | 755 | 0.017976 | 2311 | 0.055024 | 1.418 | B01 | CIRF0.192031
Freestanding | Iguana Circo Freestanding | CIRF.192034 | 192 | 34 |  | 34 | 2328 | 2328 | 2328 | 0.055429 | 871 | 0.020738 | 2666 | 0.063476 | 1.418 | B01 | CIRF0.192034
Freestanding | Iguana Circo Freestanding | CIRF.200027 | 200 | 27 |  | 27 | 1773 | 1773 | 1773 | 0.042214 | 668 | 0.015905 | 2027 | 0.048262 | 1.406 | B01 | CIRF0.200027
Freestanding | Iguana Circo Freestanding | CIRF.200031 | 200 | 31 |  | 31 | 2096 | 2096 | 2096 | 0.049905 | 790 | 0.01881 | 2396 | 0.057048 | 1.406 | B01 | CIRF0.200031
Freestanding | Iguana Circo Freestanding | CIRF.200034 | 200 | 34 |  | 34 | 2418 | 2418 | 2418 | 0.057571 | 912 | 0.021714 | 2764 | 0.06581 | 1.406 | B01 | CIRF0.200034
Freestanding | Iguana Circo Freestanding | CIRF.220027 | 220 | 27 |  | 27 | 1923 | 1923 | 1923 | 0.045786 | 742 | 0.017667 | 2192 | 0.05219 | 1.375 | B01 | CIRF0.220027
Freestanding | Iguana Circo Freestanding | CIRF.220031 | 220 | 31 |  | 31 | 2272 | 2272 | 2272 | 0.054095 | 877 | 0.020881 | 2590 | 0.061667 | 1.375 | B01 | CIRF0.220031
Freestanding | Iguana Circo Freestanding | CIRF.220034 | 220 | 34 |  | 34 | 2622 | 2622 | 2622 | 0.062429 | 1012 | 0.024095 | 2989 | 0.071167 | 1.375 | B01 | CIRF0.220034
Freestanding | Iguana Circo Freestanding | CIRF.240027 | 240 | 27 |  | 27 | 2048 | 2048 | 2048 | 0.048762 | 807 | 0.019214 | 2329 | 0.055452 | 1.345 | B01 | CIRF0.240027
Freestanding | Iguana Circo Freestanding | CIRF.240031 | 240 | 31 |  | 31 | 2421 | 2421 | 2421 | 0.057643 | 954 | 0.022714 | 2753 | 0.065548 | 1.345 | B01 | CIRF0.240031
Freestanding | Iguana Circo Freestanding | CIRF.240034 | 240 | 34 |  | 34 | 2793 | 2793 | 2793 | 0.0665 | 1100 | 0.02619 | 3176 | 0.075619 | 1.345 | B01 | CIRF0.240034
Freestanding | Iguana Circo Pillar Cover | CIRP.180027 | 180 | 27 |  | 27 | 1602 | 1602 | 1602 | 0.038143 | 593 | 0.014119 | 1837 | 0.043738 | 1.436 | B01 | CIRP0.180027
Freestanding | Iguana Circo Pillar Cover | CIRP.180031 | 180 | 31 |  | 31 | 1893 | 1893 | 1893 | 0.045071 | 700 | 0.016667 | 2171 | 0.05169 | 1.436 | B01 | CIRP0.180031
Freestanding | Iguana Circo Pillar Cover | CIRP.180034 | 180 | 34 |  | 34 | 2184 | 2184 | 2184 | 0.052 | 808 | 0.019238 | 2505 | 0.059643 | 1.436 | B01 | CIRP0.180034
Freestanding | Iguana Circo Pillar Cover | CIRP.192027 | 192 | 27 |  | 27 | 1707 | 1707 | 1707 | 0.040643 | 638 | 0.01519 | 1955 | 0.046548 | 1.418 | B01 | CIRP0.192027
Freestanding | Iguana Circo Pillar Cover | CIRP.192031 | 192 | 31 |  | 31 | 2018 | 2018 | 2018 | 0.048048 | 755 | 0.017976 | 2311 | 0.055024 | 1.418 | B01 | CIRP0.192031
Freestanding | Iguana Circo Pillar Cover | CIRP.192034 | 192 | 34 |  | 34 | 2328 | 2328 | 2328 | 0.055429 | 871 | 0.020738 | 2666 | 0.063476 | 1.418 | B01 | CIRP0.192034
Freestanding | Iguana Circo Pillar Cover | CIRP.200027 | 200 | 27 |  | 27 | 1773 | 1773 | 1773 | 0.042214 | 668 | 0.015905 | 2027 | 0.048262 | 1.406 | B01 | CIRP0.200027
Freestanding | Iguana Circo Pillar Cover | CIRP.200031 | 200 | 31 |  | 31 | 2096 | 2096 | 2096 | 0.049905 | 790 | 0.01881 | 2396 | 0.057048 | 1.406 | B01 | CIRP0.200031
Freestanding | Iguana Circo Pillar Cover | CIRP.200034 | 200 | 34 |  | 34 | 2418 | 2418 | 2418 | 0.057571 | 912 | 0.021714 | 2764 | 0.06581 | 1.406 | B01 | CIRP0.200034
Freestanding | Iguana Circo Pillar Cover | CIRP.220027 | 220 | 27 |  | 27 | 1923 | 1923 | 1923 | 0.045786 | 742 | 0.017667 | 2192 | 0.05219 | 1.375 | B01 | CIRP0.220027
Freestanding | Iguana Circo Pillar Cover | CIRP.220031 | 220 | 31 |  | 31 | 2272 | 2272 | 2272 | 0.054095 | 877 | 0.020881 | 2590 | 0.061667 | 1.375 | B01 | CIRP0.220031
Freestanding | Iguana Circo Pillar Cover | CIRP.220034 | 220 | 34 |  | 34 | 2622 | 2622 | 2622 | 0.062429 | 1012 | 0.024095 | 2989 | 0.071167 | 1.375 | B01 | CIRP0.220034
Freestanding | Iguana Circo Pillar Cover | CIRP.240027 | 240 | 27 |  | 27 | 2048 | 2048 | 2048 | 0.048762 | 807 | 0.019214 | 2329 | 0.055452 | 1.345 | B01 | CIRP0.240027
Freestanding | Iguana Circo Pillar Cover | CIRP.240031 | 240 | 31 |  | 31 | 2421 | 2421 | 2421 | 0.057643 | 954 | 0.022714 | 2753 | 0.065548 | 1.345 | B01 | CIRP0.240031
Freestanding | Iguana Circo Pillar Cover | CIRP.240034 | 240 | 34 |  | 34 | 2793 | 2793 | 2793 | 0.0665 | 1100 | 0.02619 | 3176 | 0.075619 | 1.345 | B01 | CIRP0.240034
Vertical Wall | Iguana Circo Corner PLUS | COPW.125031 | 125 | 31 |  | 31 | 860 | 860 | 860 | 0.020476 | 342 | 0.0081429 | 976 | 0.023238 | 1.329 | B01 | COPW0.125031
Vertical Wall | Iguana Circo Corner PLUS | COPW.150031 | 150 | 31 |  | 31 | 990 | 990 | 990 | 0.023571 | 392 | 0.0093333 | 1125 | 0.026786 | 1.335 | B01 | COPW0.150031
Vertical Wall | Iguana Circo Corner PLUS | COPW.180031 | 180 | 31 |  | 31 | 1145 | 1145 | 1145 | 0.027262 | 451 | 0.010738 | 1302 | 0.031 | 1.343 | B01 | COPW0.180031
Vertical Wall | Iguana Circo Corner PLUS | COPW.192031 | 192 | 31 |  | 31 | 1207 | 1207 | 1207 | 0.028738 | 474 | 0.011286 | 1372 | 0.032667 | 1.346 | B01 | COPW0.192031
Vertical Wall | Iguana Circo Corner PLUS | COPW.200031 | 200 | 31 |  | 31 | 1249 | 1249 | 1249 | 0.029738 | 491 | 0.01169 | 1420 | 0.03381 | 1.348 | B01 | COPW0.200031
Vertical Wall | Iguana Circo Corner PLUS | COPW.220031 | 220 | 31 |  | 31 | 1352 | 1352 | 1352 | 0.03219 | 529 | 0.012595 | 1539 | 0.036643 | 1.353 | B01 | COPW0.220031
Vertical Wall | Iguana Circo Corner PLUS | COPW.240031 | 240 | 31 |  | 31 | 1458 | 1458 | 1458 | 0.034714 | 569 | 0.013548 | 1659 | 0.0395 | 1.358 | B01 | COPW0.240031
Horizontal Wall | Geo Horizontaal | GEHW.060100 | 60 | 100 |  | 14 | 1099 | 1099 | 1099 | 0.026167 | 423 | 0.010071 | 1253 | 0.029833 | 1.3752 | B02 | GEHW.060100
Horizontal Wall | Geo Horizontaal | GEHW.060120 | 60 | 120 |  | 14 | 1375 | 1375 | 1375 | 0.032738 | 534 | 0.012714 | 1566 | 0.037286 | 1.3643 | B02 | GEHW.060120
Horizontal Wall | Geo Horizontaal | GEHW.060140 | 60 | 140 |  | 14 | 1652 | 1652 | 1652 | 0.039333 | 646 | 0.015381 | 1880 | 0.044762 | 1.3533 | B02 | GEHW.060140
Horizontal Wall | Geo Horizontaal | GEHW.060160 | 60 | 160 |  | 14 | 1924 | 1924 | 1924 | 0.04581 | 758 | 0.018048 | 2186 | 0.052048 | 1.3423 | B02 | GEHW.060160
Horizontal Wall | Geo Horizontaal | GEHW.060180 | 60 | 180 |  | 14 | 2191 | 2191 | 2191 | 0.052167 | 870 | 0.020714 | 2487 | 0.059214 | 1.3313 | B02 | GEHW.060180
Vertical Wall | Geo Verticaal | GEVW.150050 | 150 | 50 |  | 8 | 631 | 631 | 631 | 0.015024 | 273 | 0.0065 | 708 | 0.016857 | 1.206 | B02 | GEVW.150050
Vertical Wall | Geo Verticaal | GEVW.180060 | 180 | 60 |  | 11 | 971 | 971 | 971 | 0.023119 | 410 | 0.0097619 | 1093 | 0.026024 | 1.246 | B02 | GEVW.180060
Vertical Wall | Heatwave | HEAW.001LA | 104 | 209 | LA | 6 | 820 | 820 | 820 | 0.019524 | 363 | 0.0086429 | 918 | 0.021857 | 1.176 | B06 | HEAW0.0010L
Vertical Wall | Heatwave | HEAW.001ME | 73 | 145 | ME | 6 | 430 | 430 | 430 | 0.010238 | 198 | 0.0047143 | 479 | 0.011405 | 1.119 | B06 | HEAW0.0010M
Vertical Wall | Heatwave | HEAW.001SM | 54 | 78 | SM | 6 | 232 | 232 | 232 | 0.0055238 | 103 | 0.0024524 | 260 | 0.0061905 | 1.176 | B06 | HEAW0.0010S
Vertical Wall | Heatwave | HEAW.001XL | 135 | 272 | XL | 6 | 1255 | 1255 | 1255 | 0.029881 | 577 | 0.013738 | 1397 | 0.033262 | 1.119 | B06 | HEAW0.001XL
Towel rail | Sani Ronda | SROW.063040 | 63 | 40 |  | 4 | 268 | 268 | 268 | 0.006381 | 112 | 0.0026667 | 302 | 0.0071905 | 1.256 | C08 | SROW0.063040
Towel rail | Sani Ronda | SROW.063050 | 63 | 50 |  | 4 | 322 | 322 | 322 | 0.0076667 | 134 | 0.0031905 | 363 | 0.0086429 | 1.267 | C08 | SROW0.063050
Towel rail | Sani Ronda | SROW.063060 | 63 | 60 |  | 4 | 376 | 376 | 376 | 0.0089524 | 156 | 0.0037143 | 425 | 0.010119 | 1.274 | C08 | SROW0.063060
Towel rail | Sani Ronda | SROW.063070 | 63 | 70 |  | 4 | 429 | 429 | 429 | 0.010214 | 177 | 0.0042143 | 485 | 0.011548 | 1.28 | C08 | SROW0.063070
Towel rail | Sani Ronda | SROW.063080 | 63 | 80 |  | 4 | 483 | 483 | 483 | 0.0115 | 199 | 0.0047381 | 546 | 0.013 | 1.284 | C08 | SROW0.063080
Towel rail | Sani Ronda | SROW.063100 | 63 | 100 |  | 4 | 590 | 590 | 590 | 0.014048 | 241 | 0.0057381 | 667 | 0.015881 | 1.29 | C08 | SROW0.063100
Towel rail | Sani Ronda | SROW.093040 | 93 | 40 |  | 4 | 407 | 407 | 407 | 0.0096905 | 168 | 0.004 | 460 | 0.010952 | 1.272 | C08 | SROW0.093040
Towel rail | Sani Ronda | SROW.093050 | 93 | 50 |  | 4 | 494 | 494 | 494 | 0.011762 | 204 | 0.0048571 | 558 | 0.013286 | 1.279 | C08 | SROW0.093050
Towel rail | Sani Ronda | SROW.093050/SP | 93 | 50 | /SP | 4 | 296 | 296 | 296 | 0.0070476 | 122 | 0.0029048 | 334 | 0.0079524 | 1.275 | C08 | SROW0.093050/SP
Towel rail | Sani Ronda | SROW.093060 | 93 | 60 |  | 4 | 581 | 581 | 581 | 0.013833 | 239 | 0.0056905 | 657 | 0.015643 | 1.284 | C08 | SROW0.093060
Towel rail | Sani Ronda | SROW.093070 | 93 | 70 |  | 4 | 668 | 668 | 668 | 0.015905 | 274 | 0.0065238 | 756 | 0.018 | 1.288 | C08 | SROW0.093070
Towel rail | Sani Ronda | SROW.093080 | 93 | 80 |  | 4 | 755 | 755 | 755 | 0.017976 | 309 | 0.0073571 | 854 | 0.020333 | 1.291 | C08 | SROW0.093080
Towel rail | Sani Ronda | SROW.093100 | 93 | 100 |  | 4 | 929 | 929 | 929 | 0.022119 | 379 | 0.0090238 | 1051 | 0.025024 | 1.295 | C08 | SROW0.093100
Towel rail | Sani Ronda | SROW.122040 | 122 | 40 |  | 4 | 546 | 546 | 546 | 0.013 | 224 | 0.0053333 | 618 | 0.014714 | 1.287 | C08 | SROW0.122040
Towel rail | Sani Ronda | SROW.122050 | 122 | 50 |  | 4 | 665 | 665 | 665 | 0.015833 | 272 | 0.0064762 | 752 | 0.017905 | 1.291 | C08 | SROW0.122050
Towel rail | Sani Ronda | SROW.122050/SP | 122 | 50 | /SP | 4 | 401 | 401 | 401 | 0.0095476 | 164 | 0.0039048 | 454 | 0.01081 | 1.293 | C08 | SROW0.122050/SP
Towel rail | Sani Ronda | SROW.122060 | 122 | 60 |  | 4 | 784 | 784 | 784 | 0.018667 | 320 | 0.007619 | 887 | 0.021119 | 1.294 | C08 | SROW0.122060
Towel rail | Sani Ronda | SROW.122060/SP | 122 | 60 | /SP | 4 | 479 | 479 | 479 | 0.011405 | 197 | 0.0046905 | 541 | 0.012881 | 1.283 | C08 | SROW0.122060/SP
Towel rail | Sani Ronda | SROW.122070 | 122 | 70 |  | 4 | 903 | 903 | 903 | 0.0215 | 368 | 0.0087619 | 1021 | 0.02431 | 1.296 | C08 | SROW0.122070
Towel rail | Sani Ronda | SROW.122080 | 122 | 80 |  | 4 | 1023 | 1023 | 1023 | 0.024357 | 416 | 0.0099048 | 1158 | 0.027571 | 1.298 | C08 | SROW0.122080
Towel rail | Sani Ronda | SROW.122100 | 122 | 100 |  | 4 | 1261 | 1261 | 1261 | 0.030024 | 512 | 0.01219 | 1427 | 0.033976 | 1.301 | C08 | SROW0.122100
Towel rail | Sani Ronda | SROW.137040 | 137 | 40 |  | 4 | 617 | 617 | 617 | 0.01469 | 252 | 0.006 | 698 | 0.016619 | 1.295 | C08 | SROW0.137040
Towel rail | Sani Ronda | SROW.137050 | 137 | 50 |  | 4 | 752 | 752 | 752 | 0.017905 | 306 | 0.0072857 | 851 | 0.020262 | 1.297 | C08 | SROW0.137050
Towel rail | Sani Ronda | SROW.137050/SP | 137 | 50 | /SP | 4 | 456 | 456 | 456 | 0.010857 | 185 | 0.0044048 | 516 | 0.012286 | 1.302 | C08 | SROW0.137050/SP
Towel rail | Sani Ronda | SROW.137060 | 137 | 60 |  | 4 | 887 | 887 | 887 | 0.021119 | 360 | 0.0085714 | 1004 | 0.023905 | 1.299 | C08 | SROW0.137060
Towel rail | Sani Ronda | SROW.137060/SP | 137 | 60 | /SP | 4 | 544 | 544 | 544 | 0.012952 | 222 | 0.0052857 | 615 | 0.014643 | 1.29 | C08 | SROW0.137060/SP
Towel rail | Sani Ronda | SROW.137070 | 137 | 70 |  | 4 | 1022 | 1022 | 1022 | 0.024333 | 415 | 0.009881 | 1157 | 0.027548 | 1.3 | C08 | SROW0.137070
Towel rail | Sani Ronda | SROW.137080 | 137 | 80 |  | 4 | 1157 | 1157 | 1157 | 0.027548 | 470 | 0.01119 | 1310 | 0.03119 | 1.302 | C08 | SROW0.137080
Towel rail | Sani Ronda | SROW.137100 | 137 | 100 |  | 4 | 1427 | 1427 | 1427 | 0.033976 | 578 | 0.013762 | 1615 | 0.038452 | 1.303 | C08 | SROW0.137100
Towel rail | Sani Ronda | SROW.175040 | 175 | 40 |  | 4 | 766 | 766 | 766 | 0.018238 | 309 | 0.0073571 | 868 | 0.020667 | 1.31 | C08 | SROW0.175040
Towel rail | Sani Ronda | SROW.175050 | 175 | 50 |  | 4 | 931 | 931 | 931 | 0.022167 | 376 | 0.0089524 | 1055 | 0.025119 | 1.309 | C08 | SROW0.175050
Towel rail | Sani Ronda | SROW.175050/SP | 175 | 50 | /SP | 4 | 571 | 571 | 571 | 0.013595 | 229 | 0.0054524 | 648 | 0.015429 | 1.32 | C08 | SROW0.175050/SP
Towel rail | Sani Ronda | SROW.175060 | 175 | 60 |  | 4 | 1097 | 1097 | 1097 | 0.026119 | 443 | 0.010548 | 1243 | 0.029595 | 1.309 | C08 | SROW0.175060
Towel rail | Sani Ronda | SROW.175060/SP | 175 | 60 | /SP | 4 | 679 | 679 | 679 | 0.016167 | 275 | 0.0065476 | 769 | 0.01831 | 1.303 | C08 | SROW0.175060/SP
Towel rail | Sani Ronda | SROW.175070 | 175 | 70 |  | 4 | 1262 | 1262 | 1262 | 0.030048 | 510 | 0.012143 | 1430 | 0.034048 | 1.309 | C08 | SROW0.175070
Towel rail | Sani Ronda | SROW.175080 | 175 | 80 |  | 4 | 1428 | 1428 | 1428 | 0.034 | 577 | 0.013738 | 1618 | 0.038524 | 1.309 | C08 | SROW0.175080
Towel rail | Sani Ronda | SROW.175100 | 175 | 100 |  | 4 | 1759 | 1759 | 1759 | 0.041881 | 711 | 0.016929 | 1993 | 0.047452 | 1.308 | C08 | SROW0.175100
Towel rail | Sani Ronda | SROW.205040 | 205 | 40 |  | 4 | 923 | 923 | 923 | 0.021976 | 368 | 0.0087619 | 1048 | 0.024952 | 1.325 | C08 | SROW0.205040
Towel rail | Sani Ronda | SROW.205050 | 205 | 50 |  | 4 | 1118 | 1118 | 1118 | 0.026619 | 447 | 0.010643 | 1268 | 0.03019 | 1.321 | C08 | SROW0.205050
Towel rail | Sani Ronda | SROW.205060 | 205 | 60 |  | 4 | 1314 | 1314 | 1314 | 0.031286 | 527 | 0.012548 | 1490 | 0.035476 | 1.319 | C08 | SROW0.205060
Towel rail | Sani Ronda | SROW.205070 | 205 | 70 |  | 4 | 1509 | 1509 | 1509 | 0.035929 | 605 | 0.014405 | 1711 | 0.040738 | 1.317 | C08 | SROW0.205070
Towel rail | Sani Ronda | SROW.205080 | 205 | 80 |  | 4 | 1705 | 1705 | 1705 | 0.040595 | 685 | 0.01631 | 1933 | 0.046024 | 1.316 | C08 | SROW0.205080
Towel rail | Sani Ronda | SROW.205100 | 205 | 100 |  | 4 | 2096 | 2096 | 2096 | 0.049905 | 843 | 0.020071 | 2375 | 0.056548 | 1.313 | C08 | SROW0.205100
Vertical Wall | Tetra | TETW.180033 | 180 | 33 |  | 12 | 984 | 984 | 984 | 0.023429 | 411 | 0.0097857 | 1110 | 0.026429 | 1.26 | B11 | TETW0.180033
Vertical Wall | Tetra | TETW.180041 | 180 | 41 |  | 12 | 1230 | 1230 | 1230 | 0.029286 | 514 | 0.012238 | 1387 | 0.033024 | 1.26 | B11 | TETW0.180041
Vertical Wall | Tetra | TETW.180050 | 180 | 50 |  | 12 | 1476 | 1476 | 1476 | 0.035143 | 617 | 0.01469 | 1665 | 0.039643 | 1.26 | B11 | TETW0.180050
Vertical Wall | Tetra | TETW.180058 | 180 | 58 |  | 12 | 1722 | 1722 | 1722 | 0.041 | 720 | 0.017143 | 1942 | 0.046238 | 1.26 | B11 | TETW0.180058
Vertical Wall | Tetra | TETW.180067 | 180 | 67 |  | 12 | 1968 | 1968 | 1968 | 0.046857 | 823 | 0.019595 | 2220 | 0.052857 | 1.26 | B11 | TETW0.180067
Vertical Wall | Tetra | TETW.200033 | 200 | 33 |  | 12 | 1120 | 1120 | 1120 | 0.026667 | 461 | 0.010976 | 1266 | 0.030143 | 1.28 | B11 | TETW0.200033
Vertical Wall | Tetra | TETW.200041 | 200 | 41 |  | 12 | 1400 | 1400 | 1400 | 0.033333 | 577 | 0.013738 | 1582 | 0.037667 | 1.28 | B11 | TETW0.200041
Vertical Wall | Tetra | TETW.200050 | 200 | 50 |  | 12 | 1680 | 1680 | 1680 | 0.04 | 692 | 0.016476 | 1898 | 0.04519 | 1.28 | B11 | TETW0.200050
Vertical Wall | Tetra | TETW.200058 | 200 | 58 |  | 12 | 1960 | 1960 | 1960 | 0.046667 | 808 | 0.019238 | 2215 | 0.052738 | 1.28 | B11 | TETW0.200058
Vertical Wall | Tetra | TETW.200067 | 200 | 67 |  | 12 | 2240 | 2240 | 2240 | 0.053333 | 923 | 0.021976 | 2531 | 0.060262 | 1.28 | B11 | TETW0.200067
Vertical Wall | Iguana Visio PLUS | VIPW.180051 | 180 | 51 |  | 16 | 908 | 908 | 908 | 0.021619 | 350 | 0.0083333 | 1035 | 0.024643 | 1.372 | B01 | VIPW0.180051
Vertical Wall | Iguana Visio PLUS | VIPW.180062 | 180 | 62 |  | 16 | 1271 | 1271 | 1271 | 0.030262 | 491 | 0.01169 | 1449 | 0.0345 | 1.372 | B01 | VIPW0.180062
Vertical Wall | Iguana Visio PLUS | VIPW.180073 | 180 | 73 |  | 18 | 1634 | 1634 | 1634 | 0.038905 | 631 | 0.015024 | 1863 | 0.044357 | 1.372 | B01 | VIPW0.180073
Vertical Wall | Iguana Visio PLUS | VIPW.200051 | 200 | 51 |  | 16 | 978 | 978 | 978 | 0.023286 | 380 | 0.0090476 | 1114 | 0.026524 | 1.362 | B01 | VIPW0.200051
Vertical Wall | Iguana Visio PLUS | VIPW.200062 | 200 | 62 |  | 16 | 1369 | 1369 | 1369 | 0.032595 | 533 | 0.01269 | 1559 | 0.037119 | 1.362 | B01 | VIPW0.200062
Vertical Wall | Iguana Visio PLUS | VIPW.200073 | 200 | 73 |  | 18 | 1760 | 1760 | 1760 | 0.041905 | 685 | 0.01631 | 2005 | 0.047738 | 1.362 | B01 | VIPW0.200073
Vertical Wall | Iguana Visio PLUS | VIPW.220051 | 220 | 51 |  | 16 | 1042 | 1042 | 1042 | 0.02481 | 407 | 0.0096905 | 1186 | 0.028238 | 1.353 | B01 | VIPW0.220051
Vertical Wall | Iguana Visio PLUS | VIPW.220062 | 220 | 62 |  | 16 | 1459 | 1459 | 1459 | 0.034738 | 570 | 0.013571 | 1660 | 0.039524 | 1.353 | B01 | VIPW0.220062
Vertical Wall | Iguana Visio PLUS | VIPW.220073 | 220 | 73 |  | 18 | 1876 | 1876 | 1876 | 0.044667 | 734 | 0.017476 | 2135 | 0.050833 | 1.353 | B01 | VIPW0.220073
Selectionmodel 2015-07
Metric

## 24V ECM Fan Coils
[10 empty] | HEATING | [5 empty] | TOTAL COOLING
[10 empty] | Entering T | 75 |  |  |  |  | Entering T | 7 |  | max | max
[6 empty] | Return water temperature increases in certain cases. |  |  |  | Return T | 65 |  |  |  |  | Return T | 12 |  | med | med
[10 empty] | Air T | 20 |  |  |  |  | Air T | 25 |  | min | min
[10 empty] | Mean T | 70
[7 empty] | 75/65/20ºC |  |  | speed | max |  | 7/12/25ºC |  |  | speed | max
LA/220615 | [9 empty] | 75/65/20º | [5 empty] | 7/12/25º (50% RH)
Group | Model | Productcode | H in cm | L in cm | Type | D in cm | max | med | min | Watt | Flow in l/s | AirFlow in m³/h | max | med | min | Watt | Flow in l/s | AirFlow in m³/h | N-Waarde (EN442) | SalesGroup | JagaSourceCode Stnd
Build-In | Brise Build-In Ceiling | BRBC.02 | 23 | 83 | 2pipe | 53 | 4000 | 3600 | 3040 | 4000 | 0.095238 | 380 | 1630 | 1470 | 1240 | 1630 | 0.077619 | 380 | 1 | D02 | BRBC0.02
Build-In | Brise Build-In Ceiling | BRBC.03 | 23 | 83 | 2pipe | 53 | 5560 | 5000 | 4220 | 5560 | 0.13238 | 500 | 2280 | 2050 | 1730 | 2280 | 0.10857 | 500 | 1 | D02 | BRBC0.03
Build-In | Brise Build-In Ceiling | BRBC.04 | 23 | 110 | 2pipe | 53 | 8070 | 7260 | 6130 | 8070 | 0.19214 | 700 | 3370 | 3030 | 2560 | 3370 | 0.16048 | 700 | 1 | D02 | BRBC0.04
Build-In | Brise Build-In Ceiling | BRBC.06 | 23 | 110 | 2pipe | 53 | 11530 | 10380 | 8760 | 11530 | 0.27452 | 880 | 4880 | 4390 | 3710 | 4880 | 0.23238 | 880 | 1 | D02 | BRBC0.06
Build-In | Brise Build-In Wall | BRBW.02 | 53 | 83 | 2pipe | 23 | 4000 | 3600 | 3040 | 4000 | 0.095238 | 380 | 1630 | 1470 | 1240 | 1630 | 0.077619 | 380 | 1 | D02 | BRBW0.02
Build-In | Brise Build-In Wall | BRBW.03 | 53 | 83 | 2pipe | 23 | 5560 | 5000 | 4220 | 5560 | 0.13238 | 500 | 2280 | 2050 | 1730 | 2280 | 0.10857 | 500 | 1 | D02 | BRBW0.03
Build-In | Brise Build-In Wall | BRBW.04 | 53 | 110 | 2pipe | 23 | 8070 | 7260 | 6130 | 8070 | 0.19214 | 700 | 3370 | 3030 | 2560 | 3370 | 0.16048 | 700 | 1 | D02 | BRBW0.04
Build-In | Brise Build-In Wall | BRBW.06 | 53 | 110 | 2pipe | 23 | 11530 | 10380 | 8760 | 11530 | 0.27452 | 880 | 4880 | 4390 | 3710 | 4880 | 0.23238 | 880 | 1 | D02 | BRBW0.06
Ceiling | Brise Ceiling | BRIC.02 | 23 | 83 | 2pipe | 53 | 4000 | 3600 | 3040 | 4000 | 0.095238 | 380 | 1630 | 1470 | 1240 | 1630 | 0.077619 | 380 | 1 | D02 | BRIC0.02
Ceiling | Brise Ceiling | BRIC.03 | 23 | 83 | 2pipe | 53 | 5560 | 5000 | 4220 | 5560 | 0.13238 | 500 | 2280 | 2050 | 1730 | 2280 | 0.10857 | 500 | 1 | D02 | BRIC0.03
Ceiling | Brise Ceiling | BRIC.04 | 23 | 110 | 2pipe | 53 | 8070 | 7260 | 6130 | 8070 | 0.19214 | 700 | 3370 | 3030 | 2560 | 3370 | 0.16048 | 700 | 1 | D02 | BRIC0.04
Ceiling | Brise Ceiling | BRIC.06 | 23 | 110 | 2pipe | 53 | 11530 | 10380 | 8760 | 11530 | 0.27452 | 880 | 4880 | 4390 | 3710 | 4880 | 0.23238 | 880 | 1 | D02 | BRIC0.06
Freestanding | Brise Freestanding | BRIF.02 | 53 | 83 | 2pipe | 23 | 4000 | 3600 | 3040 | 4000 | 0.095238 | 380 | 1630 | 1470 | 1240 | 1630 | 0.077619 | 380 | 1 | D02 | BRIF0.02
Freestanding | Brise Freestanding | BRIF.03 | 53 | 83 | 2pipe | 23 | 5560 | 5000 | 4220 | 5560 | 0.13238 | 500 | 2280 | 2050 | 1730 | 2280 | 0.10857 | 500 | 1 | D02 | BRIF0.03
Freestanding | Brise Freestanding | BRIF.04 | 53 | 110 | 2pipe | 23 | 8070 | 7260 | 6130 | 8070 | 0.19214 | 700 | 3370 | 3030 | 2560 | 3370 | 0.16048 | 700 | 1 | D02 | BRIF0.04
Freestanding | Brise Freestanding | BRIF.06 | 53 | 110 | 2pipe | 23 | 11530 | 10380 | 8760 | 11530 | 0.27452 | 880 | 4880 | 4390 | 3710 | 4880 | 0.23238 | 880 | 1 | D02 | BRIF0.06
Horizontal Wall | Brise | BRIW.02 | 53 | 83 | 2pipe | 23 | 4000 | 3600 | 3040 | 4000 | 0.095238 | 380 | 1630 | 1470 | 1240 | 1630 | 0.077619 | 380 | 1 | D02 | BRIW0.02
Horizontal Wall | Brise | BRIW.03 | 53 | 83 | 2pipe | 23 | 5560 | 5000 | 4220 | 5560 | 0.13238 | 500 | 2280 | 2050 | 1730 | 2280 | 0.10857 | 500 | 1 | D02 | BRIW0.03
Horizontal Wall | Brise | BRIW.04 | 53 | 110 | 2pipe | 23 | 8070 | 7260 | 6130 | 8070 | 0.19214 | 700 | 3370 | 3030 | 2560 | 3370 | 0.16048 | 700 | 1 | D02 | BRIW0.04
Horizontal Wall | Brise | BRIW.06 | 53 | 110 | 2pipe | 23 | 11530 | 10380 | 8760 | 11530 | 0.27452 | 880 | 4880 | 4390 | 3710 | 4880 | 0.23238 | 880 | 1 | D02 | BRIW0.06
Build-In | Briza Build-In Ceiling | BZBC.038052 | 38 | 52 | 2pipe | 12 | 1836 | 1421 | 1068 | 1836 | 0.043714 | 250 | 486 | 390 | 280 | 486 | 0.023143 | 250 | 1 | D04 | BZBC0.03805200
Build-In | Briza Build-In Ceiling | BZBC.038052/4 | 38 | 52 | 4pipe | 12 | 1468 | 1136 | 854 | 1468 | 0.034952 | 250 | 388 | 312 | 224 | 388 | 0.018476 | 250 | 1 | D04 | BZBC0.03805200/4
Build-In | Briza Build-In Ceiling | BZBC.038072 | 38 | 72 | 2pipe | 12 | 3021 | 2247 | 1757 | 3021 | 0.071929 | 400 | 800 | 622 | 460 | 800 | 0.038095 | 400 | 1 | D04 | BZBC0.03807200
Build-In | Briza Build-In Ceiling | BZBC.038072/4 | 38 | 72 | 4pipe | 12 | 2416 | 1800 | 1405 | 2416 | 0.057524 | 400 | 640 | 496 | 368 | 640 | 0.030476 | 400 | 1 | D04 | BZBC0.03807200/4
Build-In | Briza Build-In Ceiling | BZBC.038105 | 38 | 105 | 2pipe | 12 | 4798 | 3655 | 2791 | 4798 | 0.11424 | 500 | 1270 | 971 | 730 | 1270 | 0.060476 | 500 | 1 | D04 | BZBC0.03810500
Build-In | Briza Build-In Ceiling | BZBC.038105/4 | 38 | 105 | 4pipe | 12 | 3838 | 2920 | 2232 | 3838 | 0.091381 | 500 | 1016 | 776 | 584 | 1016 | 0.048381 | 500 | 1 | D04 | BZBC0.03810500/4
Build-In | Briza Build-In Ceiling | BZBC.038125 | 38 | 125 | 2pipe | 12 | 5983 | 4611 | 3479 | 5983 | 0.14245 | 725 | 1584 | 1223 | 910 | 1584 | 0.075429 | 725 | 1 | D04 | BZBC0.03812500
Build-In | Briza Build-In Ceiling | BZBC.038125/4 | 38 | 125 | 4pipe | 12 | 4786 | 3680 | 2783 | 4786 | 0.11395 | 725 | 1264 | 976 | 728 | 1264 | 0.06019 | 725 | 1 | D04 | BZBC0.03812500/4
Build-In | Briza Build-In Ceiling | BZBC.052052 | 52 | 52 | 2pipe | 12 | 2717 | 2269 | 1596 | 2717 | 0.06469 | 223 | 721 | 602 | 423 | 721 | 0.034333 | 223 | 1 | D04 | BZBC0.05205200
Build-In | Briza Build-In Ceiling | BZBC.052052/4 | 52 | 52 | 4pipe | 12 | 1157 | 895 | 673 | 1157 | 0.027548 | 223 | 541 | 451 | 318 | 541 | 0.025762 | 223 | 1 | D04 | BZBC0.05205200/4
Build-In | Briza Build-In Ceiling | BZBC.052072 | 52 | 72 | 2pipe | 12 | 4499 | 3757 | 2643 | 4499 | 0.10712 | 375 | 1193 | 997 | 70 | 1193 | 0.05681 | 375 | 1 | D04 | BZBC0.05207200
Build-In | Briza Build-In Ceiling | BZBC.052072/4 | 52 | 72 | 4pipe | 12 | 1903 | 1418 | 1107 | 1903 | 0.04531 | 375 | 895 | 747 | 526 | 895 | 0.042619 | 375 | 1 | D04 | BZBC0.05207200/4
Build-In | Briza Build-In Ceiling | BZBC.052105 | 52 | 105 | 2pipe | 12 | 7172 | 5988 | 4213 | 7172 | 0.17076 | 456 | 1902 | 1588 | 1117 | 1902 | 0.090571 | 456 | 1 | D04 | BZBC0.05210500
Build-In | Briza Build-In Ceiling | BZBC.052105/4 | 52 | 105 | 4pipe | 12 | 3023 | 2300 | 1758 | 3023 | 0.071976 | 456 | 1427 | 1191 | 838 | 1427 | 0.067952 | 456 | 1 | D04 | BZBC0.05210500/4
Build-In | Briza Build-In Ceiling | BZBC.052125 | 52 | 125 | 2pipe | 12 | 8953 | 7476 | 5259 | 8953 | 0.21317 | 672 | 2375 | 1983 | 1395 | 2375 | 0.1131 | 672 | 1 | D04 | BZBC0.05212500
Build-In | Briza Build-In Ceiling | BZBC.052125/4 | 52 | 125 | 4pipe | 12 | 3769 | 2898 | 2192 | 3769 | 0.089738 | 672 | 1781 | 1487 | 1046 | 1781 | 0.08481 | 672 | 1 | D04 | BZBC0.05212500/4
Build-In | Briza Build-In Wall | BZBW.038052 | 38 | 52 | 2pipe | 12 | 1836 | 1421 | 1068 | 1836 | 0.043714 | 250 | 486 | 390 | 280 | 486 | 0.023143 | 250 | 1 | D04 | BZBW0.03805200
Build-In | Briza Build-In Wall | BZBW.038052/4 | 38 | 52 | 4pipe | 12 | 1468 | 1136 | 854 | 1468 | 0.034952 | 250 | 388 | 312 | 224 | 388 | 0.018476 | 250 | 1 | D04 | BZBW0.03805200/4
Build-In | Briza Build-In Wall | BZBW.038072 | 38 | 72 | 2pipe | 12 | 3021 | 2247 | 1757 | 3021 | 0.071929 | 400 | 800 | 622 | 460 | 800 | 0.038095 | 400 | 1 | D04 | BZBW0.03807200
Build-In | Briza Build-In Wall | BZBW.038072/4 | 38 | 72 | 4pipe | 12 | 2416 | 1800 | 1405 | 2416 | 0.057524 | 400 | 640 | 496 | 368 | 640 | 0.030476 | 400 | 1 | D04 | BZBW0.03807200/4
Build-In | Briza Build-In Wall | BZBW.038105 | 38 | 105 | 2pipe | 12 | 4798 | 3655 | 2791 | 4798 | 0.11424 | 500 | 1270 | 971 | 730 | 1270 | 0.060476 | 500 | 1 | D04 | BZBW0.03810500
Build-In | Briza Build-In Wall | BZBW.038105/4 | 38 | 105 | 4pipe | 12 | 3838 | 2920 | 2232 | 3838 | 0.091381 | 500 | 1016 | 776 | 584 | 1016 | 0.048381 | 500 | 1 | D04 | BZBW0.03810500/4
Build-In | Briza Build-In Wall | BZBW.038125 | 38 | 125 | 2pipe | 12 | 5983 | 4611 | 3479 | 5983 | 0.14245 | 725 | 1584 | 1223 | 910 | 1584 | 0.075429 | 725 | 1 | D04 | BZBW0.03812500
Build-In | Briza Build-In Wall | BZBW.038125/4 | 38 | 125 | 4pipe | 12 | 4786 | 3680 | 2783 | 4786 | 0.11395 | 725 | 1264 | 976 | 728 | 1264 | 0.06019 | 725 | 1 | D04 | BZBW0.03812500/4
Build-In | Briza Build-In Wall | BZBW.052052 | 52 | 52 | 2pipe | 12 | 2717 | 2269 | 1596 | 2717 | 0.06469 | 223 | 721 | 602 | 423 | 721 | 0.034333 | 223 | 1 | D04 | BZBW0.05205200
Build-In | Briza Build-In Wall | BZBW.052052/4 | 52 | 52 | 4pipe | 12 | 1157 | 895 | 673 | 1157 | 0.027548 | 223 | 541 | 451 | 318 | 541 | 0.025762 | 223 | 1 | D04 | BZBW0.05205200/4
Build-In | Briza Build-In Wall | BZBW.052072 | 52 | 72 | 2pipe | 12 | 4499 | 3757 | 2643 | 4499 | 0.10712 | 375 | 1193 | 997 | 730 | 1193 | 0.05681 | 375 | 1 | D04 | BZBW0.05207200
Build-In | Briza Build-In Wall | BZBW.052072/4 | 52 | 72 | 4pipe | 12 | 1903 | 1418 | 1107 | 1903 | 0.04531 | 375 | 895 | 747 | 526 | 895 | 0.042619 | 375 | 1 | D04 | BZBW0.05207200/4
Build-In | Briza Build-In Wall | BZBW.052105 | 52 | 105 | 2pipe | 12 | 7172 | 5988 | 4213 | 7172 | 0.17076 | 456 | 1902 | 1588 | 1117 | 1902 | 0.090571 | 456 | 1 | D04 | BZBW0.05210500
Build-In | Briza Build-In Wall | BZBW.052105/4 | 52 | 105 | 4pipe | 12 | 3023 | 2300 | 1758 | 3023 | 0.071976 | 456 | 1427 | 1191 | 838 | 1427 | 0.067952 | 456 | 1 | D04 | BZBW0.05210500/4
Build-In | Briza Build-In Wall | BZBW.052125 | 52 | 125 | 2pipe | 12 | 8953 | 7476 | 5259 | 8953 | 0.21317 | 672 | 2375 | 1983 | 1395 | 2375 | 0.1131 | 672 | 1 | D04 | BZBW0.05212500
Build-In | Briza Build-In Wall | BZBW.052125/4 | 52 | 125 | 4pipe | 12 | 3769 | 2898 | 2192 | 3769 | 0.089738 | 672 | 1781 | 1487 | 1046 | 1781 | 0.08481 | 672 | 1 | D04 | BZBW0.05212500/4
Ceiling | Briza Ceiling | BZMC.041072 | 41 | 72 | 2pipe | 13 | 1670 | 1292 | 972 | 1670 | 0.039762 | 250 | 442 | 354 | 254 | 442 | 0.021048 | 250 | 1 | D04 | BZMC0.04107200
Ceiling | Briza Ceiling | BZMC.041072/4 | 41 | 72 | 4pipe | 13 | 1336 | 1033 | 777 | 1336 | 0.03181 | 250 | 353 | 283 | 203 | 353 | 0.01681 | 250 | 1 | D04 | BZMC0.04107200/4
Ceiling | Briza Ceiling | BZMC.041092 | 41 | 92 | 2pipe | 13 | 2749 | 2047 | 1598 | 2749 | 0.065452 | 400 | 728 | 564 | 418 | 728 | 0.034667 | 400 | 1 | D04 | BZMC0.04109200
Ceiling | Briza Ceiling | BZMC.041092/4 | 41 | 92 | 4pipe | 13 | 2199 | 1638 | 1279 | 2199 | 0.052357 | 400 | 582 | 451 | 334 | 582 | 0.027714 | 400 | 1 | D04 | BZMC0.04109200/4
Ceiling | Briza Ceiling | BZMC.041125 | 41 | 125 | 2pipe | 13 | 4366 | 3321 | 2540 | 4366 | 0.10395 | 500 | 1155 | 882 | 664 | 1155 | 0.055 | 500 | 1 | D04 | BZMC0.04112500
Ceiling | Briza Ceiling | BZMC.041125/4 | 41 | 125 | 4pipe | 13 | 3492 | 2657 | 2031 | 3492 | 0.083143 | 500 | 924 | 706 | 531 | 924 | 0.044 | 500 | 1 | D04 | BZMC0.04112500/4
Ceiling | Briza Ceiling | BZMC.041145 | 41 | 145 | 2pipe | 13 | 5444 | 4186 | 3165 | 5444 | 0.12962 | 725 | 1441 | 1110 | 888 | 1441 | 0.068619 | 725 | 1 | D04 | BZMC0.04114500
Ceiling | Briza Ceiling | BZMC.041145/4 | 41 | 145 | 4pipe | 13 | 4355 | 3348 | 2532 | 4355 | 0.10369 | 725 | 1153 | 888 | 662 | 1153 | 0.054905 | 725 | 1 | D04 | BZMC0.04114500/4
Ceiling | Briza Ceiling | BZMC.055072 | 55 | 72 | 2pipe | 13 | 2588 | 2161 | 1520 | 2588 | 0.061619 | 223 | 686 | 573 | 403 | 686 | 0.032667 | 223 | 1 | D04 | BZMC0.05507200
Ceiling | Briza Ceiling | BZMC.055072/4 | 55 | 72 | 4pipe | 13 | 1102 | 852 | 641 | 1102 | 0.026238 | 223 | 515 | 430 | 302 | 515 | 0.024524 | 223 | 1 | D04 | BZMC0.05507200/4
Ceiling | Briza Ceiling | BZMC.055092 | 55 | 92 | 2pipe | 13 | 4285 | 3578 | 2517 | 4285 | 0.10202 | 375 | 1137 | 949 | 668 | 1137 | 0.054143 | 375 | 1 | D04 | BZMC0.05509200
Ceiling | Briza Ceiling | BZMC.055092/4 | 55 | 92 | 4pipe | 13 | 1813 | 1350 | 1054 | 1813 | 0.043167 | 375 | 852 | 712 | 501 | 852 | 0.040571 | 375 | 1 | D04 | BZMC0.05509200/4
Ceiling | Briza Ceiling | BZMC.055125 | 55 | 125 | 2pipe | 13 | 6830 | 5703 | 4012 | 6830 | 0.16262 | 456 | 1812 | 1513 | 1064 | 1812 | 0.086286 | 456 | 1 | D04 | BZMC0.05512500
Ceiling | Briza Ceiling | BZMC.055125/4 | 55 | 125 | 4pipe | 13 | 2879 | 2190 | 1675 | 2879 | 0.068548 | 456 | 1359 | 1135 | 798 | 1359 | 0.064714 | 456 | 1 | D04 | BZMC0.05512500/4
Ceiling | Briza Ceiling | BZMC.055145 | 55 | 145 | 2pipe | 13 | 8527 | 7120 | 5009 | 8527 | 0.20302 | 672 | 2264 | 1889 | 1329 | 2264 | 0.10781 | 672 | 1 | D04 | BZMC0.05514500
Ceiling | Briza Ceiling | BZMC.055145/4 | 55 | 145 | 4pipe | 13 | 3590 | 2760 | 2087 | 3590 | 0.085476 | 672 | 1696 | 1416 | 996 | 1696 | 0.080762 | 672 | 1 | D04 | BZMC0.05514500/4
Horizontal Wall | Briza | BZMW.041072 | 41 | 72 | 2pipe | 13 | 1670 | 1292 | 972 | 1670 | 0.039762 | 250 | 442 | 354 | 254 | 442 | 0.021048 | 250 | 1 | D04 | BZMW0.04107200
Horizontal Wall | Briza | BZMW.041072/4 | 41 | 72 | 4pipe | 13 | 1336 | 1033 | 777 | 1336 | 0.03181 | 250 | 353 | 283 | 203 | 353 | 0.01681 | 250 | 1 | D04 | BZMW0.04107200/4
Horizontal Wall | Briza | BZMW.041092 | 41 | 92 | 2pipe | 13 | 2749 | 2047 | 1598 | 2749 | 0.065452 | 400 | 728 | 564 | 418 | 728 | 0.034667 | 400 | 1 | D04 | BZMW0.04109200
Horizontal Wall | Briza | BZMW.041092/4 | 41 | 92 | 4pipe | 13 | 2199 | 1638 | 1279 | 2199 | 0.052357 | 400 | 582 | 451 | 334 | 582 | 0.027714 | 400 | 1 | D04 | BZMW0.04109200/4
Horizontal Wall | Briza | BZMW.041125 | 41 | 125 | 2pipe | 13 | 4366 | 3321 | 2540 | 4366 | 0.10395 | 500 | 1155 | 882 | 664 | 1155 | 0.055 | 500 | 1 | D04 | BZMW0.04112500
Horizontal Wall | Briza | BZMW.041125/4 | 41 | 125 | 4pipe | 13 | 3492 | 2657 | 2031 | 3492 | 0.083143 | 500 | 924 | 706 | 531 | 924 | 0.044 | 500 | 1 | D04 | BZMW0.04112500/4
Horizontal Wall | Briza | BZMW.041145 | 41 | 145 | 2pipe | 13 | 5444 | 4186 | 3165 | 5444 | 0.12962 | 725 | 1441 | 1110 | 888 | 1441 | 0.068619 | 725 | 1 | D04 | BZMW0.04114500
Horizontal Wall | Briza | BZMW.041145/4 | 41 | 145 | 4pipe | 13 | 4355 | 3348 | 2532 | 4355 | 0.10369 | 725 | 1153 | 888 | 662 | 1153 | 0.054905 | 725 | 1 | D04 | BZMW0.04114500/4
Horizontal Wall | Briza | BZMW.055072 | 55 | 72 | 2pipe | 13 | 2588 | 2161 | 1520 | 2588 | 0.061619 | 223 | 686 | 573 | 403 | 686 | 0.032667 | 223 | 1 | D04 | BZMW0.05507200
Horizontal Wall | Briza | BZMW.055072/4 | 55 | 72 | 4pipe | 13 | 1102 | 852 | 641 | 1102 | 0.026238 | 223 | 515 | 430 | 302 | 515 | 0.024524 | 223 | 1 | D04 | BZMW0.05507200/4
Horizontal Wall | Briza | BZMW.055092 | 55 | 92 | 2pipe | 13 | 4285 | 3578 | 2517 | 4285 | 0.10202 | 375 | 1137 | 949 | 668 | 1137 | 0.054143 | 375 | 1 | D04 | BZMW0.05509200
Horizontal Wall | Briza | BZMW.055092/4 | 55 | 92 | 4pipe | 13 | 1813 | 1350 | 1054 | 1813 | 0.043167 | 375 | 852 | 712 | 501 | 852 | 0.040571 | 375 | 1 | D04 | BZMW0.05509200/4
Horizontal Wall | Briza | BZMW.055125 | 55 | 125 | 2pipe | 13 | 6830 | 5703 | 4012 | 6830 | 0.16262 | 456 | 1812 | 1513 | 1064 | 1812 | 0.086286 | 456 | 1 | D04 | BZMW0.05512500
Horizontal Wall | Briza | BZMW.055125/4 | 55 | 125 | 4pipe | 13 | 2879 | 2190 | 1675 | 2879 | 0.068548 | 456 | 1359 | 1135 | 798 | 1359 | 0.064714 | 456 | 1 | D04 | BZMW0.05512500/4
Horizontal Wall | Briza | BZMW.055145 | 55 | 145 | 2pipe | 13 | 8527 | 7120 | 5009 | 8527 | 0.20302 | 672 | 2264 | 1889 | 1329 | 2264 | 0.10781 | 672 | 1 | D04 | BZMW0.05514500
Horizontal Wall | Briza | BZMW.055145/4 | 55 | 145 | 4pipe | 13 | 3590 | 2760 | 2087 | 3590 | 0.085476 | 672 | 1696 | 1416 | 996 | 1696 | 0.080762 | 672 | 1 | D04 | BZMW0.05514500/4
Build-In Floor | Clima Canal Metal | CLCM.00807218/BBN | 8 | 72 | 2pipe | 18 | 945 | 903 | 517 | 945 | 0.0225 | 70 | [6 empty] | 1 | A12 | CLCM0.00807218/BBN
Build-In Floor | Clima Canal Metal | CLCM.00807218/BBV | 8 | 72 | 2pipe | 18 | 945 | 903 | 517 | 945 | 0.0225 | 70 | [6 empty] | 1 | A12 | CLCM0.00807218/BBV
Build-In Floor | Clima Canal Metal | CLCM.00807218/BNA | 8 | 72 | 2pipe | 18 | 945 | 903 | 517 | 945 | 0.0225 | 70 | [6 empty] | 1 | A12 | CLCM0.00807218/BNA
Build-In Floor | Clima Canal Metal | CLCM.00807218/BNC | 8 | 72 | 2pipe | 18 | 945 | 903 | 517 | 945 | 0.0225 | 70 | [6 empty] | 1 | A12 | CLCM0.00807218/BNC
Build-In Floor | Clima Canal Metal | CLCM.00807218/BON | 8 | 72 | 2pipe | 18 | 945 | 903 | 517 | 945 | 0.0225 | 70 | [6 empty] | 1 | A12 | CLCM0.00807218/BON
Build-In Floor | Clima Canal Metal | CLCM.00807218/BOV | 8 | 72 | 2pipe | 18 | 945 | 903 | 517 | 945 | 0.0225 | 70 | [6 empty] | 1 | A12 | CLCM0.00807218/BOV
Build-In Floor | Clima Canal Metal | CLCM.00810818/BBN | 8 | 108 | 2pipe | 18 | 2075 | 2009 | 1137 | 2075 | 0.049405 | 142 | [6 empty] | 1 | A12 | CLCM0.00810818/BBN
Build-In Floor | Clima Canal Metal | CLCM.00810818/BBV | 8 | 108 | 2pipe | 18 | 2075 | 2009 | 1137 | 2075 | 0.049405 | 142 | [6 empty] | 1 | A12 | CLCM0.00810818/BBV
Build-In Floor | Clima Canal Metal | CLCM.00810818/BNA | 8 | 108 | 2pipe | 18 | 2075 | 2009 | 1137 | 2075 | 0.049405 | 142 | [6 empty] | 1 | A12 | CLCM0.00810818/BNA
Build-In Floor | Clima Canal Metal | CLCM.00810818/BNC | 8 | 108 | 2pipe | 18 | 2075 | 2009 | 1137 | 2075 | 0.049405 | 142 | [6 empty] | 1 | A12 | CLCM0.00810818/BNC
Build-In Floor | Clima Canal Metal | CLCM.00810818/BON | 8 | 108 | 2pipe | 18 | 2075 | 2009 | 1137 | 2075 | 0.049405 | 142 | [6 empty] | 1 | A12 | CLCM0.00810818/BON
Build-In Floor | Clima Canal Metal | CLCM.00810818/BOV | 8 | 108 | 2pipe | 18 | 2075 | 2009 | 1137 | 2075 | 0.049405 | 142 | [6 empty] | 1 | A12 | CLCM0.00810818/BOV
Build-In Floor | Clima Canal Metal | CLCM.00814418/BBN | 8 | 144 | 2pipe | 18 | 3011 | 2912 | 1654 | 3011 | 0.07169 | 213 | [6 empty] | 1 | A12 | CLCM0.00814418/BBN
Build-In Floor | Clima Canal Metal | CLCM.00814418/BBV | 8 | 144 | 2pipe | 18 | 3011 | 2912 | 1654 | 3011 | 0.07169 | 213 | [6 empty] | 1 | A12 | CLCM0.00814418/BBV
Build-In Floor | Clima Canal Metal | CLCM.00814418/BNA | 8 | 144 | 2pipe | 18 | 3011 | 2912 | 1654 | 3011 | 0.07169 | 213 | [6 empty] | 1 | A12 | CLCM0.00814418/BNA
Build-In Floor | Clima Canal Metal | CLCM.00814418/BNC | 8 | 144 | 2pipe | 18 | 3011 | 2912 | 1654 | 3011 | 0.07169 | 213 | [6 empty] | 1 | A12 | CLCM0.00814418/BNC
Build-In Floor | Clima Canal Metal | CLCM.00814418/BON | 8 | 144 | 2pipe | 18 | 3011 | 2912 | 1654 | 3011 | 0.07169 | 213 | [6 empty] | 1 | A12 | CLCM0.00814418/BON
Build-In Floor | Clima Canal Metal | CLCM.00814418/BOV | 8 | 144 | 2pipe | 18 | 3011 | 2912 | 1654 | 3011 | 0.07169 | 213 | [6 empty] | 1 | A12 | CLCM0.00814418/BOV
Build-In Floor | Clima Canal Metal | CLCM.00818018/BBN | 8 | 180 | 2pipe | 18 | 4145 | 4018 | 2274 | 4145 | 0.09869 | 284 | [6 empty] | 1 | A12 | CLCM0.00818018/BBN
Build-In Floor | Clima Canal Metal | CLCM.00818018/BBV | 8 | 180 | 2pipe | 18 | 4145 | 4018 | 2274 | 4145 | 0.09869 | 284 | [6 empty] | 1 | A12 | CLCM0.00818018/BBV
Build-In Floor | Clima Canal Metal | CLCM.00818018/BNA | 8 | 180 | 2pipe | 18 | 4145 | 4018 | 2274 | 4145 | 0.09869 | 284 | [6 empty] | 1 | A12 | CLCM0.00818018/BNA
Build-In Floor | Clima Canal Metal | CLCM.00818018/BNC | 8 | 180 | 2pipe | 18 | 4145 | 4018 | 2274 | 4145 | 0.09869 | 284 | [6 empty] | 1 | A12 | CLCM0.00818018/BNC
Build-In Floor | Clima Canal Metal | CLCM.00818018/BON | 8 | 180 | 2pipe | 18 | 4145 | 4018 | 2274 | 4145 | 0.09869 | 284 | [6 empty] | 1 | A12 | CLCM0.00818018/BON
Build-In Floor | Clima Canal Metal | CLCM.00818018/BOV | 8 | 180 | 2pipe | 18 | 4145 | 4018 | 2274 | 4145 | 0.09869 | 284 | [6 empty] | 1 | A12 | CLCM0.00818018/BOV
Build-In Floor | Clima Canal Hybrid | CLCM.01007218/BBN | 10 | 72 | 2pipe | 18 | 945 | 903 | 517 | 945 | 0.0225 | 70 | 284 | 273 | 110 | 284 | 0.013524 | 70 | 1 | A12 | CLCM0.01007218/BBN
Build-In Floor | Clima Canal Hybrid | CLCM.01007218/BBV | 10 | 72 | 2pipe | 18 | 945 | 903 | 517 | 945 | 0.0225 | 70 | 284 | 273 | 110 | 284 | 0.013524 | 70 | 1 | A12 | CLCM0.01007218/BBV
Build-In Floor | Clima Canal Hybrid | CLCM.01007218/BNA | 10 | 72 | 2pipe | 18 | 945 | 903 | 517 | 945 | 0.0225 | 70 | 284 | 273 | 110 | 284 | 0.013524 | 70 | 1 | A12 | CLCM0.01007218/BNA
Build-In Floor | Clima Canal Hybrid | CLCM.01007218/BNC | 10 | 72 | 2pipe | 18 | 945 | 903 | 517 | 945 | 0.0225 | 70 | 284 | 273 | 110 | 284 | 0.013524 | 70 | 1 | A12 | CLCM0.01007218/BNC
Build-In Floor | Clima Canal Hybrid | CLCM.01007218/BON | 10 | 72 | 2pipe | 18 | 945 | 903 | 517 | 945 | 0.0225 | 70 | 284 | 273 | 110 | 284 | 0.013524 | 70 | 1 | A12 | CLCM0.01007218/BON
Build-In Floor | Clima Canal Hybrid | CLCM.01007218/BOV | 10 | 72 | 2pipe | 18 | 945 | 903 | 517 | 945 | 0.0225 | 70 | 284 | 273 | 110 | 284 | 0.013524 | 70 | 1 | A12 | CLCM0.01007218/BOV
Build-In Floor | Clima Canal Hybrid | CLCM.01010818/BBN | 10 | 108 | 2pipe | 18 | 2075 | 2009 | 1137 | 2075 | 0.049405 | 142 | 576 | 545 | 219 | 576 | 0.027429 | 142 | 1 | A12 | CLCM0.01010818/BBN
Build-In Floor | Clima Canal Hybrid | CLCM.01010818/BBV | 10 | 108 | 2pipe | 18 | 2075 | 2009 | 1137 | 2075 | 0.049405 | 142 | 576 | 545 | 219 | 576 | 0.027429 | 142 | 1 | A12 | CLCM0.01010818/BBV
Build-In Floor | Clima Canal Hybrid | CLCM.01010818/BNA | 10 | 108 | 2pipe | 18 | 2075 | 2009 | 1137 | 2075 | 0.049405 | 142 | 576 | 545 | 219 | 576 | 0.027429 | 142 | 1 | A12 | CLCM0.01010818/BNA
Build-In Floor | Clima Canal Hybrid | CLCM.01010818/BNC | 10 | 108 | 2pipe | 18 | 2075 | 2009 | 1137 | 2075 | 0.049405 | 142 | 576 | 545 | 219 | 576 | 0.027429 | 142 | 1 | A12 | CLCM0.01010818/BNC
Build-In Floor | Clima Canal Hybrid | CLCM.01010818/BON | 10 | 108 | 2pipe | 18 | 2075 | 2009 | 1137 | 2075 | 0.049405 | 142 | 576 | 545 | 219 | 576 | 0.027429 | 142 | 1 | A12 | CLCM0.01010818/BON
Build-In Floor | Clima Canal Hybrid | CLCM.01010818/BOV | 10 | 108 | 2pipe | 18 | 2075 | 2009 | 1137 | 2075 | 0.049405 | 142 | 576 | 545 | 219 | 576 | 0.027429 | 142 | 1 | A12 | CLCM0.01010818/BOV
Build-In Floor | Clima Canal Hybrid | CLCM.01014418/BBN | 10 | 144 | 2pipe | 18 | 3011 | 2912 | 1654 | 3011 | 0.07169 | 213 | 849 | 818 | 330 | 849 | 0.040429 | 213 | 1 | A12 | CLCM0.01014418/BBN
Build-In Floor | Clima Canal Hybrid | CLCM.01014418/BBV | 10 | 144 | 2pipe | 18 | 3011 | 2912 | 1654 | 3011 | 0.07169 | 213 | 849 | 818 | 330 | 849 | 0.040429 | 213 | 1 | A12 | CLCM0.01014418/BBV
Build-In Floor | Clima Canal Hybrid | CLCM.01014418/BNA | 10 | 144 | 2pipe | 18 | 3011 | 2912 | 1654 | 3011 | 0.07169 | 213 | 849 | 818 | 330 | 849 | 0.040429 | 213 | 1 | A12 | CLCM0.01014418/BNA
Build-In Floor | Clima Canal Hybrid | CLCM.01014418/BNC | 10 | 144 | 2pipe | 18 | 3011 | 2912 | 1654 | 3011 | 0.07169 | 213 | 849 | 818 | 330 | 849 | 0.040429 | 213 | 1 | A12 | CLCM0.01014418/BNC
Build-In Floor | Clima Canal Hybrid | CLCM.01014418/BON | 10 | 144 | 2pipe | 18 | 3011 | 2912 | 1654 | 3011 | 0.07169 | 213 | 849 | 818 | 330 | 849 | 0.040429 | 213 | 1 | A12 | CLCM0.01014418/BON
Build-In Floor | Clima Canal Hybrid | CLCM.01014418/BOV | 10 | 144 | 2pipe | 18 | 3011 | 2912 | 1654 | 3011 | 0.07169 | 213 | 849 | 818 | 330 | 849 | 0.040429 | 213 | 1 | A12 | CLCM0.01014418/BOV
Build-In Floor | Clima Canal Hybrid | CLCM.01018018/BBN | 10 | 180 | 2pipe | 18 | 4145 | 4018 | 2274 | 4145 | 0.09869 | 284 | 1152 | 1090 | 440 | 1152 | 0.054857 | 284 | 1 | A12 | CLCM0.01018018/BBN
Build-In Floor | Clima Canal Hybrid | CLCM.01018018/BBV | 10 | 180 | 2pipe | 18 | 4145 | 4018 | 2274 | 4145 | 0.09869 | 284 | 1152 | 1090 | 440 | 1152 | 0.054857 | 284 | 1 | A12 | CLCM0.01018018/BBV
Build-In Floor | Clima Canal Hybrid | CLCM.01018018/BNA | 10 | 180 | 2pipe | 18 | 4145 | 4018 | 2274 | 4145 | 0.09869 | 284 | 1152 | 1090 | 440 | 1152 | 0.054857 | 284 | 1 | A12 | CLCM0.01018018/BNA
Build-In Floor | Clima Canal Hybrid | CLCM.01018018/BNC | 10 | 180 | 2pipe | 18 | 4145 | 4018 | 2274 | 4145 | 0.09869 | 284 | 1152 | 1090 | 440 | 1152 | 0.054857 | 284 | 1 | A12 | CLCM0.01018018/BNC
Build-In Floor | Clima Canal Hybrid | CLCM.01018018/BON | 10 | 180 | 2pipe | 18 | 4145 | 4018 | 2274 | 4145 | 0.09869 | 284 | 1152 | 1090 | 440 | 1152 | 0.054857 | 284 | 1 | A12 | CLCM0.01018018/BON
Build-In Floor | Clima Canal Hybrid | CLCM.01018018/BOV | 10 | 180 | 2pipe | 18 | 4145 | 4018 | 2274 | 4145 | 0.09869 | 284 | 1152 | 1090 | 440 | 1152 | 0.054857 | 284 | 1 | A12 | CLCM0.01018018/BOV
Freestanding | Freedom Clima | FDCF.02007419/BNA | 20 | 74 | BNA | 19 | 1219 | 984 | 653 | 1219 | 0.029024 | 100 | 124 | 87 | 59 | 124 | 0.0059048 | 100
Freestanding | Freedom Clima | FDCF.02007419/BNC | 20 | 74 | BNC | 19 | 1219 | 984 | 653 | 1219 | 0.029024 | 100 | 124 | 87 | 59 | 124 | 0.0059048 | 100
Freestanding | Freedom Clima | FDCF.02011019/BNA | 20 | 110 | BNA | 19 | 2438 | 1969 | 1305 | 2438 | 0.058048 | 201 | 247 | 174 | 119 | 247 | 0.011762 | 201
Freestanding | Freedom Clima | FDCF.02011019/BNC | 20 | 110 | BNC | 19 | 2438 | 1969 | 1305 | 2438 | 0.058048 | 201 | 247 | 174 | 119 | 247 | 0.011762 | 201
Freestanding | Freedom Clima | FDCF.02014519/BNA | 20 | 145 | BNA | 19 | 3657 | 2953 | 1958 | 3657 | 0.087071 | 301 | 371 | 261 | 178 | 371 | 0.017667 | 301
Freestanding | Freedom Clima | FDCF.02014519/BNC | 20 | 145 | BNC | 19 | 3657 | 2953 | 1958 | 3657 | 0.087071 | 301 | 371 | 261 | 178 | 371 | 0.017667 | 301
Freestanding | Freedom Clima | FDCF.02018119/BNA | 20 | 181 | BNA | 19 | 4876 | 3937 | 2611 | 4876 | 0.1161 | 401 | 495 | 347 | 237 | 495 | 0.023571 | 401
Freestanding | Freedom Clima | FDCF.02018119/BNC | 20 | 181 | BNC | 19 | 4876 | 3937 | 2611 | 4876 | 0.1161 | 401 | 495 | 347 | 237 | 495 | 0.023571 | 401
Freestanding | Freedom Micro | FDMF.01906214/SSC | 19 | 62 | SSC | 14 | 424 |  |  | 424 | 0.010095 | 52 | 64 |  |  | 64 | 0.0030476 | 52
Freestanding | Freedom Micro | FDMF.01906214/SSS | 19 | 62 | SSS | 14 | 424 |  |  | 424 | 0.010095 | 52 | 64 |  |  | 64 | 0.0030476 | 52
Freestanding | Freedom Micro | FDMF.01909714/SSC | 19 | 97 | SSC | 14 | 848 |  |  | 848 | 0.02019 | 104 | 129 |  |  | 129 | 0.0061429 | 104
Freestanding | Freedom Micro | FDMF.01909714/SSS | 19 | 97 | SSS | 14 | 848 |  |  | 848 | 0.02019 | 104 | 129 |  |  | 129 | 0.0061429 | 104
Freestanding | Freedom Micro | FDMF.01913214/SSC | 19 | 132 | SSC | 14 | 1272 |  |  | 1272 | 0.030286 | 156 | 193 |  |  | 193 | 0.0091905 | 156
Freestanding | Freedom Micro | FDMF.01913214/SSS | 19 | 132 | SSS | 14 | 1272 |  |  | 1272 | 0.030286 | 156 | 193 |  |  | 193 | 0.0091905 | 156
Freestanding | Freedom Micro | FDMF.01916714/SSC | 19 | 167 | SSC | 14 | 1969 |  |  | 1969 | 0.046881 | 208 | 257 |  |  | 257 | 0.012238 | 208
Freestanding | Freedom Micro | FDMF.01916714/SSS | 19 | 167 | SSS | 14 | 1969 |  |  | 1969 | 0.046881 | 208 | 257 |  |  | 257 | 0.012238 | 208
Freestanding | Freedom Micro | FDMF.01920214/SSC | 19 | 202 | SSC | 14 | 2120 |  |  | 2120 | 0.050476 | 260 | 322 |  |  | 322 | 0.015333 | 260
Freestanding | Freedom Micro | FDMF.01920214/SSS | 19 | 202 | SSS | 14 | 2120 |  |  | 2120 | 0.050476 | 260 | 322 |  |  | 322 | 0.015333 | 260
Build-In Floor | Micro Canal | MIRF.00606014/SSS | 6 | 60 | 2pipe | 14 | 390 |  |  | 390 | 0.0092857 | [7 empty] | 1 | D05 | MIRF0.00606014
Build-In Floor | Micro Canal | MIRF.00609514/SSS | 6 | 95 | 2pipe | 14 | 780 |  |  | 780 | 0.018571 | [7 empty] | 1 | D05 | MIRF0.00609514
Build-In Floor | Micro Canal | MIRF.00613014/SSS | 6 | 130 | 2pipe | 14 | 1170 |  |  | 1170 | 0.027857 | [7 empty] | 1 | D05 | MIRF0.00613014
Build-In Floor | Micro Canal | MIRF.00616514/SSS | 6 | 165 | 2pipe | 14 | 1560 |  |  | 1560 | 0.037143 | [7 empty] | 1 | D05 | MIRF0.00616514
Build-In Floor | Micro Canal | MIRF.00620014/SSS | 6 | 200 | 2pipe | 14 | 1950 |  |  | 1950 | 0.046429 | [7 empty] | 1 | D05 | MIRF0.00620014
Build-In Floor | Quatro Canal Hybrid | QUAF.01308027/BBN | 13 | 80 | 4pipe | 27 | 1140 | 780 | 735 | 1140 | 0.027143 | 70 | 307 | 230 | 198 | 307 | 0.014619 | 70 | 1 | D07 | QUAF0.01308027/BBN
Build-In Floor | Quatro Canal Hybrid | QUAF.01308027/BBV | 13 | 80 | 4pipe | 27 | 1140 | 780 | 735 | 1140 | 0.027143 | 70 | 307 | 230 | 198 | 307 | 0.014619 | 70 | 1 | D07 | QUAF0.01308027/BBV
Build-In Floor | Quatro Canal Hybrid | QUAF.01308027/BNA | 13 | 80 | 4pipe | 27 | 1140 | 780 | 735 | 1140 | 0.027143 | 70 | 307 | 230 | 198 | 307 | 0.014619 | 70 | 1 | D07 | QUAF0.01308027/BNA
Build-In Floor | Quatro Canal Hybrid | QUAF.01308027/BNC | 13 | 80 | 4pipe | 27 | 1140 | 780 | 735 | 1140 | 0.027143 | 70 | 307 | 230 | 198 | 307 | 0.014619 | 70 | 1 | D07 | QUAF0.01308027/BNC
Build-In Floor | Quatro Canal Hybrid | QUAF.01308027/BON | 13 | 80 | 4pipe | 27 | 1140 | 780 | 735 | 1140 | 0.027143 | 70 | 307 | 230 | 198 | 307 | 0.014619 | 70 | 1 | D07 | QUAF0.01308027/BON
Build-In Floor | Quatro Canal Hybrid | QUAF.01308027/BOV | 13 | 80 | 4pipe | 27 | 1140 | 780 | 735 | 1140 | 0.027143 | 70 | 307 | 230 | 198 | 307 | 0.014619 | 70 | 1 | D07 | QUAF0.01308027/BOV
Build-In Floor | Quatro Canal Hybrid | QUAF.01311027/BBN | 13 | 110 | 4pipe | 27 | 1840 | 1400 | 1187 | 1840 | 0.04381 | 142 | 544 | 400 | 350 | 544 | 0.025905 | 142 | 1 | D07 | QUAF0.01311027/BBN
Build-In Floor | Quatro Canal Hybrid | QUAF.01311027/BBV | 13 | 110 | 4pipe | 27 | 1840 | 1400 | 1187 | 1840 | 0.04381 | 142 | 544 | 400 | 350 | 544 | 0.025905 | 142 | 1 | D07 | QUAF0.01311027/BBV
Build-In Floor | Quatro Canal Hybrid | QUAF.01311027/BNA | 13 | 110 | 4pipe | 27 | 1840 | 1400 | 1187 | 1840 | 0.04381 | 142 | 544 | 400 | 350 | 544 | 0.025905 | 142 | 1 | D07 | QUAF0.01311027/BNA
Build-In Floor | Quatro Canal Hybrid | QUAF.01311027/BNC | 13 | 110 | 4pipe | 27 | 1840 | 1400 | 1187 | 1840 | 0.04381 | 142 | 544 | 400 | 350 | 544 | 0.025905 | 142 | 1 | D07 | QUAF0.01311027/BNC
Build-In Floor | Quatro Canal Hybrid | QUAF.01311027/BON | 13 | 110 | 4pipe | 27 | 1840 | 1400 | 1187 | 1840 | 0.04381 | 142 | 544 | 400 | 350 | 544 | 0.025905 | 142 | 1 | D07 | QUAF0.01311027/BON
Build-In Floor | Quatro Canal Hybrid | QUAF.01311027/BOV | 13 | 110 | 4pipe | 27 | 1840 | 1400 | 1187 | 1840 | 0.04381 | 142 | 544 | 400 | 350 | 544 | 0.025905 | 142 | 1 | D07 | QUAF0.01311027/BOV
Build-In Floor | Quatro Canal Hybrid | QUAF.01316027/BBN | 13 | 160 | 4pipe | 27 | 2880 | 2150 | 1858 | 2880 | 0.068571 | 213 | 851 | 625 | 548 | 851 | 0.040524 | 213 | 1 | D07 | QUAF0.01316027/BBN
Build-In Floor | Quatro Canal Hybrid | QUAF.01316027/BBV | 13 | 160 | 4pipe | 27 | 2880 | 2150 | 1858 | 2880 | 0.068571 | 213 | 851 | 625 | 548 | 851 | 0.040524 | 213 | 1 | D07 | QUAF0.01316027/BBV
Build-In Floor | Quatro Canal Hybrid | QUAF.01316027/BNA | 13 | 160 | 4pipe | 27 | 2880 | 2150 | 1858 | 2880 | 0.068571 | 213 | 851 | 625 | 548 | 851 | 0.040524 | 213 | 1 | D07 | QUAF0.01316027/BNA
Build-In Floor | Quatro Canal Hybrid | QUAF.01316027/BNC | 13 | 160 | 4pipe | 27 | 2880 | 2150 | 1858 | 2880 | 0.068571 | 213 | 851 | 625 | 548 | 851 | 0.040524 | 213 | 1 | D07 | QUAF0.01316027/BNC
Build-In Floor | Quatro Canal Hybrid | QUAF.01316027/BON | 13 | 160 | 4pipe | 27 | 2880 | 2150 | 1858 | 2880 | 0.068571 | 213 | 851 | 625 | 548 | 851 | 0.040524 | 213 | 1 | D07 | QUAF0.01316027/BON
Build-In Floor | Quatro Canal Hybrid | QUAF.01316027/BOV | 13 | 160 | 4pipe | 27 | 2880 | 2150 | 1858 | 2880 | 0.068571 | 213 | 851 | 625 | 548 | 851 | 0.040524 | 213 | 1 | D07 | QUAF0.01316027/BOV
Build-In Floor | Quatro Canal Hybrid | QUAF.01318027/BBN | 13 | 180 | 4pipe | 27 | 3578 | 2600 | 2308 | 3578 | 0.08519 | 284 | 1088 | 805 | 700 | 1088 | 0.05181 | 284 | 1 | D07 | QUAF0.01318027/BBN
Build-In Floor | Quatro Canal Hybrid | QUAF.01318027/BBV | 13 | 180 | 4pipe | 27 | 3578 | 2600 | 2308 | 3578 | 0.08519 | 284 | 1088 | 805 | 700 | 1088 | 0.05181 | 284 | 1 | D07 | QUAF0.01318027/BBV
Build-In Floor | Quatro Canal Hybrid | QUAF.01318027/BNA | 13 | 180 | 4pipe | 27 | 3578 | 2600 | 2308 | 3578 | 0.08519 | 284 | 1088 | 805 | 700 | 1088 | 0.05181 | 284 | 1 | D07 | QUAF0.01318027/BNA
Build-In Floor | Quatro Canal Hybrid | QUAF.01318027/BNC | 13 | 180 | 4pipe | 27 | 3578 | 2600 | 2308 | 3578 | 0.08519 | 284 | 1088 | 805 | 700 | 1088 | 0.05181 | 284 | 1 | D07 | QUAF0.01318027/BNC
Build-In Floor | Quatro Canal Hybrid | QUAF.01318027/BON | 13 | 180 | 4pipe | 27 | 3578 | 2600 | 2308 | 3578 | 0.08519 | 284 | 1088 | 805 | 700 | 1088 | 0.05181 | 284 | 1 | D07 | QUAF0.01318027/BON
Build-In Floor | Quatro Canal Hybrid | QUAF.01318027/BOV | 13 | 180 | 4pipe | 27 | 3578 | 2600 | 2308 | 3578 | 0.08519 | 284 | 1088 | 805 | 700 | 1088 | 0.05181 | 284 | 1 | D07 | QUAF0.01318027/BOV
Vertical Wall | Vertiga Glow | VERW.20004108/GLO/02 | 200 | 41 | 2pipe | 13 | 1620 | 1448 | 1315 | 1620 | 0.038571 | [7 empty] | 1 | B12 | VERW0.20004108/GLO/02
Vertical Wall | Vertiga Primo | VERW.20004108/PRI/02 | 200 | 41 | 2pipe | 13 | 1620 | 1448 | 1315 | 1620 | 0.038571 | [7 empty] | 1 | B12 | VERW0.20004108/PRI/02
Vertical Wall | Vertiga Glow | VERW.20005208/GLO/02 | 200 | 52 | 2pipe | 13 | 2289 | 1632 | 1427 | 2289 | 0.0545 | [7 empty] | 1 | B12 | VERW0.20005208/GLO/02
Vertical Wall | Vertiga Primo | VERW.20005208/PRI/02 | 200 | 52 | 2pipe | 13 | 2289 | 1632 | 1427 | 2289 | 0.0545 | [7 empty] | 1 | B12 | VERW0.20005208/PRI/02
Vertical Wall | Vertiga Glow | VERW.20005312/GLO/02 | 200 | 53 | 2pipe | 13 | 2925 | 2868 | 2800 | 2925 | 0.069643 | [7 empty] | 1 | B12 | VERW0.20005312/GLO/02
Vertical Wall | Vertiga Primo | VERW.20005312/PRI/02 | 200 | 53 | 2pipe | 13 | 2925 | 2868 | 2800 | 2925 | 0.069643 | [7 empty] | 1 | B12 | VERW0.20005312/PRI/02
Vertical Wall | Vertiga Glow | VERW.20006508/GLO/02 | 200 | 65 | 2pipe | 13 | 3042 | 1870 | 1640 | 3042 | 0.072429 | [7 empty] | 1 | B12 | VERW0.20006508/GLO/02
Vertical Wall | Vertiga Primo | VERW.20006508/PRI/02 | 200 | 65 | 2pipe | 13 | 3042 | 1870 | 1640 | 3042 | 0.072429 | [7 empty] | 1 | B12 | VERW0.20006508/PRI/02
Vertical Wall | Vertiga Glow | VERW.20007012/GLO/02 | 200 | 70 | 2pipe | 13 | 4536 | 4170 | 3416 | 4536 | 0.108 | [7 empty] | 1 | B12 | VERW0.20007012/GLO/02
Vertical Wall | Vertiga Primo | VERW.20007012/PRI/02 | 200 | 70 | 2pipe | 13 | 4536 | 4170 | 3416 | 4536 | 0.108 | [7 empty] | 1 | B12 | VERW0.20007012/PRI/02
Vertical Wall | Vertiga Glow | VERW.20009012/GLO/02 | 200 | 90 | 2pipe | 13 | 5605 | 4761 | 3461 | 5605 | 0.13345 | [7 empty] | 1 | B12 | VERW0.20009012/GLO/02
Vertical Wall | Vertiga Primo | VERW.20009012/PRI/02 | 200 | 90 | 2pipe | 13 | 5605 | 4761 | 3461 | 5605 | 0.13345 | [7 empty] | 1 | B12 | VERW0.20009012/PRI/02
Selectionmodel 2015-07
Metric

## Pressure Drop Curves
Jaga Briza
Jaga Clima Canal
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector
Jaga LowH2O Convector